## WaterClockReadings DB
| Rainwater inlet meter in cupboard | Rainwater meter on pipe to tank | Mains backup meter on pipe to tank
| m3 | m3 | m3
2004-04-01 |  | 0 | 0
2010-04-01 | 0 |  |  | According to Devonshire Tour document
2012-07-01 | 1000 |  |  | According to Devonshire Tour document
2013-02-07 | 1273 |  |  | According to Devonshire Tour document
2013-09-01 | 1500 |  |  | According to Devonshire Tour document
2013-11-07 | 1538 |  |  | Photo
2014-07-07 | 1801 | 2149 | 2786 | Photos
2019-01-31 |  | 3141 | 6307 | Photos
Repair in Jan 2020 |  | 3141
Rainwater harvest from 01/04/2004 to 01/04/2010
m3 | 348
m3/year | 58
Rainwater harvest from 01/04/2010 to 07/07/2014 when the rainwater harvesting system was operational
m3 | 1801
m3/year | 423.7647
Rainwater harvest from 07/07/2014 to 31/01/2019
m3 | 992
m3/year | 220.4444
6656
416

## WaterClockReadings USB
| Mains supply on street boundary (Demeter) | Mains supply basement | Rainwater NGIF | Cat 5 1 NGIF | Cat 5 2 NGIF | Cat 5 USB | Potable USB
| m3 | m3 | m3 | m3 | m3 | m3 | m3
2021-04-19 | 10160 | 7584 | 781 | 699 | 111 | 3580 | 1439
[6 empty] | 2020-02-26 | 2020-02-26
Stopped on date of flooding incident
|  |  | Theoretical RWH | NGIF demand
|  |  | 1631.8223 | 1591 |  | 71.3289 | Cat as % total

## Rainfall Durham and RWHS pot
yyyy | mm | tmax | tmin | af | rain |  |  | DB roof area | USB roof area
|  | degC | degC | days | mm | Annual rainfall |  | m2 | m2
1880 | 1 | 4.2 | -1.4 | 22 | 13.5 | 693.35 | Median 2004-2019 | 800 | 821
1880 | 2 | 8.7 | 0.6 | 12 | 44.3
1880 | 3 | 9.2 | 1 | 12 | 32.5 |  |  | RWHS potential |  | Collection efficiency
1880 | 4 | 11.6 | 2.7 | 2 | 51.5 |  |  | m3/y | m3/y | 0.8
1880 | 5 | 14.1 | 3.7 | 4 | 38.1 |  |  | 443.744 | 455.3923
1880 | 6 | 17.7 | 7.7 | 0 | 66.5
1880 | 7 | 19.2 | 10.1 | 0 | 106 |  |  | 16 years | 43 months
1880 | 8 | 19.8 | 10.9 | 0 | 49.1 |  |  | m3 | m3
1880 | 9 | 18.9 | 8.9 | 0 | 128.6 |  |  | 7099.904 | 1631.8223
1880 | 10 | 10.1 | 2.9 | 7 | 150
1880 | 11 | 8.2 | 0.1 | 15 | 56.7 |  |  | Actual versus theoretical
1880 | 12 | 6.3 | 0.4 | 15 | 70.2 |  |  | 44.24 | 47.8606
1881 | 1 | 1.5 | -5.7 | 24 | 22.3
1881 | 2 | 4.1 | -1.2 | 18 | 70.4
1881 | 3 | 7.8 | -0.6 | 18 | 56.2
1881 | 4 | 9.7 | 1.1 | 13 | 24.9
1881 | 5 | 15.9 | 4.6 | 1 | 31.7
1881 | 6 | 18.4 | 7.3 | 0 | 54.8
1881 | 7 | 20.9 | 10.6 | 0 | 78.5
1881 | 8 | 17.7 | 9.1 | 0 | 97.9
1881 | 9 | 15.3 | 8.4 | 0 | 81.5
1881 | 10 | 10.3 | 3.6 | 6 | 90.9
1881 | 11 | 10.5 | 4.5 | 2 | 44.4
1881 | 12 | 5.9 | 0.7 | 10 | 57.9
1882 | 1 | 7.3 | 2 | 3 | 18.4
1882 | 2 | 8.9 | 2.2 | 4 | 23.3
1882 | 3 | 11.1 | 2.2 | 7 | 37.6
1882 | 4 | 10.2 | 2.9 | 4 | 91.4
1882 | 5 | 15.6 | 4.4 | 2 | 57.7
1882 | 6 | 17.6 | 7.8 | 0 | 84.5
1882 | 7 | 20.2 | 10.2 | 0 | 90.6
1882 | 8 | 19.9 | 9.8 | 0 | 73.3
1882 | 9 | 15.8 | 6.8 | 0 | 53.4
1882 | 10 | 12.3 | 6.3 | 1 | 121.8
1882 | 11 | 7.3 | 1.8 | 5 | 84
1882 | 12 | 3.8 | -0.4 | 16 | 114.2
1883 | 1 | 5.5 | 0.7 | 10 | 47.9
1883 | 2 | 8.1 | 1.5 | 4 | 42.4
1883 | 3 | 5.5 | -2.3 | 25 | 47.7
1883 | 4 | 12.2 | 1.8 | 8 | 40.5
1883 | 5 | 14.3 | 4.1 | 0 | 46.1
1883 | 6 | 17.5 | 7.9 | 0 | 62.3
1883 | 7 | 19.2 | 9.2 | 0 | 94.7
1883 | 8 | 20.3 | 9.4 | 0 | 30.4
1883 | 9 | 16 | 8.9 | 0 | 104.5
1883 | 10 | 12.5 | 4.7 | 1 | 60
1883 | 11 | 8.3 | 2.4 | 5 | 23.7
1883 | 12 | --- | --- | --- | 37.1
1884 | 1 | 8.2 | 2.6 | 6 | 80.6
1884 | 2 | 7.2 | 1.1 | 8 | 32.4
1884 | 3 | 9.4 | 1.7 | 4 | 64.4
1884 | 4 | 10.5 | 2 | 5 | 51.9
1884 | 5 | 15.6 | 4.4 | 0 | 17
1884 | 6 | 18.6 | 7.3 | 0 | 25.8
1884 | 7 | 20.9 | 9.8 | 0 | 98.8
1884 | 8 | 22 | 9.6 | 0 | 18.6
1884 | 9 | 17.7 | 8.5 | 0 | 35.4
1884 | 10 | 12.8 | 4.4 | 2 | 38.2
1884 | 11 | 8.4 | 1.9 | 6 | 46.8
1884 | 12 | 5.9 | 0.8 | 13 | 32.3
1885 | 1 | 4.2 | 0.1 | 17 | 50.1
1885 | 2 | 7.6 | 1.1 | 11 | 22.7
1885 | 3 | 7.5 | -0.1 | 19 | 56.9
1885 | 4 | 11.4 | 2.4 | 7 | 38.7
1885 | 5 | 12.2 | 3.1 | 5 | 98.1
1885 | 6 | 17.8 | 7.6 | 0 | 43
1885 | 7 | 21.4 | 9.7 | 0 | 32.9
1885 | 8 | 16.5 | 8.7 | 0 | 69.5
1885 | 9 | 16.2 | 6.2 | 0 | 61.3
1885 | 10 | 9.8 | 3.7 | 1 | 115.2
1885 | 11 | 7.9 | 2.4 | 5 | 48.2
1885 | 12 | 6.3 | -0.1 | 13 | 14.3
1886 | 1 | 3.8 | -1.4 | 21 | 96.4
1886 | 2 | 4 | -1.8 | 22 | 23.1
1886 | 3 | 6.5 | -0.1 | 18 | 62.8
1886 | 4 | 10 | 2.4 | 2 | 38.4
1886 | 5 | 12.9 | 4.7 | 1 | 67
1886 | 6 | 17.5 | 7.7 | 0 | 23.7
1886 | 7 | 20.8 | 10.3 | 0 | 129.2
1886 | 8 | 19.9 | 10.3 | 0 | 23.5
1886 | 9 | 16.4 | 8.6 | 0 | 38.5
1886 | 10 | 12.9 | 7.3 | 0 | 128.4
1886 | 11 | 9.2 | 2.5 | 3 | 90.8
1886 | 12 | 3.7 | -1.4 | 18 | 90.3
1887 | 1 | 4.4 | -1.1 | 18 | 37.1
1887 | 2 | 7.4 | 0.1 | 14 | 13.6
1887 | 3 | 7.7 | -0.5 | 16 | 52.8
1887 | 4 | 10.4 | 0.9 | 12 | 19.6
1887 | 5 | 12.4 | 4.3 | 2 | 51.8
1887 | 6 | 20.3 | 9.1 | 0 | 6.4
1887 | 7 | 23 | 11.2 | 0 | 20.7
1887 | 8 | 20.4 | 9.1 | 0 | 38.1
1887 | 9 | 15 | 6.9 | 1 | 114.6
1887 | 10 | 10.3 | 3.3 | 7 | 58.2
1887 | 11 | 6.6 | 1.5 | 9 | 75.9
1887 | 12 | 4.7 | -0.1 | 20 | 58.3
1888 | 1 | 6 | 0.3 | 13 | 18.6
1888 | 2 | 4.2 | -0.4 | 20 | 31.8
1888 | 3 | 4.9 | -0.3 | 23 | 103.4
1888 | 4 | 9.3 | 1.8 | 10 | 61.8
1888 | 5 | 15 | 4.6 | 2 | 13.3
1888 | 6 | 15.1 | 7 | 0 | 40.7
1888 | 7 | 16.7 | 8.6 | 0 | 209.7
1888 | 8 | 17.6 | 9 | 0 | 43.5
1888 | 9 | 15.4 | 6.7 | 0 | 32.8
1888 | 10 | 12.1 | 4.1 | 6 | 17.2
1888 | 11 | 9.1 | 4.4 | 0 | 104
1888 | 12 | 6.9 | 1.3 | 13 | 18.6
1889 | 1 | 6.4 | 0.6 | 12 | 20.7
1889 | 2 | 5.6 | -0.5 | 19 | 26
1889 | 3 | 8 | 0.3 | 13 | 57.5
1889 | 4 | 9.7 | 2.6 | 1 | 54.5
1889 | 5 | 17 | 7 | 0 | 38
1889 | 6 | 20 | 9 | 0 | 9.5
1889 | 7 | 19.4 | 9.5 | 0 | 68.1
1889 | 8 | 18.3 | 10.4 | 0 | 81.9
1889 | 9 | 15.8 | 7.8 | 0 | 21.5
1889 | 10 | 11.2 | 5.2 | 0 | 94
1889 | 11 | 8.8 | 2.6 | 8 | 23
1889 | 12 | 5.7 | -0.2 | 15 | 30.1
1890 | 1 | 8 | 1.9 | 8 | 52.5
1890 | 2 | 5.8 | 0.3 | 14 | 33.5
1890 | 3 | 9.8 | 2.5 | 8 | 51.4
1890 | 4 | 10.6 | 1.4 | 11 | 16.9
1890 | 5 | 15.2 | 6 | 0 | 59.1
1890 | 6 | 18.2 | 8.5 | 0 | 59.9
1890 | 7 | 18.7 | 9.6 | 0 | 45.3
1890 | 8 | 18.4 | 9.4 | 0 | 126.5
1890 | 9 | 19.8 | 10.3 | 0 | 46.3
1890 | 10 | 13.2 | 6 | 2 | 37.5
1890 | 11 | 8.5 | 1.1 | 9 | 85.6
1890 | 12 | 2.7 | -1.4 | 19 | 44.1
1891 | 1 | 4.6 | -1.7 | 19 | 25.7
1891 | 2 | 9.3 | 0 | 14 | 2.1
1891 | 3 | 6.7 | -0.1 | 13 | 69
1891 | 4 | 8.9 | 1.2 | 7 | 41.9
1891 | 5 | 13.2 | 3.6 | 4 | 36.9
1891 | 6 | 18.1 | 8.9 | 0 | 4.1
1891 | 7 | 19.5 | 10.6 | 0 | 106.6
1891 | 8 | 17.9 | 10 | 0 | 126.7
1891 | 9 | 17.6 | 9.1 | 0 | 47.4
1891 | 10 | 12.3 | 4.9 | 3 | 48.9
1891 | 11 | 7.5 | 2.2 | 8 | 56.9
1891 | 12 | 5.6 | -0.5 | 12 | 57.5
1892 | 1 | 4.4 | -1.4 | 19 | 48.6
1892 | 2 | 5.6 | -0.6 | 12 | 49.2
1892 | 3 | 6.6 | -1.9 | 25 | 28.9
1892 | 4 | 11.4 | 1 | 12 | 33.3
1892 | 5 | 15.2 | 5.4 | 2 | 59.5
1892 | 6 | 17.2 | 7.4 | 0 | 80.2
1892 | 7 | 17.3 | 9.2 | 0 | 42.9
1892 | 8 | 18.5 | 9.9 | 0 | 99.7
1892 | 9 | 15.3 | 7.5 | 0 | 74.2
1892 | 10 | 9.7 | 2.9 | 6 | 141.7
1892 | 11 | 8.5 | 2.6 | 5 | 31.5
1892 | 12 | 3.8 | -1.9 | 22 | 24.4
1893 | 1 | 4.7 | -0.4 | 10 | 33.5
1893 | 2 | 6.4 | 0.5 | 11 | 54
1893 | 3 | 12.1 | 1.7 | 11 | 11.1
1893 | 4 | 13.9 | 2.5 | 2 | 9.4
1893 | 5 | 16.8 | 6.3 | 0 | 59
1893 | 6 | 19.5 | 9.5 | 0 | 20.7
1893 | 7 | 20 | 10.2 | 0 | 114.1
1893 | 8 | 22.1 | 11.6 | 0 | 54.1
1893 | 9 | 16.6 | 7.4 | 0 | 45.1
1893 | 10 | 13.7 | 4.9 | 3 | 18.1
1893 | 11 | 8.3 | 1.7 | 9 | 60.1
1893 | 12 | 7.6 | 1.5 | 7 | 32.9
1894 | 1 | 5.2 | -0.6 | 13 | 27.3
1894 | 2 | 7.5 | 0.1 | 11 | 52.1
1894 | 3 | 11.5 | 0.7 | 11 | 22.9
1894 | 4 | 13 | 3.3 | 3 | 28
1894 | 5 | 11.9 | 3.4 | 5 | 72.3
1894 | 6 | 16.9 | 7.7 | 0 | 94.1
1894 | 7 | 20.7 | 10.9 | 0 | 40.4
1894 | 8 | 18 | 9.3 | 0 | 64
1894 | 9 | 14.5 | 6.9 | 0 | 22.1
1894 | 10 | 11.3 | 4.3 | 3 | 128.9
1894 | 11 | 10 | 4.5 | 0 | 19.8
1894 | 12 | 7 | 0.8 | 15 | 32.7
1895 | 1 | 1.7 | -3.7 | 26 | 94.6
1895 | 2 | 2.1 | -4.8 | 23 | 34
1895 | 3 | 8.2 | 0.8 | 11 | 48.9
1895 | 4 | 12 | 3.1 | 7 | 33.8
1895 | 5 | 16.5 | 5.5 | 0 | 21
1895 | 6 | 19.6 | 7.4 | 0 | 32.5
1895 | 7 | 19.2 | 9.8 | 0 | 126.1
1895 | 8 | 20.1 | 10.9 | 0 | 59
1895 | 9 | 20.5 | 9.4 | 0 | 15.1
1895 | 10 | 10.5 | 2.4 | 10 | 125.4
1895 | 11 | 9.6 | 3.2 | 5 | 62.7
1895 | 12 | 5.4 | 0.2 | 14 | 47.1
1896 | 1 | 7.2 | 1.5 | 11 | 17.9
1896 | 2 | 7.6 | 1.1 | 11 | 12.8
1896 | 3 | 10.1 | 1.6 | 9 | 46.7
1896 | 4 | 13.5 | 3.8 | 1 | 20.6
1896 | 5 | 16.4 | 5.2 | 1 | 13.6
1896 | 6 | 20.9 | 9.8 | 0 | 50.8
1896 | 7 | 21 | 10.1 | 0 | 64.1
1896 | 8 | 17.7 | 9.7 | 0 | 53.3
1896 | 9 | 15.6 | 8.5 | 0 | 56.7
1896 | 10 | 9.4 | 2.7 | 6 | 148.8
1896 | 11 | 7.5 | 1.5 | 11 | 34.1
1896 | 12 | 5.6 | 0.7 | 14 | 103.9
1897 | 1 | 3.3 | -1.2 | 19 | 47.2
1897 | 2 | 7.5 | 1.7 | 11 | 24
1897 | 3 | 8.7 | 1.9 | 9 | 61.6
1897 | 4 | 9.9 | 1.7 | 8 | 42.2
1897 | 5 | 12.9 | 3.8 | 2 | 37.1
1897 | 6 | 17.9 | 9 | 0 | 74.7
1897 | 7 | 20.8 | 10.2 | 0 | 31.3
1897 | 8 | 21.4 | 10.8 | 0 | 60.7
1897 | 9 | 15.6 | 6.6 | 0 | 54.4
1897 | 10 | 13.3 | 5.6 | 2 | 36.1
1897 | 11 | 9.7 | 4.2 | 4 | 44.5
1897 | 12 | 6.9 | 0.9 | 11 | 40.4
1898 | 1 | 9.3 | 3 | 6 | 25.4
1898 | 2 | 7.5 | 0.3 | 13 | 19.1
1898 | 3 | 8 | 0.1 | 17 | 49.7
1898 | 4 | 12.1 | 3.3 | 2 | 51.8
1898 | 5 | 12.9 | 4.1 | 1 | 41.4
1898 | 6 | 17.6 | 7.9 | 0 | 38.8
1898 | 7 | 20 | 8.9 | 0 | 16.4
1898 | 8 | 20.5 | 10.4 | 0 | 45.5
1898 | 9 | 19.3 | 9.8 | 0 | 8.1
1898 | 10 | 14.2 | 7.5 | 0 | 123.6
1898 | 11 | 9.4 | 2.9 | 6 | 77.5
1898 | 12 | 9.6 | 2.9 | 5 | 30.5
1899 | 1 | 6.3 | 0.6 | 10 | 56
1899 | 2 | 7.3 | -0.5 | 17 | 33.6
1899 | 3 | 9.2 | 0.2 | 16 | 31.5
1899 | 4 | 11.3 | 2.6 | 5 | 55.3
1899 | 5 | 12.4 | 4.2 | 1 | 80.3
1899 | 6 | 20.5 | 8.2 | 0 | 34.3
1899 | 7 | 21.5 | 11.7 | 0 | 77
1899 | 8 | 21.3 | 11 | 0 | 29
1899 | 9 | 17.3 | 8.1 | 1 | 61.5
1899 | 10 | 13 | 3.8 | 3 | 48.8
1899 | 11 | 11.5 | 4.3 | 5 | 39.7
1899 | 12 | 3.6 | -1.7 | 18 | 63.7
1900 | 1 | 5.7 | 0.4 | 16 | 47.3
1900 | 2 | 3.6 | -2.3 | 19 | 93.8
1900 | 3 | 5.7 | -0.1 | 12 | 35.7
1900 | 4 | 12.4 | 2.7 | 6 | 24.3
1900 | 5 | 13.2 | 5 | 1 | 30.3
1900 | 6 | 18.1 | 8.8 | 0 | 79.9
1900 | 7 | 21.1 | 12.3 | 0 | 28.5
1900 | 8 | 17.6 | 9.9 | 0 | 130.3
1900 | 9 | 17.3 | 8.4 | 0 | 17.2
1900 | 10 | 12.4 | 4.6 | 2 | 137.7
1900 | 11 | 8.6 | 3.9 | 4 | 60.8
1900 | 12 | 8.9 | 4 | 4 | 46.3
1901 | 1 | 5 | -0.4 | 17 | 27.2
1901 | 2 | 4.5 | -0.5 | 17 | 28.9
1901 | 3 | 7 | 0.4 | 11 | 35.4
1901 | 4 | 12.4 | 2.6 | 5 | 24.6
1901 | 5 | 14.7 | 5 | 1 | 42.2
1901 | 6 | 17.8 | 7.6 | 0 | 31.1
1901 | 7 | 22.4 | 12 | 0 | 65
1901 | 8 | 20.2 | 10.5 | 0 | 56.6
1901 | 9 | 16.5 | 9.4 | 0 | 35
1901 | 10 | 12.4 | 4.5 | 3 | 60.2
1901 | 11 | 8.3 | 2 | 10 | 129.9
1901 | 12 | 5 | 0.2 | 15 | 48.1
1902 | 1 | 6.6 | 1.4 | 14 | 13.3
1902 | 2 | 3.3 | -2.1 | 16 | 26.4
1902 | 3 | 9.5 | 1.7 | 5 | 14.1
1902 | 4 | 10.8 | 2 | 6 | 37.3
1902 | 5 | 11 | 3.7 | 3 | 57.9
1902 | 6 | 15.6 | 7.5 | 0 | 50.1
1902 | 7 | 17.6 | 9 | 0 | 69.9
1902 | 8 | 16.4 | 8.4 | 0 | 45.1
1902 | 9 | 15.9 | 8.2 | 0 | 23.1
1902 | 10 | 11.8 | 5.9 | 0 | 53.2
1902 | 11 | 8.9 | 3.9 | 5 | 28.3
1902 | 12 | 6.9 | 2 | 12 | 52.1
1903 | 1 | 5.3 | -0.2 | 13 | 57.9
1903 | 2 | 9 | 2.9 | 6 | 26.7
1903 | 3 | 9.3 | 2.2 | 5 | 30.6
1903 | 4 | 9.2 | 0.6 | 13 | 35.2
1903 | 5 | 12.8 | 5.1 | 1 | 68.6
1903 | 6 | 15.4 | 7.2 | 0 | 60.8
1903 | 7 | 18 | 10.1 | 0 | 122.8
1903 | 8 | 17.2 | 9.1 | 0 | 42
1903 | 9 | 15.4 | 7.9 | 0 | 59.5
1903 | 10 | 11.9 | 6.1 | 0 | 201.8
1903 | 11 | 8.4 | 2.2 | 8 | 52.1
1903 | 12 | 4.4 | 0.3 | 11 | 25.6
1904 | 1 | 6 | 0.9 | 13 | 44.8
1904 | 2 | 4.7 | -0.1 | 15 | 42
1904 | 3 | 6.6 | 0.4 | 13 | 31.2
1904 | 4 | 12.1 | 4 | 0 | 25.6
1904 | 5 | 13.3 | 5.4 | 1 | 74.9
1904 | 6 | 16.5 | 8.4 | 0 | 33.1
1904 | 7 | 19.5 | 11 | 0 | 43.3
1904 | 8 | 18.4 | 9.9 | 0 | 63.1
1904 | 9 | 16.2 | 7.4 | 0 | 25
1904 | 10 | 12.7 | 4.9 | 4 | 18.5
1904 | 11 | 8.3 | 2.1 | 9 | 45.6
1904 | 12 | 5.8 | -0.2 | 16 | 35.2
1905 | 1 | 6.6 | 1.2 | 13 | 9.1
1905 | 2 | 7.4 | 1.4 | 9 | 18.3
1905 | 3 | 10.2 | 2.2 | 4 | 30.8
1905 | 4 | 9.7 | 2.2 | 5 | 72.5
1905 | 5 | 13.8 | 5 | 2 | 8.1
1905 | 6 | 17.9 | 8.8 | 0 | 17.5
1905 | 7 | 21.7 | 11.4 | 0 | 19.1
1905 | 8 | 17.6 | 9.9 | 0 | 69.3
1905 | 9 | 15.4 | 8.1 | 0 | 56.4
1905 | 10 | 10.4 | 3.2 | 4 | 56.8
1905 | 11 | 7.1 | 1.9 | 9 | 116.8
1905 | 12 | 7.5 | 2.8 | 1 | 13.1
1906 | 1 | 6.9 | 2.1 | 4 | 57.7
1906 | 2 | 5.4 | -0.9 | 17 | 27
1906 | 3 | 7.6 | 0.8 | 12 | 34.2
1906 | 4 | 11.6 | 0.2 | 15 | 22.1
1906 | 5 | 12.6 | 5.6 | 3 | 94.6
1906 | 6 | 18.1 | 8.8 | 0 | 21.1
1906 | 7 | 19.7 | 9.7 | 0 | 35.1
1906 | 8 | 20.1 | 11.1 | 0 | 64.9
1906 | 9 | 17.5 | 8 | 0 | 11.7
1906 | 10 | 12.8 | 6.5 | 0 | 113.4
1906 | 11 | 9.7 | 4.6 | 3 | 72.3
1906 | 12 | 5.1 | -0.1 | 19 | 50.3
1907 | 1 | 5.8 | 0.5 | 14 | 13.8
1907 | 2 | 5.9 | -0.7 | 17 | 26.4
1907 | 3 | 10.6 | 0.6 | 10 | 21.6
1907 | 4 | 10.7 | 2.9 | 4 | 51.4
1907 | 5 | 12.1 | 5.2 | 0 | 94.6
1907 | 6 | 15.2 | 7.7 | 0 | 77
1907 | 7 | 16.9 | 8.7 | 0 | 39.7
1907 | 8 | 17.3 | 9.2 | 0 | 38
1907 | 9 | 17.4 | 7.2 | 1 | 6.3
1907 | 10 | 12.5 | 5.6 | 2 | 142
1907 | 11 | 8.5 | 2.5 | 8 | 48.2
1907 | 12 | 6.4 | 1.2 | 8 | 72.6
1908 | 1 | 5.1 | -0.7 | 18 | 27.3
1908 | 2 | 8.1 | 1.4 | 8 | 27.7
1908 | 3 | 6.5 | 0.3 | 13 | 74.5
1908 | 4 | 8.4 | 1.6 | 8 | 70.7
1908 | 5 | 15.6 | 6.9 | 0 | 45.4
1908 | 6 | 17.5 | 7.9 | 0 | 11.8
1908 | 7 | 19 | 10.2 | 0 | 63.7
1908 | 8 | 17.4 | 9.2 | 0 | 51.7
1908 | 9 | 16.3 | 9 | 0 | 42
1908 | 10 | 15.1 | 7.7 | 0 | 33.8
1908 | 11 | 9.4 | 2.7 | 6 | 27.4
1908 | 12 | 5.3 | -0.1 | 13 | 17.1
1909 | 1 | 5.6 | -0.3 | 17 | 15.1
1909 | 2 | 5.6 | -0.6 | 18 | 35.3
1909 | 3 | 5.6 | -0.2 | 14 | 108.1
1909 | 4 | 13.1 | 2.6 | 5 | 56.8
1909 | 5 | 14.7 | 4.5 | 4 | 33.5
1909 | 6 | 15.2 | 6.6 | 0 | 48.4
1909 | 7 | 18 | 10 | 0 | 55.7
1909 | 8 | 19.2 | 10.3 | 0 | 74.5
1909 | 9 | 14.1 | 7.3 | 0 | 50.4
1909 | 10 | 12.5 | 5.5 | 4 | 53.3
1909 | 11 | 7.6 | 1.4 | 12 | 19.3
1909 | 12 | 5.3 | 0.4 | 13 | 79.4
1910 | 1 | 5.5 | -0.3 | 15 | 55
1910 | 2 | 6.3 | 0.7 | 12 | 53
1910 | 3 | 9.6 | 2 | 6 | 16
1910 | 4 | 10 | 2 | 4 | 61.1
1910 | 5 | 13.3 | 5.1 | 2 | 42.1
1910 | 6 | 17.8 | 8.5 | 0 | 60.8
1910 | 7 | 17 | 9.5 | 0 | 73.4
1910 | 8 | 18.4 | 10.7 | 0 | 62.2
1910 | 9 | 15.6 | 7.3 | 0 | 9.5
1910 | 10 | 13 | 7.1 | 0 | 73.8
1910 | 11 | 5.4 | -0.4 | 16 | 75.7
1910 | 12 | 7.9 | 3.1 | 2 | 48.7
1911 | 1 | 6.4 | 0.6 | 9 | 37.1
1911 | 2 | 7.4 | 1.1 | 11 | 21.1
1911 | 3 | 6.5 | 1.5 | 4 | 43.8
1911 | 4 | 9.9 | 3.4 | 6 | 27.6
1911 | 5 | 16 | 6.8 | 0 | 17.7
1911 | 6 | 18.2 | 7.7 | 0 | 90.7
1911 | 7 | 22.2 | 10.3 | 0 | 16.4
1911 | 8 | 20.6 | 11.7 | 0 | 50.5
1911 | 9 | 17.4 | 7.5 | 0 | 41.2
1911 | 10 | 11.2 | 5 | 4 | 61.9
1911 | 11 | 8 | 2.5 | 7 | 89.9
1911 | 12 | 7.5 | 2.3 | 4 | 86.5
1912 | 1 | 4.9 | -0.2 | 14 | 79
1912 | 2 | 6.5 | 1 | 8 | 49.2
1912 | 3 | 9.4 | 3.1 | 4 | 49
1912 | 4 | 12.5 | 2.5 | 5 | 2.4
1912 | 5 | 14.5 | 5.7 | 1 | 57.5
1912 | 6 | 16.1 | 8.8 | 0 | 111.7
1912 | 7 | 17.2 | 10.4 | 0 | 89.5
1912 | 8 | 15.4 | 8.1 | 0 | 105.9
1912 | 9 | 13.9 | 6.5 | 0 | 42.6
1912 | 10 | 11.6 | 3.8 | 4 | 65.3
1912 | 11 | 8.4 | 2.7 | 8 | 50.5
1912 | 12 | 8.1 | 1.8 | 4 | 38.2
1913 | 1 | 4.8 | 0.1 | 14 | 64.3
1913 | 2 | 7.3 | 0.8 | 11 | 16.7
1913 | 3 | 8.1 | 1.2 | 7 | 56
1913 | 4 | 10.1 | 3.4 | 2 | 101.6
1913 | 5 | 13.7 | 5.9 | 1 | 63.6
1913 | 6 | 17.6 | 8.5 | 0 | 25.4
1913 | 7 | 17.2 | 9.5 | 0 | 22.5
1913 | 8 | 18.9 | 9.1 | 0 | 46.8
1913 | 9 | 16.9 | 9.4 | 0 | 71.1
1913 | 10 | 12.6 | 6.5 | 3 | 67.4
1913 | 11 | 10.4 | 4.3 | 3 | 30.1
1913 | 12 | 6.7 | 1.6 | 9 | 28.8
1914 | 1 | 6.1 | 0.7 | 12 | 36.2
1914 | 2 | 9.1 | 3 | 2 | 33.2
1914 | 3 | 8.4 | 1.6 | 7 | 34.6
1914 | 4 | 14.7 | 3.2 | 2 | 8.7
1914 | 5 | 14.1 | 4.9 | 3 | 35.7
1914 | 6 | 18.9 | 7.8 | 0 | 113.8
1914 | 7 | 19 | 10.3 | 0 | 66.9
1914 | 8 | 19.5 | 10 | 0 | 36.6
1914 | 9 | 17.4 | 7.2 | 2 | 41.7
1914 | 10 | 13 | 6.2 | 0 | 48.5
1914 | 11 | 9 | 3.1 | 6 | 87.4
1914 | 12 | 6 | 0.9 | 9 | 115.3
1915 | 1 | 5.6 | 0.8 | 10 | 52.9
1915 | 2 | 6.2 | 0.4 | 10 | 63.1
1915 | 3 | 8.4 | 0.8 | 11 | 52.4
1915 | 4 | 11.3 | 2.4 | 4 | 14.5
1915 | 5 | 12.8 | 3.8 | 3 | 55.5
1915 | 6 | 17.8 | 7.5 | 1 | 9.4
1915 | 7 | 18.4 | 9.6 | 0 | 90.1
1915 | 8 | 19 | 10 | 0 | 76.4
1915 | 9 | 16.5 | 7.2 | 0 | 39
1915 | 10 | 11.7 | 4.1 | 3 | 32.4
1915 | 11 | 5.7 | -0.3 | 16 | 40.1
1915 | 12 | 5.8 | 1.2 | 7 | 133.7
1916 | 1 | 9.8 | 3.7 | 2 | 16.1
1916 | 2 | 5.7 | -0.2 | 15 | 73.5
1916 | 3 | 4.5 | -0.3 | 17 | 90.5
1916 | 4 | 11.7 | 2.7 | 5 | 39.3
1916 | 5 | 14.5 | 5.3 | 0 | 61.4
1916 | 6 | 14.6 | 6.8 | 0 | 42
1916 | 7 | 19.5 | 10 | 0 | 59.2
1916 | 8 | 20 | 10.7 | 0 | 81.5
1916 | 9 | 16.3 | 7.6 | 0 | 36.5
1916 | 10 | 12.5 | 4.9 | 5 | 62.4
1916 | 11 | 9.5 | 3.8 | 4 | 65.8
1916 | 12 | 4.7 | -0.9 | 17 | 62.8
1917 | 1 | 3.3 | 0 | 20 | 80.4
1917 | 2 | 3.8 | -2 | 17 | 21.9
1917 | 3 | 5.9 | -1.4 | 23 | 52.5
1917 | 4 | 8.5 | 0.2 | 15 | 46.2
1917 | 5 | 15.2 | 5.5 | 1 | 76.6
1917 | 6 | 18.7 | 7.8 | 0 | 34.5
1917 | 7 | 20.2 | 9.9 | 0 | 26.1
1917 | 8 | 18.7 | 11 | 0 | 157
1917 | 9 | 17.3 | 8.9 | 0 | 24.6
1917 | 10 | 11.2 | 2.8 | 5 | 50.3
1917 | 11 | 10.5 | 4.6 | 2 | 22.7
1917 | 12 | 4.8 | -0.3 | 18 | 67.4
1918 | 1 | 5.8 | -0.3 | 14 | 50.7
1918 | 2 | 8.1 | 2.3 | 6 | 31.4
1918 | 3 | 8 | 1.3 | 4 | 31.5
1918 | 4 | 8.9 | 2.4 | 2 | 36.6
1918 | 5 | 16.9 | 6.3 | 1 | 35.2
1918 | 6 | 17.9 | 7 | 0 | 8.1
1918 | 7 | 19.7 | 9.7 | 0 | 86.1
1918 | 8 | 19.2 | 10.8 | 0 | 35.8
1918 | 9 | 14.2 | 6.4 | 0 | 116.8
1918 | 10 | 11.8 | 5.3 | 0 | 49.6
1918 | 11 | 8 | 0.8 | 14 | 29.4
1918 | 12 | 7.9 | 2.3 | 8 | 62.4
1919 | 1 | 3.9 | -0.5 | 14 | 69.4
1919 | 2 | 3.9 | -1.7 | 16 | 40.5
1919 | 3 | 5.8 | -1 | 17 | 73.1
1919 | 4 | 11.1 | 2.5 | 6 | 39.1
1919 | 5 | 16.8 | 5.6 | 1 | 20.9
1919 | 6 | 18.3 | 8 | 0 | 22.5
1919 | 7 | 17.4 | 8.4 | 0 | 48.5
1919 | 8 | 19.9 | 9.7 | 0 | 59.1
1919 | 9 | 17.2 | 7.2 | 1 | 19.7
1919 | 10 | 11.8 | 2.6 | 1 | 119.7
1919 | 11 | 5.4 | -0.5 | 13 | 91.6
1919 | 12 | 6.3 | 0.9 | 5 | 57.6
1920 | 1 | 6.9 | 0.9 | 9 | 65.1
1920 | 2 | 8.5 | 1.4 | 6 | 21.2
1920 | 3 | 9.8 | 2 | 7 | 69
1920 | 4 | 9.7 | 3.2 | 2 | 67.5
1920 | 5 | 14.7 | 6 | 1 | 84
1920 | 6 | 17.7 | 7.7 | 1 | 21.7
1920 | 7 | 17 | 9.6 | 0 | 108.2
1920 | 8 | 17.5 | 8 | 0 | 32.3
1920 | 9 | 16.9 | 7.3 | 0 | 26.7
1920 | 10 | 13 | 5.5 | 0 | 56
1920 | 11 | 9.2 | 3.7 | 4 | 21.1
1920 | 12 | 6.2 | 0.7 | 14 | 80.7
1921 | 1 | 8.7 | 2.3 | 3 | 77.4
1921 | 2 | 7.3 | 0.8 | 11 | 3.7
1921 | 3 | 10.1 | 2.1 | 6 | 18.4
1921 | 4 | 12.4 | 2.4 | 6 | 31.4
1921 | 5 | 15.8 | 4.6 | 1 | 45.8
1921 | 6 | 19 | 7.3 | 0 | 19.6
1921 | 7 | 21.2 | 10.5 | 0 | 37.4
1921 | 8 | 17.8 | 9.7 | 0 | 104.6
1921 | 9 | 17.7 | 8.1 | 0 | 16.7
1921 | 10 | 16.2 | 7.7 | 1 | 33
1921 | 11 | 6.8 | 0.5 | 11 | 63.3
1921 | 12 | 9.3 | 2.7 | 5 | 39
1922 | 1 | 4.1 | -1.5 | 19 | 80.7
1922 | 2 | 5.8 | -0.3 | 14 | 48.2
1922 | 3 | 6.8 | 0.5 | 8 | 39.5
1922 | 4 | 8.7 | -0.1 | 15 | 49.5
1922 | 5 | 16.2 | 6.4 | 1 | 13.5
1922 | 6 | 18 | 7.3 | 0 | 37.6
1922 | 7 | 17 | 8.1 | 0 | 115.2
1922 | 8 | 16.5 | 8.4 | 0 | 59.4
1922 | 9 | 14.1 | 6.8 | 0 | 95.8
1922 | 10 | 11.1 | 4.1 | 1 | 38
1922 | 11 | 9.1 | 2.1 | 8 | 18.9
1922 | 12 | 7.5 | 1.8 | 7 | 86.5
1923 | 1 | 8.6 | 2.5 | 5 | 25
1923 | 2 | 5.7 | 1.1 | 11 | 89.1
1923 | 3 | 8.5 | 1.8 | 5 | 39.8
1923 | 4 | 9 | 2.3 | 3 | 50.1
1923 | 5 | 11.6 | 3.4 | 1 | 63.9
1923 | 6 | 15.5 | 7.1 | 0 | 24.4
1923 | 7 | 20.7 | 11.3 | 0 | 39.2
1923 | 8 | 18.7 | 10.1 | 0 | 76
1923 | 9 | 15.5 | 7.3 | 0 | 34.9
1923 | 10 | 12.2 | 4.5 | 2 | 47.6
1923 | 11 | 5.8 | -0.1 | 13 | 83.2
1923 | 12 | 4.8 | -0.5 | 17 | 58.1
1924 | 1 | 5.7 | 0.1 | 13 | 40.6
1924 | 2 | 5.8 | 0 | 16 | 25.6
1924 | 3 | 6.9 | -2.7 | 28 | 24.6
1924 | 4 | 9.9 | 1.5 | 8 | 44.8
1924 | 5 | 13.1 | 5.9 | 0 | 154
1924 | 6 | 16.7 | 7.6 | 0 | 50.1
1924 | 7 | 18.4 | 10 | 0 | 98.9
1924 | 8 | 17.2 | 9.1 | 0 | 59
1924 | 9 | 15.6 | 8.6 | 0 | 72.9
1924 | 10 | 12.7 | 5.6 | 2 | 70
1924 | 11 | 9 | 3.6 | 4 | 31.5
1924 | 12 | 8.6 | 3.5 | 0 | 55.5
1925 | 1 | 6.8 | 1.2 | 5 | 42.3
1925 | 2 | 6.7 | 0.7 | 9 | 58.1
1925 | 3 | 7.7 | 1.3 | 9 | 41.7
1925 | 4 | 10.1 | 2.1 | 5 | 80.3
1925 | 5 | 14.2 | 6.1 | 1 | 58.9
1925 | 6 | 18.1 | 7.9 | 0 | 1.7
1925 | 7 | 21.1 | 10.9 | 0 | 52.6
1925 | 8 | 18.3 | 9.8 | 0 | 66.9
1925 | 9 | 14.5 | 6.1 | 0 | 59.8
1925 | 10 | 13.5 | 4.8 | 3 | 63.9
1925 | 11 | 5.8 | -0.8 | 20 | 57.8
1925 | 12 | 4.3 | -1.2 | 18 | 79.4
1926 | 1 | 5.9 | 0.7 | 12 | 53.1
1926 | 2 | 7.8 | 2.4 | 6 | 40.2
1926 | 3 | 8.9 | 1.8 | 5 | 19.7
1926 | 4 | 12.6 | 3.3 | 2 | 23
1926 | 5 | 12.7 | 4 | 3 | 42.6
1926 | 6 | 17.1 | 8 | 0 | 77.2
1926 | 7 | 20.3 | 11.5 | 0 | 80.5
1926 | 8 | 20 | 10.5 | 0 | 59.5
1926 | 9 | 17.1 | 8.6 | 0 | 56.4
1926 | 10 | 10.6 | 2.9 | 9 | 70.3
1926 | 11 | 7.7 | 1.4 | 7 | 89.7
1926 | 12 | 6.9 | 1.1 | 8 | 17.7
1927 | 1 | 6.6 | 0.7 | 12 | 26.6
1927 | 2 | 7.1 | 0.1 | 13 | 16.8
1927 | 3 | 9.5 | 2.4 | 2 | 36.4
1927 | 4 | 10.7 | 2.4 | 8 | 32.7
1927 | 5 | 12.5 | 4 | 2 | 39.5
1927 | 6 | 15.3 | 6 | 1 | 77
1927 | 7 | 18.1 | 10.3 | 0 | 96.5
1927 | 8 | 18.6 | 9.9 | 0 | 158.3
1927 | 9 | 15 | 7.5 | 0 | 92.4
1927 | 10 | 13.1 | 5.2 | 2 | 36.2
1927 | 11 | 8.1 | 2.1 | 10 | 53.4
1927 | 12 | 3 | -0.8 | 12 | 70.7
1928 | 1 | 7 | 0.6 | 6 | 60.9
1928 | 2 | 8.1 | 1.1 | 11 | 28.2
1928 | 3 | 7.3 | 1.2 | 9 | 56.3
1928 | 4 | 10.9 | 2.5 | 7 | 18.5
1928 | 5 | 12.5 | 4.5 | 2 | 40.6
1928 | 6 | 15.1 | 6.5 | 0 | 117.4
1928 | 7 | 19 | 9.9 | 0 | 38.9
1928 | 8 | 18.7 | 9.9 | 0 | 64.5
1928 | 9 | 15.7 | 7 | 0 | 17.2
1928 | 10 | 12.1 | 5 | 2 | 62.5
1928 | 11 | 9.7 | 3.7 | 2 | 56.9
1928 | 12 | 5.3 | -0.7 | 18 | 36.3
1929 | 1 | 3.4 | -0.9 | 19 | 39.8
1929 | 2 | 2.2 | -3.6 | 22 | 24.7
1929 | 3 | 11.7 | 0.8 | 10 | 4.2
1929 | 4 | 9 | 0.9 | 7 | 24.8
1929 | 5 | 14.8 | 4.7 | 1 | 22.7
1929 | 6 | 16.5 | 7.4 | 0 | 40.5
1929 | 7 | 19.9 | 9.5 | 0 | 58.5
1929 | 8 | 18.2 | 9.8 | 0 | 71.6
1929 | 9 | 18.9 | 8.3 | 0 | 32.4
1929 | 10 | 12.4 | 4.4 | 5 | 49.1
1929 | 11 | 8.7 | 2.3 | 5 | 65.3
1929 | 12 | 7 | 1.6 | 8 | 78.9
1930 | 1 | 7.1 | 1 | 10 | 89.7
1930 | 2 | 4.1 | -0.6 | 14 | 42.3
1930 | 3 | 7.6 | 0.3 | 12 | 62.4
1930 | 4 | 9.8 | 3.7 | 0 | 54.9
1930 | 5 | 13 | 4.5 | 2 | 38.6
1930 | 6 | 18.7 | 8.4 | 0 | 29.2
1930 | 7 | 17.9 | 10.4 | 0 | 183.9
1930 | 8 | 19.1 | 10.2 | 0 | 113.2
1930 | 9 | 15.1 | 8.8 | 0 | 77.7
1930 | 10 | 12.5 | 5.8 | 0 | 50
1930 | 11 | 8.3 | 1.5 | 9 | 80
1930 | 12 | 6 | 0 | 14 | 63.8
1931 | 1 | 5.3 | -0.5 | 16 | 50.3
1931 | 2 | 5.6 | -0.3 | 15 | 30.5
1931 | 3 | 6.4 | -1.4 | 22 | 37.7
1931 | 4 | 10 | 2.9 | 2 | 78.6
1931 | 5 | 14.1 | 5.4 | 1 | 70.6
1931 | 6 | 16.2 | 8.3 | 0 | 92
1931 | 7 | 18.2 | 10.6 | 0 | 101.6
1931 | 8 | 16.5 | 8.8 | 0 | 56.1
1931 | 9 | 14.7 | 6.4 | 1 | 84.4
1931 | 10 | 12.3 | 3.8 | 7 | 27
1931 | 11 | 9.2 | 3.3 | 3 | 53.3
1931 | 12 | 7.4 | 0.8 | 12 | 25
1932 | 1 | 8.6 | 1.5 | 12 | 37.7
1932 | 2 | 6.7 | 1 | 8 | 26.4
1932 | 3 | 7.5 | 0.6 | 7 | 56.7
1932 | 4 | 9.6 | 1.5 | 6 | 32.5
1932 | 5 | 11.8 | 5.4 | 1 | 104.2
1932 | 6 | 16.4 | 7.7 | 0 | 29.7
1932 | 7 | 18.5 | 11 | 0 | 110.6
1932 | 8 | 19.3 | 10.7 | 0 | 65.6
1932 | 9 | 15.8 | 7.6 | 2 | 55.4
1932 | 10 | 11 | 4.1 | 1 | 101.3
1932 | 11 | 8.4 | 3.2 | 5 | 18.8
1932 | 12 | 7.5 | 3 | 3 | 23.4
1933 | 1 | 4.5 | -1.2 | 16 | 42.5
1933 | 2 | 6.1 | 0.6 | 11 | 85.3
1933 | 3 | 11 | 1.8 | 7 | 27.2
1933 | 4 | 12.2 | 4.4 | 2 | 26.4
1933 | 5 | 13.8 | 6.5 | 0 | 59.3
1933 | 6 | 19.1 | 8.9 | 0 | 36.4
1933 | 7 | 21.8 | 11.9 | 0 | 44.7
1933 | 8 | 21.5 | 11.4 | 0 | 24.1
1933 | 9 | 18 | 9.4 | 0 | 54.2
1933 | 10 | 12.6 | 6 | 0 | 79
1933 | 11 | 8 | 2.8 | 3 | 90.5
1933 | 12 | 4.2 | 0 | 15 | 50
1934 | 1 | 7.1 | 1.1 | 6 | 30.1
1934 | 2 | 8.4 | 1.6 | 8 | 10.9
1934 | 3 | 8.1 | 0.7 | 7 | 64.6
1934 | 4 | 10.2 | 3.1 | 3 | 94
1934 | 5 | 15 | 5.4 | 0 | 32.9
1934 | 6 | 17.8 | 8.5 | 0 | 53.3
1934 | 7 | 21.7 | 11.4 | 0 | 55.5
1934 | 8 | 18.9 | 9.6 | 0 | 61.8
1934 | 9 | 18.2 | 8.3 | 0 | 43
1934 | 10 | 12.9 | 6.3 | 1 | 79.4
1934 | 11 | 8.6 | 3.3 | 5 | 60.6
1934 | 12 | 9 | 4.5 | 1 | 104
1935 | 1 | 7.1 | 1.1 | 10 | 57.2
1935 | 2 | 8 | 1.9 | 6 | 81.3
1935 | 3 | 9.5 | 2.9 | 4 | 15.2
1935 | 4 | 10.2 | 3.2 | 4 | 81.3
1935 | 5 | 12.6 | 4.1 | 3 | 20.4
1935 | 6 | 18.2 | 9.1 | 0 | 71.1
1935 | 7 | 21.4 | 10.6 | 0 | 7.7
1935 | 8 | 21.4 | 10.7 | 0 | 50.6
1935 | 9 | 16.1 | 7.9 | 0 | 135.1
1935 | 10 | 12.4 | 4.7 | 3 | 91.9
1935 | 11 | 8.6 | 3 | 2 | 103.2
1935 | 12 | 4.6 | 0.4 | 14 | 45.2
1936 | 1 | 5.1 | 0.6 | 9 | 86.6
1936 | 2 | 4.6 | -1.5 | 15 | 87.7
1936 | 3 | 9 | 2.9 | 3 | 59.4
1936 | 4 | 9.8 | 1.5 | 6 | 37
1936 | 5 | 13.9 | 5.7 | 0 | 42.3
1936 | 6 | 17.9 | 7.8 | 0 | 88.1
1936 | 7 | 18.9 | 11 | 0 | 77
1936 | 8 | 20.4 | 10.9 | 0 | 52.4
1936 | 9 | 16.8 | 10.4 | 0 | 68.6
1936 | 10 | 12.9 | 4.9 | 1 | 34.5
1936 | 11 | 8.6 | 1.7 | 6 | 62
1936 | 12 | 7.6 | 1.7 | 9 | 45
1937 | 1 | 6.7 | 1.6 | 10 | 69.6
1937 | 2 | 6.8 | 1.1 | 6 | 77.2
1937 | 3 | 5.4 | -0.4 | 17 | 78.9
1937 | 4 | 10.8 | 4.4 | 2 | 56.4
1937 | 5 | 15.4 | 6.6 | 0 | 70.5
1937 | 6 | 17.5 | 9.1 | 0 | 43.2
1937 | 7 | 19.7 | 11.4 | 0 | 79.8
1937 | 8 | 20.2 | 11 | 0 | 38
1937 | 9 | 16.5 | 7.7 | 0 | 39.8
1937 | 10 | 13 | 6 | 0 | 42.2
1937 | 11 | 8.1 | 3 | 6 | 34.1
1937 | 12 | 4.4 | -0.4 | 13 | 161.4
1938 | 1 | 7.8 | 2.5 | 2 | 50.4
1938 | 2 | 7.4 | 2.2 | 5 | 28.5
1938 | 3 | 13.1 | 5.6 | 1 | 7.6
1938 | 4 | 11.6 | 2.8 | 7 | 2.2
1938 | 5 | 14 | 4.8 | 4 | 87
1938 | 6 | 17.6 | 8.8 | 0 | 68.6
1938 | 7 | 18.6 | 10 | 0 | 58.6
1938 | 8 | 18.9 | 10.3 | 0 | 40.3
1938 | 9 | 17.2 | 8.7 | 0 | 61
1938 | 10 | 13 | 6.2 | 0 | 79.9
1938 | 11 | 10.9 | 5 | 1 | 59.5
1938 | 12 | 6.2 | 1.4 | 7 | 105.3
1939 | 1 | 5.4 | 0.6 | 15 | 121.8
1939 | 2 | 8.2 | 2.3 | 3 | 18.5
1939 | 3 | 8.7 | 2 | 3 | 72.3
1939 | 4 | 11.9 | 3.9 | 1 | 28.4
1939 | 5 | 15.2 | 5.6 | 1 | 33.8
1939 | 6 | 18.3 | 7.9 | 0 | 63
1939 | 7 | 19 | 10.4 | 0 | 79
1939 | 8 | 19.7 | 11.5 | 0 | 109
1939 | 9 | 17.2 | 9.3 | 0 | 35
1939 | 10 | 11.7 | 4.1 | 3 | 142.6
1939 | 11 | 10.3 | 4.5 | 0 | 63.4
1939 | 12 | 5.8 | 1.3 | 9 | 32.2
1940 | 1 | 1.6 | -4.6 | 28 | 40.9
1940 | 2 | 3.4 | -0.8 | 15 | 50.8
1940 | 3 | 9 | 1.5 | 11 | 46.8
1940 | 4 | 10.7 | 2.7 | 5 | 39.6
1940 | 5 | 16.5 | 5.6 | 0 | 39.7
1940 | 6 | 22.3 | 9.2 | 0 | 33.2
1940 | 7 | 18.6 | 9 | 0 | 133.4
1940 | 8 | 18.7 | 9.5 | 0 | 21.2
1940 | 9 | 16.1 | 7.1 | 0 | 33
1940 | 10 | 11.5 | 5.8 | 1 | 77.9
1940 | 11 | 8.9 | 3.3 | 3 | 88.1
1940 | 12 | 5.9 | 1.4 | 5 | 53.3
1941 | 1 | 1.8 | -2.7 | 18 | 85.2
1941 | 2 | 4.5 | -1.6 | 15 | 152.5
1941 | 3 | 7.1 | -0.1 | 15 | 63.8
1941 | 4 | 8.9 | 2.1 | 4 | 27
1941 | 5 | 12.8 | 3.9 | 3 | 30.1
1941 | 6 | 18.6 | 9 | 0 | 21.7
1941 | 7 | 22 | 11.5 | 0 | 36.3
1941 | 8 | 18.2 | 9.8 | 0 | 58.2
1941 | 9 | 18.4 | 9.9 | 0 | 12.8
1941 | 10 | 13.3 | 5.8 | 1 | 90.8
1941 | 11 | 8.8 | 2.5 | 4 | 88.3
1941 | 12 | 8.8 | 2.8 | 6 | 14.5
1942 | 1 | 3 | -1.7 | 21 | 49.3
1942 | 2 | 2.8 | -3.4 | 26 | 42.2
1942 | 3 | 7.6 | -0.6 | 19 | 27.3
1942 | 4 | 12.3 | 2.6 | 3 | 20.5
1942 | 5 | 14.8 | 4.2 | 4 | 39.2
1942 | 6 | 18.6 | 7.9 | 0 | 28.5
1942 | 7 | 19.3 | 9.3 | 0 | 76.1
1942 | 8 | 19.6 | 11.1 | 0 | 51.2
1942 | 9 | 17 | 8 | 1 | 67.3
1942 | 10 | 14 | 6 | 1 | 43.4
1942 | 11 | 8.4 | 1.7 | 6 | 16.8
1942 | 12 | 8.3 | 1.4 | 9 | 52.8
1943 | 1 | 5.8 | -0.5 | 15 | 80.1
1943 | 2 | 9.7 | 1 | 9 | 19.1
1943 | 3 | 10.7 | 1.1 | 10 | 16.2
1943 | 4 | 14 | 4.5 | 2 | 24.5
1943 | 5 | 16.1 | 4.9 | 2 | 58.3
1943 | 6 | 18.3 | 8.3 | 0 | 29.9
1943 | 7 | 19.7 | 9 | 0 | 39.3
1943 | 8 | 18.8 | 9.6 | 0 | 98.4
1943 | 9 | 16.6 | 7.3 | 0 | 87.2
1943 | 10 | 13.6 | 5.1 | 1 | 42.3
1943 | 11 | 8.4 | 2.3 | 7 | 44.5
1943 | 12 | 7 | 0.4 | 11 | 29.9
1944 | 1 | 8.7 | 1.6 | 10 | 22.5
1944 | 2 | 6.4 | 0.2 | 11 | 55.1
1944 | 3 | 9.5 | 0.5 | 11 | 9.7
1944 | 4 | 13.7 | 4.1 | 1 | 54.4
1944 | 5 | 15 | 4.9 | 1 | 43.9
1944 | 6 | 16.9 | 7.2 | 0 | 54.4
1944 | 7 | 19.2 | 10.4 | 0 | 86.4
1944 | 8 | 20.4 | 11.1 | 0 | 36.5
1944 | 9 | 16 | 6.9 | 0 | 131.4
1944 | 10 | 11.8 | 5.1 | 0 | 82.5
1944 | 11 | 8.5 | 2.3 | 2 | 126.2
1944 | 12 | 6.1 | 1.2 | 11 | 34.1
1945 | 1 | 3.5 | -2.5 | 20 | 92.8
1945 | 2 | 9.8 | 3.3 | 3 | 36.9
1945 | 3 | 12.5 | 2.8 | 8 | 11.6
1945 | 4 | 13.8 | 4 | 3 | 32.8
1945 | 5 | 15.6 | 6.1 | 2 | 78.2
1945 | 6 | 17.9 | 9.1 | 0 | 53.6
1945 | 7 | 21.3 | 11.4 | 0 | 40.9
1945 | 8 | 19.6 | 10.6 | 0 | 85.5
1945 | 9 | 18 | 9.1 | 0 | 48.2
1945 | 10 | 15.3 | 7 | 0 | 93.8
1945 | 11 | 10 | 4.7 | 1 | 22.3
1945 | 12 | 6.7 | 1.8 | 6 | 34.3
1946 | 1 | 5.1 | -0.4 | 14 | 33.3
1946 | 2 | 8.4 | 2.2 | 8 | 8.1
1946 | 3 | 8.8 | 1.4 | 12 | 35.9
1946 | 4 | 13.9 | 4.6 | 1 | 46
1946 | 5 | 13.4 | 4.8 | 0 | 55.4
1946 | 6 | 17.2 | 7.9 | 0 | 43.7
1946 | 7 | 20.3 | 10.8 | 0 | 75.8
1946 | 8 | 18 | 9.4 | 0 | 91.9
1946 | 9 | 16.3 | 9 | 0 | 100.4
1946 | 10 | 11.6 | 5.9 | 3 | 41.1
1946 | 11 | 9.9 | 4.7 | 0 | 121.4
1946 | 12 | 5.7 | 0.7 | 11 | 69.6
1947 | 1 | 4.7 | 0.1 | 14 | 48
1947 | 2 | 0.6 | -2.9 | 26 | 80.5
1947 | 3 | 4.7 | -1.1 | 16 | 97.9
1947 | 4 | 11.1 | 4 | 2 | 87.7
1947 | 5 | 16.7 | 6.6 | 0 | 49.6
1947 | 6 | 18.5 | 10.1 | 0 | 47.8
1947 | 7 | 20.2 | 12 | 0 | 56.2
1947 | 8 | 23 | 11.4 | 0 | 7.7
1947 | 9 | 19.1 | 8.8 | 0 | 42.7
1947 | 10 | 14.6 | 6.5 | 0 | 14
1947 | 11 | 9 | 2.7 | 8 | 52.7
1947 | 12 | 7.4 | 2.2 | 7 | 38.3
1948 | 1 | 6.2 | 1.6 | 4 | 188
1948 | 2 | 6.9 | 1.7 | 5 | 29.1
1948 | 3 | 11.9 | 3.1 | 3 | 20.2
1948 | 4 | 12.9 | 3.8 | 0 | 35.1
1948 | 5 | 14.9 | 4.6 | 4 | 29.2
1948 | 6 | 16.2 | 8.2 | 0 | 83.7
1948 | 7 | 19.2 | 10.5 | 0 | 42.8
1948 | 8 | 17.4 | 10 | 0 | 96.8
1948 | 9 | 16.6 | 9 | 0 | 98.8
1948 | 10 | 13.5 | 5.6 | 3 | 39.5
1948 | 11 | 9.4 | 3.4 | 7 | 34.1
1948 | 12 | 7.2 | 1.6 | 9 | 58
1949 | 1 | 7.9 | 1.1 | 11 | 14.5
1949 | 2 | 8.6 | 1.7 | 6 | 12.6
1949 | 3 | 8.3 | 1.3 | 11 | 28.3
1949 | 4 | 14 | 5.6 | 0 | 38.7
1949 | 5 | 15.9 | 5.1 | 0 | 15.5
1949 | 6 | 19.5 | 7.9 | 0 | 33
1949 | 7 | 21.2 | 11.2 | 0 | 50.8
1949 | 8 | 20.5 | 11.3 | 0 | 44.5
1949 | 9 | 19.4 | 11.1 | 0 | 20
1949 | 10 | 14.5 | 7.3 | 2 | 61.9
1949 | 11 | 8.9 | 3.3 | 2 | 100.2
1949 | 12 | 7.9 | 2.3 | 4 | 52
1950 | 1 | 6.4 | 1.8 | 11 | 41.6
1950 | 2 | 7 | 0.8 | 9 | 76.8
1950 | 3 | 11.1 | 2.8 | 2 | 20.8
1950 | 4 | 10.6 | 2.6 | 6 | 33.2
1950 | 5 | 12.9 | 5.9 | 0 | 37.9
1950 | 6 | 20.6 | 9.8 | 0 | 19.6
1950 | 7 | 19.8 | 10.9 | 0 | 100.4
1950 | 8 | 18.9 | 9.8 | 0 | 122.3
1950 | 9 | 15.6 | 8.4 | 0 | 106.8
1950 | 10 | 12.8 | 5.9 | 2 | 22.9
1950 | 11 | 8.3 | 2.5 | 4 | 140.8
1950 | 12 | 3.3 | -1.2 | 18 | 80.6
1951 | 1 | 5.5 | -0.1 | 14 | 29.2
1951 | 2 | 5.9 | 0.2 | 9 | 61.9
1951 | 3 | 7.1 | -0.3 | 19 | 85.5
1951 | 4 | 10.3 | 1.7 | 4 | 28.6
1951 | 5 | 11.8 | 4.6 | 0 | 99.5
1951 | 6 | 16.8 | 7.4 | 0 | 23
1951 | 7 | 20.3 | 10.7 | 0 | 43.2
1951 | 8 | 18.1 | 10 | 0 | 105.5
1951 | 9 | 17.5 | 8.9 | 0 | 26.8
1951 | 10 | 13.3 | 5.9 | 2 | 44.5
1951 | 11 | 10.5 | 5 | 2 | 140.4
1951 | 12 | 7.3 | 1.3 | 10 | 56.8
1952 | 1 | 4.2 | -0.8 | 15 | 42.3
1952 | 2 | 6.9 | 0.5 | 13 | 10.7
1952 | 3 | 8.8 | 2.2 | 6 | 30.6
1952 | 4 | 13.3 | 3.7 | 3 | 43.4
1952 | 5 | 17.4 | 7.4 | 0 | 27
1952 | 6 | 18.8 | 8.7 | 0 | 29.6
1952 | 7 | 20.9 | 11.1 | 0 | 16
1952 | 8 | 19.5 | 10.7 | 0 | 55.7
1952 | 9 | 14.2 | 6.8 | 0 | 107.3
1952 | 10 | 11.5 | 5.3 | 1 | 73.4
1952 | 11 | 6.6 | 1.1 | 8 | 78
1952 | 12 | 5.1 | 0.2 | 12 | 56.9
1953 | 1 | 6.8 | 1.5 | 7 | 13.4
1953 | 2 | 7.3 | 1.6 | 11 | 51.4
1953 | 3 | 11.9 | 0.6 | 10 | 1.3
1953 | 4 | 10.3 | 1.8 | 6 | 51
1953 | 5 | 16.5 | 7.5 | 0 | 42.2
1953 | 6 | 16.6 | 8.6 | 0 | 60.7
1953 | 7 | 18.6 | 10.4 | 0 | 58.3
1953 | 8 | 19.9 | 10.6 | 0 | 129.1
1953 | 9 | 17.6 | 9.1 | 0 | 30.8
1953 | 10 | 12.7 | 4.5 | 1 | 41.3
1953 | 11 | 10.3 | 5.3 | 0 | 25
1953 | 12 | 8.4 | 3.4 | 4 | 17.4
1954 | 1 | 5.1 | 0.2 | 14 | 56.7
1954 | 2 | 3.9 | -1.3 | 15 | 48
1954 | 3 | 7.7 | 1.5 | 4 | 33.6
1954 | 4 | 11.1 | 2.7 | 4 | 10.1
1954 | 5 | 14.2 | 6.4 | 0 | 120
1954 | 6 | 15.8 | 8.9 | 0 | 40.3
1954 | 7 | 17.7 | 9.7 | 0 | 47
1954 | 8 | 16.8 | 10 | 0 | 124.7
1954 | 9 | 16 | 6.9 | 1 | 49.2
1954 | 10 | 14.1 | 7.5 | 0 | 106.4
1954 | 11 | 9.1 | 3.1 | 2 | 90.7
1954 | 12 | 8.7 | 2.9 | 7 | 54.3
1955 | 1 | 3.9 | -0.7 | 13 | 54
1955 | 2 | 2.9 | -2.2 | 18 | 60.7
1955 | 3 | 6.3 | -0.7 | 16 | 42.4
1955 | 4 | 13.3 | 4.1 | 2 | 14.1
1955 | 5 | 12.5 | 4.1 | 0 | 41.1
1955 | 6 | 15.8 | 7.7 | 0 | 63.8
1955 | 7 | 22.1 | 10.7 | 0 | 24.7
1955 | 8 | 21.2 | 11.6 | 0 | 15.6
1955 | 9 | 18 | 8.9 | 0 | 18.6
1955 | 10 | 12.8 | 4.5 | 4 | 35.5
1955 | 11 | 9.3 | 4.4 | 4 | 44.6
1955 | 12 | 6.9 | 1.3 | 10 | 69.1
1956 | 1 | 5.3 | -0.3 | 15 | 82.5
1956 | 2 | 3.3 | -3.1 | 22 | 54.1
1956 | 3 | 8.2 | 1.6 | 8 | 12.7
1956 | 4 | 10.2 | 0.7 | 11 | 18.9
1956 | 5 | 16.1 | 5.8 | 0 | 13.7
1956 | 6 | 16 | 7.9 | 0 | 81.2
1956 | 7 | 18.2 | 10.9 | 0 | 47.2
1956 | 8 | 16.1 | 8.6 | 0 | 175.7
1956 | 9 | 16.5 | 9.3 | 0 | 48.4
1956 | 10 | 12.9 | 5.8 | 0 | 33.6
1956 | 11 | 8.6 | 2.9 | 4 | 16.3
1956 | 12 | 7.5 | 2.3 | 11 | 44
1957 | 1 | 7.8 | 2.2 | 6 | 43.5
1957 | 2 | 7.1 | 0.2 | 13 | 57.2
1957 | 3 | 11.2 | 4.4 | 3 | 25.9
1957 | 4 | 11.9 | 3.1 | 4 | 6.9
1957 | 5 | 13.9 | 4.8 | 2 | 39.5
1957 | 6 | 19.3 | 7.7 | 0 | 32.8
1957 | 7 | 18.6 | 11.9 | 0 | 76.7
1957 | 8 | 17.7 | 10.8 | 0 | 77.1
1957 | 9 | 14.9 | 7.5 | 0 | 85.7
1957 | 10 | 13.6 | 5.6 | 2 | 38
1957 | 11 | 9 | 4 | 2 | 32.5
1957 | 12 | 6.9 | 1.2 | 9 | 34.4
1958 | 1 | 5 | -0.8 | 14 | 34.9
1958 | 2 | 6.2 | 0.4 | 14 | 94.1
1958 | 3 | 5.5 | -0.7 | 18 | 55.3
1958 | 4 | 10.8 | 2.5 | 9 | 30.3
1958 | 5 | 13.6 | 5 | 1 | 91.8
1958 | 6 | 15.8 | 8.2 | 0 | 71.9
1958 | 7 | 19.1 | 10.2 | 0 | 51.2
1958 | 8 | 19.1 | 10.6 | 0 | 62.6
1958 | 9 | 17.7 | 9.9 | 0 | 43.8
1958 | 10 | 13.7 | 5.8 | 0 | 34.2
1958 | 11 | 8.7 | 2.3 | 7 | 12.2
1958 | 12 | 6.3 | 1.7 | 6 | 82.5
1959 | 1 | 3.6 | -2.2 | 25 | 50.7
1959 | 2 | 6.9 | 0.8 | 13 | 15.1
1959 | 3 | 9.8 | 3.1 | 1 | 14.5
1959 | 4 | 13 | 3.7 | 4 | 38.2
1959 | 5 | 16.4 | 6.1 | 0 | 13.3
1959 | 6 | 19 | 9.1 | 0 | 61.1
1959 | 7 | 21.4 | 10.9 | 0 | 31.1
1959 | 8 | 21.7 | 11.2 | 0 | 6.4
1959 | 9 | 19.4 | 7.8 | 0 | 17.7
1959 | 10 | 15.7 | 7.5 | 0 | 25
1959 | 11 | 9.5 | 3.2 | 4 | 89.6
1959 | 12 | 7.6 | 2.2 | 1 | 77.1
1960 | 1 | 6 | 0.4 | 14 | 107.5
1960 | 2 | 5.9 | -0.2 | 15 | 57.1
1960 | 3 | 7.2 | 2.6 | 1 | 44.3
1960 | 4 | 13.1 | 3.8 | 2 | 27.3
1960 | 5 | 16.1 | 6.2 | 1 | 49.8
1960 | 6 | 20.1 | 9.6 | 0 | 5.3
1960 | 7 | 18.4 | 9.8 | 0 | 84.4
1960 | 8 | 18.4 | 9.5 | 0 | 59.3
1960 | 9 | 16.2 | 8.5 | 0 | 56.3
1960 | 10 | 12.1 | 7.1 | 0 | 172.4
1960 | 11 | 8.7 | 2.6 | 2 | 71
1960 | 12 | 6 | 0.8 | 9 | 48.6
1961 | 1 | 5.5 | 0.1 | 10 | 103.4
1961 | 2 | 9.2 | 2.7 | 3 | 28.4
1961 | 3 | 12.3 | 3.8 | 1 | 23.4
1961 | 4 | 11.9 | 4.8 | 2 | 59.7
1961 | 5 | 13.8 | 5.8 | 0 | 48.4
1961 | 6 | 18.1 | 8.9 | 0 | 47.6
1961 | 7 | 18 | 9.9 | 0 | 93.4
1961 | 8 | 19.2 | 9.6 | 0 | 81.9
1961 | 9 | 18.4 | 9.6 | 0 | 40.6
1961 | 10 | 13.3 | 6.2 | 0 | 76.5
1961 | 11 | 8.3 | 2.4 | 7 | 26.5
1961 | 12 | 4 | -1.8 | 20 | 80
1962 | 1 | 6.9 | 0.7 | 9 | 48.7
1962 | 2 | 7.5 | 1.3 | 7 | 20.6
1962 | 3 | 5.7 | -1.8 | 18 | 27.4
1962 | 4 | 11.3 | 2.7 | 1 | 52.9
1962 | 5 | 13.8 | 5.5 | 1 | 59
1962 | 6 | 17.5 | 7.5 | 0 | 20.9
1962 | 7 | 17.2 | 9.2 | 0 | 58.1
1962 | 8 | 17.3 | 9.3 | 0 | 64
1962 | 9 | 15.7 | 7.9 | 0 | 70.2
1962 | 10 | 13.8 | 6.2 | 2 | 13.2
1962 | 11 | 7.9 | 1.4 | 9 | 72.8
1962 | 12 | 4.7 | -2.2 | 23 | 67.6
1963 | 1 | 2.1 | -3.2 | 28 | 74.4
1963 | 2 | 1.5 | -3.9 | 28 | 71.8
1963 | 3 | 8.2 | 1.2 | 8 | 42.7
1963 | 4 | 11.4 | 4.4 | 0 | 41.7
1963 | 5 | 14.1 | 5.7 | 0 | 24.6
1963 | 6 | 17.5 | 9.6 | 0 | 77.7
1963 | 7 | 18.6 | 9.8 | 0 | 33.3
1963 | 8 | 17.2 | 9.2 | 0 | 93.7
1963 | 9 | 16.7 | 7.3 | 0 | 45.2
1963 | 10 | 13.6 | 6.3 | 0 | 33.4
1963 | 11 | 9.2 | 4 | 3 | 96.8
1963 | 12 | 5.7 | 0.2 | 10 | 37.3
1964 | 1 | 6.3 | 0.1 | 16 | 10.8
1964 | 2 | 6.7 | 0.6 | 12 | 25
1964 | 3 | 5.2 | 0.8 | 10 | 92.9
1964 | 4 | 12.1 | 4.7 | 1 | 51.8
1964 | 5 | 16.7 | 7.4 | 0 | 24.6
1964 | 6 | 16.7 | 8.8 | 0 | 66.6
1964 | 7 | 19.2 | 10.2 | 0 | 41.5
1964 | 8 | 19 | 9.7 | 0 | 44
1964 | 9 | 18 | 8.2 | 0 | 39.5
1964 | 10 | 12.5 | 4.5 | 1 | 36.9
1964 | 11 | 9.9 | 2.9 | 8 | 28.7
1964 | 12 | 5.5 | -1.3 | 19 | 54.9
1965 | 1 | 5.5 | -0.5 | 14 | 90.7
1965 | 2 | 6.1 | 0.7 | 8 | 26.8
1965 | 3 | 7.7 | -0.4 | 16 | 51.2
1965 | 4 | 11.9 | 2.6 | 4 | 60.3
1965 | 5 | 14.5 | 5.7 | 1 | 60.7
1965 | 6 | 18.3 | 8.5 | 0 | 35.4
1965 | 7 | 16.9 | 8.3 | 0 | 93.9
1965 | 8 | 18.2 | 8.7 | 0 | 55
1965 | 9 | 15.3 | 8.4 | 0 | 95.6
1965 | 10 | 13.7 | 6.3 | 1 | 20.4
1965 | 11 | 6.2 | 0.6 | 16 | 186.1
1965 | 12 | 5.5 | -0.4 | 10 | 38.5
1966 | 1 | 3.9 | -0.8 | 19 | 50.6
1966 | 2 | 6 | 0.6 | 12 | 98.6
1966 | 3 | 10.2 | 2.2 | 6 | 9.6
1966 | 4 | 7.9 | 2.3 | 6 | 79.9
1966 | 5 | 15.1 | 5.3 | 0 | 57
1966 | 6 | 18.5 | 10 | 0 | 62.5
1966 | 7 | 18.7 | 9.5 | 0 | 67.5
1966 | 8 | 17.3 | 9.8 | 0 | 112.6
1966 | 9 | 17.1 | 9.3 | 0 | 27.1
1966 | 10 | 12.6 | 5.7 | 0 | 100.9
1966 | 11 | 8.4 | 2.2 | 4 | 49.1
1966 | 12 | 6.7 | 0.9 | 8 | 49.6
1967 | 1 | 6.3 | 0.2 | 12 | 32.3
1967 | 2 | 7.8 | 2.2 | 6 | 53
1967 | 3 | 9.6 | 3.2 | 3 | 23.5
1967 | 4 | 11.5 | 3.2 | 3 | 37.9
1967 | 5 | 12.6 | 4.8 | 2 | 97.9
1967 | 6 | 17.9 | 8 | 0 | 34.6
1967 | 7 | 19.3 | 10.5 | 0 | 69.3
1967 | 8 | 19 | 10.2 | 0 | 115.3
1967 | 9 | 16.6 | 8.5 | 0 | 52.8
1967 | 10 | 12.8 | 6.1 | 0 | 87
1967 | 11 | 8.5 | 0.8 | 9 | 81.3
1967 | 12 | 7 | 0.2 | 13 | 34.3
1968 | 1 | 6.4 | 0.2 | 15 | 25.2
1968 | 2 | 4.6 | -2 | 23 | 54.2
1968 | 3 | 9.7 | 2.1 | 8 | 30.1
1968 | 4 | 12.2 | 2.2 | 11 | 47.7
1968 | 5 | 12.7 | 3.6 | 3 | 49.3
1968 | 6 | 18.6 | 8.4 | 0 | 50.6
1968 | 7 | 16.8 | 9.6 | 0 | 102.4
1968 | 8 | 17.8 | 10.7 | 0 | 42.2
1968 | 9 | 17 | 9.2 | 0 | 113.6
1968 | 10 | 14.6 | 8.6 | 0 | 65
1968 | 11 | 7.8 | 3.9 | 1 | 65.6
1968 | 12 | 4.6 | 0.4 | 13 | 97.3
1969 | 1 | 7.1 | 1 | 11 | 47.9
1969 | 2 | 3 | -2.6 | 20 | 88.5
1969 | 3 | 5 | -0.5 | 16 | 85.9
1969 | 4 | 10.7 | 2.1 | 6 | 45.5
1969 | 5 | 13.1 | 5.9 | 0 | 102
1969 | 6 | 18.1 | 8.1 | 0 | 78
1969 | 7 | 20.4 | 11.4 | 0 | 44.3
1969 | 8 | 19.9 | 11.7 | 0 | 35.8
1969 | 9 | 17.1 | 9.9 | 0 | 58.4
1969 | 10 | 15.7 | 8.7 | 0 | 9.6
1969 | 11 | 6.9 | 1 | 12 | 116.9
1969 | 12 | 5 | 0.3 | 13 | 45.7
1970 | 1 | 5 | -0.2 | 14 | 90.1
1970 | 2 | 5.5 | -1.2 | 14 | 47.7
1970 | 3 | 7.5 | -0.3 | 13 | 32.4
1970 | 4 | 9.7 | 2 | 10 | 49.4
1970 | 5 | 16 | 7.2 | 0 | 22.7
1970 | 6 | 20.3 | 9.5 | 0 | 18.6
1970 | 7 | 18.4 | 10.8 | 0 | 46.7
1970 | 8 | 20.1 | 11.3 | 0 | 63.5
1970 | 9 | 17.4 | 10 | 0 | 34.3
1970 | 10 | 13.9 | 6.3 | 0 | 22.8
1970 | 11 | 9.2 | 3 | 5 | 62.6
1970 | 12 | 6.6 | 2 | 6 | 72.1
1971 | 1 | 6.3 | 1.2 | 11 | 45.8
1971 | 2 | 7.8 | 1.3 | 7 | 16.7
1971 | 3 | 8.2 | 1.8 | 9 | 62
1971 | 4 | 10.7 | 3.5 | 3 | 48.8
1971 | 5 | 15.5 | 5.9 | 1 | 47.7
1971 | 6 | 14.8 | 7.6 | 0 | 59
1971 | 7 | 20.7 | 11.1 | 0 | 32.3
1971 | 8 | 18.2 | 10.9 | 0 | 127.7
1971 | 9 | 18.2 | 9.3 | 0 | 12.8
1971 | 10 | 14.4 | 6.5 | 5 | 20.9
1971 | 11 | 8.4 | 2.6 | 11 | 47.7
1971 | 12 | 9.1 | 3.9 | 4 | 19.7
1972 | 1 | 5.1 | 1.2 | 10 | 116
1972 | 2 | 5.7 | 1 | 6 | 56
1972 | 3 | 8.9 | 1.9 | 4 | 51.9
1972 | 4 | 11.7 | 4.4 | 1 | 30.6
1972 | 5 | 13.9 | 5.8 | 0 | 57.3
1972 | 6 | 15.4 | 7.2 | 0 | 59.6
1972 | 7 | 19 | 9.8 | 0 | 50.9
1972 | 8 | 18.8 | 10.1 | 0 | 14.6
1972 | 9 | 15.5 | 6.9 | 0 | 23.8
1972 | 10 | 13.5 | 5.9 | 1 | 11.9
1972 | 11 | 8.5 | 2.4 | 7 | 52.7
1972 | 12 | 7 | 1.7 | 8 | 26
1973 | 1 | 6.3 | 1.7 | 10 | 27.3
1973 | 2 | 7.7 | 0.8 | 11 | 12.1
1973 | 3 | 10.7 | 2.3 | 5 | 9.1
1973 | 4 | 9.7 | 2.3 | 6 | 70.5
1973 | 5 | 14.1 | 6.2 | 0 | 56.8
1973 | 6 | 18.8 | 9.9 | 0 | 35.2
1973 | 7 | 19.2 | 10.6 | 0 | 78.3
1973 | 8 | 19 | 10.1 | 0 | 66.2
1973 | 9 | 16.7 | 8.9 | 0 | 48.8
1973 | 10 | 11.8 | 5.2 | 1 | 41
1973 | 11 | 7.9 | 1.7 | 10 | 21.6
1973 | 12 | 7 | 0.5 | 12 | 36.5
1974 | 1 | 7.7 | 1.8 | 5 | 74.7
1974 | 2 | 7.5 | 2.1 | 7 | 45.3
1974 | 3 | 7.7 | 1.6 | 7 | 52.3
1974 | 4 | 9.6 | 2.6 | 3 | 16.5
1974 | 5 | 15.1 | 5.7 | 1 | 19.7
1974 | 6 | 16.7 | 7.9 | 1 | 34.4
1974 | 7 | 18.2 | 9.8 | 0 | 65.4
1974 | 8 | 18.5 | 9.8 | 0 | 48.4
1974 | 9 | 15 | 7.4 | 0 | 65.4
1974 | 10 | 10 | 4.4 | 0 | 76.1
1974 | 11 | 8.5 | 2.9 | 4 | 55.1
1974 | 12 | 9.6 | 3.6 | 4 | 35.7
1975 | 1 | 8.8 | 2.4 | 6 | 43.9
1975 | 2 | 6.3 | 0.8 | 12 | 21.6
1975 | 3 | 7.6 | 0.7 | 13 | 45
1975 | 4 | 11.6 | 3.7 | 5 | 59.5
1975 | 5 | 12.2 | 3.7 | 1 | 49.6
1975 | 6 | 18.6 | 7.8 | 0 | 24.8
1975 | 7 | 20.1 | 11.7 | 0 | 61.5
1975 | 8 | 22.8 | 12.4 | 0 | 84.5
1975 | 9 | 16.1 | 7.9 | 0 | 78.6
1975 | 10 | 12.5 | 5.1 | 3 | 20.5
1975 | 11 | 8.7 | 2 | 7 | 34.2
1975 | 12 | 8.4 | 2.3 | 3 | 22.5
1976 | 1 | 7.4 | 2.1 | 10 | 46.2
1976 | 2 | 6.5 | 1.7 | 5 | 17.5
1976 | 3 | 7.1 | 1.1 | 8 | 26
1976 | 4 | 10.7 | 3.5 | 4 | 31.4
1976 | 5 | 14.5 | 6.5 | 0 | 78.9
1976 | 6 | 20.3 | 10.4 | 0 | 24.9
1976 | 7 | 22.1 | 10.7 | 0 | 30
1976 | 8 | 21.9 | 9.9 | 0 | 18.4
1976 | 9 | 15.4 | 8.6 | 0 | 193.2
1976 | 10 | 12.8 | 6.7 | 0 | 142.6
1976 | 11 | 8 | 1.5 | 11 | 22.8
1976 | 12 | 4 | -0.5 | 16 | 50.9
1977 | 1 | 4.5 | -0.8 | 17 | 101
1977 | 2 | 5.9 | 0.9 | 6 | 63.6
1977 | 3 | 9.2 | 2.7 | 5 | 54.8
1977 | 4 | 10.3 | 2.6 | 5 | 33
1977 | 5 | 13.6 | 4.7 | 1 | 35.3
1977 | 6 | 15.9 | 7.2 | 0 | 63.4
1977 | 7 | 18.8 | 10.3 | 0 | 9.4
1977 | 8 | 18.6 | 10.1 | 0 | 37.8
1977 | 9 | 16.1 | 8.5 | 0 | 16.3
1977 | 10 | 13.5 | 7.7 | 0 | 41.5
1977 | 11 | 8.4 | 2.9 | 4 | 74.2
1977 | 12 | 7.4 | 2.8 | 4 | 63.9
1978 | 1 | 4.8 | -0.9 | 17 | 80.8
1978 | 2 | 3.7 | -2 | 19 | 71.3
1978 | 3 | 9.9 | 2.8 | 4 | 29.5
1978 | 4 | 9.4 | 2.4 | 5 | 34.4
1978 | 5 | 15.4 | 6 | 0 | 53.1
1978 | 6 | 17 | 8.5 | 0 | 32.8
1978 | 7 | 17.8 | 9.8 | 0 | 61.4
1978 | 8 | 17.7 | 10.7 | 0 | 92.7
1978 | 9 | 16.6 | 10 | 0 | 51.4
1978 | 10 | 14.5 | 8.3 | 0 | 20.3
1978 | 11 | 10.7 | 4.7 | 5 | 24.7
1978 | 12 | 4.7 | 0.1 | 14 | 195.5
1979 | 1 | 2.4 | -3.5 | 23 | 49.6
1979 | 2 | 2.8 | -1.1 | 18 | 30.6
1979 | 3 | 6.4 | 0.9 | 13 | 166
1979 | 4 | 10 | 3.4 | 1 | 44.7
1979 | 5 | 12.8 | 4.6 | 4 | 96.5
1979 | 6 | 17.8 | 9.1 | 0 | 49.3
1979 | 7 | 19.6 | 11 | 0 | 25.3
1979 | 8 | 18 | 9.8 | 0 | 67.3
1979 | 9 | 16.7 | 8.4 | 0 | 39.2
1979 | 10 | 13.5 | 7.5 | 0 | 54.5
1979 | 11 | 9.4 | 2.8 | 7 | 69.1
1979 | 12 | 6.9 | 2.4 | 8 | 91
1980 | 1 | 4 | -0.1 | 18 | 66.2
1980 | 2 | 6.8 | 2.3 | 5 | 55.4
1980 | 3 | 6.9 | 0.7 | 9 | 95.6
1980 | 4 | 12.4 | 4.1 | 3 | 16.5
1980 | 5 | 14.6 | 4.6 | 1 | 37.4
1980 | 6 | 16.6 | 9 | 0 | 191.4
1980 | 7 | 18 | 10 | 0 | 55.7
1980 | 8 | 18.9 | 10.9 | 0 | 92.7
1980 | 9 | 17.5 | 10 | 0 | 27
1980 | 10 | 11.5 | 4.7 | 2 | 67.2
1980 | 11 | 8.8 | 3.8 | 6 | 61.8
1980 | 12 | 8.1 | 2.7 | 7 | 41.8
1981 | 1 | 7.1 | 0.1 | 20 | 28.3
1981 | 2 | 5.5 | 0.3 | 13 | 31.7
1981 | 3 | 9.6 | 3.1 | 5 | 113.5
1981 | 4 | 10.8 | 3.1 | 3 | 49.7
1981 | 5 | 15.1 | 6.3 | 2 | 47.7
1981 | 6 | 16.5 | 8.8 | 0 | 25.6
1981 | 7 | 19.2 | 10.6 | 0 | 36.4
1981 | 8 | 20.3 | 10.8 | 0 | 33.5
1981 | 9 | 18.3 | 9.5 | 0 | 117.2
1981 | 10 | 10.9 | 3.3 | 5 | 95
1981 | 11 | 10.5 | 3.7 | 3 | 56.6
1981 | 12 | 2.9 | -3.3 | 21 | 58.1
1982 | 1 | 4.8 | -2.1 | 14 | 64.6
1982 | 2 | 7.4 | 1.5 | 7 | 11.4
1982 | 3 | 9.3 | 1.8 | 6 | 29.6
1982 | 4 | 13.1 | 3.6 | 3 | 11.8
1982 | 5 | 15.5 | 5.5 | 3 | 26.5
1982 | 6 | 17 | 9.8 | 0 | 113.7
1982 | 7 | 19.2 | 11.2 | 0 | 25.5
1982 | 8 | 19.3 | 11.2 | 0 | 59.5
1982 | 9 | 18 | 8.7 | 0 | 34.3
1982 | 10 | 12.2 | 6.4 | 1 | 89.8
1982 | 11 | 9.3 | 4.4 | 2 | 68.8
1982 | 12 | 6.3 | 0.2 | 15 | 49.6
1983 | 1 | 8.5 | 2.9 | 5 | 30.3
1983 | 2 | 4.2 | -1.2 | 17 | 52.3
1983 | 3 | 9 | 2.9 | 2 | 58.6
1983 | 4 | 9.3 | 2 | 8 | 102.6
1983 | 5 | 12.1 | 5.5 | 0 | 102.4
1983 | 6 | 17 | 8.7 | 0 | 38.4
1983 | 7 | 22.9 | 12.6 | 0 | 20.2
1983 | 8 | 21.1 | 11.4 | 0 | 41.9
1983 | 9 | 16.1 | 9.1 | 0 | 61.4
1983 | 10 | 13.2 | 6.2 | 3 | 36.2
1983 | 11 | 9.2 | 4.2 | 6 | 33
1983 | 12 | 8.1 | 2.2 | 7 | 98.1
1984 | 1 | 4.8 | -0.5 | 20 | 83.7
1984 | 2 | 5.6 | 0.4 | 12 | 27.7
1984 | 3 | 6.9 | 1.9 | 4 | 52.2
1984 | 4 | 12.4 | 2.5 | 7 | 12.9
1984 | 5 | 13.9 | 4.4 | 3 | 30.7
1984 | 6 | 17.7 | 9.2 | 0 | 36.8
1984 | 7 | 21.2 | 10.4 | 0 | 21.4
1984 | 8 | 20.9 | 10.8 | 0 | 55.7
1984 | 9 | 16 | 9.3 | 0 | 96.3
1984 | 10 | 14.1 | 6.8 | 0 | 39.8
1984 | 11 | 9.5 | 5.2 | 0 | 134.3
1984 | 12 | 7.1 | 1.6 | 8 | 23.9
1985 | 1 | 3.3 | -1.5 | 22 | 82
1985 | 2 | 5.5 | -1.4 | 19 | 5.7
1985 | 3 | 7.7 | 0.6 | 12 | 62.1
1985 | 4 | 11 | 4 | 4 | 74.8
1985 | 5 | 13.5 | 5.9 | 0 | 63.9
1985 | 6 | 15.9 | 6.9 | 0 | 34.6
1985 | 7 | 19 | 10.7 | 0 | 59.6
1985 | 8 | 17.6 | 10.2 | 0 | 81.5
1985 | 9 | 17.5 | 9.5 | 0 | 51.9
1985 | 10 | 14.1 | 7.5 | 1 | 21.2
1985 | 11 | 6.4 | 0.2 | 12 | 68.1
1985 | 12 | 7.5 | 2.3 | 12 | 40.5
1986 | 1 | 5 | -0.3 | 14 | 63.1
1986 | 2 | 1.8 | -3 | 23 | 37.6
1986 | 3 | 7.8 | 0.8 | 11 | 38.8
1986 | 4 | 8.4 | 1.7 | 5 | 109.5
1986 | 5 | 14.4 | 6.7 | 0 | 65.5
1986 | 6 | 18.1 | 8.9 | 0 | 32.1
1986 | 7 | 19.2 | 10.8 | 0 | 24.2
1986 | 8 | 15.9 | 8.7 | 0 | 169.1
1986 | 9 | 16.2 | 6.4 | 0 | 28
1986 | 10 | 13.7 | 6.3 | 0 | 31
1986 | 11 | 10.5 | 4.3 | 1 | 36.2
1986 | 12 | 7.8 | 2.4 | 2 | 74.2
1987 | 1 | 2.9 | -1.5 | 18 | 39.1
1987 | 2 | 6.5 | 0.2 | 12 | 34.7
1987 | 3 | 7.2 | 0.5 | 14 | 81.2
1987 | 4 | 13.5 | 5 | 0 | 59.4
1987 | 5 | 13.3 | 4.9 | 0 | 42.7
1987 | 6 | 15.1 | 7.7 | 0 | 92.4
1987 | 7 | 19 | 11.1 | 0 | 84.9
1987 | 8 | 18.3 | 11.1 | 0 | 53.7
1987 | 9 | 16.7 | 8.6 | 0 | 46.2
1987 | 10 | 11.8 | 5.1 | 3 | 99.6
1987 | 11 | 8.9 | 3.4 | 3 | 61.3
1987 | 12 | 8.2 | 3 | 7 | 34.7
1988 | 1 | 7 | 1.3 | 7 | 79.8
1988 | 2 | 7.5 | 1.4 | 7 | 34.4
1988 | 3 | 9.1 | 1.7 | 9 | 54.5
1988 | 4 | 11.6 | 3.8 | 5 | 26
1988 | 5 | 14.8 | 5.9 | 0 | 58
1988 | 6 | 18.4 | 9.4 | 0 | 16.2
1988 | 7 | 17.9 | 10.4 | 0 | 115.1
1988 | 8 | 19.3 | 10.2 | 0 | 46
1988 | 9 | 16.6 | 8.5 | 0 | 44.3
1988 | 10 | 13 | 6.7 | 3 | 75.8
1988 | 11 | 9 | 2 | 6 | 64.7
1988 | 12 | 10.1 | 4.4 | 0 | 27.9
1989 | 1 | 9.5 | 3.1 | 2 | 7.2
1989 | 2 | 8.6 | 2.1 | 9 | 47.6
1989 | 3 | 10.8 | 2.2 | 7 | 20.7
1989 | 4 | 9.7 | 2.3 | 5 | 50.3
1989 | 5 | 16.5 | 6.3 | 0 | 7.7
1989 | 6 | 19 | 8 | 0 | 52.1
1989 | 7 | 22.5 | 11.2 | 0 | 10.1
1989 | 8 | 20.2 | 10.7 | 0 | 61.5
1989 | 9 | 18 | 8.7 | 0 | 11.7
1989 | 10 | 14.7 | 6.9 | 0 | 48.5
1989 | 11 | 9.2 | 2.9 | 7 | 34.8
1989 | 12 | 6.6 | 0.5 | 11 | 63.7
1990 | 1 | 8.7 | 2.1 | 6 | 72.6
1990 | 2 | 9.6 | 3.1 | 5 | 60.4
1990 | 3 | 12.1 | 4.2 | 4 | 14.1
1990 | 4 | 12.7 | 2.3 | 6 | 10.1
1990 | 5 | 16.6 | 5.8 | 0 | 42.1
1990 | 6 | 17.3 | 8.1 | 0 | 46.3
1990 | 7 | 20.6 | 9.7 | 0 | 30.9
1990 | 8 | 22.3 | 11.8 | 0 | 52.8
1990 | 9 | 16.5 | 7.7 | 0 | 43.2
1990 | 10 | 13.8 | 7.8 | 0 | 78.7
1990 | 11 | 9.2 | 3.5 | 4 | 53.1
1990 | 12 | 7.2 | 1.6 | 4 | 93.3
1991 | 1 | 5.5 | -0.9 | 20 | 47.1
1991 | 2 | 4.9 | -0.8 | 20 | 80
1991 | 3 | 10.8 | 3.6 | 2 | 60.8
1991 | 4 | 11.1 | 3.1 | 4 | 27.7
1991 | 5 | 14.4 | 6.2 | 0 | 19.3
1991 | 6 | 15.7 | 6.8 | 1 | 53.9
1991 | 7 | 21 | 11.4 | 0 | 43.9
1991 | 8 | 21.3 | 11.1 | 0 | 21.2
1991 | 9 | 18.1 | 7.5 | 1 | 24.3
1991 | 10 | 12.6 | 5.8 | 1 | 50
1991 | 11 | 9.1 | 1.6 | 8 | 60
1991 | 12 | 7.8 | -0.1 | 14 | 44.6
1992 | 1 | 7.1 | 0 | 15 | 22.7
1992 | 2 | 9.1 | 1.7 | 8 | 34
1992 | 3 | 10.4 | 3 | 3 | 62.7
1992 | 4 | 11.9 | 4.1 | 2 | 95
1992 | 5 | 16.6 | 6.6 | 1 | 19
1992 | 6 | 19.7 | 9.5 | 0 | 20.2
1992 | 7 | 19.6 | 10.7 | 0 | 54.1
1992 | 8 | 18.8 | 9.8 | 0 | 68.8
1992 | 9 | 15.7 | 8.5 | 0 | 97.7
1992 | 10 | 10.5 | 3.2 | 7 | 61
1992 | 11 | 9.8 | 2.4 | 6 | 60.9
1992 | 12 | 5.9 | 0 | 16 | 44.7
1993 | 1 | 8.3 | 1.1 | 10 | 40.1
1993 | 2 | 8.2 | 2.1 | 7 | 15.6
1993 | 3 | 10.1 | 1.8 | 8 | 10.1
1993 | 4 | 11.8 | 4.4 | 2 | 94.9
1993 | 5 | 14.3 | 5.8 | 0 | 92.7
1993 | 6 | 18.1 | 8.9 | 0 | 31.4
1993 | 7 | 18.6 | 10.2 | 0 | 42
1993 | 8 | 18.6 | 9.1 | 0 | 89.4
1993 | 9 | 15.2 | 7.7 | 0 | 117.6
1993 | 10 | 11 | 4.2 | 5 | 73.6
1993 | 11 | 5.9 | 0.7 | 12 | 64.6
1993 | 12 | 6.3 | 1 | 15 | 77.7
1994 | 1 | 6.5 | 1 | 12 | 70.8
1994 | 2 | 4.7 | -1.3 | 15 | 53.4
1994 | 3 | 10 | 3 | 3 | 31.7
1994 | 4 | 11 | 3.4 | 4 | 37.8
1994 | 5 | 12.9 | 5 | 1 | 45.9
1994 | 6 | 17.7 | 9 | 0 | 22.2
1994 | 7 | 21.3 | 10.6 | 0 | 44.2
1994 | 8 | 18.4 | 10 | 0 | 49.1
1994 | 9 | 15.3 | 7.6 | 0 | 69.2
1994 | 10 | 12.6 | 5 | 1 | 58.7
1994 | 11 | 11.5 | 5.2 | 2 | 61.9
1994 | 12 | 8.1 | 2.4 | 7 | 66.7
1995 | 1 | 5.9 | 0.3 | 14 | 75.2
1995 | 2 | 8.3 | 2.6 | 4 | 62.1
1995 | 3 | 8.1 | 0.9 | 14 | 39.5
1995 | 4 | 12.3 | 3.6 | 8 | 27.5
1995 | 5 | 15.3 | 5.8 | 2 | 31.2
1995 | 6 | 17.3 | 8.3 | 0 | 16.2
1995 | 7 | 21.6 | 11.7 | 0 | 24.5
1995 | 8 | 23.1 | 11.3 | 0 | 14.2
1995 | 9 | 16.7 | 8.7 | 0 | 86.2
1995 | 10 | 15.6 | 8 | 2 | 25.2
1995 | 11 | 10 | 4 | 5 | 116.1
1995 | 12 | 4.5 | -0.9 | 15 | 87.6
1996 | 1 | 5.1 | 1.9 | 5 | 29.9
1996 | 2 | 5.7 | -0.7 | 19 | 66.7
1996 | 3 | 5.4 | 1.2 | 9 | 25.9
1996 | 4 | 11.5 | 3.7 | 8 | 33.8
1996 | 5 | 12.6 | 3.9 | 3 | 36
1996 | 6 | 18.2 | 7.9 | 0 | 8.6
1996 | 7 | 20.1 | 10.2 | 0 | 46.8
1996 | 8 | 20.7 | 10.6 | 0 | 71.8
1996 | 9 | 16.4 | 8.8 | 0 | 24.6
1996 | 10 | 14.3 | 6.9 | 0 | 36.3
1996 | 11 | 7.9 | 1.8 | 13 | 77.3
1996 | 12 | 5.1 | 0.4 | 13 | 62.5
1997 | 1 | 5.3 | -0.3 | 19 | 13.8
1997 | 2 | 9 | 2.2 | 3 | 71.6
1997 | 3 | 11.8 | 3.9 | 4 | 12.4
1997 | 4 | 12.7 | 4.1 | 4 | 5.8
1997 | 5 | 14.6 | 4.9 | 4 | 54.5
1997 | 6 | 16 | 9 | 0 | 174.4
1997 | 7 | 20.8 | 11.1 | 0 | 67
1997 | 8 | 22 | 12.3 | 0 | 48.1
1997 | 9 | 17.2 | 8 | 0 | 11.3
1997 | 10 | 13.1 | 5.4 | 3 | 31.7
1997 | 11 | 10.2 | 5 | 2 | 68.2
1997 | 12 | 7.9 | 2.7 | 4 | 82.8
1998 | 1 | 6.8 | 1.4 | 6 | 92
1998 | 2 | 10.9 | 4.3 | 5 | 6.1
1998 | 3 | 11 | 3.1 | 7 | 59.3
1998 | 4 | 10.6 | 3.4 | 5 | 151
1998 | 5 | 16.3 | 7.3 | 0 | 71.8
1998 | 6 | 16.8 | 9.1 | 0 | 97.8
1998 | 7 | 18.5 | 10.5 | 0 | 52.6
1998 | 8 | 18.7 | 11 | 0 | 44.9
1998 | 9 | 16.7 | 10.3 | 0 | 53.4
1998 | 10 | 12.8 | 5.9 | 1 | 96.9
1998 | 11 | 8.3 | 1.7 | 6 | 64.9
1998 | 12 | 7.8 | 1.5 | 8 | 27.3
1999 | 1 | 7.7 | 1.6 | 6 | 57.5
1999 | 2 | 8.2 | 1.4 | 10 | 15.6
1999 | 3 | 9.9 | 3.1 | 2 | 92.7
1999 | 4 | 12.6 | 4 | 6 | 42.5
1999 | 5 | 15.8 | 7.6 | 0 | 50.2
1999 | 6 | 16.7 | 8.3 | 0 | 67.2
1999 | 7 | 20.8 | 11.5 | 0 | 12.1
1999 | 8 | 19 | 10.8 | 0 | 81.3
1999 | 9 | 19.6 | 10.2 | 0 | 52
1999 | 10 | 13.6* | 6.1* | 1* | 42.6*
1999 | 11 | 10.3* | 4.3* | 3* | 46.8*
1999 | 12 | 6.3 | 0.7 | 13 | 64.1*
2000 | 1 | 7.9 | 1.9 | 6 | 35.1*
2000 | 2 | 8.7 | 2.4 | 6 | 29.5*
2000 | 3 | 10.8 | 3.6 | 4 | 21
2000 | 4 | 11 | 3.4 | 5 | 149.8
2000 | 5 | 15.2 | 6.5 | 0 | 46
2000 | 6 | 17.2 | 9.4 | 0 | 89.4
2000 | 7 | 17.8 | 10.4 | 0 | 49.4
2000 | 8 | 20.2 | 10.9 | 0 | 43.8
2000 | 9 | 17.3 | 9.7 | 0 | 84.2
2000 | 10 | 13 | 6 | 1 | 119.2
2000 | 11 | 8.8 | 3.4 | 0 | 148.4
2000 | 12 | 6.8 | 2.3 | 11 | 72.4
2001 | 1 | 5.7 | 0.1 | 15 | 46.2
2001 | 2 | 7.4 | -0.4 | 16 | 103.6
2001 | 3 | 7.5 | 0.1 | 11 | 43.4
2001 | 4 | 10.5 | 3 | 3 | 59.8
2001 | 5 | 16.7 | 6.4 | 0 | 15
2001 | 6 | 16.8 | 8.9 | 0 | 38.2
2001 | 7 | 20.1 | 12 | 0 | 13.2
2001 | 8 | 20.3 | 11.7 | 0 | 76.3*
2001 | 9 | 16 | 9.7 | 0 | 74.7*
2001 | 10 | 15.7 | 9.9 | 0 | 77.1*
2001 | 11 | 11 | 4.2 | 3 | 35.8
2001 | 12 | 6 | 0.3 | 17 | 54.4
2002 | 1 | 7.5 | 1.5 | 12 | 37
2002 | 2 | 9.3 | 2.8 | 4 | 83.6
2002 | 3 | 11.1 | 2.8 | 4 | 37.4
2002 | 4 | 13.3 | 4.1 | 4 | 19.4
2002 | 5 | 15.1 | 7.6 | 0 | 53
2002 | 6 | 17.5 | 9.9 | 0 | 47
2002 | 7 | 19.3 | 10.6 | 0 | 79.6
2002 | 8 | 20.5 | 12.7 | 0 | 91.2
2002 | 9 | 17.4 | 9.5 | 0 | 25.2
2002 | 10 | 12.4 | 5.4 | 3 | 86
2002 | 11 | 9.6 | 4.6 | 1 | 83.8
2002 | 12 | 6.4 | 3.5 | 4 | 92.2
2003 | 1 | 7 | 2.2 | 9 | 62
2003 | 2 | 6.8 | -0.7 | 17 | 18
2003 | 3 | 12.1 | 2 | 8 | 17.6
2003 | 4 | 14 | 4.3 | 5 | 24
2003 | 5 | 15.8 | 7.7 | 0 | 44.4
2003 | 6 | 19.6 | 10.9 | 0 | 61
2003 | 7 | 20.4 | 12.8 | 0 | 50.4
2003 | 8 | 21 | 12.2 | 0 | 15.9
2003 | 9 | 18.3 | 8.9 | 0 | 41.1
2003 | 10 | 12.8 | 5 | 2 | 41.5*
2003 | 11 | 10.5 | 4.4 | 4 | 45.7*
2003 | 12 | 7.7 | 0.9 | 14 | 65
2004 | 1 | 7.6 | 2.4 | 7 | 97
2004 | 2 | 8.8 | 3 | 8 | 29
2004 | 3 | 10.4 | 2.9 | 4 | 24.5
2004 | 4 | 13.1 | 5.9 | 1 | 54.4
2004 | 5 | 16.5* | 6.2* | 0* | 21.8
2004 | 6 | 18.7 | 10.1 | 0 | 67.6
2004 | 7 | 19.1 | 10.9 | 0 | 62.8
2004 | 8 | 20 | 12.5 | 0 | 155.8
2004 | 9 | 17.6 | 9.7 | 0 | 19.8
2004 | 10 | 12.6 | 6.6 | 0 | 120.2
2004 | 11 | 10 | 4.3 | 6 | 18.2
2004 | 12 | 8.3 | 1.7 | 10 | 19.8 | 690.9
2005 | 1 | 8.4 | 2.7 | 6 | 35.6
2005 | 2 | 6.9 | 1.3 | 9 | 41.5
2005 | 3 | 9.7 | 3.7 | 6 | 44.8
2005 | 4 | 11.7 | 4.1 | 1 | 82
2005 | 5 | 14.9 | 6.2 | 1 | 20.4
2005 | 6 | 18.6 | 10 | 0 | 36.2
2005 | 7 | 19.7 | 11.7 | 0 | 72.6
2005 | 8 | 20.2* | 10.5* | 0* | 38
2005 | 9 | 18.7* | 9.7* | 0* | 63.8
2005 | 10 | 14.6 | 8.9 | 0 | 74.6
2005 | 11 | 9.4 | 2.4 | 11 | 71.6
2005 | 12 | 7.3 | 1.2 | 10 | 37.8 | 618.9
2006 | 1 | 6.3 | 1.3 | 9 | 20.6
2006 | 2 | 7 | 1.1 | 9 | 44.2
2006 | 3 | 6.7 | 0.8 | 14 | 79.2
2006 | 4 | 12 | 3.9 | 3 | 24
2006 | 5 | 15.1 | 6.3 | 1 | 84.4
2006 | 6 | 19.7 | 9.9 | 0 | 13
2006 | 7 | 24.2 | 12.4 | 0 | 10
2006 | 8 | 19.2 | 11.5 | 0 | 57.4
2006 | 9 | 20 | 11.8 | 0 | 35
2006 | 10 | 15.5 | 8.6 | 0 | 53.2
2006 | 11 | 11 | 4.5 | 1 | 125.5
2006 | 12 | 7.6 | 2.2 | 9 | 77.4 | 623.9
2007 | 1 | 9.5 | 3.1 | 5 | 56.2
2007 | 2 | 8.5 | 2.1 | 8 | 70
2007 | 3 | 10.2 | 3.3 | 4 | 20.8
2007 | 4 | 15.4 | 6 | 0 | 11.4
2007 | 5 | 14.8 | 6.9 | 0 | 50
2007 | 6 | 17.4 | 9.9 | 0 | 118.8
2007 | 7 | 19 | 10.9 | 0 | 100.2
2007 | 8 | 19.2 | 10.6 | 0 | 30.6
2007 | 9 | 17.4 | 8.8 | 0 | 39.4
2007 | 10 | 14.2 | 6.1 | 3 | 13
2007 | 11 | 10.4 | 3.9 | 3 | 61.2
2007 | 12 | 6.5 | 1.1 | 14 | 52.6 | 624.2
2008 | 1 | 7.9 | 2.8 | 7 | 113.2
2008 | 2 | 8.9 | 0.7 | 11 | 13.4
2008 | 3 | 9.1 | 1.9 | 7 | 38.4
2008 | 4 | 11.2 | 3.3 | 4 | 84
2008 | 5 | 15.7 | 7.1 | 1 | 21.2
2008 | 6 | 17.8 | 9.1 | 0 | 77
2008 | 7 | 20.1 | 11.4 | 0 | 134
2008 | 8 | 19.1 | 12.2 | 0 | 95.4
2008 | 9 | 16.6 | 9.6 | 0 | 97.7
2008 | 10 | 12.8 | 5.2 | 2 | 45.2
2008 | 11 | 9 | 3.7 | 6 | 40.8
2008 | 12 | 6.4 | 0.6 | 12 | 57 | 817.3
2009 | 1 | 6 | 0.4 | 11 | 39.4
2009 | 2 | 7.6 | 2 | 12 | 35.6
2009 | 3 | 11 | 3 | 4 | 21.2
2009 | 4 | 13.7 | 4.3 | 1 | 36.8
2009 | 5 | 16 | 6.8 | 0 | 38.2
2009 | 6 | 17.9 | 8.9 | 0 | 77.8
2009 | 7 | 19.7 | 11.4 | 0 | 168.8
2009 | 8 | 20.1 | 12.1 | 0 | 37.2
2009 | 9 | 17.9 | 9.5 | 0 | 14.4
2009 | 10 | 14 | 7.1 | 0 | 46.2
2009 | 11 | 10.4 | 4.7 | 0 | 146.6
2009 | 12 | 5.1 | -0.5 | 16 | 80.8 | 743
2010 | 1 | 3.5 | -1.1 | 16 | 59.8
2010 | 2 | 4.6 | -1 | 20 | 67.6
2010 | 3 | 9.7 | 2 | 10 | 68.2
2010 | 4 | 13.5 | 4.1 | 2 | 12.4
2010 | 5 | 15 | 5.2 | 3 | 24
2010 | 6 | 19.4 | 9.5 | 0 | 56
2010 | 7 | 20.3 | 12.1 | 0 | 62
2010 | 8 | 19.1 | 10.1 | 0 | 44.8
2010 | 9 | 17.9 | 9.8 | 0 | 75.8
2010 | 10 | 13 | 6.4 | 1 | 62.2
2010 | 11 | 7.6 | 2 | 9 | 157.3
2010 | 12 | 2.7 | -3.4 | 21 | 40.7 | 730.8
2011 | 1 | 6.3 | 0.5 | 13 | 36
2011 | 2 | 8.4 | 2.8 | 2 | 58.2
2011 | 3 | 10.5 | 2.1 | 8 | 24.8
2011 | 4 | 16.5 | 5.9 | 1 | 7.2
2011 | 5 | 16 | 7.4 | 1 | 40
2011 | 6 | 18.6 | 8.8 | 0 | 48.4
2011 | 7 | 19.5 | 9.7 | 0 | 65.6
2011 | 8 | 18.6 | 10.6 | 0 | 125
2011 | 9 | 18.1 | 10.2 | 0 | 28.4
2011 | 10 | 14.6 | 8.2 | 0 | 53.8
2011 | 11 | 11.4 | 6 | 2 | 27.2
2011 | 12 | 7.5 | 2.3 | 6 | 51.6 | 566.2
2012 | 1 | 7.7 | 1.5 | 8 | 30.4
2012 | 2 | 8.1 | 1.8 | 11 | 10.2
2012 | 3 | 13.7 | 3.6 | 3 | 15
2012 | 4 | 10.8 | 2.9 | 4 | 134.4
2012 | 5 | 15.2 | 5.9 | 1 | 66.2
2012 | 6 | 16.1 | 8.7 | 0 | 136.6
2012 | 7 | 18.3 | 10.9 | 0 | 98
2012 | 8 | 19.9 | 11.3 | 0 | 103.4
2012 | 9 | 16.8 | 8.7 | 0 | 116.2
2012 | 10 | 12.4 | 4.4 | 2 | 83.6
2012 | 11 | 9.2 | 2.9 | 6 | 124.8
2012 | 12 | 6.6 | 1.1 | 10 | 99.2 | 1018
2013 | 1 | 5.5 | 0.8 | 13 | 80.9
2013 | 2 | 6 | 0.2 | 13 | 27.2
2013 | 3 | 4.9 | -0.2 | 15 | 59.4
2013 | 4 | 10.9 | 3.3 | 3 | 22.8
2013 | 5 | 15 | 5.8 | 0 | 100.8
2013 | 6 | 18.1 | 8.9 | 0 | 23
2013 | 7 | 23.2 | 12.8 | 0 | 52.8
2013 | 8 | 20.6 | 11.9 | 0 | 71.2
2013 | 9 | 17.1 | 8.8 | 0 | 84.6
2013 | 10 | 14.4 | 8.8 | 0 | 100.2
2013 | 11 | 9.2 | 2.3 | 5 | 54
2013 | 12 | 8.8 | 3.1 | 3 | 65.4 | 742.3
2014 | 1 | 7.1 | 2.3 | 6 | 91.2
2014 | 2 | 8.3 | 2.8 | 2 | 61.2
2014 | 3 | 10.9 | 3.2 | 6 | 33
2014 | 4 | 13.4 | 5.7 | 2 | 56
2014 | 5 | 15.6 | 7.7 | 1 | 78
2014 | 6 | 19 | 10.3 | 0 | 47.2
2014 | 7 | 21.8 | 11.5 | 0 | 54.4
2014 | 8 | 18.6 | 10.2 | 0 | 79.4
2014 | 9 | 18.2 | 9.9 | 0 | 15.8
2014 | 10 | 14.9 | 7.8 | 0 | 51
2014 | 11 | 10.5 | 4.9 | 2 | 63.6
2014 | 12 | 8.1 | 1.9 | 11 | 27 | 657.8
2015 | 1 | 6.7 | 1.5 | 10 | 49.4
2015 | 2 | 7.7 | 1 | 10 | 15.4
2015 | 3 | 10 | 2.2 | 6 | 39.8
2015 | 4 | 13.7 | 3.4 | 2 | 21
2015 | 5 | 14.4 | 6 | 1 | 70.6
2015 | 6 | 17.8 | 8 | 0 | 28.4
2015 | 7 | 19.1 | 10.5 | 0 | 86.2
2015 | 8 | 19.4 | 11.1 | 0 | 81
2015 | 9 | 16.7 | 7.6 | 0 | 38
2015 | 10 | 14.2 | 6.2 | 0 | 69.8
2015 | 11 | 11.4 | 5.7 | 1 | 104.4
2015 | 12 | 10.9 | 5 | 2 | 120.2 | 724.2
2016 | 1 | 7.2 | 2.2 | 10 | 116.6
2016 | 2 | 7.9 | 0.8 | 13 | 30.2
2016 | 3 | 9.7 | 2.3 | 5 | 52.4
2016 | 4 | 10.9 | 2.9 | 2 | 83.2
2016 | 5 | 15.5 | 7 | 0 | 39
2016 | 6 | 17.7 | 9.4 | 0 | 49.8
2016 | 7 | 20.2 | 12.1 | 0 | 34.6
2016 | 8 | 20.2 | 12 | 0 | 69.8
2016 | 9 | 19.2 | 11.3 | 0 | 35.6
2016 | 10 | 13.8 | 6.8 | 0 | 52.2
2016 | 11 | 8.2 | 1.7 | 8 | 86
2016 | 12 | 9 | 3.1 | 5 | 46.4 | 695.8
2017 | 1 | 6.5 | 0.7 | 16 | 33.2
2017 | 2 | 8.7* | 2.7* | 5* | 57
2017 | 3 | 11.7 | 4.1 | 3 | 42.4
2017 | 4 | 13.6 | 4.3 | 3 | 29
2017 | 5 | 17.3 | 8 | 0 | 19.8
2017 | 6 | 19 | 11.1 | 0 | 103.4
2017 | 7 | 19.2 | 11.1 | 0 | 71.2
2017 | 8 | 19.1 | 10.9 | 0 | 49
2017 | 9 | 16.8 | 9.3 | 0 | 89.4
2017 | 10 | 15.3 | 8.9 | 0 | 29
2017 | 11 | 9.5 | 2.9 | 3 | 85.6
2017 | 12 | 7.4 | 1.4 | 14 | 25.4 | 634.4
2018 | 1 | 6.7 | 1.6 | 8 | 55
2018 | 2 | 5.5 | -0.2 | 18 | 51
2018 | 3 | 7.3 | 0.9 | 12 | 76.4
2018 | 4 | 12.7* | 5.1* | 2* | 75
2018 | 5 | 18.2* | 7.1* | 1* | 25.3*
2018 | 6 | 19.9 | 9.6 | 0 | 31.2
2018 | 7 | 23.4* | 12.1* | 0* | 48.2
2018 | 8 | 20.2 | 12.1 | 0 | 49.8
2018 | 9 | 17.6 | 9.1 | 0 | 46.8
2018 | 10 | 14.2 | 5.9 | 2 | 53.4
2018 | 11 | 10.2 | 5 | 1 | 56.4
2018 | 12 | 8.6 | 2.5 | 5 | 43.8 | 587
2019 | 1 | 7.2 | 1.2 | 13 | 15
2019 | 2 | 10.6 | 2.2 | 6 | 27.6
2019 | 3 | 11.1 | 3.8 | 1 | 52.8
2019 | 4 | 12.9 | 3.5 | 4 | 30.2
2019 | 5 | 15.3 | 6 | 1 | 37.2
2019 | 6 | 17.5 | 9.4 | 0 | 108.4
2019 | 7 | 21.6 | 12.8 | 0 | 70.2
2019 | 8 | 20.4 | 12.5 | 0 | 81.2
2019 | 9 | 17.6 | 9.1 | 0 | 84.2
2019 | 10 | 12 | 5.8 | 0 | 88.4
2019 | 11 | 8.1 | 3.2 | 7 | 106.6
2019 | 12 | 8 | 2.8 | 7 | 29 | 730.8

## NPV RWHS DB theoretical
Initial investment | £ |  | 11270
Discount rate |  |  | 0.045 | BoE 2004
Inflation rate |  |  | 0.013 | CPI 2004
Theoretical annual water harvest | m3 per year |  | 443.744
Water and sewage charges | £ per m3 |  | 1.0989 | Back calculate from 2014 to 2004 using water supply inflation |  |  |  |  | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/l53b/mm23
Pumping energy demand | kWh/m3 |  | 2
Price of electricity | £/kWh |  | 0.04584 | Commercial price medium enterprise 2004 BEIS |  |  |  | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Year
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
Costs |  |  |  | -11270 | -40.6824 | -41.2113 | -41.7471 | -42.2898 | -42.8395 | -43.3965 | -43.9606 | -44.5321 | -45.111 | -45.6975 | -46.2915 | -46.8933 | -47.5029 | -48.1205 | -48.746 | -49.3797 | -50.0217 | -50.672 | -51.3307 | -51.998 | -52.674 | -53.3587 | -54.0524 | -54.7551 | -55.4669 | -56.188 | -56.9184 | -57.6583 | -58.4079 | -59.1672 | -59.9364 | -60.7155 | -61.5048 | -62.3044 | -63.1144 | -63.9349 | -64.766 | -65.608 | -66.4609 | -67.3249 | -68.2001 | -69.0867 | -69.9848 | -70.8946 | -71.8162 | -72.7499 | -73.6956 | -74.6536 | -75.6241 | -76.6073 | -77.6032 | -78.612 | -79.6339 | -80.6692 | -81.7179 | -82.7802 | -83.8564 | -84.9465 | -86.0508 | -87.1695
Savings |  |  |  |  | 487.6448 | 493.9842 | 500.406 | 506.9113 | 513.5011 | 520.1767 | 526.939 | 533.7892 | 540.7284 | 547.7579 | 554.8787 | 562.0922 | 569.3994 | 576.8016 | 584.3 | 591.8959 | 599.5905 | 607.3852 | 615.2812 | 623.2799 | 631.3825 | 639.5905 | 647.9051 | 656.3279 | 664.8602 | 673.5034 | 682.2589 | 691.1283 | 700.1129 | 709.2144 | 718.4342 | 727.7738 | 737.2349 | 746.8189 | 756.5276 | 766.3625 | 776.3252 | 786.4174 | 796.6408 | 806.9971 | 817.4881 | 828.1155 | 838.881 | 849.7864 | 860.8336 | 872.0245 | 883.3608 | 894.8445 | 906.4775 | 918.2617 | 930.1991 | 942.2917 | 954.5414 | 966.9505 | 979.5208 | 992.2546 | 1005.1539 | 1018.2209 | 1031.4578 | 1044.8667
Net savings (minus costs) | £ |  |  | -11270 | 446.9624 | 452.7729 | 458.6589 | 464.6215 | 470.6616 | 476.7802 | 482.9783 | 489.2571 | 495.6174 | 502.0604 | 508.5872 | 515.1988 | 521.8964 | 528.6811 | 535.5539 | 542.5161 | 549.5688 | 556.7132 | 563.9505 | 571.2819 | 578.7085 | 586.2317 | 593.8528 | 601.5728 | 609.3933 | 617.3154 | 625.3405 | 633.4699 | 641.705 | 650.0472 | 658.4978 | 667.0583 | 675.73 | 684.5145 | 693.4132 | 702.4276 | 711.5592 | 720.8094 | 730.1799 | 739.6723 | 749.288 | 759.0288 | 768.8961 | 778.8918 | 789.0174 | 799.2746 | 809.6652 | 820.1908 | 830.8533 | 841.6544 | 852.5959 | 863.6797 | 874.9075 | 886.2813 | 897.803 | 909.4744 | 921.2976 | 933.2744 | 945.407 | 957.6973
|  | Year | NPV
£
|  | 0 | -11270
|  | 1 | -10842.2848
|  | 2 | -10427.6671
|  | 3 | -10025.7458
|  | 4 | -9636.1322
|  | 5 | -9258.4493
|  | 6 | -8892.3318
|  | 7 | -8537.4256
|  | 8 | -8193.3873
|  | 9 | -7859.8842
|  | 10 | -7536.5935
|  | 11 | -7223.2028
|  | 12 | -6919.4086
|  | 13 | -6624.9173
|  | 14 | -6339.4438
|  | 15 | -6062.7122
|  | 16 | -5794.4546
|  | 17 | -5534.4116
|  | 18 | -5282.3316
|  | 19 | -5037.9708
|  | 20 | -4801.0929
|  | 21 | -4571.4686
|  | 22 | -4348.8759
|  | 23 | -4133.0994
|  | 24 | -3923.9305
|  | 25 | -3721.1667
|  | 26 | -3524.6119
|  | 27 | -3334.0761
|  | 28 | -3149.3748
|  | 29 | -2970.3295
|  | 30 | -2796.7668
|  | 31 | -2628.5191
|  | 32 | -2465.4234
|  | 33 | -2307.322
|  | 34 | -2154.062
|  | 35 | -2005.4951
|  | 36 | -1861.4777
|  | 37 | -1721.8703
|  | 38 | -1586.5381
|  | 39 | -1455.3499
|  | 40 | -1328.179
|  | 41 | -1204.9024
|  | 42 | -1085.4007
|  | 43 | -969.5584
|  | 44 | -857.2634
|  | 45 | -748.4071
|  | 46 | -642.8842
|  | 47 | -540.5926
|  | 48 | -441.4335
|  | 49 | -345.3107
|  | 50 | -252.1315
|  | 51 | -161.8055
|  | 52 | -74.2456
|  | 53 | 10.6331
|  | 54 | 92.9127
|  | 55 | 172.6727
|  | 56 | 249.9902
|  | 57 | 324.9402
|  | 58 | 397.595
|  | 59 | 468.025
|  | 60 | 536.2983

## NPV RWHS DB real
Initial investment | £ |  | 11270
Discount rate |  |  | 0.045 | BoE 2004
Inflation rate |  |  | 0.013 | CPI 2004
Theoretical annual water harvest | m3 per year |  | 443.744
Water and sewage charges | £ per m3 |  | 1.0989 | Back calculate from 2014 to 2004 using water supply inflation
Repair of pumps 2010 | £ |  | 10872
Bird netting 2010 | £ per m2 |  | 100 | Assumption: 20 m2
Storage tank cleaning 2017 | £ |  | 1620 | Neglected solid disposal costs, assume can be done in a day
Header tank cleaning and disinfection 2016, 2019, 2020 | £ each |  | 250
Header tank replacement | £ |  | 3960
Maintenance contract 2010-2014 | £ |  | 749.6
Maintenance contract 2015-2018 | £ |  | 832.14
Maintenance contract 2019 | £ |  | 1277.8
Pumping energy demand | kWh/m3 |  | 2 | Based on typical RWHS demand, https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/291745/scho0610bsmq-e-e.pdf
Price of electricity | £/kWh |  | 0.04584 | Based on 2004 commercial rate, assume inflation with CPI
Rainwater harvest 2004 | m3 per year |  | 348 | Assuming system worked initially to full potential
Rainwater harvest 2005-2009 | m3 per year |  | 0 | Average over 6 years based on meter reading
Rainwater harvest 2010-2014 | m3 per year |  | 423.7647 | Average over 5 years based on meter reading
Rainwater harvest 2015 | m3 per year |  | 423.7647 | Assume continuing performance as in 2010-2014
Rainwater harvest 2016 | m3 per year |  | 250.4118 | Assume continuing performance as in 2010-2014 until breakdown
Rainwater harvest 2017-2019 | m3 per year |  | 0 | Average over 5 years based on meter reading
|  |  |  | Water price inflation | 60.4 | 67.4 | 72.4 | 76.8 | 81.3 | 85.1 | 87.4 | 90.9 | 95.5 | 98.9 | 100.9 | 100 | 100.2 | 101.5 | 103.5 | 106.2 | 105.6
|  |  |  | Electricity price | 0.04584 | 0.05904 | 0.07788 | 0.08064 | 0.09168 | 0.10248 | 0.09012 | 0.09492 | 0.10308 | 0.11004 | 0.11544 | 0.12048 | 0.12012 | 0.12588 | 0.13836 | 0.15072 | 0.15864
|  |  |  | Year | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Costs electricity |  |  |  | -11270 | -31.9046 | 0 | 0 | 0 | 0 | 0 | -76.3794 | -80.4475 | -87.3633 | -93.2621 | -97.8388 | -102.1103 | -60.1589 | 0 | 0 | 0
Costs external maintenance service |  |  |  | 7: -749.6; 8: -749.6; 9: -749.6; 10: -749.6; 11: -749.6; 12: -832.14; 13: -832.14; 14: -832.14; 15: -832.14; 16: -1277.8
Cost of repairs |  |  |  | 7: -12872; 13: -250; 14: -1620; 15: -3960; 16: -250
Savings |  |  |  |  | 382.4286 | 0 | 0 | 0 | 0 | 0 | 673.8611 | 700.8464 | 736.3128 | 762.5271 | 777.9472 | 771.0082 | 456.5167 | 0 | 0 | 0
Net savings (minus costs) | £ |  |  | -11270 | 350.524 | 0 | 0 | 0 | 0 | 0 | -13024.1182 | -129.2011 | -100.6505 | -80.3351 | -69.4915 | -163.2422 | -685.7822 | -2452.14 | -4792.14 | -1527.8
|  | Year | NPV
£
|  | 0 | -11270
|  | 1 | -10934.5704
|  | 2 | -10934.5704
|  | 3 | -10934.5704
|  | 4 | -10934.5704
|  | 5 | -10934.5704
|  | 6 | -10934.5704
|  | 7 | -20505.0631
|  | 8 | -20595.9153
|  | 9 | -20663.6435
|  | 10 | -20715.3735
|  | 11 | -20758.1941
|  | 12 | -20854.4521
|  | 13 | -21241.4196
|  | 14 | -22565.5086
|  | 15 | -25041.7053
|  | 16 | -25797.1555
17
18
19
20
21

## Propelair toilets
|  | Conventional | Propelair | Total | # URBAN OBSERVATORY (http://www.urbanobservatory.ac.uk/)
Toilets USB groundfloor |  | 14 |  | 14 | # Licence info: http://www.urbanobservatory.ac.uk/licence/
Toilets First-4th floor |  | 9 | 1 | 10 | # Entity: Urban Sciences Building: Floor 2
Toilets 5-6th floor |  | 6 | 1 | 7 | # Metric: Propelair WC
# Entity ID: a1904ba6-6d62-4e79-bf0f-d12532d46d77
Total |  | 62 | 6 | 68 | # Feed ID: 93bf4738-f71e-4b58-965d-e811444980e9
# Timeseries ID: 0e912f04-3c45-4fb0-a357-3bf9ddf875f3
Water use per flush | liters | 5 | 1.5 |  | # Units: no units
Flushes per day and toilet |  | 12.6451 | 3.2963 |  | # Stored in database as: Real
Flushes per day |  | 783.9983 | 19.7778 | 803.7761 | time (ISO8601) | date (UTC) | time (UTC) | value | duration / observation window
Cat water use per day | liters | 3919.9914 | 29.6667 | 3949.658 | 2018-06-25T17:01:01.001Z | 2018-06-25 | 17:01 | 0 | -3.335
[5 empty] | 2018-06-25T16:50:37.948Z | 2018-06-25 | 16:51 | 1 | -3.582
Theoretical flushes per day | liters | 732.8546 | 70.9214 | 803.7761 | 2018-06-25T09:30:57.857Z | 2018-06-25 | 9:31 | 0 | -3.731
[5 empty] | 2018-06-25T09:16:42.309Z | 2018-06-25 | 9:17 | 1 | -4.295
Actual Cat water use savings per day | liters |  | 69.2222 |  | 2018-06-21T12:00:42.938Z | 2018-06-21 | 12:01 | 0 | -3.296
Theoretical Cat water use savings per day | liters |  | 248.225 |  | 2018-06-21T11:59:02.488Z | 2018-06-21 | 11:59 | 1 | -4.155
[5 empty] | 2018-06-20T13:00:27.543Z | 2018-06-20 | 13:00 | 0 | -3.361
Actual to theoretical savings | % |  | 27.8869 |  | 2018-06-20T12:53:06.362Z | 2018-06-20 | 12:53 | 1 | -4.324
[5 empty] | 2018-06-19T09:31:00.541Z | 2018-06-19 | 9:31 | 0 | -4.68
Predicted savings building opening to April 2021 | m3 | 320.2102 |  |  | 2018-06-19T09:29:03.905Z | 2018-06-19 | 9:29 | 1 | -4.366
Actual savings building opening to April 2021 | m3 | 89.2967 |  |  | 2018-06-18T13:00:53.303Z | 2018-06-18 | 13:01 | 0 | -3.787
[5 empty] | 2018-06-18T12:55:15.650Z | 2018-06-18 | 12:55 | 1 | -4.654
[5 empty] | 2018-06-15T11:00:40.122Z | 2018-06-15 | 11:01 | 0 | -4.494
[5 empty] | 2018-06-15T10:58:47.544Z | 2018-06-15 | 10:59 | 1 | -4.356
[5 empty] | 2018-06-14T15:30:44.262Z | 2018-06-14 | 15:31 | 0 | -3.415
[5 empty] | 2018-06-14T15:25:54.303Z | 2018-06-14 | 15:26 | 1 | -3.452
[5 empty] | 2018-06-13T10:00:20.568Z | 2018-06-13 | 10:00 | 0 | -4.203
[5 empty] | 2018-06-13T09:36:21.843Z | 2018-06-13 | 9:36 | 1 | -4.249
[5 empty] | 2018-06-11T13:30:44.464Z | 2018-06-11 | 13:31 | 0 | -4.315
[5 empty] | 2018-06-11T13:16:17.437Z | 2018-06-11 | 13:16 | 1 | -4.537
[5 empty] | 2018-06-08T16:31:38.313Z | 2018-06-08 | 16:32 | 0 | -3.587
[5 empty] | 2018-06-08T16:23:43.596Z | 2018-06-08 | 16:24 | 1 | -3.549
[5 empty] | 2018-06-07T16:00:23.890Z | 2018-06-07 | 16:00 | 0 | -4.384
[5 empty] | 2018-06-07T15:35:44.631Z | 2018-06-07 | 15:36 | 1 | -4.319
[5 empty] | 2018-06-07T10:00:17.084Z | 2018-06-07 | 10:00 | 0 | -3.244
[5 empty] | 2018-06-07T09:58:31.874Z | 2018-06-07 | 9:59 | 1 | -3.948
[5 empty] | 2018-06-06T10:31:05.089Z | 2018-06-06 | 10:31 | 0 | -4.369
[5 empty] | 2018-06-06T10:18:33.898Z | 2018-06-06 | 10:19 | 1 | -3.474
[5 empty] | 2018-06-05T10:00:45.026Z | 2018-06-05 | 10:01 | 0 | -3.748
[5 empty] | 2018-06-05T09:45:44.253Z | 2018-06-05 | 9:46 | 1 | -4.063
[5 empty] | 2018-06-01T12:00:26.368Z | 2018-06-01 | 12:00 | 0 | -4.488
[5 empty] | 2018-06-01T11:49:18.785Z | 2018-06-01 | 11:49 | 1 | -3.961
[5 empty] | 2018-05-30T13:30:52.388Z | 2018-05-30 | 13:31 | 0 | -3.345
[5 empty] | 2018-05-30T13:18:24.954Z | 2018-05-30 | 13:18 | 1 | -3.768
[5 empty] | 2018-05-25T10:00:09.451Z | 2018-05-25 | 10:00 | 0 | -4.39
[5 empty] | 2018-05-25T09:50:49.797Z | 2018-05-25 | 9:51 | 1 | -3.919
[5 empty] | 2018-05-23T18:30:40.700Z | 2018-05-23 | 18:31 | 0 | -3.804
[5 empty] | 2018-05-23T18:21:09.853Z | 2018-05-23 | 18:21 | 1 | -3.241
[5 empty] | 2018-05-22T17:30:23.420Z | 2018-05-22 | 17:30 | 0 | -5.507
[5 empty] | 2018-05-22T17:17:42.658Z | 2018-05-22 | 17:18 | 1 | -4.151
[5 empty] | 2018-05-21T10:31:03.371Z | 2018-05-21 | 10:31 | 0 | -4.298
[5 empty] | 2018-05-21T10:20:52.796Z | 2018-05-21 | 10:21 | 1 | -3.715
[5 empty] | 2018-05-18T12:00:56.257Z | 2018-05-18 | 12:01 | 0 | -3.995
[5 empty] | 2018-05-18T11:45:47.339Z | 2018-05-18 | 11:46 | 1 | -4.038
[5 empty] | 2018-05-17T08:00:24.776Z | 2018-05-17 | 8:00 | 0 | -4.395
[5 empty] | 2018-05-17T07:41:06.862Z | 2018-05-17 | 7:41 | 1 | -3.945
[5 empty] | 2018-05-16T15:00:06.077Z | 2018-05-16 | 15:00 | 0 | -5.122
[5 empty] | 2018-05-16T14:56:53.153Z | 2018-05-16 | 14:57 | 1 | -4.658
[5 empty] | 2018-05-16T10:30:58.825Z | 2018-05-16 | 10:31 | 0 | -3.507
[5 empty] | 2018-05-16T10:23:09.156Z | 2018-05-16 | 10:23 | 1 | -4.337
[5 empty] | 2018-05-15T10:30:57.182Z | 2018-05-15 | 10:31 | 0 | -3.841
[5 empty] | 2018-05-15T10:15:57.968Z | 2018-05-15 | 10:16 | 1 | -4.341
[5 empty] | 2018-05-11T08:00:53.817Z | 2018-05-11 | 8:01 | 0 | -4.583
[5 empty] | 2018-05-11T07:36:14.347Z | 2018-05-11 | 7:36 | 1 | -4.305
[5 empty] | 2018-05-09T13:00:45.200Z | 2018-05-09 | 13:01 | 0 | -4.406
[5 empty] | 2018-05-09T12:39:12.420Z | 2018-05-09 | 12:39 | 1 | -4.362
[5 empty] | 2018-05-09T10:30:43.954Z | 2018-05-09 | 10:31 | 0 | -4.432
[5 empty] | 2018-05-09T10:19:47.916Z | 2018-05-09 | 10:20 | 1 | -3.949
[5 empty] | 2018-05-08T10:31:07.005Z | 2018-05-08 | 10:31 | 0 | -4.704
[5 empty] | 2018-05-08T10:02:26.985Z | 2018-05-08 | 10:02 | 1 | -3.579
[5 empty] | 2018-05-04T11:00:53.400Z | 2018-05-04 | 11:01 | 0 | -3.376
[5 empty] | 2018-05-04T10:51:27.878Z | 2018-05-04 | 10:51 | 1 | -4.349
[5 empty] | 2018-05-02T13:30:23.269Z | 2018-05-02 | 13:30 | 0 | -4.449
[5 empty] | 2018-05-02T13:11:30.244Z | 2018-05-02 | 13:12 | 1 | -4.841
[5 empty] | 2018-04-30T09:00:44.074Z | 2018-04-30 | 9:01 | 0 | -3.455
[5 empty] | 2018-04-30T08:53:54.718Z | 2018-04-30 | 8:54 | 1 | -4.418
[5 empty] | 2018-04-27T07:00:46.486Z | 2018-04-27 | 7:01 | 0 | -4.225
[5 empty] | 2018-04-27T06:58:18.059Z | 2018-04-27 | 6:58 | 1 | -4.659
[5 empty] | 2018-04-26T07:00:07.456Z | 2018-04-26 | 7:00 | 0 | -4.303
[5 empty] | 2018-04-26T06:36:16.396Z | 2018-04-26 | 6:36 | 1 | -4.41
[5 empty] | 2018-04-24T06:30:58.257Z | 2018-04-24 | 6:31 | 0 | -3.502
[5 empty] | 2018-04-24T06:16:14.453Z | 2018-04-24 | 6:16 | 1 | -3.937
[5 empty] | 2018-04-20T07:00:10.118Z | 2018-04-20 | 7:00 | 0 | -4.192
[5 empty] | 2018-04-20T06:43:53.456Z | 2018-04-20 | 6:44 | 1 | -4.263
[5 empty] | 2018-04-18T10:00:29.654Z | 2018-04-18 | 10:00 | 0 | -4.24
[5 empty] | 2018-04-18T09:38:14.773Z | 2018-04-18 | 9:38 | 1 | -4.166
[5 empty] | 2018-04-17T08:30:39.182Z | 2018-04-17 | 8:31 | 0 | -3.391
[5 empty] | 2018-04-17T08:13:53.693Z | 2018-04-17 | 8:14 | 1 | -3.421
[5 empty] | 2018-04-16T10:00:50.245Z | 2018-04-16 | 10:01 | 0 | -3.66
[5 empty] | 2018-04-16T09:33:47.576Z | 2018-04-16 | 9:34 | 1 | -4.304
[5 empty] | 2018-04-13T11:00:32.224Z | 2018-04-13 | 11:01 | 0 | -4.487
[5 empty] | 2018-04-13T10:52:42.151Z | 2018-04-13 | 10:53 | 1 | -4.361
[5 empty] | 2018-04-13T05:30:29.601Z | 2018-04-13 | 5:30 | 0 | -4.082
[5 empty] | 2018-04-13T05:14:46.333Z | 2018-04-13 | 5:15 | 1 | -4.37
[5 empty] | 2018-04-11T17:30:29.917Z | 2018-04-11 | 17:30 | 0 | -3.141
[5 empty] | 2018-04-11T17:01:18.471Z | 2018-04-11 | 17:01 | 1 | -3.874
[5 empty] | 2018-04-11T05:30:54.678Z | 2018-04-11 | 5:31 | 0 | -4.045
[5 empty] | 2018-04-11T05:16:46.712Z | 2018-04-11 | 5:17 | 1 | -4.11
[5 empty] | 2018-04-10T06:30:17.354Z | 2018-04-10 | 6:30 | 0 | -4.215
[5 empty] | 2018-04-10T06:13:52.575Z | 2018-04-10 | 6:14 | 1 | -4.634
[5 empty] | 2018-04-06T11:00:45.757Z | 2018-04-06 | 11:01 | 0 | -4.416
[5 empty] | 2018-04-06T10:34:26.141Z | 2018-04-06 | 10:34 | 1 | -3.444
[5 empty] | 2018-04-04T10:30:11.257Z | 2018-04-04 | 10:30 | 0 | -4.266
[5 empty] | 2018-04-04T10:14:22.892Z | 2018-04-04 | 10:14 | 1 | -3.785
[5 empty] | 2018-04-03T06:00:45.979Z | 2018-04-03 | 6:01 | 0 | -3.39
[5 empty] | 2018-04-03T05:56:36.176Z | 2018-04-03 | 5:57 | 1 | -3.962
[5 empty] | 2018-03-29T06:30:25.482Z | 2018-03-29 | 6:30 | 0 | -3.47
[5 empty] | 2018-03-29T06:24:43.349Z | 2018-03-29 | 6:25 | 1 | -3.388
[5 empty] | 2018-03-28T09:00:50.114Z | 2018-03-28 | 9:01 | 0 | -4.284
[5 empty] | 2018-03-28T08:39:51.589Z | 2018-03-28 | 8:40 | 1 | -4.443
[5 empty] | 2018-03-26T10:30:17.421Z | 2018-03-26 | 10:30 | 0 | -3.323
[5 empty] | 2018-03-26T10:25:43.927Z | 2018-03-26 | 10:26 | 1 | -3.247
[5 empty] | 2018-03-21T17:30:28.321Z | 2018-03-21 | 17:30 | 0 | -4.062
[5 empty] | 2018-03-21T17:01:05.593Z | 2018-03-21 | 17:01 | 1 | -4.293
[5 empty] | 2018-03-20T11:30:16.529Z | 2018-03-20 | 11:30 | 0 | -4.207
[5 empty] | 2018-03-20T11:19:41.729Z | 2018-03-20 | 11:20 | 1 | -4.106
[5 empty] | 2018-03-16T11:30:20.459Z | 2018-03-16 | 11:30 | 0 | -4.32
[5 empty] | 2018-03-16T11:22:46.764Z | 2018-03-16 | 11:23 | 1 | -4.187
[5 empty] | 2018-03-12T11:30:48.024Z | 2018-03-12 | 11:31 | 0 | -4.16
[5 empty] | 2018-03-12T11:27:42.784Z | 2018-03-12 | 11:28 | 1 | -3.379
[5 empty] | 2018-03-09T06:31:04.219Z | 2018-03-09 | 6:31 | 0 | -3.369
[5 empty] | 2018-03-09T06:24:14.416Z | 2018-03-09 | 6:24 | 1 | -4.307
[5 empty] | 2018-03-07T06:30:50.081Z | 2018-03-07 | 6:31 | 0 | -4.131
[5 empty] | 2018-03-07T06:29:37.621Z | 2018-03-07 | 6:30 | 1 | -3.893
[5 empty] | 2018-03-05T15:30:09.649Z | 2018-03-05 | 15:30 | 0 | -4.505
[5 empty] | 2018-03-05T15:06:36.090Z | 2018-03-05 | 15:07 | 1 | -4.675
[5 empty] | 2018-03-02T14:00:41.227Z | 2018-03-02 | 14:01 | 0 | -4.246
[5 empty] | 2018-03-02T13:46:13.378Z | 2018-03-02 | 13:46 | 1 | -4.599
[5 empty] | 2018-02-27T12:00:21.652Z | 2018-02-27 | 12:00 | 0 | -3.444
[5 empty] | 2018-02-27T11:53:27.056Z | 2018-02-27 | 11:53 | 1 | -4.042
[5 empty] | 2018-02-23T13:00:55.373Z | 2018-02-23 | 13:01 | 0 | -4.303
[5 empty] | 2018-02-23T12:43:35.136Z | 2018-02-23 | 12:44 | 1 | -3.976
[5 empty] | 2018-02-20T14:00:51.058Z | 2018-02-20 | 14:01 | 0 | -4.393
[5 empty] | 2018-02-20T13:37:36.245Z | 2018-02-20 | 13:38 | 1 | -4.072
[5 empty] | 2018-02-16T08:00:57.937Z | 2018-02-16 | 8:01 | 0 | -3.927
[5 empty] | 2018-02-16T07:50:30.670Z | 2018-02-16 | 7:51 | 1 | -4.016
[5 empty] | 2018-02-14T13:30:29.450Z | 2018-02-14 | 13:30 | 0 | -4.437
[5 empty] | 2018-02-14T13:24:35.847Z | 2018-02-14 | 13:25 | 1 | -3.118
[5 empty] | 2018-02-13T10:30:13.277Z | 2018-02-13 | 10:30 | 0 | -4.116
[5 empty] | 2018-02-13T10:07:42.967Z | 2018-02-13 | 10:08 | 1 | -4.007
[5 empty] | 2018-02-12T12:30:53.071Z | 2018-02-12 | 12:31 | 0 | -4.332
[5 empty] | 2018-02-12T12:22:46.550Z | 2018-02-12 | 12:23 | 1 | -3.561
[5 empty] | 2018-02-12T10:00:48.518Z | 2018-02-12 | 10:01 | 0 | -4.142
[5 empty] | 2018-02-12T09:33:28.390Z | 2018-02-12 | 9:33 | 1 | -3.755
[5 empty] | 2018-02-09T15:30:22.700Z | 2018-02-09 | 15:30 | 0 | -3.981
[5 empty] | 2018-02-09T15:10:37.470Z | 2018-02-09 | 15:11 | 1 | -4.151
[5 empty] | 2018-02-09T10:30:21.191Z | 2018-02-09 | 10:30 | 0 | -4.199
[5 empty] | 2018-02-09T10:28:44.117Z | 2018-02-09 | 10:29 | 1 | -3.101
[5 empty] | 2018-02-08T12:30:07.082Z | 2018-02-08 | 12:30 | 0 | -4.061
[5 empty] | 2018-02-08T12:24:25.317Z | 2018-02-08 | 12:24 | 1 | -4.088
[5 empty] | 2018-02-06T13:00:34.062Z | 2018-02-06 | 13:01 | 0 | -4.352
[5 empty] | 2018-02-06T12:39:48.608Z | 2018-02-06 | 12:40 | 1 | -4.102
[5 empty] | 2018-02-05T12:30:07.229Z | 2018-02-05 | 12:30 | 0 | -4.13
[5 empty] | 2018-02-05T12:28:14.316Z | 2018-02-05 | 12:28 | 1 | -3.609
[5 empty] | 2018-02-02T15:30:21.051Z | 2018-02-02 | 15:30 | 0 | -3.056
[5 empty] | 2018-02-02T15:07:56.300Z | 2018-02-02 | 15:08 | 1 | -4.056
[5 empty] | 2018-02-01T13:01:01.331Z | 2018-02-01 | 13:01 | 0 | -4.187
[5 empty] | 2018-02-01T12:32:09.167Z | 2018-02-01 | 12:32 | 1 | -4.329
[5 empty] | 2018-01-31T13:30:44.764Z | 2018-01-31 | 13:31 | 0 | -4.163
[5 empty] | 2018-01-31T13:27:03.053Z | 2018-01-31 | 13:27 | 1 | -4.124
[5 empty] | 2018-01-30T15:30:25.571Z | 2018-01-30 | 15:30 | 0 | -4.583
[5 empty] | 2018-01-30T15:14:32.674Z | 2018-01-30 | 15:15 | 1 | -2.966
[5 empty] | 2018-01-29T16:30:12.553Z | 2018-01-29 | 16:30 | 0 | -4.15
[5 empty] | 2018-01-29T16:08:35.040Z | 2018-01-29 | 16:09 | 1 | -3.54
[5 empty] | 2018-01-26T15:30:11.632Z | 2018-01-26 | 15:30 | 0 | -4.55
[5 empty] | 2018-01-26T15:08:53.658Z | 2018-01-26 | 15:09 | 1 | -4.083
[5 empty] | 2018-01-26T09:30:08.446Z | 2018-01-26 | 9:30 | 0 | -4.046
[5 empty] | 2018-01-26T09:08:59.803Z | 2018-01-26 | 9:09 | 1 | -4.257
[5 empty] | 2018-01-25T13:00:51.561Z | 2018-01-25 | 13:01 | 0 | -3.996
[5 empty] | 2018-01-25T12:54:54.193Z | 2018-01-25 | 12:55 | 1 | -3.994
[5 empty] | 2018-01-24T11:30:36.771Z | 2018-01-24 | 11:31 | 0 | -4.231
[5 empty] | 2018-01-24T11:07:14.932Z | 2018-01-24 | 11:07 | 1 | -3.96
[5 empty] | 2018-01-22T16:31:04.125Z | 2018-01-22 | 16:31 | 0 | -3.958
[5 empty] | 2018-01-22T16:10:10.795Z | 2018-01-22 | 16:10 | 1 | -3.786
[5 empty] | 2018-01-19T15:00:47.594Z | 2018-01-19 | 15:01 | 0 | -3.882
[5 empty] | 2018-01-19T14:50:33.457Z | 2018-01-19 | 14:51 | 1 | -4.338
[5 empty] | 2018-01-19T12:00:45.437Z | 2018-01-19 | 12:01 | 0 | -4.406
[5 empty] | 2018-01-19T11:55:19.254Z | 2018-01-19 | 11:55 | 1 | -3.975
[5 empty] | 2018-01-18T12:30:31.934Z | 2018-01-18 | 12:31 | 0 | -4.362
[5 empty] | 2018-01-18T12:13:48.473Z | 2018-01-18 | 12:14 | 1 | -4.025
[5 empty] | 2018-01-17T09:00:08.683Z | 2018-01-17 | 9:00 | 0 | -3.839
[5 empty] | 2018-01-17T08:51:06.365Z | 2018-01-17 | 8:51 | 1 | -4.405
[5 empty] | 2018-01-16T11:30:36.364Z | 2018-01-16 | 11:31 | 0 | -3.95
[5 empty] | 2018-01-16T11:24:35.467Z | 2018-01-16 | 11:25 | 1 | -7.303
[5 empty] | 2018-01-16T11:21:08.083Z | 2018-01-16 | 11:21 | 1 | -3.95
[5 empty] | 2017-12-20T15:09:24.048Z | 2017-12-20 | 15:09 | 1 | -3.823
[5 empty] | 180 days | June 25- Dec 20 | total | 89
[6 empty] | Average flush times per day |  | 3.2963

## NPV PropelairToilet USB theory
Initial extra investment | £ |  | 6000
Discount rate |  |  | 0.0025 | BoE 2017
Inflation rate |  |  | 0.027 | CPI 2017
Theoretical annual water savings | m3 per year |  | 90.6021
Water and sewage charges | £ per m3 |  | 1.8467 | Forward calculate from 2014 to 2017
Standard toilet cost | £ |  | 200
Propelair toilet costs | £ |  | 1200
Year
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Costs |  |  |  | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings |  |  |  |  | 167.3164 | 171.834 | 176.4735 | 181.2383 | 186.1317 | 191.1572 | 196.3185 | 201.6191 | 207.0628 | 212.6535 | 218.3951 | 224.2918 | 230.3477 | 236.5671 | 242.9544 | 249.5142 | 256.251 | 263.1698 | 270.2754 | 277.5728 | 285.0673 | 292.7641 | 300.6688 | 308.7868 | 317.1241 | 325.6864 | 334.4799 | 343.5109 | 352.7857
Net savings (minus costs) | £ |  |  | -6000 | 167.3164 | 171.834 | 176.4735 | 181.2383 | 186.1317 | 191.1572 | 196.3185 | 201.6191 | 207.0628 | 212.6535 | 218.3951 | 224.2918 | 230.3477 | 236.5671 | 242.9544 | 249.5142 | 256.251 | 263.1698 | 270.2754 | 277.5728 | 285.0673 | 292.7641 | 300.6688 | 308.7868 | 317.1241 | 325.6864 | 334.4799 | 343.5109 | 352.7857
|  | Year | NPV
£
|  | 0 | -6000
|  | 1 | -5833.1008
|  | 2 | -5662.1228
|  | 3 | -5486.9663
|  | 4 | -5307.5292
|  | 5 | -5123.7068
|  | 6 | -4935.392
|  | 7 | -4742.4749
|  | 8 | -4544.8432
|  | 9 | -4342.3816
|  | 10 | -4134.9721
|  | 11 | -3922.4937
|  | 12 | -3704.8226
|  | 13 | -3481.8318
|  | 14 | -3253.3913
|  | 15 | -3019.3681
|  | 16 | -2779.6255
|  | 17 | -2534.0239
|  | 18 | -2282.4201
|  | 19 | -2024.6674
|  | 20 | -1760.6154
|  | 21 | -1490.1104
|  | 22 | -1212.9945
|  | 23 | -929.1061
|  | 24 | -638.2799
|  | 25 | -340.3461
|  | 26 | -35.1313
|  | 27 | 277.5428
|  | 28 | 597.8582
|  | 29 | 926.0018

## NPV PropelairToilet USB actual
Initial investment | £ |  | 6000
Discount rate |  |  | 0.0025 | BoE 2017
Inflation rate |  |  | 0.027 | CPI 2017
Actual annual water savings | m3 per year |  | 25.2661
Water and sewage charges | £ per m3 |  | 1.8467 | Forward calculate from 2014 to 2017
Standard toilet cost | £ |  | 200
Propelair toilet costs | £ |  | 1200
Forward prediction based on CPI 2021
|  |  | Water price inflation |  | 101.5 | 103.5 | 106.2 | 105.6 | 106.3392 | 107.0836 | 107.8332 | 108.588 | 109.3481 | 110.1135 | 110.8843 | 111.6605 | 112.4422 | 113.2292 | 114.0219 | 114.82 | 115.6237 | 116.4331 | 117.2481 | 118.0689 | 118.8954 | 119.7276 | 120.5657 | 121.4097 | 122.2596 | 123.1154 | 123.9772 | 124.845 | 125.7189 | 126.599 | 127.4852 | 128.3776 | 129.2762 | 130.1811 | 131.0924 | 132.01 | 132.9341 | 133.8647 | 134.8017 | 135.7453 | 136.6955 | 137.6524 | 138.616 | 139.5863 | 140.5634 | 141.5473 | 142.5382 | 143.5359 | 144.5407 | 145.5525 | 146.5713 | 147.5973 | 148.6305 | 149.6709 | 150.7186 | 151.7737 | 152.8361 | 153.9059 | 154.9833 | 156.0681 | 157.1606 | 158.2607 | 159.3686 | 160.4842 | 161.6075 | 162.7388 | 163.878 | 165.0251 | 166.1803 | 167.3435 | 168.515 | 169.6946 | 170.8824 | 172.0786 | 173.2831 | 174.4961 | 175.7176 | 176.9476 | 178.1863 | 179.4336 | 180.6896 | 181.9544 | 183.2281 | 184.5107 | 185.8023 | 187.1029 | 188.4126 | 189.7315 | 191.0596 | 192.397 | 193.7438 | 195.1 | 196.4657 | 197.841 | 199.2259 | 200.6205 | 202.0248 | 203.439 | 204.863 | 206.2971
|  |  | Year |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
Costs |  |  |  | -6000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings |  |  |  |  | 46.6593 | 47.5787 | 48.8199 | 48.5441 | 48.8839 | 49.2261 | 49.5707 | 49.9177 | 50.2671 | 50.619 | 50.9733 | 51.3301 | 51.6894 | 52.0513 | 52.4156 | 52.7825 | 53.152 | 53.5241 | 53.8987 | 54.276 | 54.656 | 55.0386 | 55.4238 | 55.8118 | 56.2025 | 56.5959 | 56.9921 | 57.391 | 57.7927 | 58.1973 | 58.6047 | 59.0149 | 59.428 | 59.844 | 60.2629 | 60.6848 | 61.1095 | 61.5373 | 61.9681 | 62.4018 | 62.8387 | 63.2785 | 63.7215 | 64.1675 | 64.6167 | 65.069 | 65.5245 | 65.9832 | 66.4451 | 66.9102 | 67.3785 | 67.8502 | 68.3251 | 68.8034 | 69.285 | 69.77 | 70.2584 | 70.7502 | 71.2455 | 71.7442 | 72.2464 | 72.7521 | 73.2614 | 73.7742 | 74.2907 | 74.8107 | 75.3344 | 75.8617 | 76.3927 | 76.9275 | 77.466 | 78.0082 | 78.5543 | 79.1042 | 79.6579 | 80.2155 | 80.777 | 81.3425 | 81.9119 | 82.4852 | 83.0626 | 83.6441 | 84.2296 | 84.8192 | 85.4129 | 86.0108 | 86.6129 | 87.2192 | 87.8297 | 88.4445 | 89.0636 | 89.6871 | 90.3149 | 90.9471 | 91.5837 | 92.2248 | 92.8704 | 93.5205 | 94.1751 | 94.8344
Net savings (minus costs) | £ |  |  | -6000 | 46.6593 | 47.5787 | 48.8199 | 48.5441 | 48.8839 | 49.2261 | 49.5707 | 49.9177 | 50.2671 | 50.619 | 50.9733 | 51.3301 | 51.6894 | 52.0513 | 52.4156 | 52.7825 | 53.152 | 53.5241 | 53.8987 | 54.276 | 54.656 | 55.0386 | 55.4238 | 55.8118 | 56.2025 | 56.5959 | 56.9921 | 57.391 | 57.7927 | 58.1973 | 58.6047 | 59.0149 | 59.428 | 59.844 | 60.2629 | 60.6848 | 61.1095 | 61.5373 | 61.9681 | 62.4018 | 62.8387 | 63.2785 | 63.7215 | 64.1675 | 64.6167 | 65.069 | 65.5245 | 65.9832 | 66.4451 | 66.9102 | 67.3785 | 67.8502 | 68.3251 | 68.8034 | 69.285 | 69.77 | 70.2584 | 70.7502 | 71.2455 | 71.7442 | 72.2464 | 72.7521 | 73.2614 | 73.7742 | 74.2907 | 74.8107 | 75.3344 | 75.8617 | 76.3927 | 76.9275 | 77.466 | 78.0082 | 78.5543 | 79.1042 | 79.6579 | 80.2155 | 80.777 | 81.3425 | 81.9119 | 82.4852 | 83.0626 | 83.6441 | 84.2296 | 84.8192 | 85.4129 | 86.0108 | 86.6129 | 87.2192 | 87.8297 | 88.4445 | 89.0636 | 89.6871 | 90.3149 | 90.9471 | 91.5837 | 92.2248 | 92.8704 | 93.5205 | 94.1751 | 94.8344
|  | Year | NPV
£
|  | 0 | -6000
|  | 1 | -5953.457
|  | 2 | -5906.1153
|  | 3 | -5857.6597
|  | 4 | -5809.598
|  | 5 | -5761.3206
|  | 6 | -5712.8264
|  | 7 | -5664.1146
|  | 8 | -5615.1842
|  | 9 | -5566.0341
|  | 10 | -5516.6633
|  | 11 | -5467.071
|  | 12 | -5417.256
|  | 13 | -5367.2175
|  | 14 | -5316.9543
|  | 15 | -5266.4655
|  | 16 | -5215.7501
|  | 17 | -5164.807
|  | 18 | -5113.6353
|  | 19 | -5062.2338
|  | 20 | -5010.6016
|  | 21 | -4958.7377
|  | 22 | -4906.641
|  | 23 | -4854.3104
|  | 24 | -4801.7449
|  | 25 | -4748.9434
|  | 26 | -4695.9049
|  | 27 | -4642.6284
|  | 28 | -4589.1127
|  | 29 | -4535.3568
|  | 30 | -4481.3596
|  | 31 | -4427.12
|  | 32 | -4372.6369
|  | 33 | -4317.9093
|  | 34 | -4262.936
|  | 35 | -4207.716
|  | 36 | -4152.2481
|  | 37 | -4096.5312
|  | 38 | -4040.5642
|  | 39 | -3984.346
|  | 40 | -3927.8754
|  | 41 | -3871.1513
|  | 42 | -3814.1726
|  | 43 | -3756.9382
|  | 44 | -3699.4468
|  | 45 | -3641.6974
|  | 46 | -3583.6888
|  | 47 | -3525.4197
|  | 48 | -3466.8891
|  | 49 | -3408.0958
|  | 50 | -3349.0386
|  | 51 | -3289.7162
|  | 52 | -3230.1276
|  | 53 | -3170.2715
|  | 54 | -3110.1468
|  | 55 | -3049.7521
|  | 56 | -2989.0863
|  | 57 | -2928.1483
|  | 58 | -2866.9367
|  | 59 | -2805.4503
|  | 60 | -2743.6879
|  | 61 | -2681.6483
|  | 62 | -2619.3302
|  | 63 | -2556.7324
|  | 64 | -2493.8536
|  | 65 | -2430.6925
|  | 66 | -2367.2479
|  | 67 | -2303.5185
|  | 68 | -2239.5031
|  | 69 | -2175.2003
|  | 70 | -2110.6089
|  | 71 | -2045.7275
|  | 72 | -1980.5549
|  | 73 | -1915.0898
|  | 74 | -1849.3308
|  | 75 | -1783.2766
|  | 76 | -1716.9259
|  | 77 | -1650.2774
|  | 78 | -1583.3297
|  | 79 | -1516.0815
|  | 80 | -1448.5314
|  | 81 | -1380.6781
|  | 82 | -1312.5203
|  | 83 | -1244.0565
|  | 84 | -1175.2853
|  | 85 | -1106.2055
|  | 86 | -1036.8156
|  | 87 | -967.1142
|  | 88 | -897.1
|  | 89 | -826.7714
|  | 90 | -756.1272
|  | 91 | -685.1659
|  | 92 | -613.886
|  | 93 | -542.2862
|  | 94 | -470.365
|  | 95 | -398.1209
|  | 96 | -325.5526
|  | 97 | -252.6585
|  | 98 | -179.4372
|  | 99 | -105.8872
|  | 100 | -32.0071

## DB MainsWaterMonitoring
Location Name | Date and time | Meter read | Flow(l/h) | Baseflow (l/h) | Baseflow until leak fixed | Leak before repair
Devonshire Building | 2016-07-28 | 45418.4883 | 619.992 |  | m3 | l/h
Devonshire Building | 2016-07-28 00:15 | 45418.6483 | 640.008 |  | 3750.2378 | 1640.016
Devonshire Building | 2016-07-28 00:30 | 45418.8083 | 640.008
Devonshire Building | 2016-07-28 00:45 | 45418.9683 | 640.008
Devonshire Building | 2016-07-28 01:00 | 45419.1233 | 619.992
Devonshire Building | 2016-07-28 01:15 | 45419.2833 | 640.008
Devonshire Building | 2016-07-28 01:30 | 45419.4433 | 640.008
Devonshire Building | 2016-07-28 01:45 | 45419.5983 | 619.992
Devonshire Building | 2016-07-28 02:00 | 45419.7583 | 640.008
Devonshire Building | 2016-07-28 02:15 | 45419.9133 | 619.992
Devonshire Building | 2016-07-28 02:30 | 45420.0733 | 640.008
Devonshire Building | 2016-07-28 02:45 | 45420.2333 | 640.008
Devonshire Building | 2016-07-28 03:00 | 45420.3883 | 619.992
Devonshire Building | 2016-07-28 03:15 | 45420.5483 | 640.008
Devonshire Building | 2016-07-28 03:30 | 45420.7033 | 619.992
Devonshire Building | 2016-07-28 03:45 | 45420.8633 | 640.008
Devonshire Building | 2016-07-28 04:00 | 45421.0183 | 619.992
Devonshire Building | 2016-07-28 04:15 | 45421.1783 | 640.008
Devonshire Building | 2016-07-28 04:30 | 45421.3383 | 640.008
Devonshire Building | 2016-07-28 04:45 | 45421.4933 | 619.992
Devonshire Building | 2016-07-28 05:00 | 45421.6533 | 640.008
Devonshire Building | 2016-07-28 05:15 | 45421.8083 | 619.992
Devonshire Building | 2016-07-28 05:30 | 45421.9683 | 640.008
Devonshire Building | 2016-07-28 05:45 | 45422.1283 | 640.008
Devonshire Building | 2016-07-28 06:00 | 45422.2883 | 640.008
Devonshire Building | 2016-07-28 06:15 | 45422.4433 | 619.992
Devonshire Building | 2016-07-28 06:30 | 45422.6033 | 640.008
Devonshire Building | 2016-07-28 06:45 | 45422.7583 | 619.992
Devonshire Building | 2016-07-28 07:00 | 45422.9183 | 640.008
Devonshire Building | 2016-07-28 07:15 | 45423.0933 | 699.984
Devonshire Building | 2016-07-28 07:30 | 45423.2533 | 640.008
Devonshire Building | 2016-07-28 07:45 | 45423.6733 | 1680.012
Devonshire Building | 2016-07-28 08:00 | 45423.8483 | 699.984
Devonshire Building | 2016-07-28 08:15 | 45424.0333 | 740.016
Devonshire Building | 2016-07-28 08:30 | 45424.2133 | 720
Devonshire Building | 2016-07-28 08:45 | 45424.4133 | 799.992
Devonshire Building | 2016-07-28 09:00 | 45424.6233 | 839.988
Devonshire Building | 2016-07-28 09:15 | 45424.8333 | 839.988
Devonshire Building | 2016-07-28 09:30 | 45425.1533 | 1280.016
Devonshire Building | 2016-07-28 09:45 | 45425.7383 | 2340
Devonshire Building | 2016-07-28 10:00 | 45426.0633 | 1299.996
Devonshire Building | 2016-07-28 10:15 | 45426.4133 | 1400.004
Devonshire Building | 2016-07-28 10:30 | 45426.7133 | 1199.988
Devonshire Building | 2016-07-28 10:45 | 45426.9733 | 1040.004
Devonshire Building | 2016-07-28 11:00 | 45427.2133 | 960.012
Devonshire Building | 2016-07-28 11:15 | 45427.7033 | 1959.984
Devonshire Building | 2016-07-28 11:30 | 45427.9183 | 860.004
Devonshire Building | 2016-07-28 11:45 | 45428.1283 | 839.988
Devonshire Building | 2016-07-28 12:00 | 45428.3333 | 820.008
Devonshire Building | 2016-07-28 12:15 | 45428.5333 | 799.992
Devonshire Building | 2016-07-28 12:30 | 45428.7383 | 820.008
Devonshire Building | 2016-07-28 12:45 | 45428.9383 | 799.992
Devonshire Building | 2016-07-28 13:00 | 45429.1383 | 799.992
Devonshire Building | 2016-07-28 13:15 | 45429.3283 | 759.996
Devonshire Building | 2016-07-28 13:30 | 45429.7683 | 1760.004
Devonshire Building | 2016-07-28 13:45 | 45429.9583 | 759.996
Devonshire Building | 2016-07-28 14:00 | 45430.1483 | 759.996
Devonshire Building | 2016-07-28 14:15 | 45430.3683 | 879.984
Devonshire Building | 2016-07-28 14:30 | 45430.6233 | 1019.988
Devonshire Building | 2016-07-28 14:45 | 45430.8983 | 1100.016
Devonshire Building | 2016-07-28 15:00 | 45431.1583 | 1040.004
Devonshire Building | 2016-07-28 15:15 | 45431.6533 | 1980
Devonshire Building | 2016-07-28 15:30 | 45431.8933 | 960.012
Devonshire Building | 2016-07-28 15:45 | 45432.1483 | 1019.988
Devonshire Building | 2016-07-28 16:00 | 45432.4383 | 1159.992
Devonshire Building | 2016-07-28 16:15 | 45432.7183 | 1119.996
Devonshire Building | 2016-07-28 16:30 | 45432.9883 | 1080
Devonshire Building | 2016-07-28 16:45 | 45433.2383 | 1000.008
Devonshire Building | 2016-07-28 17:00 | 45433.4783 | 960.012
Devonshire Building | 2016-07-28 17:15 | 45433.7283 | 1000.008
Devonshire Building | 2016-07-28 17:30 | 45433.9683 | 960.012
Devonshire Building | 2016-07-28 17:45 | 45434.2083 | 960.012
Devonshire Building | 2016-07-28 18:00 | 45434.4333 | 900
Devonshire Building | 2016-07-28 18:15 | 45434.6383 | 820.008
Devonshire Building | 2016-07-28 18:30 | 45434.8383 | 799.992
Devonshire Building | 2016-07-28 18:45 | 45435.0283 | 759.996
Devonshire Building | 2016-07-28 19:00 | 45435.2133 | 740.016
Devonshire Building | 2016-07-28 19:15 | 45435.3933 | 720
Devonshire Building | 2016-07-28 19:30 | 45435.5833 | 759.996
Devonshire Building | 2016-07-28 19:45 | 45435.7583 | 699.984
Devonshire Building | 2016-07-28 20:00 | 45435.9333 | 699.984
Devonshire Building | 2016-07-28 20:15 | 45436.1033 | 680.004
Devonshire Building | 2016-07-28 20:30 | 45436.2783 | 699.984
Devonshire Building | 2016-07-28 20:45 | 45436.4483 | 680.004
Devonshire Building | 2016-07-28 21:00 | 45436.6233 | 699.984
Devonshire Building | 2016-07-28 21:15 | 45436.8083 | 740.016
Devonshire Building | 2016-07-28 21:30 | 45436.9733 | 659.988
Devonshire Building | 2016-07-28 21:45 | 45437.1383 | 659.988
Devonshire Building | 2016-07-28 22:00 | 45437.2983 | 640.008
Devonshire Building | 2016-07-28 22:15 | 45437.4633 | 659.988
Devonshire Building | 2016-07-28 22:30 | 45437.6283 | 659.988
Devonshire Building | 2016-07-28 22:45 | 45437.7933 | 659.988
Devonshire Building | 2016-07-28 23:00 | 45437.9583 | 659.988
Devonshire Building | 2016-07-28 23:15 | 45438.1233 | 659.988
Devonshire Building | 2016-07-28 23:30 | 45438.2883 | 659.988
Devonshire Building | 2016-07-28 23:45 | 45438.4533 | 659.988 | 619.992
Devonshire Building | 2016-07-29 | 45438.8438 | 1559.988
Devonshire Building | 2016-07-29 00:15 | 45439.0038 | 640.008
Devonshire Building | 2016-07-29 00:30 | 45439.1638 | 640.008
Devonshire Building | 2016-07-29 00:45 | 45439.3238 | 640.008
Devonshire Building | 2016-07-29 01:00 | 45439.4788 | 619.992
Devonshire Building | 2016-07-29 01:15 | 45439.6388 | 640.008
Devonshire Building | 2016-07-29 01:30 | 45439.7988 | 640.008
Devonshire Building | 2016-07-29 01:45 | 45439.9588 | 640.008
Devonshire Building | 2016-07-29 02:00 | 45440.1188 | 640.008
Devonshire Building | 2016-07-29 02:15 | 45440.2788 | 640.008
Devonshire Building | 2016-07-29 02:30 | 45440.4388 | 640.008
Devonshire Building | 2016-07-29 02:45 | 45440.5988 | 640.008
Devonshire Building | 2016-07-29 03:00 | 45440.7588 | 640.008
Devonshire Building | 2016-07-29 03:15 | 45440.9188 | 640.008
Devonshire Building | 2016-07-29 03:30 | 45441.0788 | 640.008
Devonshire Building | 2016-07-29 03:45 | 45441.2338 | 619.992
Devonshire Building | 2016-07-29 04:00 | 45441.3938 | 640.008
Devonshire Building | 2016-07-29 04:15 | 45441.5538 | 640.008
Devonshire Building | 2016-07-29 04:30 | 45441.7138 | 640.008
Devonshire Building | 2016-07-29 04:45 | 45441.8738 | 640.008
Devonshire Building | 2016-07-29 05:00 | 45442.0338 | 640.008
Devonshire Building | 2016-07-29 05:15 | 45442.1938 | 640.008
Devonshire Building | 2016-07-29 05:30 | 45442.3538 | 640.008
Devonshire Building | 2016-07-29 05:45 | 45442.5138 | 640.008
Devonshire Building | 2016-07-29 06:00 | 45442.6738 | 640.008
Devonshire Building | 2016-07-29 06:15 | 45442.8338 | 640.008
Devonshire Building | 2016-07-29 06:30 | 45442.9888 | 619.992
Devonshire Building | 2016-07-29 06:45 | 45443.1488 | 640.008
Devonshire Building | 2016-07-29 07:00 | 45443.3138 | 659.988
Devonshire Building | 2016-07-29 07:15 | 45443.4738 | 640.008
Devonshire Building | 2016-07-29 07:30 | 45443.6538 | 720
Devonshire Building | 2016-07-29 07:45 | 45443.8288 | 699.984
Devonshire Building | 2016-07-29 08:00 | 45444.0088 | 720
Devonshire Building | 2016-07-29 08:15 | 45444.1888 | 720
Devonshire Building | 2016-07-29 08:30 | 45444.5638 | 1500.012
Devonshire Building | 2016-07-29 08:45 | 45444.7938 | 920.016
Devonshire Building | 2016-07-29 09:00 | 45444.9788 | 740.016
Devonshire Building | 2016-07-29 09:15 | 45445.1538 | 699.984
Devonshire Building | 2016-07-29 09:30 | 45445.3538 | 799.992
Devonshire Building | 2016-07-29 09:45 | 45445.5788 | 900
Devonshire Building | 2016-07-29 10:00 | 45445.8488 | 1080
Devonshire Building | 2016-07-29 10:15 | 45446.1138 | 1059.984
Devonshire Building | 2016-07-29 10:30 | 45446.6088 | 1980
Devonshire Building | 2016-07-29 10:45 | 45446.8638 | 1019.988
Devonshire Building | 2016-07-29 11:00 | 45447.1138 | 1000.008
Devonshire Building | 2016-07-29 11:15 | 45447.3688 | 1019.988
Devonshire Building | 2016-07-29 11:30 | 45447.6088 | 960.012
Devonshire Building | 2016-07-29 11:45 | 45447.8388 | 920.016
Devonshire Building | 2016-07-29 12:00 | 45448.0588 | 879.984
Devonshire Building | 2016-07-29 12:15 | 45448.5288 | 1879.992
Devonshire Building | 2016-07-29 12:30 | 45448.7138 | 740.016
Devonshire Building | 2016-07-29 12:45 | 45448.8988 | 740.016
Devonshire Building | 2016-07-29 13:00 | 45449.0888 | 759.996
Devonshire Building | 2016-07-29 13:15 | 45449.2888 | 799.992
Devonshire Building | 2016-07-29 13:30 | 45449.4938 | 820.008
Devonshire Building | 2016-07-29 13:45 | 45449.7188 | 900
Devonshire Building | 2016-07-29 14:00 | 45449.9388 | 879.984
Devonshire Building | 2016-07-29 14:15 | 45450.4138 | 1900.008
Devonshire Building | 2016-07-29 14:30 | 45450.6288 | 860.004
Devonshire Building | 2016-07-29 14:45 | 45450.9138 | 1140.012
Devonshire Building | 2016-07-29 15:00 | 45451.2188 | 1220.004
Devonshire Building | 2016-07-29 15:15 | 45451.5138 | 1180.008
Devonshire Building | 2016-07-29 15:30 | 45451.7838 | 1080
Devonshire Building | 2016-07-29 15:45 | 45452.0288 | 979.992
Devonshire Building | 2016-07-29 16:00 | 45452.2438 | 860.004
Devonshire Building | 2016-07-29 16:15 | 45452.4588 | 860.004
Devonshire Building | 2016-07-29 16:30 | 45452.9088 | 1800
Devonshire Building | 2016-07-29 16:45 | 45453.1038 | 780.012
Devonshire Building | 2016-07-29 17:00 | 45453.3038 | 799.992
Devonshire Building | 2016-07-29 17:15 | 45453.5038 | 799.992
Devonshire Building | 2016-07-29 17:30 | 45453.6938 | 759.996
Devonshire Building | 2016-07-29 17:45 | 45453.8838 | 759.996
Devonshire Building | 2016-07-29 18:00 | 45454.0638 | 720
Devonshire Building | 2016-07-29 18:15 | 45454.2438 | 720
Devonshire Building | 2016-07-29 18:30 | 45454.4188 | 699.984
Devonshire Building | 2016-07-29 18:45 | 45454.5888 | 680.004
Devonshire Building | 2016-07-29 19:00 | 45454.7588 | 680.004
Devonshire Building | 2016-07-29 19:15 | 45454.9288 | 680.004
Devonshire Building | 2016-07-29 19:30 | 45455.0988 | 680.004
Devonshire Building | 2016-07-29 19:45 | 45455.2688 | 680.004
Devonshire Building | 2016-07-29 20:00 | 45455.4388 | 680.004
Devonshire Building | 2016-07-29 20:15 | 45455.6088 | 680.004
Devonshire Building | 2016-07-29 20:30 | 45455.7738 | 659.988
Devonshire Building | 2016-07-29 20:45 | 45455.9438 | 680.004
Devonshire Building | 2016-07-29 21:00 | 45456.1138 | 680.004
Devonshire Building | 2016-07-29 21:15 | 45456.2988 | 740.016
Devonshire Building | 2016-07-29 21:30 | 45456.4738 | 699.984
Devonshire Building | 2016-07-29 21:45 | 45456.6488 | 699.984
Devonshire Building | 2016-07-29 22:00 | 45456.8288 | 720
Devonshire Building | 2016-07-29 22:15 | 45457.0038 | 699.984
Devonshire Building | 2016-07-29 22:30 | 45457.1788 | 699.984
Devonshire Building | 2016-07-29 22:45 | 45457.3538 | 699.984
Devonshire Building | 2016-07-29 23:00 | 45457.5338 | 720
Devonshire Building | 2016-07-29 23:15 | 45457.7238 | 759.996
Devonshire Building | 2016-07-29 23:30 | 45457.9138 | 759.996
Devonshire Building | 2016-07-29 23:45 | 45458.1088 | 780.012 | 619.992
Devonshire Building | 2016-07-30 | 45458.3008 | 759.996
Devonshire Building | 2016-07-30 00:15 | 45458.4908 | 759.996
Devonshire Building | 2016-07-30 00:30 | 45458.6808 | 759.996
Devonshire Building | 2016-07-30 00:45 | 45458.8708 | 759.996
Devonshire Building | 2016-07-30 01:00 | 45459.0608 | 759.996
Devonshire Building | 2016-07-30 01:15 | 45459.2458 | 740.016
Devonshire Building | 2016-07-30 01:30 | 45459.4308 | 740.016
Devonshire Building | 2016-07-30 01:45 | 45459.6108 | 720
Devonshire Building | 2016-07-30 02:00 | 45459.7858 | 699.984
Devonshire Building | 2016-07-30 02:15 | 45459.9658 | 720
Devonshire Building | 2016-07-30 02:30 | 45460.1358 | 680.004
Devonshire Building | 2016-07-30 02:45 | 45460.3108 | 699.984
Devonshire Building | 2016-07-30 03:00 | 45460.4808 | 680.004
Devonshire Building | 2016-07-30 03:15 | 45460.6558 | 699.984
Devonshire Building | 2016-07-30 03:30 | 45460.8258 | 680.004
Devonshire Building | 2016-07-30 03:45 | 45460.9958 | 680.004
Devonshire Building | 2016-07-30 04:00 | 45461.1658 | 680.004
Devonshire Building | 2016-07-30 04:15 | 45461.3308 | 659.988
Devonshire Building | 2016-07-30 04:30 | 45461.5008 | 680.004
Devonshire Building | 2016-07-30 04:45 | 45461.6658 | 659.988
Devonshire Building | 2016-07-30 05:00 | 45461.8308 | 659.988
Devonshire Building | 2016-07-30 05:15 | 45461.9958 | 659.988
Devonshire Building | 2016-07-30 05:30 | 45462.1608 | 659.988
Devonshire Building | 2016-07-30 05:45 | 45462.3258 | 659.988
Devonshire Building | 2016-07-30 06:00 | 45462.4908 | 659.988
Devonshire Building | 2016-07-30 06:15 | 45462.6558 | 659.988
Devonshire Building | 2016-07-30 06:30 | 45462.8208 | 659.988
Devonshire Building | 2016-07-30 06:45 | 45462.9808 | 640.008
Devonshire Building | 2016-07-30 07:00 | 45463.1458 | 659.988
Devonshire Building | 2016-07-30 07:15 | 45463.3058 | 640.008
Devonshire Building | 2016-07-30 07:30 | 45463.4658 | 640.008
Devonshire Building | 2016-07-30 07:45 | 45463.6258 | 640.008
Devonshire Building | 2016-07-30 08:00 | 45463.7858 | 640.008
Devonshire Building | 2016-07-30 08:15 | 45463.9458 | 640.008
Devonshire Building | 2016-07-30 08:30 | 45464.1058 | 640.008
Devonshire Building | 2016-07-30 08:45 | 45464.2658 | 640.008
Devonshire Building | 2016-07-30 09:00 | 45464.4208 | 619.992
Devonshire Building | 2016-07-30 09:15 | 45464.5808 | 640.008
Devonshire Building | 2016-07-30 09:30 | 45464.7408 | 640.008
Devonshire Building | 2016-07-30 09:45 | 45464.9008 | 640.008
Devonshire Building | 2016-07-30 10:00 | 45465.0558 | 619.992
Devonshire Building | 2016-07-30 10:15 | 45465.2158 | 640.008
Devonshire Building | 2016-07-30 10:30 | 45465.3758 | 640.008
Devonshire Building | 2016-07-30 10:45 | 45465.5308 | 619.992
Devonshire Building | 2016-07-30 11:00 | 45465.6908 | 640.008
Devonshire Building | 2016-07-30 11:15 | 45465.8508 | 640.008
Devonshire Building | 2016-07-30 11:30 | 45466.0108 | 640.008
Devonshire Building | 2016-07-30 11:45 | 45466.1708 | 640.008
Devonshire Building | 2016-07-30 12:00 | 45466.3308 | 640.008
Devonshire Building | 2016-07-30 12:15 | 45466.4908 | 640.008
Devonshire Building | 2016-07-30 12:30 | 45466.6508 | 640.008
Devonshire Building | 2016-07-30 12:45 | 45466.8058 | 619.992
Devonshire Building | 2016-07-30 13:00 | 45466.9708 | 659.988
Devonshire Building | 2016-07-30 13:15 | 45467.1358 | 659.988
Devonshire Building | 2016-07-30 13:30 | 45467.3008 | 659.988
Devonshire Building | 2016-07-30 13:45 | 45467.4758 | 699.984
Devonshire Building | 2016-07-30 14:00 | 45467.6508 | 699.984
Devonshire Building | 2016-07-30 14:15 | 45468.0608 | 1640.016
Devonshire Building | 2016-07-30 14:30 | 45468.2408 | 720
Devonshire Building | 2016-07-30 14:45 | 45468.4158 | 699.984
Devonshire Building | 2016-07-30 15:00 | 45468.5958 | 720
Devonshire Building | 2016-07-30 15:15 | 45468.7708 | 699.984
Devonshire Building | 2016-07-30 15:30 | 45468.9458 | 699.984
Devonshire Building | 2016-07-30 15:45 | 45469.1058 | 640.008
Devonshire Building | 2016-07-30 16:00 | 45469.2658 | 640.008
Devonshire Building | 2016-07-30 16:15 | 45469.4258 | 640.008
Devonshire Building | 2016-07-30 16:30 | 45469.5858 | 640.008
Devonshire Building | 2016-07-30 16:45 | 45469.7458 | 640.008
Devonshire Building | 2016-07-30 17:00 | 45469.9108 | 659.988
Devonshire Building | 2016-07-30 17:15 | 45470.0708 | 640.008
Devonshire Building | 2016-07-30 17:30 | 45470.2308 | 640.008
Devonshire Building | 2016-07-30 17:45 | 45470.3908 | 640.008
Devonshire Building | 2016-07-30 18:00 | 45470.5508 | 640.008
Devonshire Building | 2016-07-30 18:15 | 45470.7108 | 640.008
Devonshire Building | 2016-07-30 18:30 | 45470.8758 | 659.988
Devonshire Building | 2016-07-30 18:45 | 45471.0358 | 640.008
Devonshire Building | 2016-07-30 19:00 | 45471.1958 | 640.008
Devonshire Building | 2016-07-30 19:15 | 45471.3608 | 659.988
Devonshire Building | 2016-07-30 19:30 | 45471.5208 | 640.008
Devonshire Building | 2016-07-30 19:45 | 45471.6808 | 640.008
Devonshire Building | 2016-07-30 20:00 | 45471.8458 | 659.988
Devonshire Building | 2016-07-30 20:15 | 45472.0058 | 640.008
Devonshire Building | 2016-07-30 20:30 | 45472.1658 | 640.008
Devonshire Building | 2016-07-30 20:45 | 45472.3308 | 659.988
Devonshire Building | 2016-07-30 21:00 | 45472.4908 | 640.008
Devonshire Building | 2016-07-30 21:15 | 45472.6608 | 680.004
Devonshire Building | 2016-07-30 21:30 | 45472.8258 | 659.988
Devonshire Building | 2016-07-30 21:45 | 45472.9858 | 640.008
Devonshire Building | 2016-07-30 22:00 | 45473.1458 | 640.008
Devonshire Building | 2016-07-30 22:15 | 45473.3108 | 659.988
Devonshire Building | 2016-07-30 22:30 | 45473.4708 | 640.008
Devonshire Building | 2016-07-30 22:45 | 45473.6358 | 659.988
Devonshire Building | 2016-07-30 23:00 | 45473.7958 | 640.008
Devonshire Building | 2016-07-30 23:15 | 45473.9608 | 659.988
Devonshire Building | 2016-07-30 23:30 | 45474.1258 | 659.988
Devonshire Building | 2016-07-30 23:45 | 45474.2858 | 640.008 | 619.992
Devonshire Building | 2016-07-31 | 45474.4492 | 659.988
Devonshire Building | 2016-07-31 00:15 | 45474.6092 | 640.008
Devonshire Building | 2016-07-31 00:30 | 45474.7742 | 659.988
Devonshire Building | 2016-07-31 00:45 | 45474.9342 | 640.008
Devonshire Building | 2016-07-31 01:00 | 45475.0992 | 659.988
Devonshire Building | 2016-07-31 01:15 | 45475.2592 | 640.008
Devonshire Building | 2016-07-31 01:30 | 45475.4242 | 659.988
Devonshire Building | 2016-07-31 01:45 | 45475.5842 | 640.008
Devonshire Building | 2016-07-31 02:00 | 45475.7492 | 659.988
Devonshire Building | 2016-07-31 02:15 | 45475.9092 | 640.008
Devonshire Building | 2016-07-31 02:30 | 45476.0742 | 659.988
Devonshire Building | 2016-07-31 02:45 | 45476.2342 | 640.008
Devonshire Building | 2016-07-31 03:00 | 45476.3992 | 659.988
Devonshire Building | 2016-07-31 03:15 | 45476.5592 | 640.008
Devonshire Building | 2016-07-31 03:30 | 45476.7242 | 659.988
Devonshire Building | 2016-07-31 03:45 | 45476.8842 | 640.008
Devonshire Building | 2016-07-31 04:00 | 45477.0492 | 659.988
Devonshire Building | 2016-07-31 04:15 | 45477.2092 | 640.008
Devonshire Building | 2016-07-31 04:30 | 45477.3742 | 659.988
Devonshire Building | 2016-07-31 04:45 | 45477.5342 | 640.008
Devonshire Building | 2016-07-31 05:00 | 45477.6992 | 659.988
Devonshire Building | 2016-07-31 05:15 | 45477.8592 | 640.008
Devonshire Building | 2016-07-31 05:30 | 45478.0242 | 659.988
Devonshire Building | 2016-07-31 05:45 | 45478.1842 | 640.008
Devonshire Building | 2016-07-31 06:00 | 45478.3492 | 659.988
Devonshire Building | 2016-07-31 06:15 | 45478.5092 | 640.008
Devonshire Building | 2016-07-31 06:30 | 45478.6692 | 640.008
Devonshire Building | 2016-07-31 06:45 | 45478.8342 | 659.988
Devonshire Building | 2016-07-31 07:00 | 45478.9942 | 640.008
Devonshire Building | 2016-07-31 07:15 | 45479.1542 | 640.008
Devonshire Building | 2016-07-31 07:30 | 45479.3192 | 659.988
Devonshire Building | 2016-07-31 07:45 | 45479.4792 | 640.008
Devonshire Building | 2016-07-31 08:00 | 45479.6392 | 640.008
Devonshire Building | 2016-07-31 08:15 | 45479.7992 | 640.008
Devonshire Building | 2016-07-31 08:30 | 45479.9542 | 619.992
Devonshire Building | 2016-07-31 08:45 | 45480.1142 | 640.008
Devonshire Building | 2016-07-31 09:00 | 45480.2742 | 640.008
Devonshire Building | 2016-07-31 09:15 | 45480.4342 | 640.008
Devonshire Building | 2016-07-31 09:30 | 45480.5892 | 619.992
Devonshire Building | 2016-07-31 09:45 | 45480.7492 | 640.008
Devonshire Building | 2016-07-31 10:00 | 45480.9092 | 640.008
Devonshire Building | 2016-07-31 10:15 | 45481.0692 | 640.008
Devonshire Building | 2016-07-31 10:30 | 45481.2292 | 640.008
Devonshire Building | 2016-07-31 10:45 | 45481.3892 | 640.008
Devonshire Building | 2016-07-31 11:00 | 45481.5442 | 619.992
Devonshire Building | 2016-07-31 11:15 | 45481.7042 | 640.008
Devonshire Building | 2016-07-31 11:30 | 45481.8642 | 640.008
Devonshire Building | 2016-07-31 11:45 | 45482.0242 | 640.008
Devonshire Building | 2016-07-31 12:00 | 45482.1842 | 640.008
Devonshire Building | 2016-07-31 12:15 | 45482.3442 | 640.008
Devonshire Building | 2016-07-31 12:30 | 45482.5092 | 659.988
Devonshire Building | 2016-07-31 12:45 | 45482.6692 | 640.008
Devonshire Building | 2016-07-31 13:00 | 45482.8292 | 640.008
Devonshire Building | 2016-07-31 13:15 | 45482.9892 | 640.008
Devonshire Building | 2016-07-31 13:30 | 45483.1592 | 680.004
Devonshire Building | 2016-07-31 13:45 | 45483.3392 | 720
Devonshire Building | 2016-07-31 14:00 | 45483.5142 | 699.984
Devonshire Building | 2016-07-31 14:15 | 45483.6942 | 720
Devonshire Building | 2016-07-31 14:30 | 45484.1092 | 1659.996
Devonshire Building | 2016-07-31 14:45 | 45484.2842 | 699.984
Devonshire Building | 2016-07-31 15:00 | 45484.4592 | 699.984
Devonshire Building | 2016-07-31 15:15 | 45484.6342 | 699.984
Devonshire Building | 2016-07-31 15:30 | 45484.8142 | 720
Devonshire Building | 2016-07-31 15:45 | 45484.9842 | 680.004
Devonshire Building | 2016-07-31 16:00 | 45485.1442 | 640.008
Devonshire Building | 2016-07-31 16:15 | 45485.3042 | 640.008
Devonshire Building | 2016-07-31 16:30 | 45485.4642 | 640.008
Devonshire Building | 2016-07-31 16:45 | 45485.6242 | 640.008
Devonshire Building | 2016-07-31 17:00 | 45485.7842 | 640.008
Devonshire Building | 2016-07-31 17:15 | 45485.9442 | 640.008
Devonshire Building | 2016-07-31 17:30 | 45486.1042 | 640.008
Devonshire Building | 2016-07-31 17:45 | 45486.2642 | 640.008
Devonshire Building | 2016-07-31 18:00 | 45486.4242 | 640.008
Devonshire Building | 2016-07-31 18:15 | 45486.5842 | 640.008
Devonshire Building | 2016-07-31 18:30 | 45486.7442 | 640.008
Devonshire Building | 2016-07-31 18:45 | 45486.9042 | 640.008
Devonshire Building | 2016-07-31 19:00 | 45487.0643 | 640.008
Devonshire Building | 2016-07-31 19:15 | 45487.2243 | 640.008
Devonshire Building | 2016-07-31 19:30 | 45487.3843 | 640.008
Devonshire Building | 2016-07-31 19:45 | 45487.5443 | 640.008
Devonshire Building | 2016-07-31 20:00 | 45487.7093 | 659.988
Devonshire Building | 2016-07-31 20:15 | 45487.8693 | 640.008
Devonshire Building | 2016-07-31 20:30 | 45488.0293 | 640.008
Devonshire Building | 2016-07-31 20:45 | 45488.1893 | 640.008
Devonshire Building | 2016-07-31 21:00 | 45488.3493 | 640.008
Devonshire Building | 2016-07-31 21:15 | 45488.5193 | 680.004
Devonshire Building | 2016-07-31 21:30 | 45488.6793 | 640.008
Devonshire Building | 2016-07-31 21:45 | 45488.8443 | 659.988
Devonshire Building | 2016-07-31 22:00 | 45489.0043 | 640.008
Devonshire Building | 2016-07-31 22:15 | 45489.1643 | 640.008
Devonshire Building | 2016-07-31 22:30 | 45489.3243 | 640.008
Devonshire Building | 2016-07-31 22:45 | 45489.4893 | 659.988
Devonshire Building | 2016-07-31 23:00 | 45489.6493 | 640.008
Devonshire Building | 2016-07-31 23:15 | 45489.8093 | 640.008
Devonshire Building | 2016-07-31 23:30 | 45489.9743 | 659.988
Devonshire Building | 2016-07-31 23:45 | 45490.1343 | 640.008 | 619.992
Devonshire Building | 2016-08-01 | 45490.293 | 640.008
Devonshire Building | 2016-08-01 00:15 | 45490.458 | 659.988
Devonshire Building | 2016-08-01 00:30 | 45490.618 | 640.008
Devonshire Building | 2016-08-01 00:45 | 45490.783 | 659.988
Devonshire Building | 2016-08-01 01:00 | 45490.943 | 640.008
Devonshire Building | 2016-08-01 01:15 | 45491.103 | 640.008
Devonshire Building | 2016-08-01 01:30 | 45491.268 | 659.988
Devonshire Building | 2016-08-01 01:45 | 45491.428 | 640.008
Devonshire Building | 2016-08-01 02:00 | 45491.593 | 659.988
Devonshire Building | 2016-08-01 02:15 | 45491.753 | 640.008
Devonshire Building | 2016-08-01 02:30 | 45491.918 | 659.988
Devonshire Building | 2016-08-01 02:45 | 45492.083 | 659.988
Devonshire Building | 2016-08-01 03:00 | 45492.243 | 640.008
Devonshire Building | 2016-08-01 03:15 | 45492.408 | 659.988
Devonshire Building | 2016-08-01 03:30 | 45492.568 | 640.008
Devonshire Building | 2016-08-01 03:45 | 45492.733 | 659.988
Devonshire Building | 2016-08-01 04:00 | 45492.898 | 659.988
Devonshire Building | 2016-08-01 04:15 | 45493.058 | 640.008
Devonshire Building | 2016-08-01 04:30 | 45493.223 | 659.988
Devonshire Building | 2016-08-01 04:45 | 45493.383 | 640.008
Devonshire Building | 2016-08-01 05:00 | 45493.548 | 659.988
Devonshire Building | 2016-08-01 05:15 | 45493.708 | 640.008
Devonshire Building | 2016-08-01 05:30 | 45493.868 | 640.008
Devonshire Building | 2016-08-01 05:45 | 45494.033 | 659.988
Devonshire Building | 2016-08-01 06:00 | 45494.193 | 640.008
Devonshire Building | 2016-08-01 06:15 | 45494.358 | 659.988
Devonshire Building | 2016-08-01 06:30 | 45494.518 | 640.008
Devonshire Building | 2016-08-01 06:45 | 45494.693 | 699.984
Devonshire Building | 2016-08-01 07:00 | 45494.8579 | 659.988
Devonshire Building | 2016-08-01 07:15 | 45495.2579 | 1599.984
Devonshire Building | 2016-08-01 07:30 | 45495.4279 | 680.004
Devonshire Building | 2016-08-01 07:45 | 45495.5879 | 640.008
Devonshire Building | 2016-08-01 08:00 | 45495.7629 | 699.984
Devonshire Building | 2016-08-01 08:15 | 45495.9279 | 659.988
Devonshire Building | 2016-08-01 08:30 | 45496.0979 | 680.004
Devonshire Building | 2016-08-01 08:45 | 45496.2829 | 740.016
Devonshire Building | 2016-08-01 09:00 | 45496.468 | 740.016
Devonshire Building | 2016-08-01 09:15 | 45496.663 | 780.012
Devonshire Building | 2016-08-01 09:30 | 45497.173 | 2040.012
Devonshire Building | 2016-08-01 09:45 | 45497.488 | 1260
Devonshire Building | 2016-08-01 10:00 | 45497.758 | 1080
Devonshire Building | 2016-08-01 10:15 | 45497.993 | 939.996
Devonshire Building | 2016-08-01 10:30 | 45498.218 | 900
Devonshire Building | 2016-08-01 10:45 | 45498.433 | 860.004
Devonshire Building | 2016-08-01 11:00 | 45498.643 | 839.988
Devonshire Building | 2016-08-01 11:15 | 45499.123 | 1919.988
Devonshire Building | 2016-08-01 11:30 | 45499.3229 | 799.992
Devonshire Building | 2016-08-01 11:45 | 45499.5129 | 759.996
Devonshire Building | 2016-08-01 12:00 | 45499.7329 | 879.984
Devonshire Building | 2016-08-01 12:15 | 45499.9579 | 900
Devonshire Building | 2016-08-01 12:30 | 45500.1729 | 860.004
Devonshire Building | 2016-08-01 12:45 | 45500.3929 | 879.984
Devonshire Building | 2016-08-01 13:00 | 45500.6079 | 860.004
Devonshire Building | 2016-08-01 13:15 | 45501.0629 | 1820.016
Devonshire Building | 2016-08-01 13:30 | 45501.2479 | 740.016
Devonshire Building | 2016-08-01 13:45 | 45501.4279 | 720
Devonshire Building | 2016-08-01 14:00 | 45501.6179 | 759.996
Devonshire Building | 2016-08-01 14:15 | 45501.833 | 860.004
Devonshire Building | 2016-08-01 14:30 | 45502.063 | 920.016
Devonshire Building | 2016-08-01 14:45 | 45502.298 | 939.996
Devonshire Building | 2016-08-01 15:00 | 45502.523 | 900
Devonshire Building | 2016-08-01 15:15 | 45502.983 | 1839.996
Devonshire Building | 2016-08-01 15:30 | 45503.278 | 1180.008
Devonshire Building | 2016-08-01 15:45 | 45503.598 | 1280.016
Devonshire Building | 2016-08-01 16:00 | 45503.863 | 1059.984
Devonshire Building | 2016-08-01 16:15 | 45504.093 | 920.016
Devonshire Building | 2016-08-01 16:30 | 45504.553 | 1839.996
Devonshire Building | 2016-08-01 16:45 | 45504.723 | 680.004
Devonshire Building | 2016-08-01 17:00 | 45504.898 | 699.984
Devonshire Building | 2016-08-01 17:15 | 45505.078 | 720
Devonshire Building | 2016-08-01 17:30 | 45505.258 | 720
Devonshire Building | 2016-08-01 17:45 | 45505.428 | 680.004
Devonshire Building | 2016-08-01 18:00 | 45505.603 | 699.984
Devonshire Building | 2016-08-01 18:15 | 45505.773 | 680.004
Devonshire Building | 2016-08-01 18:30 | 45505.943 | 680.004
Devonshire Building | 2016-08-01 18:45 | 45506.113 | 680.004
Devonshire Building | 2016-08-01 19:00 | 45506.283 | 680.004
Devonshire Building | 2016-08-01 19:15 | 45506.448 | 659.988
Devonshire Building | 2016-08-01 19:30 | 45506.618 | 680.004
Devonshire Building | 2016-08-01 19:45 | 45506.783 | 659.988
Devonshire Building | 2016-08-01 20:00 | 45506.9479 | 659.988
Devonshire Building | 2016-08-01 20:15 | 45507.1129 | 659.988
Devonshire Building | 2016-08-01 20:30 | 45507.2829 | 680.004
Devonshire Building | 2016-08-01 20:45 | 45507.4479 | 659.988
Devonshire Building | 2016-08-01 21:00 | 45507.6129 | 659.988
Devonshire Building | 2016-08-01 21:15 | 45507.7829 | 680.004
Devonshire Building | 2016-08-01 21:30 | 45507.9479 | 659.988
Devonshire Building | 2016-08-01 21:45 | 45508.1079 | 640.008
Devonshire Building | 2016-08-01 22:00 | 45508.2729 | 659.988
Devonshire Building | 2016-08-01 22:15 | 45508.4329 | 640.008
Devonshire Building | 2016-08-01 22:30 | 45508.5979 | 659.988
Devonshire Building | 2016-08-01 22:45 | 45508.7579 | 640.008
Devonshire Building | 2016-08-01 23:00 | 45508.9229 | 659.988
Devonshire Building | 2016-08-01 23:15 | 45509.0879 | 659.988
Devonshire Building | 2016-08-01 23:30 | 45509.2479 | 640.008
Devonshire Building | 2016-08-01 23:45 | 45509.4129 | 659.988 | 640.008
Devonshire Building | 2016-08-02 | 45509.5781 | 659.988
Devonshire Building | 2016-08-02 00:15 | 45509.7431 | 659.988
Devonshire Building | 2016-08-02 00:30 | 45509.9031 | 640.008
Devonshire Building | 2016-08-02 00:45 | 45510.0681 | 659.988
Devonshire Building | 2016-08-02 01:00 | 45510.2331 | 659.988
Devonshire Building | 2016-08-02 01:15 | 45510.3981 | 659.988
Devonshire Building | 2016-08-02 01:30 | 45510.5731 | 699.984
Devonshire Building | 2016-08-02 01:45 | 45510.7531 | 720
Devonshire Building | 2016-08-02 02:00 | 45510.9331 | 720
Devonshire Building | 2016-08-02 02:15 | 45511.1131 | 720
Devonshire Building | 2016-08-02 02:30 | 45511.2981 | 740.016
Devonshire Building | 2016-08-02 02:45 | 45511.4781 | 720
Devonshire Building | 2016-08-02 03:00 | 45511.6581 | 720
Devonshire Building | 2016-08-02 03:15 | 45511.8381 | 720
Devonshire Building | 2016-08-02 03:30 | 45512.0131 | 699.984
Devonshire Building | 2016-08-02 03:45 | 45512.1781 | 659.988
Devonshire Building | 2016-08-02 04:00 | 45512.3381 | 640.008
Devonshire Building | 2016-08-02 04:15 | 45512.5031 | 659.988
Devonshire Building | 2016-08-02 04:30 | 45512.6681 | 659.988
Devonshire Building | 2016-08-02 04:45 | 45512.8281 | 640.008
Devonshire Building | 2016-08-02 05:00 | 45512.9931 | 659.988
Devonshire Building | 2016-08-02 05:15 | 45513.1581 | 659.988
Devonshire Building | 2016-08-02 05:30 | 45513.3181 | 640.008
Devonshire Building | 2016-08-02 05:45 | 45513.4831 | 659.988
Devonshire Building | 2016-08-02 06:00 | 45513.6431 | 640.008
Devonshire Building | 2016-08-02 06:15 | 45513.8031 | 640.008
Devonshire Building | 2016-08-02 06:30 | 45513.9681 | 659.988
Devonshire Building | 2016-08-02 06:45 | 45514.1381 | 680.004
Devonshire Building | 2016-08-02 07:00 | 45514.2981 | 640.008
Devonshire Building | 2016-08-02 07:15 | 45514.7031 | 1620
Devonshire Building | 2016-08-02 07:30 | 45514.8681 | 659.988
Devonshire Building | 2016-08-02 07:45 | 45515.0381 | 680.004
Devonshire Building | 2016-08-02 08:00 | 45515.2031 | 659.988
Devonshire Building | 2016-08-02 08:15 | 45515.3731 | 680.004
Devonshire Building | 2016-08-02 08:30 | 45515.5481 | 699.984
Devonshire Building | 2016-08-02 08:45 | 45515.7431 | 780.012
Devonshire Building | 2016-08-02 09:00 | 45515.9631 | 879.984
Devonshire Building | 2016-08-02 09:15 | 45516.1881 | 900
Devonshire Building | 2016-08-02 09:30 | 45516.7181 | 2120.004
Devonshire Building | 2016-08-02 09:45 | 45517.0631 | 1379.988
Devonshire Building | 2016-08-02 10:00 | 45517.3581 | 1180.008
Devonshire Building | 2016-08-02 10:15 | 45517.6081 | 1000.008
Devonshire Building | 2016-08-02 10:30 | 45517.8281 | 879.984
Devonshire Building | 2016-08-02 10:45 | 45518.0531 | 900
Devonshire Building | 2016-08-02 11:00 | 45518.5181 | 1860.012
Devonshire Building | 2016-08-02 11:15 | 45518.7131 | 780.012
Devonshire Building | 2016-08-02 11:30 | 45518.9231 | 839.988
Devonshire Building | 2016-08-02 11:45 | 45519.1331 | 839.988
Devonshire Building | 2016-08-02 12:00 | 45519.3331 | 799.992
Devonshire Building | 2016-08-02 12:15 | 45519.5331 | 799.992
Devonshire Building | 2016-08-02 12:30 | 45519.7281 | 780.012
Devonshire Building | 2016-08-02 12:45 | 45519.9281 | 799.992
Devonshire Building | 2016-08-02 13:00 | 45520.3881 | 1839.996
Devonshire Building | 2016-08-02 13:15 | 45520.5781 | 759.996
Devonshire Building | 2016-08-02 13:30 | 45520.7781 | 799.992
Devonshire Building | 2016-08-02 13:45 | 45520.9881 | 839.988
Devonshire Building | 2016-08-02 14:00 | 45521.1931 | 820.008
Devonshire Building | 2016-08-02 14:15 | 45521.4031 | 839.988
Devonshire Building | 2016-08-02 14:30 | 45521.6081 | 820.008
Devonshire Building | 2016-08-02 14:45 | 45522.0431 | 1739.988
Devonshire Building | 2016-08-02 15:00 | 45522.2331 | 759.996
Devonshire Building | 2016-08-02 15:15 | 45522.4281 | 780.012
Devonshire Building | 2016-08-02 15:30 | 45522.6181 | 759.996
Devonshire Building | 2016-08-02 15:45 | 45522.8081 | 759.996
Devonshire Building | 2016-08-02 16:00 | 45522.9831 | 699.984
Devonshire Building | 2016-08-02 16:15 | 45523.1581 | 699.984
Devonshire Building | 2016-08-02 16:30 | 45523.3381 | 720
Devonshire Building | 2016-08-02 16:45 | 45523.7531 | 1659.996
Devonshire Building | 2016-08-02 17:00 | 45523.9281 | 699.984
Devonshire Building | 2016-08-02 17:15 | 45524.1081 | 720
Devonshire Building | 2016-08-02 17:30 | 45524.2781 | 680.004
Devonshire Building | 2016-08-02 17:45 | 45524.4681 | 759.996
Devonshire Building | 2016-08-02 18:00 | 45524.6381 | 680.004
Devonshire Building | 2016-08-02 18:15 | 45524.8081 | 680.004
Devonshire Building | 2016-08-02 18:30 | 45524.9781 | 680.004
Devonshire Building | 2016-08-02 18:45 | 45525.1481 | 680.004
Devonshire Building | 2016-08-02 19:00 | 45525.3231 | 699.984
Devonshire Building | 2016-08-02 19:15 | 45525.4931 | 680.004
Devonshire Building | 2016-08-02 19:30 | 45525.6631 | 680.004
Devonshire Building | 2016-08-02 19:45 | 45525.8331 | 680.004
Devonshire Building | 2016-08-02 20:00 | 45526.0031 | 680.004
Devonshire Building | 2016-08-02 20:15 | 45526.1731 | 680.004
Devonshire Building | 2016-08-02 20:30 | 45526.3431 | 680.004
Devonshire Building | 2016-08-02 20:45 | 45526.5131 | 680.004
Devonshire Building | 2016-08-02 21:00 | 45526.6831 | 680.004
Devonshire Building | 2016-08-02 21:15 | 45526.8581 | 699.984
Devonshire Building | 2016-08-02 21:30 | 45527.0231 | 659.988
Devonshire Building | 2016-08-02 21:45 | 45527.1881 | 659.988
Devonshire Building | 2016-08-02 22:00 | 45527.3531 | 659.988
Devonshire Building | 2016-08-02 22:15 | 45527.5181 | 659.988
Devonshire Building | 2016-08-02 22:30 | 45527.6831 | 659.988
Devonshire Building | 2016-08-02 22:45 | 45527.8481 | 659.988
Devonshire Building | 2016-08-02 23:00 | 45528.0131 | 659.988
Devonshire Building | 2016-08-02 23:15 | 45528.1781 | 659.988
Devonshire Building | 2016-08-02 23:30 | 45528.343 | 659.988
Devonshire Building | 2016-08-02 23:45 | 45528.508 | 659.988 | 640.008
Devonshire Building | 2016-08-03 | 45528.6758 | 659.988
Devonshire Building | 2016-08-03 00:15 | 45528.8408 | 659.988
Devonshire Building | 2016-08-03 00:30 | 45529.0058 | 659.988
Devonshire Building | 2016-08-03 00:45 | 45529.1708 | 659.988
Devonshire Building | 2016-08-03 01:00 | 45529.3358 | 659.988
Devonshire Building | 2016-08-03 01:15 | 45529.5008 | 659.988
Devonshire Building | 2016-08-03 01:30 | 45529.6708 | 680.004
Devonshire Building | 2016-08-03 01:45 | 45529.8358 | 659.988
Devonshire Building | 2016-08-03 02:00 | 45530.0008 | 659.988
Devonshire Building | 2016-08-03 02:15 | 45530.1658 | 659.988
Devonshire Building | 2016-08-03 02:30 | 45530.3358 | 680.004
Devonshire Building | 2016-08-03 02:45 | 45530.5008 | 659.988
Devonshire Building | 2016-08-03 03:00 | 45530.6658 | 659.988
Devonshire Building | 2016-08-03 03:15 | 45530.8307 | 659.988
Devonshire Building | 2016-08-03 03:30 | 45530.9957 | 659.988
Devonshire Building | 2016-08-03 03:45 | 45531.1607 | 659.988
Devonshire Building | 2016-08-03 04:00 | 45531.3257 | 659.988
Devonshire Building | 2016-08-03 04:15 | 45531.4907 | 659.988
Devonshire Building | 2016-08-03 04:30 | 45531.6607 | 680.004
Devonshire Building | 2016-08-03 04:45 | 45531.8257 | 659.988
Devonshire Building | 2016-08-03 05:00 | 45531.9907 | 659.988
Devonshire Building | 2016-08-03 05:15 | 45532.1557 | 659.988
Devonshire Building | 2016-08-03 05:30 | 45532.3207 | 659.988
Devonshire Building | 2016-08-03 05:45 | 45532.4857 | 659.988
Devonshire Building | 2016-08-03 06:00 | 45532.6457 | 640.008
Devonshire Building | 2016-08-03 06:15 | 45532.8107 | 659.988
Devonshire Building | 2016-08-03 06:30 | 45532.9757 | 659.988
Devonshire Building | 2016-08-03 06:45 | 45533.1407 | 659.988
Devonshire Building | 2016-08-03 07:00 | 45533.5657 | 1699.992
Devonshire Building | 2016-08-03 07:15 | 45533.7307 | 659.988
Devonshire Building | 2016-08-03 07:30 | 45533.9007 | 680.004
Devonshire Building | 2016-08-03 07:45 | 45534.0757 | 699.984
Devonshire Building | 2016-08-03 08:00 | 45534.2457 | 680.004
Devonshire Building | 2016-08-03 08:15 | 45534.5007 | 1019.988
Devonshire Building | 2016-08-03 08:30 | 45534.7857 | 1140.012
Devonshire Building | 2016-08-03 08:45 | 45535.0657 | 1119.996
Devonshire Building | 2016-08-03 09:00 | 45535.3257 | 1040.004
Devonshire Building | 2016-08-03 09:15 | 45535.5707 | 979.992
Devonshire Building | 2016-08-03 09:30 | 45536.0657 | 1980
Devonshire Building | 2016-08-03 09:45 | 45536.3107 | 979.992
Devonshire Building | 2016-08-03 10:00 | 45536.5407 | 920.016
Devonshire Building | 2016-08-03 10:15 | 45536.7557 | 860.004
Devonshire Building | 2016-08-03 10:30 | 45536.9557 | 799.992
Devonshire Building | 2016-08-03 10:45 | 45537.1507 | 780.012
Devonshire Building | 2016-08-03 11:00 | 45537.3507 | 799.992
Devonshire Building | 2016-08-03 11:15 | 45537.8157 | 1860.012
Devonshire Building | 2016-08-03 11:30 | 45538.0157 | 799.992
Devonshire Building | 2016-08-03 11:45 | 45538.2107 | 780.012
Devonshire Building | 2016-08-03 12:00 | 45538.4057 | 780.012
Devonshire Building | 2016-08-03 12:15 | 45538.6007 | 780.012
Devonshire Building | 2016-08-03 12:30 | 45538.7957 | 780.012
Devonshire Building | 2016-08-03 12:45 | 45538.9857 | 759.996
Devonshire Building | 2016-08-03 13:00 | 45539.1957 | 839.988
Devonshire Building | 2016-08-03 13:15 | 45539.6557 | 1839.996
Devonshire Building | 2016-08-03 13:30 | 45539.8657 | 839.988
Devonshire Building | 2016-08-03 13:45 | 45540.0707 | 820.008
Devonshire Building | 2016-08-03 14:00 | 45540.2807 | 839.988
Devonshire Building | 2016-08-03 14:15 | 45540.4857 | 820.008
Devonshire Building | 2016-08-03 14:30 | 45540.7007 | 860.004
Devonshire Building | 2016-08-03 14:45 | 45540.9107 | 839.988
Devonshire Building | 2016-08-03 15:00 | 45541.1307 | 879.984
Devonshire Building | 2016-08-03 15:15 | 45541.6007 | 1879.992
Devonshire Building | 2016-08-03 15:30 | 45541.8057 | 820.008
Devonshire Building | 2016-08-03 15:45 | 45542.0057 | 799.992
Devonshire Building | 2016-08-03 16:00 | 45542.2007 | 780.012
Devonshire Building | 2016-08-03 16:15 | 45542.4157 | 860.004
Devonshire Building | 2016-08-03 16:30 | 45542.6307 | 860.004
Devonshire Building | 2016-08-03 16:45 | 45542.8457 | 860.004
Devonshire Building | 2016-08-03 17:00 | 45543.0557 | 839.988
Devonshire Building | 2016-08-03 17:15 | 45543.2657 | 839.988
Devonshire Building | 2016-08-03 17:30 | 45543.4607 | 780.012
Devonshire Building | 2016-08-03 17:45 | 45543.6557 | 780.012
Devonshire Building | 2016-08-03 18:00 | 45543.8457 | 759.996
Devonshire Building | 2016-08-03 18:15 | 45544.0307 | 740.016
Devonshire Building | 2016-08-03 18:30 | 45544.2107 | 720
Devonshire Building | 2016-08-03 18:45 | 45544.3907 | 720
Devonshire Building | 2016-08-03 19:00 | 45544.5657 | 699.984
Devonshire Building | 2016-08-03 19:15 | 45544.7407 | 699.984
Devonshire Building | 2016-08-03 19:30 | 45545.1407 | 1599.984
Devonshire Building | 2016-08-03 19:45 | 45545.3057 | 659.988
Devonshire Building | 2016-08-03 20:00 | 45545.4707 | 659.988
Devonshire Building | 2016-08-03 20:15 | 45545.6357 | 659.988
Devonshire Building | 2016-08-03 20:30 | 45545.8007 | 659.988
Devonshire Building | 2016-08-03 20:45 | 45545.9657 | 659.988
Devonshire Building | 2016-08-03 21:00 | 45546.1307 | 659.988
Devonshire Building | 2016-08-03 21:15 | 45546.3057 | 699.984
Devonshire Building | 2016-08-03 21:30 | 45546.4707 | 659.988
Devonshire Building | 2016-08-03 21:45 | 45546.6357 | 659.988
Devonshire Building | 2016-08-03 22:00 | 45546.8007 | 659.988
Devonshire Building | 2016-08-03 22:15 | 45546.9657 | 659.988
Devonshire Building | 2016-08-03 22:30 | 45547.1307 | 659.988
Devonshire Building | 2016-08-03 22:45 | 45547.3007 | 680.004
Devonshire Building | 2016-08-03 23:00 | 45547.4657 | 659.988
Devonshire Building | 2016-08-03 23:15 | 45547.6307 | 659.988
Devonshire Building | 2016-08-03 23:30 | 45547.7957 | 659.988
Devonshire Building | 2016-08-03 23:45 | 45547.9607 | 659.988 | 640.008
Devonshire Building | 2016-08-04 | 45548.1289 | 680.004
Devonshire Building | 2016-08-04 00:15 | 45548.2939 | 659.988
Devonshire Building | 2016-08-04 00:30 | 45548.4589 | 659.988
Devonshire Building | 2016-08-04 00:45 | 45548.6239 | 659.988
Devonshire Building | 2016-08-04 01:00 | 45548.7939 | 680.004
Devonshire Building | 2016-08-04 01:15 | 45548.9589 | 659.988
Devonshire Building | 2016-08-04 01:30 | 45549.1239 | 659.988
Devonshire Building | 2016-08-04 01:45 | 45549.2889 | 659.988
Devonshire Building | 2016-08-04 02:00 | 45549.4539 | 659.988
Devonshire Building | 2016-08-04 02:15 | 45549.6239 | 680.004
Devonshire Building | 2016-08-04 02:30 | 45549.7889 | 659.988
Devonshire Building | 2016-08-04 02:45 | 45549.9539 | 659.988
Devonshire Building | 2016-08-04 03:00 | 45550.1189 | 659.988
Devonshire Building | 2016-08-04 03:15 | 45550.2839 | 659.988
Devonshire Building | 2016-08-04 03:30 | 45550.4489 | 659.988
Devonshire Building | 2016-08-04 03:45 | 45550.6189 | 680.004
Devonshire Building | 2016-08-04 04:00 | 45550.7839 | 659.988
Devonshire Building | 2016-08-04 04:15 | 45550.9489 | 659.988
Devonshire Building | 2016-08-04 04:30 | 45551.1139 | 659.988
Devonshire Building | 2016-08-04 04:45 | 45551.2789 | 659.988
Devonshire Building | 2016-08-04 05:00 | 45551.4489 | 680.004
Devonshire Building | 2016-08-04 05:15 | 45551.6139 | 659.988
Devonshire Building | 2016-08-04 05:30 | 45551.7789 | 659.988
Devonshire Building | 2016-08-04 05:45 | 45551.9439 | 659.988
Devonshire Building | 2016-08-04 06:00 | 45552.1039 | 640.008
Devonshire Building | 2016-08-04 06:15 | 45552.2689 | 659.988
Devonshire Building | 2016-08-04 06:30 | 45552.4339 | 659.988
Devonshire Building | 2016-08-04 06:45 | 45552.6039 | 680.004
Devonshire Building | 2016-08-04 07:00 | 45552.7839 | 720
Devonshire Building | 2016-08-04 07:15 | 45552.9489 | 659.988
Devonshire Building | 2016-08-04 07:30 | 45553.1138 | 659.988
Devonshire Building | 2016-08-04 07:45 | 45553.2738 | 640.008
Devonshire Building | 2016-08-04 08:00 | 45553.4388 | 659.988
Devonshire Building | 2016-08-04 08:15 | 45553.8489 | 1640.016
Devonshire Building | 2016-08-04 08:30 | 45554.0138 | 659.988
Devonshire Building | 2016-08-04 08:45 | 45554.1788 | 659.988
Devonshire Building | 2016-08-04 09:00 | 45554.3488 | 680.004
Devonshire Building | 2016-08-04 09:15 | 45554.5088 | 640.008
Devonshire Building | 2016-08-04 09:30 | 45554.6738 | 659.988
Devonshire Building | 2016-08-04 09:45 | 45554.8438 | 680.004
Devonshire Building | 2016-08-04 10:00 | 45555.0088 | 659.988
Devonshire Building | 2016-08-04 10:15 | 45555.1938 | 740.016
Devonshire Building | 2016-08-04 10:30 | 45555.6888 | 1980
Devonshire Building | 2016-08-04 10:45 | 45555.9088 | 879.984
Devonshire Building | 2016-08-04 11:00 | 45556.1338 | 900
Devonshire Building | 2016-08-04 11:15 | 45556.3488 | 860.004
Devonshire Building | 2016-08-04 11:30 | 45556.5588 | 839.988
Devonshire Building | 2016-08-04 11:45 | 45556.7588 | 799.992
Devonshire Building | 2016-08-04 12:00 | 45556.9488 | 759.996
Devonshire Building | 2016-08-04 12:15 | 45557.2388 | 1159.992
Devonshire Building | 2016-08-04 12:30 | 45557.5838 | 1379.988
Devonshire Building | 2016-08-04 12:45 | 45557.7888 | 820.008
Devonshire Building | 2016-08-04 13:00 | 45557.9838 | 780.012
Devonshire Building | 2016-08-04 13:15 | 45558.1788 | 780.012
Devonshire Building | 2016-08-04 13:30 | 45558.3788 | 799.992
Devonshire Building | 2016-08-04 13:45 | 45558.6088 | 920.016
Devonshire Building | 2016-08-04 14:00 | 45559.0288 | 1680.012
Devonshire Building | 2016-08-04 14:15 | 45559.3939 | 1460.016
Devonshire Building | 2016-08-04 14:30 | 45559.6789 | 1140.012
Devonshire Building | 2016-08-04 14:45 | 45559.9739 | 1180.008
Devonshire Building | 2016-08-04 15:00 | 45560.2489 | 1100.016
Devonshire Building | 2016-08-04 15:15 | 45560.5289 | 1119.996
Devonshire Building | 2016-08-04 15:30 | 45560.7739 | 979.992
Devonshire Building | 2016-08-04 15:45 | 45560.9989 | 900
Devonshire Building | 2016-08-04 16:00 | 45561.2039 | 820.008
Devonshire Building | 2016-08-04 16:15 | 45561.6289 | 1699.992
Devonshire Building | 2016-08-04 16:30 | 45561.8089 | 720
Devonshire Building | 2016-08-04 16:45 | 45561.9839 | 699.984
Devonshire Building | 2016-08-04 17:00 | 45562.1588 | 699.984
Devonshire Building | 2016-08-04 17:15 | 45562.3338 | 699.984
Devonshire Building | 2016-08-04 17:30 | 45562.5038 | 680.004
Devonshire Building | 2016-08-04 17:45 | 45562.6788 | 699.984
Devonshire Building | 2016-08-04 18:00 | 45562.8538 | 699.984
Devonshire Building | 2016-08-04 18:15 | 45563.0288 | 699.984
Devonshire Building | 2016-08-04 18:30 | 45563.1988 | 680.004
Devonshire Building | 2016-08-04 18:45 | 45563.3738 | 699.984
Devonshire Building | 2016-08-04 19:00 | 45563.5488 | 699.984
Devonshire Building | 2016-08-04 19:15 | 45563.7188 | 680.004
Devonshire Building | 2016-08-04 19:30 | 45563.8938 | 699.984
Devonshire Building | 2016-08-04 19:45 | 45564.0638 | 680.004
Devonshire Building | 2016-08-04 20:00 | 45564.2388 | 699.984
Devonshire Building | 2016-08-04 20:15 | 45564.4088 | 680.004
Devonshire Building | 2016-08-04 20:30 | 45564.5838 | 699.984
Devonshire Building | 2016-08-04 20:45 | 45564.7538 | 680.004
Devonshire Building | 2016-08-04 21:00 | 45564.9238 | 680.004
Devonshire Building | 2016-08-04 21:15 | 45565.1088 | 740.016
Devonshire Building | 2016-08-04 21:30 | 45565.2738 | 659.988
Devonshire Building | 2016-08-04 21:45 | 45565.4388 | 659.988
Devonshire Building | 2016-08-04 22:00 | 45565.6038 | 659.988
Devonshire Building | 2016-08-04 22:15 | 45565.7688 | 659.988
Devonshire Building | 2016-08-04 22:30 | 45565.9338 | 659.988
Devonshire Building | 2016-08-04 22:45 | 45566.0988 | 659.988
Devonshire Building | 2016-08-04 23:00 | 45566.2688 | 680.004
Devonshire Building | 2016-08-04 23:15 | 45566.4338 | 659.988
Devonshire Building | 2016-08-04 23:30 | 45566.5988 | 659.988
Devonshire Building | 2016-08-04 23:45 | 45566.7638 | 659.988 | 640.008
Devonshire Building | 2016-08-05 | 45566.9297 | 659.988
Devonshire Building | 2016-08-05 00:15 | 45567.0947 | 659.988
Devonshire Building | 2016-08-05 00:30 | 45567.2597 | 659.988
Devonshire Building | 2016-08-05 00:45 | 45567.4247 | 659.988
Devonshire Building | 2016-08-05 01:00 | 45567.5897 | 659.988
Devonshire Building | 2016-08-05 01:15 | 45567.7547 | 659.988
Devonshire Building | 2016-08-05 01:30 | 45567.9197 | 659.988
Devonshire Building | 2016-08-05 01:45 | 45568.0847 | 659.988
Devonshire Building | 2016-08-05 02:00 | 45568.2497 | 659.988
Devonshire Building | 2016-08-05 02:15 | 45568.4147 | 659.988
Devonshire Building | 2016-08-05 02:30 | 45568.5847 | 680.004
Devonshire Building | 2016-08-05 02:45 | 45568.7497 | 659.988
Devonshire Building | 2016-08-05 03:00 | 45568.9147 | 659.988
Devonshire Building | 2016-08-05 03:15 | 45569.0797 | 659.988
Devonshire Building | 2016-08-05 03:30 | 45569.2447 | 659.988
Devonshire Building | 2016-08-05 03:45 | 45569.4096 | 659.988
Devonshire Building | 2016-08-05 04:00 | 45569.5796 | 680.004
Devonshire Building | 2016-08-05 04:15 | 45569.7446 | 659.988
Devonshire Building | 2016-08-05 04:30 | 45569.9096 | 659.988
Devonshire Building | 2016-08-05 04:45 | 45570.0746 | 659.988
Devonshire Building | 2016-08-05 05:00 | 45570.2396 | 659.988
Devonshire Building | 2016-08-05 05:15 | 45570.4046 | 659.988
Devonshire Building | 2016-08-05 05:30 | 45570.5696 | 659.988
Devonshire Building | 2016-08-05 05:45 | 45570.9646 | 1580.004
Devonshire Building | 2016-08-05 06:00 | 45571.1296 | 659.988
Devonshire Building | 2016-08-05 06:15 | 45571.2946 | 659.988
Devonshire Building | 2016-08-05 06:30 | 45571.4546 | 640.008
Devonshire Building | 2016-08-05 06:45 | 45571.6246 | 680.004
Devonshire Building | 2016-08-05 07:00 | 45571.8046 | 720
Devonshire Building | 2016-08-05 07:15 | 45571.9696 | 659.988
Devonshire Building | 2016-08-05 07:30 | 45572.1346 | 659.988
Devonshire Building | 2016-08-05 07:45 | 45572.3046 | 680.004
Devonshire Building | 2016-08-05 08:00 | 45572.4696 | 659.988
Devonshire Building | 2016-08-05 08:15 | 45572.6396 | 680.004
Devonshire Building | 2016-08-05 08:30 | 45573.0546 | 1659.996
Devonshire Building | 2016-08-05 08:45 | 45573.2296 | 699.984
Devonshire Building | 2016-08-05 09:00 | 45573.4096 | 720
Devonshire Building | 2016-08-05 09:15 | 45573.5996 | 759.996
Devonshire Building | 2016-08-05 09:30 | 45573.8096 | 839.988
Devonshire Building | 2016-08-05 09:45 | 45574.0346 | 900
Devonshire Building | 2016-08-05 10:00 | 45574.2846 | 1000.008
Devonshire Building | 2016-08-05 10:15 | 45574.5246 | 960.012
Devonshire Building | 2016-08-05 10:30 | 45574.9946 | 1879.992
Devonshire Building | 2016-08-05 10:45 | 45575.1996 | 820.008
Devonshire Building | 2016-08-05 11:00 | 45575.4146 | 860.004
Devonshire Building | 2016-08-05 11:15 | 45575.6346 | 879.984
Devonshire Building | 2016-08-05 11:30 | 45575.8746 | 960.012
Devonshire Building | 2016-08-05 11:45 | 45576.1246 | 1000.008
Devonshire Building | 2016-08-05 12:00 | 45576.3646 | 960.012
Devonshire Building | 2016-08-05 12:15 | 45576.8646 | 2000.016
Devonshire Building | 2016-08-05 12:30 | 45577.2046 | 1360.008
Devonshire Building | 2016-08-05 12:45 | 45577.5296 | 1299.996
Devonshire Building | 2016-08-05 13:00 | 45577.8096 | 1119.996
Devonshire Building | 2016-08-05 13:15 | 45578.0496 | 960.012
Devonshire Building | 2016-08-05 13:30 | 45578.2796 | 920.016
Devonshire Building | 2016-08-05 13:45 | 45578.4996 | 879.984
Devonshire Building | 2016-08-05 14:00 | 45578.9646 | 1860.012
Devonshire Building | 2016-08-05 14:15 | 45579.1596 | 780.012
Devonshire Building | 2016-08-05 14:30 | 45579.3546 | 780.012
Devonshire Building | 2016-08-05 14:45 | 45579.5546 | 799.992
Devonshire Building | 2016-08-05 15:00 | 45579.7546 | 799.992
Devonshire Building | 2016-08-05 15:15 | 45579.9496 | 780.012
Devonshire Building | 2016-08-05 15:30 | 45580.1596 | 839.988
Devonshire Building | 2016-08-05 15:45 | 45580.3796 | 879.984
Devonshire Building | 2016-08-05 16:00 | 45580.8546 | 1900.008
Devonshire Building | 2016-08-05 16:15 | 45581.1646 | 1239.984
Devonshire Building | 2016-08-05 16:30 | 45581.5396 | 1500.012
Devonshire Building | 2016-08-05 16:45 | 45581.8596 | 1280.016
Devonshire Building | 2016-08-05 17:00 | 45582.1296 | 1080
Devonshire Building | 2016-08-05 17:15 | 45582.3996 | 1080
Devonshire Building | 2016-08-05 17:30 | 45582.6446 | 979.992
Devonshire Building | 2016-08-05 17:45 | 45582.8696 | 900
Devonshire Building | 2016-08-05 18:00 | 45583.0746 | 820.008
Devonshire Building | 2016-08-05 18:15 | 45583.2746 | 799.992
Devonshire Building | 2016-08-05 18:30 | 45583.4646 | 759.996
Devonshire Building | 2016-08-05 18:45 | 45583.6446 | 720
Devonshire Building | 2016-08-05 19:00 | 45583.8296 | 740.016
Devonshire Building | 2016-08-05 19:15 | 45584.0046 | 699.984
Devonshire Building | 2016-08-05 19:30 | 45584.1846 | 720
Devonshire Building | 2016-08-05 19:45 | 45584.3546 | 680.004
Devonshire Building | 2016-08-05 20:00 | 45584.5296 | 699.984
Devonshire Building | 2016-08-05 20:15 | 45584.7046 | 699.984
Devonshire Building | 2016-08-05 20:30 | 45584.8746 | 680.004
Devonshire Building | 2016-08-05 20:45 | 45585.0446 | 680.004
Devonshire Building | 2016-08-05 21:00 | 45585.2146 | 680.004
Devonshire Building | 2016-08-05 21:15 | 45585.4046 | 759.996
Devonshire Building | 2016-08-05 21:30 | 45585.5646 | 640.008
Devonshire Building | 2016-08-05 21:45 | 45585.7296 | 659.988
Devonshire Building | 2016-08-05 22:00 | 45585.8946 | 659.988
Devonshire Building | 2016-08-05 22:15 | 45586.0596 | 659.988
Devonshire Building | 2016-08-05 22:30 | 45586.2246 | 659.988
Devonshire Building | 2016-08-05 22:45 | 45586.3896 | 659.988
Devonshire Building | 2016-08-05 23:00 | 45586.5546 | 659.988
Devonshire Building | 2016-08-05 23:15 | 45586.7196 | 659.988
Devonshire Building | 2016-08-05 23:30 | 45586.8846 | 659.988
Devonshire Building | 2016-08-05 23:45 | 45587.0496 | 659.988 | 640.008
Devonshire Building | 2016-08-06 | 45587.2148 | 659.988
Devonshire Building | 2016-08-06 00:15 | 45587.3798 | 659.988
Devonshire Building | 2016-08-06 00:30 | 45587.5448 | 659.988
Devonshire Building | 2016-08-06 00:45 | 45587.7098 | 659.988
Devonshire Building | 2016-08-06 01:00 | 45587.8748 | 659.988
Devonshire Building | 2016-08-06 01:15 | 45588.2798 | 1620
Devonshire Building | 2016-08-06 01:30 | 45588.4498 | 680.004
Devonshire Building | 2016-08-06 01:45 | 45588.6148 | 659.988
Devonshire Building | 2016-08-06 02:00 | 45588.7798 | 659.988
Devonshire Building | 2016-08-06 02:15 | 45588.9448 | 659.988
Devonshire Building | 2016-08-06 02:30 | 45589.1098 | 659.988
Devonshire Building | 2016-08-06 02:45 | 45589.2748 | 659.988
Devonshire Building | 2016-08-06 03:00 | 45589.4398 | 659.988
Devonshire Building | 2016-08-06 03:15 | 45589.6098 | 680.004
Devonshire Building | 2016-08-06 03:30 | 45589.7748 | 659.988
Devonshire Building | 2016-08-06 03:45 | 45589.9398 | 659.988
Devonshire Building | 2016-08-06 04:00 | 45590.1048 | 659.988
Devonshire Building | 2016-08-06 04:15 | 45590.2698 | 659.988
Devonshire Building | 2016-08-06 04:30 | 45590.4348 | 659.988
Devonshire Building | 2016-08-06 04:45 | 45590.5998 | 659.988
Devonshire Building | 2016-08-06 05:00 | 45590.7698 | 680.004
Devonshire Building | 2016-08-06 05:15 | 45590.9348 | 659.988
Devonshire Building | 2016-08-06 05:30 | 45591.0998 | 659.988
Devonshire Building | 2016-08-06 05:45 | 45591.2648 | 659.988
Devonshire Building | 2016-08-06 06:00 | 45591.4298 | 659.988
Devonshire Building | 2016-08-06 06:15 | 45591.5948 | 659.988
Devonshire Building | 2016-08-06 06:30 | 45591.7598 | 659.988
Devonshire Building | 2016-08-06 06:45 | 45591.9248 | 659.988
Devonshire Building | 2016-08-06 07:00 | 45592.0898 | 659.988
Devonshire Building | 2016-08-06 07:15 | 45592.2498 | 640.008
Devonshire Building | 2016-08-06 07:30 | 45592.4148 | 659.988
Devonshire Building | 2016-08-06 07:45 | 45592.5748 | 640.008
Devonshire Building | 2016-08-06 08:00 | 45592.7398 | 659.988
Devonshire Building | 2016-08-06 08:15 | 45592.9048 | 659.988
Devonshire Building | 2016-08-06 08:30 | 45593.0648 | 640.008
Devonshire Building | 2016-08-06 08:45 | 45593.2248 | 640.008
Devonshire Building | 2016-08-06 09:00 | 45593.3898 | 659.988
Devonshire Building | 2016-08-06 09:15 | 45593.5498 | 640.008
Devonshire Building | 2016-08-06 09:30 | 45593.7098 | 640.008
Devonshire Building | 2016-08-06 09:45 | 45593.8748 | 659.988
Devonshire Building | 2016-08-06 10:00 | 45594.0348 | 640.008
Devonshire Building | 2016-08-06 10:15 | 45594.1948 | 640.008
Devonshire Building | 2016-08-06 10:30 | 45594.3548 | 640.008
Devonshire Building | 2016-08-06 10:45 | 45594.5198 | 659.988
Devonshire Building | 2016-08-06 11:00 | 45594.6798 | 640.008
Devonshire Building | 2016-08-06 11:15 | 45594.8398 | 640.008
Devonshire Building | 2016-08-06 11:30 | 45595.0048 | 659.988
Devonshire Building | 2016-08-06 11:45 | 45595.1698 | 659.988
Devonshire Building | 2016-08-06 12:00 | 45595.3298 | 640.008
Devonshire Building | 2016-08-06 12:15 | 45595.4948 | 659.988
Devonshire Building | 2016-08-06 12:30 | 45595.6598 | 659.988
Devonshire Building | 2016-08-06 12:45 | 45595.8248 | 659.988
Devonshire Building | 2016-08-06 13:00 | 45595.9898 | 659.988
Devonshire Building | 2016-08-06 13:15 | 45596.1498 | 640.008
Devonshire Building | 2016-08-06 13:30 | 45596.3198 | 680.004
Devonshire Building | 2016-08-06 13:45 | 45596.4998 | 720
Devonshire Building | 2016-08-06 14:00 | 45596.6798 | 720
Devonshire Building | 2016-08-06 14:15 | 45596.8598 | 720
Devonshire Building | 2016-08-06 14:30 | 45597.0398 | 720
Devonshire Building | 2016-08-06 14:45 | 45597.2198 | 720
Devonshire Building | 2016-08-06 15:00 | 45597.3998 | 720
Devonshire Building | 2016-08-06 15:15 | 45597.5848 | 740.016
Devonshire Building | 2016-08-06 15:30 | 45597.7498 | 659.988
Devonshire Building | 2016-08-06 15:45 | 45597.9098 | 640.008
Devonshire Building | 2016-08-06 16:00 | 45598.0748 | 659.988
Devonshire Building | 2016-08-06 16:15 | 45598.2398 | 659.988
Devonshire Building | 2016-08-06 16:30 | 45598.3998 | 640.008
Devonshire Building | 2016-08-06 16:45 | 45598.5648 | 659.988
Devonshire Building | 2016-08-06 17:00 | 45598.7248 | 640.008
Devonshire Building | 2016-08-06 17:15 | 45598.8898 | 659.988
Devonshire Building | 2016-08-06 17:30 | 45599.0498 | 640.008
Devonshire Building | 2016-08-06 17:45 | 45599.4448 | 1580.004
Devonshire Building | 2016-08-06 18:00 | 45599.6098 | 659.988
Devonshire Building | 2016-08-06 18:15 | 45599.7698 | 640.008
Devonshire Building | 2016-08-06 18:30 | 45599.9298 | 640.008
Devonshire Building | 2016-08-06 18:45 | 45600.0948 | 659.988
Devonshire Building | 2016-08-06 19:00 | 45600.2548 | 640.008
Devonshire Building | 2016-08-06 19:15 | 45600.4198 | 659.988
Devonshire Building | 2016-08-06 19:30 | 45600.5798 | 640.008
Devonshire Building | 2016-08-06 19:45 | 45600.7448 | 659.988
Devonshire Building | 2016-08-06 20:00 | 45600.9048 | 640.008
Devonshire Building | 2016-08-06 20:15 | 45601.0698 | 659.988
Devonshire Building | 2016-08-06 20:30 | 45601.2348 | 659.988
Devonshire Building | 2016-08-06 20:45 | 45601.3948 | 640.008
Devonshire Building | 2016-08-06 21:00 | 45601.5598 | 659.988
Devonshire Building | 2016-08-06 21:15 | 45601.7298 | 680.004
Devonshire Building | 2016-08-06 21:30 | 45601.8947 | 659.988
Devonshire Building | 2016-08-06 21:45 | 45602.0597 | 659.988
Devonshire Building | 2016-08-06 22:00 | 45602.2197 | 640.008
Devonshire Building | 2016-08-06 22:15 | 45602.3847 | 659.988
Devonshire Building | 2016-08-06 22:30 | 45602.5497 | 659.988
Devonshire Building | 2016-08-06 22:45 | 45602.7147 | 659.988
Devonshire Building | 2016-08-06 23:00 | 45602.8797 | 659.988
Devonshire Building | 2016-08-06 23:15 | 45603.0397 | 640.008
Devonshire Building | 2016-08-06 23:30 | 45603.2047 | 659.988
Devonshire Building | 2016-08-06 23:45 | 45603.3697 | 659.988 | 640.008
Devonshire Building | 2016-08-07 | 45603.5352 | 659.988
Devonshire Building | 2016-08-07 00:15 | 45603.7002 | 659.988
Devonshire Building | 2016-08-07 00:30 | 45603.8652 | 659.988
Devonshire Building | 2016-08-07 00:45 | 45604.0302 | 659.988
Devonshire Building | 2016-08-07 01:00 | 45604.1951 | 659.988
Devonshire Building | 2016-08-07 01:15 | 45604.3601 | 659.988
Devonshire Building | 2016-08-07 01:30 | 45604.5201 | 640.008
Devonshire Building | 2016-08-07 01:45 | 45604.6851 | 659.988
Devonshire Building | 2016-08-07 02:00 | 45604.8501 | 659.988
Devonshire Building | 2016-08-07 02:15 | 45605.0151 | 659.988
Devonshire Building | 2016-08-07 02:30 | 45605.1801 | 659.988
Devonshire Building | 2016-08-07 02:45 | 45605.3451 | 659.988
Devonshire Building | 2016-08-07 03:00 | 45605.5101 | 659.988
Devonshire Building | 2016-08-07 03:15 | 45605.6751 | 659.988
Devonshire Building | 2016-08-07 03:30 | 45605.8401 | 659.988
Devonshire Building | 2016-08-07 03:45 | 45606.0051 | 659.988
Devonshire Building | 2016-08-07 04:00 | 45606.1701 | 659.988
Devonshire Building | 2016-08-07 04:15 | 45606.3351 | 659.988
Devonshire Building | 2016-08-07 04:30 | 45606.5001 | 659.988
Devonshire Building | 2016-08-07 04:45 | 45606.6651 | 659.988
Devonshire Building | 2016-08-07 05:00 | 45606.8301 | 659.988
Devonshire Building | 2016-08-07 05:15 | 45606.9951 | 659.988
Devonshire Building | 2016-08-07 05:30 | 45607.1601 | 659.988
Devonshire Building | 2016-08-07 05:45 | 45607.3251 | 659.988
Devonshire Building | 2016-08-07 06:00 | 45607.4901 | 659.988
Devonshire Building | 2016-08-07 06:15 | 45607.6551 | 659.988
Devonshire Building | 2016-08-07 06:30 | 45607.8201 | 659.988
Devonshire Building | 2016-08-07 06:45 | 45607.9851 | 659.988
Devonshire Building | 2016-08-07 07:00 | 45608.1451 | 640.008
Devonshire Building | 2016-08-07 07:15 | 45608.3101 | 659.988
Devonshire Building | 2016-08-07 07:30 | 45608.4751 | 659.988
Devonshire Building | 2016-08-07 07:45 | 45608.6351 | 640.008
Devonshire Building | 2016-08-07 08:00 | 45608.8001 | 659.988
Devonshire Building | 2016-08-07 08:15 | 45608.9601 | 640.008
Devonshire Building | 2016-08-07 08:30 | 45609.1201 | 640.008
Devonshire Building | 2016-08-07 08:45 | 45609.2851 | 659.988
Devonshire Building | 2016-08-07 09:00 | 45609.4451 | 640.008
Devonshire Building | 2016-08-07 09:15 | 45609.6101 | 659.988
Devonshire Building | 2016-08-07 09:30 | 45609.7701 | 640.008
Devonshire Building | 2016-08-07 09:45 | 45609.9351 | 659.988
Devonshire Building | 2016-08-07 10:00 | 45610.0951 | 640.008
Devonshire Building | 2016-08-07 10:15 | 45610.2551 | 640.008
Devonshire Building | 2016-08-07 10:30 | 45610.4201 | 659.988
Devonshire Building | 2016-08-07 10:45 | 45610.5801 | 640.008
Devonshire Building | 2016-08-07 11:00 | 45610.7451 | 659.988
Devonshire Building | 2016-08-07 11:15 | 45610.9051 | 640.008
Devonshire Building | 2016-08-07 11:30 | 45611.0701 | 659.988
Devonshire Building | 2016-08-07 11:45 | 45611.2301 | 640.008
Devonshire Building | 2016-08-07 12:00 | 45611.3951 | 659.988
Devonshire Building | 2016-08-07 12:15 | 45611.5601 | 659.988
Devonshire Building | 2016-08-07 12:30 | 45611.7201 | 640.008
Devonshire Building | 2016-08-07 12:45 | 45611.8851 | 659.988
Devonshire Building | 2016-08-07 13:00 | 45612.0451 | 640.008
Devonshire Building | 2016-08-07 13:15 | 45612.2101 | 659.988
Devonshire Building | 2016-08-07 13:30 | 45612.3851 | 699.984
Devonshire Building | 2016-08-07 13:45 | 45612.5651 | 720
Devonshire Building | 2016-08-07 14:00 | 45612.7451 | 720
Devonshire Building | 2016-08-07 14:15 | 45612.9201 | 699.984
Devonshire Building | 2016-08-07 14:30 | 45613.1001 | 720
Devonshire Building | 2016-08-07 14:45 | 45613.2801 | 720
Devonshire Building | 2016-08-07 15:00 | 45613.4601 | 720
Devonshire Building | 2016-08-07 15:15 | 45613.6401 | 720
Devonshire Building | 2016-08-07 15:30 | 45614.0401 | 1599.984
Devonshire Building | 2016-08-07 15:45 | 45614.2051 | 659.988
Devonshire Building | 2016-08-07 16:00 | 45614.3651 | 640.008
Devonshire Building | 2016-08-07 16:15 | 45614.5251 | 640.008
Devonshire Building | 2016-08-07 16:30 | 45614.6901 | 659.988
Devonshire Building | 2016-08-07 16:45 | 45614.8501 | 640.008
Devonshire Building | 2016-08-07 17:00 | 45615.0101 | 640.008
Devonshire Building | 2016-08-07 17:15 | 45615.1751 | 659.988
Devonshire Building | 2016-08-07 17:30 | 45615.3351 | 640.008
Devonshire Building | 2016-08-07 17:45 | 45615.5001 | 659.988
Devonshire Building | 2016-08-07 18:00 | 45615.6601 | 640.008
Devonshire Building | 2016-08-07 18:15 | 45615.8201 | 640.008
Devonshire Building | 2016-08-07 18:30 | 45615.9851 | 659.988
Devonshire Building | 2016-08-07 18:45 | 45616.1451 | 640.008
Devonshire Building | 2016-08-07 19:00 | 45616.3051 | 640.008
Devonshire Building | 2016-08-07 19:15 | 45616.4701 | 659.988
Devonshire Building | 2016-08-07 19:30 | 45616.6401 | 680.004
Devonshire Building | 2016-08-07 19:45 | 45616.8001 | 640.008
Devonshire Building | 2016-08-07 20:00 | 45616.9651 | 659.988
Devonshire Building | 2016-08-07 20:15 | 45617.1251 | 640.008
Devonshire Building | 2016-08-07 20:30 | 45617.2901 | 659.988
Devonshire Building | 2016-08-07 20:45 | 45617.4501 | 640.008
Devonshire Building | 2016-08-07 21:00 | 45617.6151 | 659.988
Devonshire Building | 2016-08-07 21:15 | 45617.7851 | 680.004
Devonshire Building | 2016-08-07 21:30 | 45617.9501 | 659.988
Devonshire Building | 2016-08-07 21:45 | 45618.1101 | 640.008
Devonshire Building | 2016-08-07 22:00 | 45618.2751 | 659.988
Devonshire Building | 2016-08-07 22:15 | 45618.4351 | 640.008
Devonshire Building | 2016-08-07 22:30 | 45618.6001 | 659.988
Devonshire Building | 2016-08-07 22:45 | 45618.7601 | 640.008
Devonshire Building | 2016-08-07 23:00 | 45618.9251 | 659.988
Devonshire Building | 2016-08-07 23:15 | 45619.09 | 659.988
Devonshire Building | 2016-08-07 23:30 | 45619.255 | 659.988
Devonshire Building | 2016-08-07 23:45 | 45619.415 | 640.008 | 640.008
Devonshire Building | 2016-08-08 | 45619.5781 | 659.988
Devonshire Building | 2016-08-08 00:15 | 45619.7431 | 659.988
Devonshire Building | 2016-08-08 00:30 | 45619.9081 | 659.988
Devonshire Building | 2016-08-08 00:45 | 45620.0731 | 659.988
Devonshire Building | 2016-08-08 01:00 | 45620.2331 | 640.008
Devonshire Building | 2016-08-08 01:15 | 45620.3981 | 659.988
Devonshire Building | 2016-08-08 01:30 | 45620.5631 | 659.988
Devonshire Building | 2016-08-08 01:45 | 45620.7281 | 659.988
Devonshire Building | 2016-08-08 02:00 | 45620.8931 | 659.988
Devonshire Building | 2016-08-08 02:15 | 45621.0581 | 659.988
Devonshire Building | 2016-08-08 02:30 | 45621.2231 | 659.988
Devonshire Building | 2016-08-08 02:45 | 45621.3831 | 640.008
Devonshire Building | 2016-08-08 03:00 | 45621.5481 | 659.988
Devonshire Building | 2016-08-08 03:15 | 45621.7131 | 659.988
Devonshire Building | 2016-08-08 03:30 | 45621.8781 | 659.988
Devonshire Building | 2016-08-08 03:45 | 45622.0381 | 640.008
Devonshire Building | 2016-08-08 04:00 | 45622.2031 | 659.988
Devonshire Building | 2016-08-08 04:15 | 45622.3681 | 659.988
Devonshire Building | 2016-08-08 04:30 | 45622.5331 | 659.988
Devonshire Building | 2016-08-08 04:45 | 45622.6931 | 640.008
Devonshire Building | 2016-08-08 05:00 | 45622.8581 | 659.988
Devonshire Building | 2016-08-08 05:15 | 45623.0231 | 659.988
Devonshire Building | 2016-08-08 05:30 | 45623.1831 | 640.008
Devonshire Building | 2016-08-08 05:45 | 45623.3481 | 659.988
Devonshire Building | 2016-08-08 06:00 | 45623.5131 | 659.988
Devonshire Building | 2016-08-08 06:15 | 45623.6731 | 640.008
Devonshire Building | 2016-08-08 06:30 | 45623.8331 | 640.008
Devonshire Building | 2016-08-08 06:45 | 45624.0031 | 680.004
Devonshire Building | 2016-08-08 07:00 | 45624.4181 | 1659.996
Devonshire Building | 2016-08-08 07:15 | 45624.5881 | 680.004
Devonshire Building | 2016-08-08 07:30 | 45624.7481 | 640.008
Devonshire Building | 2016-08-08 07:45 | 45624.9131 | 659.988
Devonshire Building | 2016-08-08 08:00 | 45625.0781 | 659.988
Devonshire Building | 2016-08-08 08:15 | 45625.2431 | 659.988
Devonshire Building | 2016-08-08 08:30 | 45625.4581 | 860.004
Devonshire Building | 2016-08-08 08:45 | 45625.6281 | 680.004
Devonshire Building | 2016-08-08 09:00 | 45625.7931 | 659.988
Devonshire Building | 2016-08-08 09:15 | 45625.9731 | 720
Devonshire Building | 2016-08-08 09:30 | 45626.3731 | 1599.984
Devonshire Building | 2016-08-08 09:45 | 45626.5431 | 680.004
Devonshire Building | 2016-08-08 10:00 | 45626.7531 | 839.988
Devonshire Building | 2016-08-08 10:15 | 45627.1181 | 1460.016
Devonshire Building | 2016-08-08 10:30 | 45627.7481 | 2520
Devonshire Building | 2016-08-08 10:45 | 45628.1481 | 1599.984
Devonshire Building | 2016-08-08 11:00 | 45628.4331 | 1140.012
Devonshire Building | 2016-08-08 11:15 | 45628.6981 | 1059.984
Devonshire Building | 2016-08-08 11:30 | 45628.9281 | 920.016
Devonshire Building | 2016-08-08 11:45 | 45629.1331 | 820.008
Devonshire Building | 2016-08-08 12:00 | 45629.3381 | 820.008
Devonshire Building | 2016-08-08 12:15 | 45629.7731 | 1739.988
Devonshire Building | 2016-08-08 12:30 | 45629.9731 | 799.992
Devonshire Building | 2016-08-08 12:45 | 45630.1431 | 680.004
Devonshire Building | 2016-08-08 13:00 | 45630.3131 | 680.004
Devonshire Building | 2016-08-08 13:15 | 45630.4781 | 659.988
Devonshire Building | 2016-08-08 13:30 | 45630.6481 | 680.004
Devonshire Building | 2016-08-08 13:45 | 45630.8281 | 720
Devonshire Building | 2016-08-08 14:00 | 45631.0131 | 740.016
Devonshire Building | 2016-08-08 14:15 | 45631.4781 | 1860.012
Devonshire Building | 2016-08-08 14:30 | 45631.6681 | 759.996
Devonshire Building | 2016-08-08 14:45 | 45631.8581 | 759.996
Devonshire Building | 2016-08-08 15:00 | 45632.0481 | 759.996
Devonshire Building | 2016-08-08 15:15 | 45632.2381 | 759.996
Devonshire Building | 2016-08-08 15:30 | 45632.4231 | 740.016
Devonshire Building | 2016-08-08 15:45 | 45632.5881 | 659.988
Devonshire Building | 2016-08-08 16:00 | 45632.7631 | 699.984
Devonshire Building | 2016-08-08 16:15 | 45633.2181 | 1820.016
Devonshire Building | 2016-08-08 16:30 | 45633.4181 | 799.992
Devonshire Building | 2016-08-08 16:45 | 45633.6181 | 799.992
Devonshire Building | 2016-08-08 17:00 | 45633.8181 | 799.992
Devonshire Building | 2016-08-08 17:15 | 45634.0081 | 759.996
Devonshire Building | 2016-08-08 17:30 | 45634.2031 | 780.012
Devonshire Building | 2016-08-08 17:45 | 45634.3931 | 759.996
Devonshire Building | 2016-08-08 18:00 | 45634.5781 | 740.016
Devonshire Building | 2016-08-08 18:15 | 45634.7631 | 740.016
Devonshire Building | 2016-08-08 18:30 | 45634.9381 | 699.984
Devonshire Building | 2016-08-08 18:45 | 45635.1181 | 720
Devonshire Building | 2016-08-08 19:00 | 45635.2931 | 699.984
Devonshire Building | 2016-08-08 19:15 | 45635.4631 | 680.004
Devonshire Building | 2016-08-08 19:30 | 45635.6381 | 699.984
Devonshire Building | 2016-08-08 19:45 | 45635.8081 | 680.004
Devonshire Building | 2016-08-08 20:00 | 45635.9781 | 680.004
Devonshire Building | 2016-08-08 20:15 | 45636.1481 | 680.004
Devonshire Building | 2016-08-08 20:30 | 45636.3181 | 680.004
Devonshire Building | 2016-08-08 20:45 | 45636.4831 | 659.988
Devonshire Building | 2016-08-08 21:00 | 45636.6531 | 680.004
Devonshire Building | 2016-08-08 21:15 | 45636.8331 | 720
Devonshire Building | 2016-08-08 21:30 | 45636.9981 | 659.988
Devonshire Building | 2016-08-08 21:45 | 45637.1581 | 640.008
Devonshire Building | 2016-08-08 22:00 | 45637.3231 | 659.988
Devonshire Building | 2016-08-08 22:15 | 45637.4831 | 640.008
Devonshire Building | 2016-08-08 22:30 | 45637.6481 | 659.988
Devonshire Building | 2016-08-08 22:45 | 45637.8081 | 640.008
Devonshire Building | 2016-08-08 23:00 | 45637.9731 | 659.988
Devonshire Building | 2016-08-08 23:15 | 45638.1331 | 640.008
Devonshire Building | 2016-08-08 23:30 | 45638.2981 | 659.988
Devonshire Building | 2016-08-08 23:45 | 45638.4581 | 640.008 | 640.008
Devonshire Building | 2016-08-09 | 45638.625 | 659.988
Devonshire Building | 2016-08-09 00:15 | 45638.79 | 659.988
Devonshire Building | 2016-08-09 00:30 | 45638.95 | 640.008
Devonshire Building | 2016-08-09 00:45 | 45639.115 | 659.988
Devonshire Building | 2016-08-09 01:00 | 45639.28 | 659.988
Devonshire Building | 2016-08-09 01:15 | 45639.445 | 659.988
Devonshire Building | 2016-08-09 01:30 | 45639.61 | 659.988
Devonshire Building | 2016-08-09 01:45 | 45639.77 | 640.008
Devonshire Building | 2016-08-09 02:00 | 45639.935 | 659.988
Devonshire Building | 2016-08-09 02:15 | 45640.1 | 659.988
Devonshire Building | 2016-08-09 02:30 | 45640.265 | 659.988
Devonshire Building | 2016-08-09 02:45 | 45640.43 | 659.988
Devonshire Building | 2016-08-09 03:00 | 45640.595 | 659.988
Devonshire Building | 2016-08-09 03:15 | 45640.76 | 659.988
Devonshire Building | 2016-08-09 03:30 | 45640.925 | 659.988
Devonshire Building | 2016-08-09 03:45 | 45641.09 | 659.988
Devonshire Building | 2016-08-09 04:00 | 45641.25 | 640.008
Devonshire Building | 2016-08-09 04:15 | 45641.415 | 659.988
Devonshire Building | 2016-08-09 04:30 | 45641.58 | 659.988
Devonshire Building | 2016-08-09 04:45 | 45641.745 | 659.988
Devonshire Building | 2016-08-09 05:00 | 45641.91 | 659.988
Devonshire Building | 2016-08-09 05:15 | 45642.075 | 659.988
Devonshire Building | 2016-08-09 05:30 | 45642.2399 | 659.988
Devonshire Building | 2016-08-09 05:45 | 45642.4049 | 659.988
Devonshire Building | 2016-08-09 06:00 | 45642.5649 | 640.008
Devonshire Building | 2016-08-09 06:15 | 45642.7299 | 659.988
Devonshire Building | 2016-08-09 06:30 | 45643.1599 | 1720.008
Devonshire Building | 2016-08-09 06:45 | 45643.3249 | 659.988
Devonshire Building | 2016-08-09 07:00 | 45643.4899 | 659.988
Devonshire Building | 2016-08-09 07:15 | 45643.6549 | 659.988
Devonshire Building | 2016-08-09 07:30 | 45643.8199 | 659.988
Devonshire Building | 2016-08-09 07:45 | 45643.9799 | 640.008
Devonshire Building | 2016-08-09 08:00 | 45644.1449 | 659.988
Devonshire Building | 2016-08-09 08:15 | 45644.3199 | 699.984
Devonshire Building | 2016-08-09 08:30 | 45644.4999 | 720
Devonshire Building | 2016-08-09 08:45 | 45644.6849 | 740.016
Devonshire Building | 2016-08-09 09:00 | 45644.8699 | 740.016
Devonshire Building | 2016-08-09 09:15 | 45645.3199 | 1800
Devonshire Building | 2016-08-09 09:30 | 45645.5149 | 780.012
Devonshire Building | 2016-08-09 09:45 | 45645.7249 | 839.988
Devonshire Building | 2016-08-09 10:00 | 45645.9799 | 1019.988
Devonshire Building | 2016-08-09 10:15 | 45646.2299 | 1000.008
Devonshire Building | 2016-08-09 10:30 | 45646.7249 | 1980
Devonshire Building | 2016-08-09 10:45 | 45647.0299 | 1220.004
Devonshire Building | 2016-08-09 11:00 | 45647.3049 | 1100.016
Devonshire Building | 2016-08-09 11:15 | 45647.5849 | 1119.996
Devonshire Building | 2016-08-09 11:30 | 45647.8599 | 1100.016
Devonshire Building | 2016-08-09 11:45 | 45648.1249 | 1059.984
Devonshire Building | 2016-08-09 12:00 | 45648.3699 | 979.992
Devonshire Building | 2016-08-09 12:15 | 45648.7649 | 1580.004
Devonshire Building | 2016-08-09 12:30 | 45649.0699 | 1220.004
Devonshire Building | 2016-08-09 12:45 | 45649.2949 | 900
Devonshire Building | 2016-08-09 13:00 | 45649.5149 | 879.984
Devonshire Building | 2016-08-09 13:15 | 45649.7249 | 839.988
Devonshire Building | 2016-08-09 13:30 | 45649.9249 | 799.992
Devonshire Building | 2016-08-09 13:45 | 45650.1199 | 780.012
Devonshire Building | 2016-08-09 14:00 | 45650.3049 | 740.016
Devonshire Building | 2016-08-09 14:15 | 45650.4899 | 740.016
Devonshire Building | 2016-08-09 14:30 | 45650.6799 | 759.996
Devonshire Building | 2016-08-09 14:45 | 45651.1149 | 1739.988
Devonshire Building | 2016-08-09 15:00 | 45651.2849 | 680.004
Devonshire Building | 2016-08-09 15:15 | 45651.4549 | 680.004
Devonshire Building | 2016-08-09 15:30 | 45651.6399 | 740.016
Devonshire Building | 2016-08-09 15:45 | 45651.8699 | 920.016
Devonshire Building | 2016-08-09 16:00 | 45652.1249 | 1019.988
Devonshire Building | 2016-08-09 16:15 | 45652.3749 | 1000.008
Devonshire Building | 2016-08-09 16:30 | 45652.8899 | 2059.992
Devonshire Building | 2016-08-09 16:45 | 45653.1599 | 1080
Devonshire Building | 2016-08-09 17:00 | 45653.4149 | 1019.988
Devonshire Building | 2016-08-09 17:15 | 45653.6449 | 920.016
Devonshire Building | 2016-08-09 17:30 | 45653.8599 | 860.004
Devonshire Building | 2016-08-09 17:45 | 45654.0599 | 799.992
Devonshire Building | 2016-08-09 18:00 | 45654.2499 | 759.996
Devonshire Building | 2016-08-09 18:15 | 45654.4399 | 759.996
Devonshire Building | 2016-08-09 18:30 | 45654.6249 | 740.016
Devonshire Building | 2016-08-09 18:45 | 45654.8049 | 720
Devonshire Building | 2016-08-09 19:00 | 45654.9849 | 720
Devonshire Building | 2016-08-09 19:15 | 45655.1599 | 699.984
Devonshire Building | 2016-08-09 19:30 | 45655.3349 | 699.984
Devonshire Building | 2016-08-09 19:45 | 45655.5099 | 699.984
Devonshire Building | 2016-08-09 20:00 | 45655.6849 | 699.984
Devonshire Building | 2016-08-09 20:15 | 45655.8599 | 699.984
Devonshire Building | 2016-08-09 20:30 | 45656.0299 | 680.004
Devonshire Building | 2016-08-09 20:45 | 45656.1999 | 680.004
Devonshire Building | 2016-08-09 21:00 | 45656.3749 | 699.984
Devonshire Building | 2016-08-09 21:15 | 45656.5599 | 740.016
Devonshire Building | 2016-08-09 21:30 | 45656.7299 | 680.004
Devonshire Building | 2016-08-09 21:45 | 45656.8949 | 659.988
Devonshire Building | 2016-08-09 22:00 | 45657.0599 | 659.988
Devonshire Building | 2016-08-09 22:15 | 45657.2299 | 680.004
Devonshire Building | 2016-08-09 22:30 | 45657.3949 | 659.988
Devonshire Building | 2016-08-09 22:45 | 45657.5649 | 680.004
Devonshire Building | 2016-08-09 23:00 | 45657.7299 | 659.988
Devonshire Building | 2016-08-09 23:15 | 45657.8999 | 680.004
Devonshire Building | 2016-08-09 23:30 | 45658.0649 | 659.988
Devonshire Building | 2016-08-09 23:45 | 45658.2349 | 680.004 | 640.008
Devonshire Building | 2016-08-10 | 45658.4062 | 680.004
Devonshire Building | 2016-08-10 00:15 | 45658.5712 | 659.988
Devonshire Building | 2016-08-10 00:30 | 45658.7412 | 680.004
Devonshire Building | 2016-08-10 00:45 | 45658.9112 | 680.004
Devonshire Building | 2016-08-10 01:00 | 45659.0762 | 659.988
Devonshire Building | 2016-08-10 01:15 | 45659.2462 | 680.004
Devonshire Building | 2016-08-10 01:30 | 45659.4162 | 680.004
Devonshire Building | 2016-08-10 01:45 | 45659.5862 | 680.004
Devonshire Building | 2016-08-10 02:00 | 45659.7562 | 680.004
Devonshire Building | 2016-08-10 02:15 | 45659.9263 | 680.004
Devonshire Building | 2016-08-10 02:30 | 45660.0963 | 680.004
Devonshire Building | 2016-08-10 02:45 | 45660.5063 | 1640.016
Devonshire Building | 2016-08-10 03:00 | 45660.6763 | 680.004
Devonshire Building | 2016-08-10 03:15 | 45660.8463 | 680.004
Devonshire Building | 2016-08-10 03:30 | 45661.0163 | 680.004
Devonshire Building | 2016-08-10 03:45 | 45661.1863 | 680.004
Devonshire Building | 2016-08-10 04:00 | 45661.3563 | 680.004
Devonshire Building | 2016-08-10 04:15 | 45661.5263 | 680.004
Devonshire Building | 2016-08-10 04:30 | 45661.6963 | 680.004
Devonshire Building | 2016-08-10 04:45 | 45661.8663 | 680.004
Devonshire Building | 2016-08-10 05:00 | 45662.0313 | 659.988
Devonshire Building | 2016-08-10 05:15 | 45662.2013 | 680.004
Devonshire Building | 2016-08-10 05:30 | 45662.3713 | 680.004
Devonshire Building | 2016-08-10 05:45 | 45662.5413 | 680.004
Devonshire Building | 2016-08-10 06:00 | 45662.7113 | 680.004
Devonshire Building | 2016-08-10 06:15 | 45662.8813 | 680.004
Devonshire Building | 2016-08-10 06:30 | 45663.0513 | 680.004
Devonshire Building | 2016-08-10 06:45 | 45663.2213 | 680.004
Devonshire Building | 2016-08-10 07:00 | 45663.3913 | 680.004
Devonshire Building | 2016-08-10 07:15 | 45663.5613 | 680.004
Devonshire Building | 2016-08-10 07:30 | 45663.7513 | 759.996
Devonshire Building | 2016-08-10 07:45 | 45663.9363 | 740.016
Devonshire Building | 2016-08-10 08:00 | 45664.1313 | 780.012
Devonshire Building | 2016-08-10 08:15 | 45664.3263 | 780.012
Devonshire Building | 2016-08-10 08:30 | 45664.5113 | 740.016
Devonshire Building | 2016-08-10 08:45 | 45664.6963 | 740.016
Devonshire Building | 2016-08-10 09:00 | 45665.1363 | 1760.004
Devonshire Building | 2016-08-10 09:15 | 45665.3313 | 780.012
Devonshire Building | 2016-08-10 09:30 | 45665.5413 | 839.988
Devonshire Building | 2016-08-10 09:45 | 45665.7713 | 920.016
Devonshire Building | 2016-08-10 10:00 | 45666.0213 | 1000.008
Devonshire Building | 2016-08-10 10:15 | 45666.2463 | 900
Devonshire Building | 2016-08-10 10:30 | 45666.7063 | 1839.996
Devonshire Building | 2016-08-10 10:45 | 45666.9163 | 839.988
Devonshire Building | 2016-08-10 11:00 | 45667.1263 | 839.988
Devonshire Building | 2016-08-10 11:15 | 45667.3363 | 839.988
Devonshire Building | 2016-08-10 11:30 | 45667.5463 | 839.988
Devonshire Building | 2016-08-10 11:45 | 45667.7513 | 820.008
Devonshire Building | 2016-08-10 12:00 | 45668.2113 | 1839.996
Devonshire Building | 2016-08-10 12:15 | 45668.4263 | 860.004
Devonshire Building | 2016-08-10 12:30 | 45668.6363 | 839.988
Devonshire Building | 2016-08-10 12:45 | 45668.8513 | 860.004
Devonshire Building | 2016-08-10 13:00 | 45669.0613 | 839.988
Devonshire Building | 2016-08-10 13:15 | 45669.2813 | 879.984
Devonshire Building | 2016-08-10 13:30 | 45669.4963 | 860.004
Devonshire Building | 2016-08-10 13:45 | 45669.7063 | 839.988
Devonshire Building | 2016-08-10 14:00 | 45670.1713 | 1860.012
Devonshire Building | 2016-08-10 14:15 | 45670.3663 | 780.012
Devonshire Building | 2016-08-10 14:30 | 45670.5563 | 759.996
Devonshire Building | 2016-08-10 14:45 | 45670.7513 | 780.012
Devonshire Building | 2016-08-10 15:00 | 45670.9463 | 780.012
Devonshire Building | 2016-08-10 15:15 | 45671.1413 | 780.012
Devonshire Building | 2016-08-10 15:30 | 45671.3413 | 799.992
Devonshire Building | 2016-08-10 15:45 | 45671.6763 | 1339.992
Devonshire Building | 2016-08-10 16:00 | 45672.3513 | 2700
Devonshire Building | 2016-08-10 16:15 | 45672.6663 | 1260
Devonshire Building | 2016-08-10 16:30 | 45672.9563 | 1159.992
Devonshire Building | 2016-08-10 16:45 | 45673.2363 | 1119.996
Devonshire Building | 2016-08-10 17:00 | 45673.4713 | 939.996
Devonshire Building | 2016-08-10 17:15 | 45673.6863 | 860.004
Devonshire Building | 2016-08-10 17:30 | 45673.8863 | 799.992
Devonshire Building | 2016-08-10 17:45 | 45674.0813 | 780.012
Devonshire Building | 2016-08-10 18:00 | 45674.2713 | 759.996
Devonshire Building | 2016-08-10 18:15 | 45674.4563 | 740.016
Devonshire Building | 2016-08-10 18:30 | 45674.6413 | 740.016
Devonshire Building | 2016-08-10 18:45 | 45674.8213 | 720
Devonshire Building | 2016-08-10 19:00 | 45675.0013 | 720
Devonshire Building | 2016-08-10 19:15 | 45675.1813 | 720
Devonshire Building | 2016-08-10 19:30 | 45675.3613 | 720
Devonshire Building | 2016-08-10 19:45 | 45675.5363 | 699.984
Devonshire Building | 2016-08-10 20:00 | 45675.7163 | 720
Devonshire Building | 2016-08-10 20:15 | 45675.8963 | 720
Devonshire Building | 2016-08-10 20:30 | 45676.0713 | 699.984
Devonshire Building | 2016-08-10 20:45 | 45676.2463 | 699.984
Devonshire Building | 2016-08-10 21:00 | 45676.4213 | 699.984
Devonshire Building | 2016-08-10 21:15 | 45676.6163 | 780.012
Devonshire Building | 2016-08-10 21:30 | 45676.7863 | 680.004
Devonshire Building | 2016-08-10 21:45 | 45676.9563 | 680.004
Devonshire Building | 2016-08-10 22:00 | 45677.1263 | 680.004
Devonshire Building | 2016-08-10 22:15 | 45677.3013 | 699.984
Devonshire Building | 2016-08-10 22:30 | 45677.4713 | 680.004
Devonshire Building | 2016-08-10 22:45 | 45677.6463 | 699.984
Devonshire Building | 2016-08-10 23:00 | 45677.8163 | 680.004
Devonshire Building | 2016-08-10 23:15 | 45677.9863 | 680.004
Devonshire Building | 2016-08-10 23:30 | 45678.1613 | 699.984
Devonshire Building | 2016-08-10 23:45 | 45678.3313 | 680.004 | 659.988
Devonshire Building | 2016-08-11 | 45678.5039 | 699.984
Devonshire Building | 2016-08-11 00:15 | 45678.6789 | 699.984
Devonshire Building | 2016-08-11 00:30 | 45678.8489 | 680.004
Devonshire Building | 2016-08-11 00:45 | 45679.0239 | 699.984
Devonshire Building | 2016-08-11 01:00 | 45679.1989 | 699.984
Devonshire Building | 2016-08-11 01:15 | 45679.3689 | 680.004
Devonshire Building | 2016-08-11 01:30 | 45679.5439 | 699.984
Devonshire Building | 2016-08-11 01:45 | 45679.7189 | 699.984
Devonshire Building | 2016-08-11 02:00 | 45679.8939 | 699.984
Devonshire Building | 2016-08-11 02:15 | 45680.0639 | 680.004
Devonshire Building | 2016-08-11 02:30 | 45680.2389 | 699.984
Devonshire Building | 2016-08-11 02:45 | 45680.4139 | 699.984
Devonshire Building | 2016-08-11 03:00 | 45680.5839 | 680.004
Devonshire Building | 2016-08-11 03:15 | 45680.7589 | 699.984
Devonshire Building | 2016-08-11 03:30 | 45680.9339 | 699.984
Devonshire Building | 2016-08-11 03:45 | 45681.1039 | 680.004
Devonshire Building | 2016-08-11 04:00 | 45681.2789 | 699.984
Devonshire Building | 2016-08-11 04:15 | 45681.4539 | 699.984
Devonshire Building | 2016-08-11 04:30 | 45681.6239 | 680.004
Devonshire Building | 2016-08-11 04:45 | 45681.7989 | 699.984
Devonshire Building | 2016-08-11 05:00 | 45681.9739 | 699.984
Devonshire Building | 2016-08-11 05:15 | 45682.1489 | 699.984
Devonshire Building | 2016-08-11 05:30 | 45682.3189 | 680.004
Devonshire Building | 2016-08-11 05:45 | 45682.4939 | 699.984
Devonshire Building | 2016-08-11 06:00 | 45682.6688 | 699.984
Devonshire Building | 2016-08-11 06:15 | 45682.8438 | 699.984
Devonshire Building | 2016-08-11 06:30 | 45683.0138 | 680.004
Devonshire Building | 2016-08-11 06:45 | 45683.4638 | 1800
Devonshire Building | 2016-08-11 07:00 | 45683.6488 | 740.016
Devonshire Building | 2016-08-11 07:15 | 45683.8238 | 699.984
Devonshire Building | 2016-08-11 07:30 | 45683.9938 | 680.004
Devonshire Building | 2016-08-11 07:45 | 45684.1838 | 759.996
Devonshire Building | 2016-08-11 08:00 | 45684.3738 | 759.996
Devonshire Building | 2016-08-11 08:15 | 45684.5638 | 759.996
Devonshire Building | 2016-08-11 08:30 | 45684.7538 | 759.996
Devonshire Building | 2016-08-11 08:45 | 45684.9488 | 780.012
Devonshire Building | 2016-08-11 09:00 | 45685.1388 | 759.996
Devonshire Building | 2016-08-11 09:15 | 45685.6188 | 1919.988
Devonshire Building | 2016-08-11 09:30 | 45685.8388 | 879.984
Devonshire Building | 2016-08-11 09:45 | 45686.0688 | 920.016
Devonshire Building | 2016-08-11 10:00 | 45686.3238 | 1019.988
Devonshire Building | 2016-08-11 10:15 | 45686.5788 | 1019.988
Devonshire Building | 2016-08-11 10:30 | 45686.8288 | 1000.008
Devonshire Building | 2016-08-11 10:45 | 45687.0938 | 1059.984
Devonshire Building | 2016-08-11 11:00 | 45687.6288 | 2139.984
Devonshire Building | 2016-08-11 11:15 | 45687.9188 | 1159.992
Devonshire Building | 2016-08-11 11:30 | 45688.1938 | 1100.016
Devonshire Building | 2016-08-11 11:45 | 45688.4438 | 1000.008
Devonshire Building | 2016-08-11 12:00 | 45688.6788 | 939.996
Devonshire Building | 2016-08-11 12:15 | 45688.9038 | 900
Devonshire Building | 2016-08-11 12:30 | 45689.1238 | 879.984
Devonshire Building | 2016-08-11 12:45 | 45689.3588 | 939.996
Devonshire Building | 2016-08-11 13:00 | 45689.5938 | 939.996
Devonshire Building | 2016-08-11 13:15 | 45689.8288 | 939.996
Devonshire Building | 2016-08-11 13:30 | 45690.3088 | 1919.988
Devonshire Building | 2016-08-11 13:45 | 45690.5438 | 939.996
Devonshire Building | 2016-08-11 14:00 | 45690.7888 | 979.992
Devonshire Building | 2016-08-11 14:15 | 45691.0288 | 960.012
Devonshire Building | 2016-08-11 14:30 | 45691.2788 | 1000.008
Devonshire Building | 2016-08-11 14:45 | 45691.5138 | 939.996
Devonshire Building | 2016-08-11 15:00 | 45691.7538 | 960.012
Devonshire Building | 2016-08-11 15:15 | 45691.9788 | 900
Devonshire Building | 2016-08-11 15:30 | 45692.4388 | 1839.996
Devonshire Building | 2016-08-11 15:45 | 45692.6488 | 839.988
Devonshire Building | 2016-08-11 16:00 | 45692.8488 | 799.992
Devonshire Building | 2016-08-11 16:15 | 45693.0538 | 820.008
Devonshire Building | 2016-08-11 16:30 | 45693.2538 | 799.992
Devonshire Building | 2016-08-11 16:45 | 45693.4538 | 799.992
Devonshire Building | 2016-08-11 17:00 | 45693.6538 | 799.992
Devonshire Building | 2016-08-11 17:15 | 45693.8588 | 820.008
Devonshire Building | 2016-08-11 17:30 | 45694.0538 | 780.012
Devonshire Building | 2016-08-11 17:45 | 45694.2538 | 799.992
Devonshire Building | 2016-08-11 18:00 | 45694.4488 | 780.012
Devonshire Building | 2016-08-11 18:15 | 45694.6438 | 780.012
Devonshire Building | 2016-08-11 18:30 | 45694.8438 | 799.992
Devonshire Building | 2016-08-11 18:45 | 45695.0338 | 759.996
Devonshire Building | 2016-08-11 19:00 | 45695.2288 | 780.012
Devonshire Building | 2016-08-11 19:15 | 45695.4138 | 740.016
Devonshire Building | 2016-08-11 19:30 | 45695.6038 | 759.996
Devonshire Building | 2016-08-11 19:45 | 45695.7888 | 740.016
Devonshire Building | 2016-08-11 20:00 | 45695.9738 | 740.016
Devonshire Building | 2016-08-11 20:15 | 45696.1588 | 740.016
Devonshire Building | 2016-08-11 20:30 | 45696.3388 | 720
Devonshire Building | 2016-08-11 20:45 | 45696.5238 | 740.016
Devonshire Building | 2016-08-11 21:00 | 45696.7088 | 740.016
Devonshire Building | 2016-08-11 21:15 | 45696.9039 | 780.012
Devonshire Building | 2016-08-11 21:30 | 45697.0839 | 720
Devonshire Building | 2016-08-11 21:45 | 45697.2588 | 699.984
Devonshire Building | 2016-08-11 22:00 | 45697.4338 | 699.984
Devonshire Building | 2016-08-11 22:15 | 45697.6088 | 699.984
Devonshire Building | 2016-08-11 22:30 | 45697.7888 | 720
Devonshire Building | 2016-08-11 22:45 | 45697.9638 | 699.984
Devonshire Building | 2016-08-11 23:00 | 45698.1388 | 699.984
Devonshire Building | 2016-08-11 23:15 | 45698.3188 | 720
Devonshire Building | 2016-08-11 23:30 | 45698.4938 | 699.984
Devonshire Building | 2016-08-11 23:45 | 45698.6738 | 720 | 680.004
Devonshire Building | 2016-08-12 | 45699.0898 | 1659.996
Devonshire Building | 2016-08-12 00:15 | 45699.2648 | 699.984
Devonshire Building | 2016-08-12 00:30 | 45699.4448 | 720
Devonshire Building | 2016-08-12 00:45 | 45699.6248 | 720
Devonshire Building | 2016-08-12 01:00 | 45699.7998 | 699.984
Devonshire Building | 2016-08-12 01:15 | 45699.9798 | 720
Devonshire Building | 2016-08-12 01:30 | 45700.1548 | 699.984
Devonshire Building | 2016-08-12 01:45 | 45700.3348 | 720
Devonshire Building | 2016-08-12 02:00 | 45700.5098 | 699.984
Devonshire Building | 2016-08-12 02:15 | 45700.6898 | 720
Devonshire Building | 2016-08-12 02:30 | 45700.8648 | 699.984
Devonshire Building | 2016-08-12 02:45 | 45701.0448 | 720
Devonshire Building | 2016-08-12 03:00 | 45701.2198 | 699.984
Devonshire Building | 2016-08-12 03:15 | 45701.3998 | 720
Devonshire Building | 2016-08-12 03:30 | 45701.5748 | 699.984
Devonshire Building | 2016-08-12 03:45 | 45701.7548 | 720
Devonshire Building | 2016-08-12 04:00 | 45701.9348 | 720
Devonshire Building | 2016-08-12 04:15 | 45702.1098 | 699.984
Devonshire Building | 2016-08-12 04:30 | 45702.2898 | 720
Devonshire Building | 2016-08-12 04:45 | 45702.4648 | 699.984
Devonshire Building | 2016-08-12 05:00 | 45702.6448 | 720
Devonshire Building | 2016-08-12 05:15 | 45702.8198 | 699.984
Devonshire Building | 2016-08-12 05:30 | 45702.9998 | 720
Devonshire Building | 2016-08-12 05:45 | 45703.1848 | 740.016
Devonshire Building | 2016-08-12 06:00 | 45703.3648 | 720
Devonshire Building | 2016-08-12 06:15 | 45703.5548 | 759.996
Devonshire Building | 2016-08-12 06:30 | 45703.7498 | 780.012
Devonshire Building | 2016-08-12 06:45 | 45703.9248 | 699.984
Devonshire Building | 2016-08-12 07:00 | 45704.1048 | 720
Devonshire Building | 2016-08-12 07:15 | 45704.2848 | 720
Devonshire Building | 2016-08-12 07:30 | 45704.4698 | 740.016
Devonshire Building | 2016-08-12 07:45 | 45704.6648 | 780.012
Devonshire Building | 2016-08-12 08:00 | 45704.8598 | 780.012
Devonshire Building | 2016-08-12 08:15 | 45705.0748 | 860.004
Devonshire Building | 2016-08-12 08:30 | 45705.5948 | 2080.008
Devonshire Building | 2016-08-12 08:45 | 45705.9048 | 1239.984
Devonshire Building | 2016-08-12 09:00 | 45706.1898 | 1140.012
Devonshire Building | 2016-08-12 09:15 | 45706.4498 | 1040.004
Devonshire Building | 2016-08-12 09:30 | 45706.6898 | 960.012
Devonshire Building | 2016-08-12 09:45 | 45706.9348 | 979.992
Devonshire Building | 2016-08-12 10:00 | 45707.4348 | 2000.016
Devonshire Building | 2016-08-12 10:15 | 45707.6648 | 920.016
Devonshire Building | 2016-08-12 10:30 | 45707.9048 | 960.012
Devonshire Building | 2016-08-12 10:45 | 45708.1398 | 939.996
Devonshire Building | 2016-08-12 11:00 | 45708.3748 | 939.996
Devonshire Building | 2016-08-12 11:15 | 45708.6048 | 920.016
Devonshire Building | 2016-08-12 11:30 | 45708.8348 | 920.016
Devonshire Building | 2016-08-12 11:45 | 45709.0648 | 920.016
Devonshire Building | 2016-08-12 12:00 | 45709.5748 | 2040.012
Devonshire Building | 2016-08-12 12:15 | 45709.8748 | 1199.988
Devonshire Building | 2016-08-12 12:30 | 45710.1498 | 1100.016
Devonshire Building | 2016-08-12 12:45 | 45710.3948 | 979.992
Devonshire Building | 2016-08-12 13:00 | 45710.6248 | 920.016
Devonshire Building | 2016-08-12 13:15 | 45710.8448 | 879.984
Devonshire Building | 2016-08-12 13:30 | 45711.0548 | 839.988
Devonshire Building | 2016-08-12 13:45 | 45711.2548 | 799.992
Devonshire Building | 2016-08-12 14:00 | 45711.4598 | 820.008
Devonshire Building | 2016-08-12 14:15 | 45711.9048 | 1779.984
Devonshire Building | 2016-08-12 14:30 | 45712.0898 | 740.016
Devonshire Building | 2016-08-12 14:45 | 45712.2798 | 759.996
Devonshire Building | 2016-08-12 15:00 | 45712.4648 | 740.016
Devonshire Building | 2016-08-12 15:15 | 45712.6548 | 759.996
Devonshire Building | 2016-08-12 15:30 | 45712.8348 | 720
Devonshire Building | 2016-08-12 15:45 | 45713.0198 | 740.016
Devonshire Building | 2016-08-12 16:00 | 45713.1998 | 720
Devonshire Building | 2016-08-12 16:15 | 45713.3848 | 740.016
Devonshire Building | 2016-08-12 16:30 | 45713.7998 | 1659.996
Devonshire Building | 2016-08-12 16:45 | 45713.9848 | 740.016
Devonshire Building | 2016-08-12 17:00 | 45714.1648 | 720
Devonshire Building | 2016-08-12 17:15 | 45714.3448 | 720
Devonshire Building | 2016-08-12 17:30 | 45714.5299 | 740.016
Devonshire Building | 2016-08-12 17:45 | 45714.7149 | 740.016
Devonshire Building | 2016-08-12 18:00 | 45714.8949 | 720
Devonshire Building | 2016-08-12 18:15 | 45715.0749 | 720
Devonshire Building | 2016-08-12 18:30 | 45715.2599 | 740.016
Devonshire Building | 2016-08-12 18:45 | 45715.4449 | 740.016
Devonshire Building | 2016-08-12 19:00 | 45715.6249 | 720
Devonshire Building | 2016-08-12 19:15 | 45715.8049 | 720
Devonshire Building | 2016-08-12 19:30 | 45715.9899 | 740.016
Devonshire Building | 2016-08-12 19:45 | 45716.1699 | 720
Devonshire Building | 2016-08-12 20:00 | 45716.3549 | 740.016
Devonshire Building | 2016-08-12 20:15 | 45716.5349 | 720
Devonshire Building | 2016-08-12 20:30 | 45716.7149 | 720
Devonshire Building | 2016-08-12 20:45 | 45716.8999 | 740.016
Devonshire Building | 2016-08-12 21:00 | 45717.0799 | 720
Devonshire Building | 2016-08-12 21:15 | 45717.2849 | 820.008
Devonshire Building | 2016-08-12 21:30 | 45717.4649 | 720
Devonshire Building | 2016-08-12 21:45 | 45717.6499 | 740.016
Devonshire Building | 2016-08-12 22:00 | 45717.8349 | 740.016
Devonshire Building | 2016-08-12 22:15 | 45718.0149 | 720
Devonshire Building | 2016-08-12 22:30 | 45718.1999 | 740.016
Devonshire Building | 2016-08-12 22:45 | 45718.3849 | 740.016
Devonshire Building | 2016-08-12 23:00 | 45718.5699 | 740.016
Devonshire Building | 2016-08-12 23:15 | 45718.7499 | 720
Devonshire Building | 2016-08-12 23:30 | 45718.9349 | 740.016
Devonshire Building | 2016-08-12 23:45 | 45719.1199 | 740.016 | 699.984
Devonshire Building | 2016-08-13 | 45719.3047 | 740.016
Devonshire Building | 2016-08-13 00:15 | 45719.4847 | 720
Devonshire Building | 2016-08-13 00:30 | 45719.6697 | 740.016
Devonshire Building | 2016-08-13 00:45 | 45719.8547 | 740.016
Devonshire Building | 2016-08-13 01:00 | 45720.0397 | 740.016
Devonshire Building | 2016-08-13 01:15 | 45720.2197 | 720
Devonshire Building | 2016-08-13 01:30 | 45720.4047 | 740.016
Devonshire Building | 2016-08-13 01:45 | 45720.6047 | 799.992
Devonshire Building | 2016-08-13 02:00 | 45720.8047 | 799.992
Devonshire Building | 2016-08-13 02:15 | 45721.0047 | 799.992
Devonshire Building | 2016-08-13 02:30 | 45721.2047 | 799.992
Devonshire Building | 2016-08-13 02:45 | 45721.4047 | 799.992
Devonshire Building | 2016-08-13 03:00 | 45721.6047 | 799.992
Devonshire Building | 2016-08-13 03:15 | 45721.7997 | 780.012
Devonshire Building | 2016-08-13 03:30 | 45721.9947 | 780.012
Devonshire Building | 2016-08-13 03:45 | 45722.1747 | 720
Devonshire Building | 2016-08-13 04:00 | 45722.3547 | 720
Devonshire Building | 2016-08-13 04:15 | 45722.5397 | 740.016
Devonshire Building | 2016-08-13 04:30 | 45722.7197 | 720
Devonshire Building | 2016-08-13 04:45 | 45722.8997 | 720
Devonshire Building | 2016-08-13 05:00 | 45723.0797 | 720
Devonshire Building | 2016-08-13 05:15 | 45723.2597 | 720
Devonshire Building | 2016-08-13 05:30 | 45723.4447 | 740.016
Devonshire Building | 2016-08-13 05:45 | 45723.6247 | 720
Devonshire Building | 2016-08-13 06:00 | 45723.8047 | 720
Devonshire Building | 2016-08-13 06:15 | 45723.9847 | 720
Devonshire Building | 2016-08-13 06:30 | 45724.1647 | 720
Devonshire Building | 2016-08-13 06:45 | 45724.3447 | 720
Devonshire Building | 2016-08-13 07:00 | 45724.5197 | 699.984
Devonshire Building | 2016-08-13 07:15 | 45724.6997 | 720
Devonshire Building | 2016-08-13 07:30 | 45724.8797 | 720
Devonshire Building | 2016-08-13 07:45 | 45725.0547 | 699.984
Devonshire Building | 2016-08-13 08:00 | 45725.2297 | 699.984
Devonshire Building | 2016-08-13 08:15 | 45725.4047 | 699.984
Devonshire Building | 2016-08-13 08:30 | 45725.5847 | 720
Devonshire Building | 2016-08-13 08:45 | 45725.7597 | 699.984
Devonshire Building | 2016-08-13 09:00 | 45725.9347 | 699.984
Devonshire Building | 2016-08-13 09:15 | 45726.1097 | 699.984
Devonshire Building | 2016-08-13 09:30 | 45726.5147 | 1620
Devonshire Building | 2016-08-13 09:45 | 45726.6897 | 699.984
Devonshire Building | 2016-08-13 10:00 | 45726.8647 | 699.984
Devonshire Building | 2016-08-13 10:15 | 45727.0397 | 699.984
Devonshire Building | 2016-08-13 10:30 | 45727.2147 | 699.984
Devonshire Building | 2016-08-13 10:45 | 45727.3897 | 699.984
Devonshire Building | 2016-08-13 11:00 | 45727.5647 | 699.984
Devonshire Building | 2016-08-13 11:15 | 45727.7447 | 720
Devonshire Building | 2016-08-13 11:30 | 45727.9197 | 699.984
Devonshire Building | 2016-08-13 11:45 | 45728.0946 | 699.984
Devonshire Building | 2016-08-13 12:00 | 45728.2696 | 699.984
Devonshire Building | 2016-08-13 12:15 | 45728.4446 | 699.984
Devonshire Building | 2016-08-13 12:30 | 45728.6196 | 699.984
Devonshire Building | 2016-08-13 12:45 | 45728.7996 | 720
Devonshire Building | 2016-08-13 13:00 | 45728.9746 | 699.984
Devonshire Building | 2016-08-13 13:15 | 45729.1496 | 699.984
Devonshire Building | 2016-08-13 13:30 | 45729.3246 | 699.984
Devonshire Building | 2016-08-13 13:45 | 45729.4996 | 699.984
Devonshire Building | 2016-08-13 14:00 | 45729.6746 | 699.984
Devonshire Building | 2016-08-13 14:15 | 45729.8496 | 699.984
Devonshire Building | 2016-08-13 14:30 | 45730.0246 | 699.984
Devonshire Building | 2016-08-13 14:45 | 45730.1996 | 699.984
Devonshire Building | 2016-08-13 15:00 | 45730.3746 | 699.984
Devonshire Building | 2016-08-13 15:15 | 45730.5546 | 720
Devonshire Building | 2016-08-13 15:30 | 45730.7296 | 699.984
Devonshire Building | 2016-08-13 15:45 | 45730.9046 | 699.984
Devonshire Building | 2016-08-13 16:00 | 45731.0796 | 699.984
Devonshire Building | 2016-08-13 16:15 | 45731.2546 | 699.984
Devonshire Building | 2016-08-13 16:30 | 45731.4296 | 699.984
Devonshire Building | 2016-08-13 16:45 | 45731.6096 | 720
Devonshire Building | 2016-08-13 17:00 | 45731.7846 | 699.984
Devonshire Building | 2016-08-13 17:15 | 45731.9596 | 699.984
Devonshire Building | 2016-08-13 17:30 | 45732.1346 | 699.984
Devonshire Building | 2016-08-13 17:45 | 45732.3096 | 699.984
Devonshire Building | 2016-08-13 18:00 | 45732.4896 | 720
Devonshire Building | 2016-08-13 18:15 | 45732.6646 | 699.984
Devonshire Building | 2016-08-13 18:30 | 45732.8396 | 699.984
Devonshire Building | 2016-08-13 18:45 | 45733.0196 | 720
Devonshire Building | 2016-08-13 19:00 | 45733.1946 | 699.984
Devonshire Building | 2016-08-13 19:15 | 45733.3746 | 720
Devonshire Building | 2016-08-13 19:30 | 45733.5495 | 699.984
Devonshire Building | 2016-08-13 19:45 | 45733.7245 | 699.984
Devonshire Building | 2016-08-13 20:00 | 45733.9045 | 720
Devonshire Building | 2016-08-13 20:15 | 45734.0795 | 699.984
Devonshire Building | 2016-08-13 20:30 | 45734.2595 | 720
Devonshire Building | 2016-08-13 20:45 | 45734.4345 | 699.984
Devonshire Building | 2016-08-13 21:00 | 45734.6145 | 720
Devonshire Building | 2016-08-13 21:15 | 45734.8095 | 780.012
Devonshire Building | 2016-08-13 21:30 | 45734.9895 | 720
Devonshire Building | 2016-08-13 21:45 | 45735.1645 | 699.984
Devonshire Building | 2016-08-13 22:00 | 45735.3445 | 720
Devonshire Building | 2016-08-13 22:15 | 45735.5195 | 699.984
Devonshire Building | 2016-08-13 22:30 | 45735.6995 | 720
Devonshire Building | 2016-08-13 22:45 | 45735.8795 | 720
Devonshire Building | 2016-08-13 23:00 | 45736.0545 | 699.984
Devonshire Building | 2016-08-13 23:15 | 45736.2345 | 720
Devonshire Building | 2016-08-13 23:30 | 45736.4145 | 720
Devonshire Building | 2016-08-13 23:45 | 45736.5895 | 699.984 | 699.984
Devonshire Building | 2016-08-14 | 45736.7695 | 720
Devonshire Building | 2016-08-14 00:15 | 45736.9495 | 720
Devonshire Building | 2016-08-14 00:30 | 45737.1295 | 720
Devonshire Building | 2016-08-14 00:45 | 45737.3045 | 699.984
Devonshire Building | 2016-08-14 01:00 | 45737.4845 | 720
Devonshire Building | 2016-08-14 01:15 | 45737.6645 | 720
Devonshire Building | 2016-08-14 01:30 | 45737.8545 | 759.996
Devonshire Building | 2016-08-14 01:45 | 45738.0495 | 780.012
Devonshire Building | 2016-08-14 02:00 | 45738.2445 | 780.012
Devonshire Building | 2016-08-14 02:15 | 45738.4395 | 780.012
Devonshire Building | 2016-08-14 02:30 | 45738.6345 | 780.012
Devonshire Building | 2016-08-14 02:45 | 45738.8295 | 780.012
Devonshire Building | 2016-08-14 03:00 | 45739.0245 | 780.012
Devonshire Building | 2016-08-14 03:15 | 45739.2195 | 780.012
Devonshire Building | 2016-08-14 03:30 | 45739.4045 | 740.016
Devonshire Building | 2016-08-14 03:45 | 45739.5845 | 720
Devonshire Building | 2016-08-14 04:00 | 45739.7645 | 720
Devonshire Building | 2016-08-14 04:15 | 45739.9395 | 699.984
Devonshire Building | 2016-08-14 04:30 | 45740.1195 | 720
Devonshire Building | 2016-08-14 04:45 | 45740.2995 | 720
Devonshire Building | 2016-08-14 05:00 | 45740.4795 | 720
Devonshire Building | 2016-08-14 05:15 | 45740.6595 | 720
Devonshire Building | 2016-08-14 05:30 | 45740.8345 | 699.984
Devonshire Building | 2016-08-14 05:45 | 45741.0145 | 720
Devonshire Building | 2016-08-14 06:00 | 45741.1945 | 720
Devonshire Building | 2016-08-14 06:15 | 45741.3745 | 720
Devonshire Building | 2016-08-14 06:30 | 45741.5495 | 699.984
Devonshire Building | 2016-08-14 06:45 | 45741.7295 | 720
Devonshire Building | 2016-08-14 07:00 | 45741.9045 | 699.984
Devonshire Building | 2016-08-14 07:15 | 45742.0845 | 720
Devonshire Building | 2016-08-14 07:30 | 45742.2595 | 699.984
Devonshire Building | 2016-08-14 07:45 | 45742.4395 | 720
Devonshire Building | 2016-08-14 08:00 | 45742.6145 | 699.984
Devonshire Building | 2016-08-14 08:15 | 45742.7945 | 720
Devonshire Building | 2016-08-14 08:30 | 45742.9695 | 699.984
Devonshire Building | 2016-08-14 08:45 | 45743.1445 | 699.984
Devonshire Building | 2016-08-14 09:00 | 45743.3195 | 699.984
Devonshire Building | 2016-08-14 09:15 | 45743.4945 | 699.984
Devonshire Building | 2016-08-14 09:30 | 45743.6695 | 699.984
Devonshire Building | 2016-08-14 09:45 | 45743.8445 | 699.984
Devonshire Building | 2016-08-14 10:00 | 45744.0245 | 720
Devonshire Building | 2016-08-14 10:15 | 45744.1995 | 699.984
Devonshire Building | 2016-08-14 10:30 | 45744.3745 | 699.984
Devonshire Building | 2016-08-14 10:45 | 45744.5495 | 699.984
Devonshire Building | 2016-08-14 11:00 | 45744.7245 | 699.984
Devonshire Building | 2016-08-14 11:15 | 45744.8995 | 699.984
Devonshire Building | 2016-08-14 11:30 | 45745.0745 | 699.984
Devonshire Building | 2016-08-14 11:45 | 45745.2495 | 699.984
Devonshire Building | 2016-08-14 12:00 | 45745.6595 | 1640.016
Devonshire Building | 2016-08-14 12:15 | 45745.8345 | 699.984
Devonshire Building | 2016-08-14 12:30 | 45746.0095 | 699.984
Devonshire Building | 2016-08-14 12:45 | 45746.1845 | 699.984
Devonshire Building | 2016-08-14 13:00 | 45746.3645 | 720
Devonshire Building | 2016-08-14 13:15 | 45746.5445 | 720
Devonshire Building | 2016-08-14 13:30 | 45746.7345 | 759.996
Devonshire Building | 2016-08-14 13:45 | 45746.9295 | 780.012
Devonshire Building | 2016-08-14 14:00 | 45747.1245 | 780.012
Devonshire Building | 2016-08-14 14:15 | 45747.3195 | 780.012
Devonshire Building | 2016-08-14 14:30 | 45747.5145 | 780.012
Devonshire Building | 2016-08-14 14:45 | 45747.7045 | 759.996
Devonshire Building | 2016-08-14 15:00 | 45747.8995 | 780.012
Devonshire Building | 2016-08-14 15:15 | 45748.0945 | 780.012
Devonshire Building | 2016-08-14 15:30 | 45748.2895 | 780.012
Devonshire Building | 2016-08-14 15:45 | 45748.4795 | 759.996
Devonshire Building | 2016-08-14 16:00 | 45748.6745 | 780.012
Devonshire Building | 2016-08-14 16:15 | 45748.8545 | 720
Devonshire Building | 2016-08-14 16:30 | 45749.0295 | 699.984
Devonshire Building | 2016-08-14 16:45 | 45749.2045 | 699.984
Devonshire Building | 2016-08-14 17:00 | 45749.3795 | 699.984
Devonshire Building | 2016-08-14 17:15 | 45749.5595 | 720
Devonshire Building | 2016-08-14 17:30 | 45749.7345 | 699.984
Devonshire Building | 2016-08-14 17:45 | 45749.9095 | 699.984
Devonshire Building | 2016-08-14 18:00 | 45750.0845 | 699.984
Devonshire Building | 2016-08-14 18:15 | 45750.2595 | 699.984
Devonshire Building | 2016-08-14 18:30 | 45750.4345 | 699.984
Devonshire Building | 2016-08-14 18:45 | 45750.6095 | 699.984
Devonshire Building | 2016-08-14 19:00 | 45750.7844 | 699.984
Devonshire Building | 2016-08-14 19:15 | 45750.9594 | 699.984
Devonshire Building | 2016-08-14 19:30 | 45751.1394 | 720
Devonshire Building | 2016-08-14 19:45 | 45751.3144 | 699.984
Devonshire Building | 2016-08-14 20:00 | 45751.4894 | 699.984
Devonshire Building | 2016-08-14 20:15 | 45751.6644 | 699.984
Devonshire Building | 2016-08-14 20:30 | 45751.8394 | 699.984
Devonshire Building | 2016-08-14 20:45 | 45752.0194 | 720
Devonshire Building | 2016-08-14 21:00 | 45752.1944 | 699.984
Devonshire Building | 2016-08-14 21:15 | 45752.3844 | 759.996
Devonshire Building | 2016-08-14 21:30 | 45752.5644 | 720
Devonshire Building | 2016-08-14 21:45 | 45752.7394 | 699.984
Devonshire Building | 2016-08-14 22:00 | 45752.9194 | 720
Devonshire Building | 2016-08-14 22:15 | 45753.0944 | 699.984
Devonshire Building | 2016-08-14 22:30 | 45753.2744 | 720
Devonshire Building | 2016-08-14 22:45 | 45753.4494 | 699.984
Devonshire Building | 2016-08-14 23:00 | 45753.6294 | 720
Devonshire Building | 2016-08-14 23:15 | 45753.8044 | 699.984
Devonshire Building | 2016-08-14 23:30 | 45753.9844 | 720
Devonshire Building | 2016-08-14 23:45 | 45754.1594 | 699.984 | 699.984
Devonshire Building | 2016-08-15 | 45754.3398 | 720
Devonshire Building | 2016-08-15 00:15 | 45754.5198 | 720
Devonshire Building | 2016-08-15 00:30 | 45754.6948 | 699.984
Devonshire Building | 2016-08-15 00:45 | 45754.8748 | 720
Devonshire Building | 2016-08-15 01:00 | 45755.0498 | 699.984
Devonshire Building | 2016-08-15 01:15 | 45755.2298 | 720
Devonshire Building | 2016-08-15 01:30 | 45755.4048 | 699.984
Devonshire Building | 2016-08-15 01:45 | 45755.5848 | 720
Devonshire Building | 2016-08-15 02:00 | 45755.7648 | 720
Devonshire Building | 2016-08-15 02:15 | 45755.9398 | 699.984
Devonshire Building | 2016-08-15 02:30 | 45756.1198 | 720
Devonshire Building | 2016-08-15 02:45 | 45756.2998 | 720
Devonshire Building | 2016-08-15 03:00 | 45756.4748 | 699.984
Devonshire Building | 2016-08-15 03:15 | 45756.6548 | 720
Devonshire Building | 2016-08-15 03:30 | 45756.8348 | 720
Devonshire Building | 2016-08-15 03:45 | 45757.0098 | 699.984
Devonshire Building | 2016-08-15 04:00 | 45757.1898 | 720
Devonshire Building | 2016-08-15 04:15 | 45757.3698 | 720
Devonshire Building | 2016-08-15 04:30 | 45757.5498 | 720
Devonshire Building | 2016-08-15 04:45 | 45757.7248 | 699.984
Devonshire Building | 2016-08-15 05:00 | 45757.9048 | 720
Devonshire Building | 2016-08-15 05:15 | 45758.0848 | 720
Devonshire Building | 2016-08-15 05:30 | 45758.2598 | 699.984
Devonshire Building | 2016-08-15 05:45 | 45758.4398 | 720
Devonshire Building | 2016-08-15 06:00 | 45758.6148 | 699.984
Devonshire Building | 2016-08-15 06:15 | 45758.7948 | 720
Devonshire Building | 2016-08-15 06:30 | 45758.9898 | 780.012
Devonshire Building | 2016-08-15 06:45 | 45759.1698 | 720
Devonshire Building | 2016-08-15 07:00 | 45759.5898 | 1680.012
Devonshire Building | 2016-08-15 07:15 | 45759.7648 | 699.984
Devonshire Building | 2016-08-15 07:30 | 45759.9448 | 720
Devonshire Building | 2016-08-15 07:45 | 45760.1298 | 740.016
Devonshire Building | 2016-08-15 08:00 | 45760.3098 | 720
Devonshire Building | 2016-08-15 08:15 | 45760.5348 | 900
Devonshire Building | 2016-08-15 08:30 | 45760.8348 | 1199.988
Devonshire Building | 2016-08-15 08:45 | 45761.1248 | 1159.992
Devonshire Building | 2016-08-15 09:00 | 45761.4448 | 1280.016
Devonshire Building | 2016-08-15 09:15 | 45761.7848 | 1360.008
Devonshire Building | 2016-08-15 09:30 | 45762.1098 | 1299.996
Devonshire Building | 2016-08-15 09:45 | 45762.6298 | 2080.008
Devonshire Building | 2016-08-15 10:00 | 45762.8898 | 1040.004
Devonshire Building | 2016-08-15 10:15 | 45763.1448 | 1019.988
Devonshire Building | 2016-08-15 10:30 | 45763.3948 | 1000.008
Devonshire Building | 2016-08-15 10:45 | 45763.6398 | 979.992
Devonshire Building | 2016-08-15 11:00 | 45763.8848 | 979.992
Devonshire Building | 2016-08-15 11:15 | 45764.3798 | 1980
Devonshire Building | 2016-08-15 11:30 | 45764.5948 | 860.004
Devonshire Building | 2016-08-15 11:45 | 45764.7948 | 799.992
Devonshire Building | 2016-08-15 12:00 | 45764.9948 | 799.992
Devonshire Building | 2016-08-15 12:15 | 45765.1948 | 799.992
Devonshire Building | 2016-08-15 12:30 | 45765.3948 | 799.992
Devonshire Building | 2016-08-15 12:45 | 45765.5998 | 820.008
Devonshire Building | 2016-08-15 13:00 | 45765.7998 | 799.992
Devonshire Building | 2016-08-15 13:15 | 45766.2598 | 1839.996
Devonshire Building | 2016-08-15 13:30 | 45766.4548 | 780.012
Devonshire Building | 2016-08-15 13:45 | 45766.6898 | 939.996
Devonshire Building | 2016-08-15 14:00 | 45766.9248 | 939.996
Devonshire Building | 2016-08-15 14:15 | 45767.1598 | 939.996
Devonshire Building | 2016-08-15 14:30 | 45767.3898 | 920.016
Devonshire Building | 2016-08-15 14:45 | 45767.6098 | 879.984
Devonshire Building | 2016-08-15 15:00 | 45767.8248 | 860.004
Devonshire Building | 2016-08-15 15:15 | 45768.2898 | 1860.012
Devonshire Building | 2016-08-15 15:30 | 45768.4848 | 780.012
Devonshire Building | 2016-08-15 15:45 | 45768.6798 | 780.012
Devonshire Building | 2016-08-15 16:00 | 45768.8698 | 759.996
Devonshire Building | 2016-08-15 16:15 | 45769.0698 | 799.992
Devonshire Building | 2016-08-15 16:30 | 45769.2648 | 780.012
Devonshire Building | 2016-08-15 16:45 | 45769.4598 | 780.012
Devonshire Building | 2016-08-15 17:00 | 45769.6498 | 759.996
Devonshire Building | 2016-08-15 17:15 | 45769.8398 | 759.996
Devonshire Building | 2016-08-15 17:30 | 45770.0298 | 759.996
Devonshire Building | 2016-08-15 17:45 | 45770.2248 | 780.012
Devonshire Building | 2016-08-15 18:00 | 45770.4098 | 740.016
Devonshire Building | 2016-08-15 18:15 | 45770.5998 | 759.996
Devonshire Building | 2016-08-15 18:30 | 45770.7898 | 759.996
Devonshire Building | 2016-08-15 18:45 | 45770.9798 | 759.996
Devonshire Building | 2016-08-15 19:00 | 45771.1648 | 740.016
Devonshire Building | 2016-08-15 19:15 | 45771.3548 | 759.996
Devonshire Building | 2016-08-15 19:30 | 45771.5398 | 740.016
Devonshire Building | 2016-08-15 19:45 | 45771.9598 | 1680.012
Devonshire Building | 2016-08-15 20:00 | 45772.1398 | 720
Devonshire Building | 2016-08-15 20:15 | 45772.3198 | 720
Devonshire Building | 2016-08-15 20:30 | 45772.4948 | 699.984
Devonshire Building | 2016-08-15 20:45 | 45772.6748 | 720
Devonshire Building | 2016-08-15 21:00 | 45772.8548 | 720
Devonshire Building | 2016-08-15 21:15 | 45773.0398 | 740.016
Devonshire Building | 2016-08-15 21:30 | 45773.2148 | 699.984
Devonshire Building | 2016-08-15 21:45 | 45773.3948 | 720
Devonshire Building | 2016-08-15 22:00 | 45773.5748 | 720
Devonshire Building | 2016-08-15 22:15 | 45773.7498 | 699.984
Devonshire Building | 2016-08-15 22:30 | 45773.9298 | 720
Devonshire Building | 2016-08-15 22:45 | 45774.1098 | 720
Devonshire Building | 2016-08-15 23:00 | 45774.2898 | 720
Devonshire Building | 2016-08-15 23:15 | 45774.4698 | 720
Devonshire Building | 2016-08-15 23:30 | 45774.6498 | 720
Devonshire Building | 2016-08-15 23:45 | 45774.8298 | 720 | 699.984
Devonshire Building | 2016-08-16 | 45775.0078 | 720
Devonshire Building | 2016-08-16 00:15 | 45775.1878 | 720
Devonshire Building | 2016-08-16 00:30 | 45775.3678 | 720
Devonshire Building | 2016-08-16 00:45 | 45775.5478 | 720
Devonshire Building | 2016-08-16 01:00 | 45775.7228 | 699.984
Devonshire Building | 2016-08-16 01:15 | 45775.9028 | 720
Devonshire Building | 2016-08-16 01:30 | 45776.0828 | 720
Devonshire Building | 2016-08-16 01:45 | 45776.2628 | 720
Devonshire Building | 2016-08-16 02:00 | 45776.4428 | 720
Devonshire Building | 2016-08-16 02:15 | 45776.6228 | 720
Devonshire Building | 2016-08-16 02:30 | 45776.8028 | 720
Devonshire Building | 2016-08-16 02:45 | 45776.9828 | 720
Devonshire Building | 2016-08-16 03:00 | 45777.1628 | 720
Devonshire Building | 2016-08-16 03:15 | 45777.3428 | 720
Devonshire Building | 2016-08-16 03:30 | 45777.5228 | 720
Devonshire Building | 2016-08-16 03:45 | 45777.6978 | 699.984
Devonshire Building | 2016-08-16 04:00 | 45777.8778 | 720
Devonshire Building | 2016-08-16 04:15 | 45778.0578 | 720
Devonshire Building | 2016-08-16 04:30 | 45778.2378 | 720
Devonshire Building | 2016-08-16 04:45 | 45778.4178 | 720
Devonshire Building | 2016-08-16 05:00 | 45778.5928 | 699.984
Devonshire Building | 2016-08-16 05:15 | 45778.7728 | 720
Devonshire Building | 2016-08-16 05:30 | 45778.9528 | 720
Devonshire Building | 2016-08-16 05:45 | 45779.1278 | 699.984
Devonshire Building | 2016-08-16 06:00 | 45779.3078 | 720
Devonshire Building | 2016-08-16 06:15 | 45779.4828 | 699.984
Devonshire Building | 2016-08-16 06:30 | 45779.6678 | 740.016
Devonshire Building | 2016-08-16 06:45 | 45779.8428 | 699.984
Devonshire Building | 2016-08-16 07:00 | 45780.0178 | 699.984
Devonshire Building | 2016-08-16 07:15 | 45780.1928 | 699.984
Devonshire Building | 2016-08-16 07:30 | 45780.3728 | 720
Devonshire Building | 2016-08-16 07:45 | 45780.5578 | 740.016
Devonshire Building | 2016-08-16 08:00 | 45780.9878 | 1720.008
Devonshire Building | 2016-08-16 08:15 | 45781.1828 | 780.012
Devonshire Building | 2016-08-16 08:30 | 45781.3778 | 780.012
Devonshire Building | 2016-08-16 08:45 | 45781.5728 | 780.012
Devonshire Building | 2016-08-16 09:00 | 45781.7678 | 780.012
Devonshire Building | 2016-08-16 09:15 | 45781.9628 | 780.012
Devonshire Building | 2016-08-16 09:30 | 45782.1578 | 780.012
Devonshire Building | 2016-08-16 09:45 | 45782.6728 | 2059.992
Devonshire Building | 2016-08-16 10:00 | 45782.9528 | 1119.996
Devonshire Building | 2016-08-16 10:15 | 45783.2278 | 1100.016
Devonshire Building | 2016-08-16 10:30 | 45783.4878 | 1040.004
Devonshire Building | 2016-08-16 10:45 | 45783.7328 | 979.992
Devonshire Building | 2016-08-16 11:00 | 45783.9678 | 939.996
Devonshire Building | 2016-08-16 11:15 | 45784.3828 | 1659.996
Devonshire Building | 2016-08-16 11:30 | 45784.6528 | 1080
Devonshire Building | 2016-08-16 11:45 | 45784.8528 | 799.992
Devonshire Building | 2016-08-16 12:00 | 45785.0528 | 799.992
Devonshire Building | 2016-08-16 12:15 | 45785.2778 | 900
Devonshire Building | 2016-08-16 12:30 | 45785.5028 | 900
Devonshire Building | 2016-08-16 12:45 | 45785.7378 | 939.996
Devonshire Building | 2016-08-16 13:00 | 45785.9628 | 900
Devonshire Building | 2016-08-16 13:15 | 45786.4378 | 1900.008
Devonshire Building | 2016-08-16 13:30 | 45786.6578 | 879.984
Devonshire Building | 2016-08-16 13:45 | 45786.8778 | 879.984
Devonshire Building | 2016-08-16 14:00 | 45787.1078 | 920.016
Devonshire Building | 2016-08-16 14:15 | 45787.3328 | 900
Devonshire Building | 2016-08-16 14:30 | 45787.5528 | 879.984
Devonshire Building | 2016-08-16 14:45 | 45787.7678 | 860.004
Devonshire Building | 2016-08-16 15:00 | 45787.9728 | 820.008
Devonshire Building | 2016-08-16 15:15 | 45788.2228 | 1000.008
Devonshire Building | 2016-08-16 15:30 | 45788.6278 | 1620
Devonshire Building | 2016-08-16 15:45 | 45788.8128 | 740.016
Devonshire Building | 2016-08-16 16:00 | 45789.0028 | 759.996
Devonshire Building | 2016-08-16 16:15 | 45789.2128 | 839.988
Devonshire Building | 2016-08-16 16:30 | 45789.4428 | 920.016
Devonshire Building | 2016-08-16 16:45 | 45789.6728 | 920.016
Devonshire Building | 2016-08-16 17:00 | 45789.8978 | 900
Devonshire Building | 2016-08-16 17:15 | 45790.1478 | 1000.008
Devonshire Building | 2016-08-16 17:30 | 45790.3978 | 1000.008
Devonshire Building | 2016-08-16 17:45 | 45790.6328 | 939.996
Devonshire Building | 2016-08-16 18:00 | 45790.8628 | 920.016
Devonshire Building | 2016-08-16 18:15 | 45791.0728 | 839.988
Devonshire Building | 2016-08-16 18:30 | 45791.2778 | 820.008
Devonshire Building | 2016-08-16 18:45 | 45791.4728 | 780.012
Devonshire Building | 2016-08-16 19:00 | 45791.6678 | 780.012
Devonshire Building | 2016-08-16 19:15 | 45792.0928 | 1699.992
Devonshire Building | 2016-08-16 19:30 | 45792.2678 | 699.984
Devonshire Building | 2016-08-16 19:45 | 45792.4478 | 720
Devonshire Building | 2016-08-16 20:00 | 45792.6278 | 720
Devonshire Building | 2016-08-16 20:15 | 45792.8028 | 699.984
Devonshire Building | 2016-08-16 20:30 | 45792.9828 | 720
Devonshire Building | 2016-08-16 20:45 | 45793.1628 | 720
Devonshire Building | 2016-08-16 21:00 | 45793.3428 | 720
Devonshire Building | 2016-08-16 21:15 | 45793.5228 | 720
Devonshire Building | 2016-08-16 21:30 | 45793.7028 | 720
Devonshire Building | 2016-08-16 21:45 | 45793.8828 | 720
Devonshire Building | 2016-08-16 22:00 | 45794.0578 | 699.984
Devonshire Building | 2016-08-16 22:15 | 45794.2378 | 720
Devonshire Building | 2016-08-16 22:30 | 45794.4178 | 720
Devonshire Building | 2016-08-16 22:45 | 45794.5928 | 699.984
Devonshire Building | 2016-08-16 23:00 | 45794.7728 | 720
Devonshire Building | 2016-08-16 23:15 | 45794.9478 | 699.984
Devonshire Building | 2016-08-16 23:30 | 45795.1278 | 720
Devonshire Building | 2016-08-16 23:45 | 45795.3028 | 699.984 | 699.984
Devonshire Building | 2016-08-17 | 45795.4844 | 720
Devonshire Building | 2016-08-17 00:15 | 45795.6594 | 699.984
Devonshire Building | 2016-08-17 00:30 | 45795.8394 | 720
Devonshire Building | 2016-08-17 00:45 | 45796.0194 | 720
Devonshire Building | 2016-08-17 01:00 | 45796.1944 | 699.984
Devonshire Building | 2016-08-17 01:15 | 45796.3694 | 699.984
Devonshire Building | 2016-08-17 01:30 | 45796.5494 | 720
Devonshire Building | 2016-08-17 01:45 | 45796.7244 | 699.984
Devonshire Building | 2016-08-17 02:00 | 45796.9044 | 720
Devonshire Building | 2016-08-17 02:15 | 45797.0794 | 699.984
Devonshire Building | 2016-08-17 02:30 | 45797.2544 | 699.984
Devonshire Building | 2016-08-17 02:45 | 45797.4344 | 720
Devonshire Building | 2016-08-17 03:00 | 45797.6094 | 699.984
Devonshire Building | 2016-08-17 03:15 | 45797.7843 | 699.984
Devonshire Building | 2016-08-17 03:30 | 45797.9643 | 720
Devonshire Building | 2016-08-17 03:45 | 45798.1393 | 699.984
Devonshire Building | 2016-08-17 04:00 | 45798.3143 | 699.984
Devonshire Building | 2016-08-17 04:15 | 45798.4893 | 699.984
Devonshire Building | 2016-08-17 04:30 | 45798.6693 | 720
Devonshire Building | 2016-08-17 04:45 | 45798.8443 | 699.984
Devonshire Building | 2016-08-17 05:00 | 45799.0193 | 699.984
Devonshire Building | 2016-08-17 05:15 | 45799.1943 | 699.984
Devonshire Building | 2016-08-17 05:30 | 45799.3693 | 699.984
Devonshire Building | 2016-08-17 05:45 | 45799.5443 | 699.984
Devonshire Building | 2016-08-17 06:00 | 45799.7243 | 720
Devonshire Building | 2016-08-17 06:15 | 45799.8993 | 699.984
Devonshire Building | 2016-08-17 06:30 | 45800.0743 | 699.984
Devonshire Building | 2016-08-17 06:45 | 45800.2493 | 699.984
Devonshire Building | 2016-08-17 07:00 | 45800.4193 | 680.004
Devonshire Building | 2016-08-17 07:15 | 45800.6093 | 759.996
Devonshire Building | 2016-08-17 07:30 | 45800.7793 | 680.004
Devonshire Building | 2016-08-17 07:45 | 45801.2093 | 1720.008
Devonshire Building | 2016-08-17 08:00 | 45801.3943 | 740.016
Devonshire Building | 2016-08-17 08:15 | 45801.5843 | 759.996
Devonshire Building | 2016-08-17 08:30 | 45801.7793 | 780.012
Devonshire Building | 2016-08-17 08:45 | 45801.9693 | 759.996
Devonshire Building | 2016-08-17 09:00 | 45802.1643 | 780.012
Devonshire Building | 2016-08-17 09:15 | 45802.6343 | 1879.992
Devonshire Building | 2016-08-17 09:30 | 45802.8543 | 879.984
Devonshire Building | 2016-08-17 09:45 | 45803.0843 | 920.016
Devonshire Building | 2016-08-17 10:00 | 45803.3143 | 920.016
Devonshire Building | 2016-08-17 10:15 | 45803.5393 | 900
Devonshire Building | 2016-08-17 10:30 | 45803.7593 | 879.984
Devonshire Building | 2016-08-17 10:45 | 45803.9693 | 839.988
Devonshire Building | 2016-08-17 11:00 | 45804.4343 | 1860.012
Devonshire Building | 2016-08-17 11:15 | 45804.6293 | 780.012
Devonshire Building | 2016-08-17 11:30 | 45804.8293 | 799.992
Devonshire Building | 2016-08-17 11:45 | 45805.0243 | 780.012
Devonshire Building | 2016-08-17 12:00 | 45805.2393 | 860.004
Devonshire Building | 2016-08-17 12:15 | 45805.4693 | 920.016
Devonshire Building | 2016-08-17 12:30 | 45805.7043 | 939.996
Devonshire Building | 2016-08-17 12:45 | 45805.9443 | 960.012
Devonshire Building | 2016-08-17 13:00 | 45806.4343 | 1959.984
Devonshire Building | 2016-08-17 13:15 | 45806.6493 | 860.004
Devonshire Building | 2016-08-17 13:30 | 45806.8643 | 860.004
Devonshire Building | 2016-08-17 13:45 | 45807.0793 | 860.004
Devonshire Building | 2016-08-17 14:00 | 45807.2943 | 860.004
Devonshire Building | 2016-08-17 14:15 | 45807.5043 | 839.988
Devonshire Building | 2016-08-17 14:30 | 45807.7193 | 860.004
Devonshire Building | 2016-08-17 14:45 | 45807.9243 | 820.008
Devonshire Building | 2016-08-17 15:00 | 45808.1293 | 820.008
Devonshire Building | 2016-08-17 15:15 | 45808.5893 | 1839.996
Devonshire Building | 2016-08-17 15:30 | 45808.7943 | 820.008
Devonshire Building | 2016-08-17 15:45 | 45809.0043 | 839.988
Devonshire Building | 2016-08-17 16:00 | 45809.2043 | 799.992
Devonshire Building | 2016-08-17 16:15 | 45809.4143 | 839.988
Devonshire Building | 2016-08-17 16:30 | 45809.6393 | 900
Devonshire Building | 2016-08-17 16:45 | 45809.8793 | 960.012
Devonshire Building | 2016-08-17 17:00 | 45810.1143 | 939.996
Devonshire Building | 2016-08-17 17:15 | 45810.3493 | 939.996
Devonshire Building | 2016-08-17 17:30 | 45810.5843 | 939.996
Devonshire Building | 2016-08-17 17:45 | 45810.8243 | 960.012
Devonshire Building | 2016-08-17 18:00 | 45811.0593 | 939.996
Devonshire Building | 2016-08-17 18:15 | 45811.2843 | 900
Devonshire Building | 2016-08-17 18:30 | 45811.4993 | 860.004
Devonshire Building | 2016-08-17 18:45 | 45811.7043 | 820.008
Devonshire Building | 2016-08-17 19:00 | 45811.9043 | 799.992
Devonshire Building | 2016-08-17 19:15 | 45812.0943 | 759.996
Devonshire Building | 2016-08-17 19:30 | 45812.2793 | 740.016
Devonshire Building | 2016-08-17 19:45 | 45812.4643 | 740.016
Devonshire Building | 2016-08-17 20:00 | 45812.6443 | 720
Devonshire Building | 2016-08-17 20:15 | 45812.8243 | 720
Devonshire Building | 2016-08-17 20:30 | 45813.0043 | 720
Devonshire Building | 2016-08-17 20:45 | 45813.1793 | 699.984
Devonshire Building | 2016-08-17 21:00 | 45813.3543 | 699.984
Devonshire Building | 2016-08-17 21:15 | 45813.5493 | 780.012
Devonshire Building | 2016-08-17 21:30 | 45813.7143 | 659.988
Devonshire Building | 2016-08-17 21:45 | 45813.8843 | 680.004
Devonshire Building | 2016-08-17 22:00 | 45814.0543 | 680.004
Devonshire Building | 2016-08-17 22:15 | 45814.2243 | 680.004
Devonshire Building | 2016-08-17 22:30 | 45814.3943 | 680.004
Devonshire Building | 2016-08-17 22:45 | 45814.5643 | 680.004
Devonshire Building | 2016-08-17 23:00 | 45814.7343 | 680.004
Devonshire Building | 2016-08-17 23:15 | 45814.9043 | 680.004
Devonshire Building | 2016-08-17 23:30 | 45815.0743 | 680.004
Devonshire Building | 2016-08-17 23:45 | 45815.2443 | 680.004 | 659.988
Devonshire Building | 2016-08-18 | 45815.418 | 699.984
Devonshire Building | 2016-08-18 00:15 | 45815.828 | 1640.016
Devonshire Building | 2016-08-18 00:30 | 45815.998 | 680.004
Devonshire Building | 2016-08-18 00:45 | 45816.168 | 680.004
Devonshire Building | 2016-08-18 01:00 | 45816.343 | 699.984
Devonshire Building | 2016-08-18 01:15 | 45816.513 | 680.004
Devonshire Building | 2016-08-18 01:30 | 45816.683 | 680.004
Devonshire Building | 2016-08-18 01:45 | 45816.853 | 680.004
Devonshire Building | 2016-08-18 02:00 | 45817.023 | 680.004
Devonshire Building | 2016-08-18 02:15 | 45817.193 | 680.004
Devonshire Building | 2016-08-18 02:30 | 45817.363 | 680.004
Devonshire Building | 2016-08-18 02:45 | 45817.533 | 680.004
Devonshire Building | 2016-08-18 03:00 | 45817.703 | 680.004
Devonshire Building | 2016-08-18 03:15 | 45817.878 | 699.984
Devonshire Building | 2016-08-18 03:30 | 45818.048 | 680.004
Devonshire Building | 2016-08-18 03:45 | 45818.218 | 680.004
Devonshire Building | 2016-08-18 04:00 | 45818.388 | 680.004
Devonshire Building | 2016-08-18 04:15 | 45818.558 | 680.004
Devonshire Building | 2016-08-18 04:30 | 45818.733 | 699.984
Devonshire Building | 2016-08-18 04:45 | 45818.903 | 680.004
Devonshire Building | 2016-08-18 05:00 | 45819.073 | 680.004
Devonshire Building | 2016-08-18 05:15 | 45819.243 | 680.004
Devonshire Building | 2016-08-18 05:30 | 45819.413 | 680.004
Devonshire Building | 2016-08-18 05:45 | 45819.588 | 699.984
Devonshire Building | 2016-08-18 06:00 | 45819.758 | 680.004
Devonshire Building | 2016-08-18 06:15 | 45819.928 | 680.004
Devonshire Building | 2016-08-18 06:30 | 45820.108 | 720
Devonshire Building | 2016-08-18 06:45 | 45820.278 | 680.004
Devonshire Building | 2016-08-18 07:00 | 45820.463 | 740.016
Devonshire Building | 2016-08-18 07:15 | 45820.628 | 659.988
Devonshire Building | 2016-08-18 07:30 | 45820.798 | 680.004
Devonshire Building | 2016-08-18 07:45 | 45820.978 | 720
Devonshire Building | 2016-08-18 08:00 | 45821.168 | 759.996
Devonshire Building | 2016-08-18 08:15 | 45821.363 | 780.012
Devonshire Building | 2016-08-18 08:30 | 45821.568 | 820.008
Devonshire Building | 2016-08-18 08:45 | 45821.768 | 799.992
Devonshire Building | 2016-08-18 09:00 | 45821.973 | 820.008
Devonshire Building | 2016-08-18 09:15 | 45822.453 | 1919.988
Devonshire Building | 2016-08-18 09:30 | 45822.658 | 820.008
Devonshire Building | 2016-08-18 09:45 | 45822.873 | 860.004
Devonshire Building | 2016-08-18 10:00 | 45823.113 | 960.012
Devonshire Building | 2016-08-18 10:15 | 45823.348 | 939.996
Devonshire Building | 2016-08-18 10:30 | 45823.578 | 920.016
Devonshire Building | 2016-08-18 10:45 | 45823.793 | 860.004
Devonshire Building | 2016-08-18 11:00 | 45824.253 | 1839.996
Devonshire Building | 2016-08-18 11:15 | 45824.458 | 820.008
Devonshire Building | 2016-08-18 11:30 | 45824.663 | 820.008
Devonshire Building | 2016-08-18 11:45 | 45824.873 | 839.988
Devonshire Building | 2016-08-18 12:00 | 45825.078 | 820.008
Devonshire Building | 2016-08-18 12:15 | 45825.283 | 820.008
Devonshire Building | 2016-08-18 12:30 | 45825.478 | 780.012
Devonshire Building | 2016-08-18 12:45 | 45825.923 | 1779.984
Devonshire Building | 2016-08-18 13:00 | 45826.113 | 759.996
Devonshire Building | 2016-08-18 13:15 | 45826.303 | 759.996
Devonshire Building | 2016-08-18 13:30 | 45826.493 | 759.996
Devonshire Building | 2016-08-18 13:45 | 45826.688 | 780.012
Devonshire Building | 2016-08-18 14:00 | 45826.878 | 759.996
Devonshire Building | 2016-08-18 14:15 | 45827.068 | 759.996
Devonshire Building | 2016-08-18 14:30 | 45827.258 | 759.996
Devonshire Building | 2016-08-18 14:45 | 45827.443 | 740.016
Devonshire Building | 2016-08-18 15:00 | 45827.628 | 740.016
Devonshire Building | 2016-08-18 15:15 | 45828.063 | 1739.988
Devonshire Building | 2016-08-18 15:30 | 45828.258 | 780.012
Devonshire Building | 2016-08-18 15:45 | 45828.448 | 759.996
Devonshire Building | 2016-08-18 16:00 | 45828.633 | 740.016
Devonshire Building | 2016-08-18 16:15 | 45828.823 | 759.996
Devonshire Building | 2016-08-18 16:30 | 45829.013 | 759.996
Devonshire Building | 2016-08-18 16:45 | 45829.198 | 740.016
Devonshire Building | 2016-08-18 17:00 | 45829.383 | 740.016
Devonshire Building | 2016-08-18 17:15 | 45829.568 | 740.016
Devonshire Building | 2016-08-18 17:30 | 45829.753 | 740.016
Devonshire Building | 2016-08-18 17:45 | 45829.948 | 780.012
Devonshire Building | 2016-08-18 18:00 | 45830.128 | 720
Devonshire Building | 2016-08-18 18:15 | 45830.308 | 720
Devonshire Building | 2016-08-18 18:30 | 45830.488 | 720
Devonshire Building | 2016-08-18 18:45 | 45830.663 | 699.984
Devonshire Building | 2016-08-18 19:00 | 45830.838 | 699.984
Devonshire Building | 2016-08-18 19:15 | 45831.013 | 699.984
Devonshire Building | 2016-08-18 19:30 | 45831.183 | 680.004
Devonshire Building | 2016-08-18 19:45 | 45831.358 | 699.984
Devonshire Building | 2016-08-18 20:00 | 45831.533 | 699.984
Devonshire Building | 2016-08-18 20:15 | 45831.703 | 680.004
Devonshire Building | 2016-08-18 20:30 | 45831.873 | 680.004
Devonshire Building | 2016-08-18 20:45 | 45832.048 | 699.984
Devonshire Building | 2016-08-18 21:00 | 45832.218 | 680.004
Devonshire Building | 2016-08-18 21:15 | 45832.408 | 759.996
Devonshire Building | 2016-08-18 21:30 | 45832.573 | 659.988
Devonshire Building | 2016-08-18 21:45 | 45832.743 | 680.004
Devonshire Building | 2016-08-18 22:00 | 45832.908 | 659.988
Devonshire Building | 2016-08-18 22:15 | 45833.073 | 659.988
Devonshire Building | 2016-08-18 22:30 | 45833.243 | 680.004
Devonshire Building | 2016-08-18 22:45 | 45833.408 | 659.988
Devonshire Building | 2016-08-18 23:00 | 45833.578 | 680.004
Devonshire Building | 2016-08-18 23:15 | 45833.743 | 659.988
Devonshire Building | 2016-08-18 23:30 | 45833.913 | 680.004
Devonshire Building | 2016-08-18 23:45 | 45834.083 | 680.004 | 659.988
Devonshire Building | 2016-08-19 | 45834.25 | 659.988
Devonshire Building | 2016-08-19 00:15 | 45834.42 | 680.004
Devonshire Building | 2016-08-19 00:30 | 45834.585 | 659.988
Devonshire Building | 2016-08-19 00:45 | 45834.755 | 680.004
Devonshire Building | 2016-08-19 01:00 | 45834.925 | 680.004
Devonshire Building | 2016-08-19 01:15 | 45835.09 | 659.988
Devonshire Building | 2016-08-19 01:30 | 45835.26 | 680.004
Devonshire Building | 2016-08-19 01:45 | 45835.425 | 659.988
Devonshire Building | 2016-08-19 02:00 | 45835.595 | 680.004
Devonshire Building | 2016-08-19 02:15 | 45835.765 | 680.004
Devonshire Building | 2016-08-19 02:30 | 45835.93 | 659.988
Devonshire Building | 2016-08-19 02:45 | 45836.345 | 1659.996
Devonshire Building | 2016-08-19 03:00 | 45836.515 | 680.004
Devonshire Building | 2016-08-19 03:15 | 45836.68 | 659.988
Devonshire Building | 2016-08-19 03:30 | 45836.85 | 680.004
Devonshire Building | 2016-08-19 03:45 | 45837.015 | 659.988
Devonshire Building | 2016-08-19 04:00 | 45837.185 | 680.004
Devonshire Building | 2016-08-19 04:15 | 45837.355 | 680.004
Devonshire Building | 2016-08-19 04:30 | 45837.52 | 659.988
Devonshire Building | 2016-08-19 04:45 | 45837.69 | 680.004
Devonshire Building | 2016-08-19 05:00 | 45837.86 | 680.004
Devonshire Building | 2016-08-19 05:15 | 45838.025 | 659.988
Devonshire Building | 2016-08-19 05:30 | 45838.195 | 680.004
Devonshire Building | 2016-08-19 05:45 | 45838.36 | 659.988
Devonshire Building | 2016-08-19 06:00 | 45838.53 | 680.004
Devonshire Building | 2016-08-19 06:15 | 45838.695 | 659.988
Devonshire Building | 2016-08-19 06:30 | 45838.865 | 680.004
Devonshire Building | 2016-08-19 06:45 | 45839.03 | 659.988
Devonshire Building | 2016-08-19 07:00 | 45839.205 | 699.984
Devonshire Building | 2016-08-19 07:15 | 45839.37 | 659.988
Devonshire Building | 2016-08-19 07:30 | 45839.54 | 680.004
Devonshire Building | 2016-08-19 07:45 | 45839.72 | 720
Devonshire Building | 2016-08-19 08:00 | 45839.915 | 780.012
Devonshire Building | 2016-08-19 08:15 | 45840.1 | 740.016
Devonshire Building | 2016-08-19 08:30 | 45840.285 | 740.016
Devonshire Building | 2016-08-19 08:45 | 45840.47 | 740.016
Devonshire Building | 2016-08-19 09:00 | 45840.65 | 720
Devonshire Building | 2016-08-19 09:15 | 45841.1 | 1800
Devonshire Building | 2016-08-19 09:30 | 45841.285 | 740.016
Devonshire Building | 2016-08-19 09:45 | 45841.485 | 799.992
Devonshire Building | 2016-08-19 10:00 | 45841.68 | 780.012
Devonshire Building | 2016-08-19 10:15 | 45841.885 | 820.008
Devonshire Building | 2016-08-19 10:30 | 45842.095 | 839.988
Devonshire Building | 2016-08-19 10:45 | 45842.305 | 839.988
Devonshire Building | 2016-08-19 11:00 | 45842.765 | 1839.996
Devonshire Building | 2016-08-19 11:15 | 45842.97 | 820.008
Devonshire Building | 2016-08-19 11:30 | 45843.175 | 820.008
Devonshire Building | 2016-08-19 11:45 | 45843.38 | 820.008
Devonshire Building | 2016-08-19 12:00 | 45843.58 | 799.992
Devonshire Building | 2016-08-19 12:15 | 45843.775 | 780.012
Devonshire Building | 2016-08-19 12:30 | 45843.97 | 780.012
Devonshire Building | 2016-08-19 12:45 | 45844.16 | 759.996
Devonshire Building | 2016-08-19 13:00 | 45844.35 | 759.996
Devonshire Building | 2016-08-19 13:15 | 45844.535 | 740.016
Devonshire Building | 2016-08-19 13:30 | 45844.985 | 1800
Devonshire Building | 2016-08-19 13:45 | 45845.19 | 820.008
Devonshire Building | 2016-08-19 14:00 | 45845.395 | 820.008
Devonshire Building | 2016-08-19 14:15 | 45845.6 | 820.008
Devonshire Building | 2016-08-19 14:30 | 45845.81 | 839.988
Devonshire Building | 2016-08-19 14:45 | 45846.01 | 799.992
Devonshire Building | 2016-08-19 15:00 | 45846.22 | 839.988
Devonshire Building | 2016-08-19 15:15 | 45846.42 | 799.992
Devonshire Building | 2016-08-19 15:30 | 45846.625 | 820.008
Devonshire Building | 2016-08-19 15:45 | 45846.825 | 799.992
Devonshire Building | 2016-08-19 16:00 | 45847.01 | 740.016
Devonshire Building | 2016-08-19 16:15 | 45847.315 | 1220.004
Devonshire Building | 2016-08-19 16:30 | 45847.615 | 1199.988
Devonshire Building | 2016-08-19 16:45 | 45847.78 | 659.988
Devonshire Building | 2016-08-19 17:00 | 45847.95 | 680.004
Devonshire Building | 2016-08-19 17:15 | 45848.115 | 659.988
Devonshire Building | 2016-08-19 17:30 | 45848.28 | 659.988
Devonshire Building | 2016-08-19 17:45 | 45848.45 | 680.004
Devonshire Building | 2016-08-19 18:00 | 45848.615 | 659.988
Devonshire Building | 2016-08-19 18:15 | 45848.78 | 659.988
Devonshire Building | 2016-08-19 18:30 | 45848.945 | 659.988
Devonshire Building | 2016-08-19 18:45 | 45849.11 | 659.988
Devonshire Building | 2016-08-19 19:00 | 45849.275 | 659.988
Devonshire Building | 2016-08-19 19:15 | 45849.44 | 659.988
Devonshire Building | 2016-08-19 19:30 | 45849.605 | 659.988
Devonshire Building | 2016-08-19 19:45 | 45849.77 | 659.988
Devonshire Building | 2016-08-19 20:00 | 45849.935 | 659.988
Devonshire Building | 2016-08-19 20:15 | 45850.105 | 680.004
Devonshire Building | 2016-08-19 20:30 | 45850.27 | 659.988
Devonshire Building | 2016-08-19 20:45 | 45850.435 | 659.988
Devonshire Building | 2016-08-19 21:00 | 45850.605 | 680.004
Devonshire Building | 2016-08-19 21:15 | 45850.78 | 699.984
Devonshire Building | 2016-08-19 21:30 | 45850.945 | 659.988
Devonshire Building | 2016-08-19 21:45 | 45851.11 | 659.988
Devonshire Building | 2016-08-19 22:00 | 45851.28 | 680.004
Devonshire Building | 2016-08-19 22:15 | 45851.4449 | 659.988
Devonshire Building | 2016-08-19 22:30 | 45851.6099 | 659.988
Devonshire Building | 2016-08-19 22:45 | 45851.7799 | 680.004
Devonshire Building | 2016-08-19 23:00 | 45851.9449 | 659.988
Devonshire Building | 2016-08-19 23:15 | 45852.1149 | 680.004
Devonshire Building | 2016-08-19 23:30 | 45852.2799 | 659.988
Devonshire Building | 2016-08-19 23:45 | 45852.4449 | 659.988 | 659.988
Devonshire Building | 2016-08-20 | 45852.6133 | 680.004
Devonshire Building | 2016-08-20 00:15 | 45852.7783 | 659.988
Devonshire Building | 2016-08-20 00:30 | 45852.9483 | 680.004
Devonshire Building | 2016-08-20 00:45 | 45853.1133 | 659.988
Devonshire Building | 2016-08-20 01:00 | 45853.2833 | 680.004
Devonshire Building | 2016-08-20 01:15 | 45853.4483 | 659.988
Devonshire Building | 2016-08-20 01:30 | 45853.6133 | 659.988
Devonshire Building | 2016-08-20 01:45 | 45853.7833 | 680.004
Devonshire Building | 2016-08-20 02:00 | 45853.9483 | 659.988
Devonshire Building | 2016-08-20 02:15 | 45854.1133 | 659.988
Devonshire Building | 2016-08-20 02:30 | 45854.2833 | 680.004
Devonshire Building | 2016-08-20 02:45 | 45854.4483 | 659.988
Devonshire Building | 2016-08-20 03:00 | 45854.6133 | 659.988
Devonshire Building | 2016-08-20 03:15 | 45854.7783 | 659.988
Devonshire Building | 2016-08-20 03:30 | 45854.9433 | 659.988
Devonshire Building | 2016-08-20 03:45 | 45855.1133 | 680.004
Devonshire Building | 2016-08-20 04:00 | 45855.2783 | 659.988
Devonshire Building | 2016-08-20 04:15 | 45855.4432 | 659.988
Devonshire Building | 2016-08-20 04:30 | 45855.6082 | 659.988
Devonshire Building | 2016-08-20 04:45 | 45855.7732 | 659.988
Devonshire Building | 2016-08-20 05:00 | 45855.9432 | 680.004
Devonshire Building | 2016-08-20 05:15 | 45856.1082 | 659.988
Devonshire Building | 2016-08-20 05:30 | 45856.2732 | 659.988
Devonshire Building | 2016-08-20 05:45 | 45856.4382 | 659.988
Devonshire Building | 2016-08-20 06:00 | 45856.6032 | 659.988
Devonshire Building | 2016-08-20 06:15 | 45856.7682 | 659.988
Devonshire Building | 2016-08-20 06:30 | 45856.9332 | 659.988
Devonshire Building | 2016-08-20 06:45 | 45857.0982 | 659.988
Devonshire Building | 2016-08-20 07:00 | 45857.2632 | 659.988
Devonshire Building | 2016-08-20 07:15 | 45857.4282 | 659.988
Devonshire Building | 2016-08-20 07:30 | 45857.5932 | 659.988
Devonshire Building | 2016-08-20 07:45 | 45857.7532 | 640.008
Devonshire Building | 2016-08-20 08:00 | 45857.9182 | 659.988
Devonshire Building | 2016-08-20 08:15 | 45858.0782 | 640.008
Devonshire Building | 2016-08-20 08:30 | 45858.2432 | 659.988
Devonshire Building | 2016-08-20 08:45 | 45858.4032 | 640.008
Devonshire Building | 2016-08-20 09:00 | 45858.5682 | 659.988
Devonshire Building | 2016-08-20 09:15 | 45858.7282 | 640.008
Devonshire Building | 2016-08-20 09:30 | 45858.8882 | 640.008
Devonshire Building | 2016-08-20 09:45 | 45859.0532 | 659.988
Devonshire Building | 2016-08-20 10:00 | 45859.2132 | 640.008
Devonshire Building | 2016-08-20 10:15 | 45859.3782 | 659.988
Devonshire Building | 2016-08-20 10:30 | 45859.5382 | 640.008
Devonshire Building | 2016-08-20 10:45 | 45859.6982 | 640.008
Devonshire Building | 2016-08-20 11:00 | 45859.8632 | 659.988
Devonshire Building | 2016-08-20 11:15 | 45860.0232 | 640.008
Devonshire Building | 2016-08-20 11:30 | 45860.1882 | 659.988
Devonshire Building | 2016-08-20 11:45 | 45860.3482 | 640.008
Devonshire Building | 2016-08-20 12:00 | 45860.5132 | 659.988
Devonshire Building | 2016-08-20 12:15 | 45860.6732 | 640.008
Devonshire Building | 2016-08-20 12:30 | 45860.8382 | 659.988
Devonshire Building | 2016-08-20 12:45 | 45861.0082 | 680.004
Devonshire Building | 2016-08-20 13:00 | 45861.4032 | 1580.004
Devonshire Building | 2016-08-20 13:15 | 45861.5632 | 640.008
Devonshire Building | 2016-08-20 13:30 | 45861.7432 | 720
Devonshire Building | 2016-08-20 13:45 | 45861.9232 | 720
Devonshire Building | 2016-08-20 14:00 | 45862.1082 | 740.016
Devonshire Building | 2016-08-20 14:15 | 45862.2832 | 699.984
Devonshire Building | 2016-08-20 14:30 | 45862.4632 | 720
Devonshire Building | 2016-08-20 14:45 | 45862.6432 | 720
Devonshire Building | 2016-08-20 15:00 | 45862.8182 | 699.984
Devonshire Building | 2016-08-20 15:15 | 45862.9982 | 720
Devonshire Building | 2016-08-20 15:30 | 45863.1732 | 699.984
Devonshire Building | 2016-08-20 15:45 | 45863.3432 | 680.004
Devonshire Building | 2016-08-20 16:00 | 45863.5082 | 659.988
Devonshire Building | 2016-08-20 16:15 | 45863.6682 | 640.008
Devonshire Building | 2016-08-20 16:30 | 45863.8332 | 659.988
Devonshire Building | 2016-08-20 16:45 | 45863.9932 | 640.008
Devonshire Building | 2016-08-20 17:00 | 45864.1532 | 640.008
Devonshire Building | 2016-08-20 17:15 | 45864.3182 | 659.988
Devonshire Building | 2016-08-20 17:30 | 45864.4782 | 640.008
Devonshire Building | 2016-08-20 17:45 | 45864.6432 | 659.988
Devonshire Building | 2016-08-20 18:00 | 45864.8032 | 640.008
Devonshire Building | 2016-08-20 18:15 | 45864.9682 | 659.988
Devonshire Building | 2016-08-20 18:30 | 45865.1282 | 640.008
Devonshire Building | 2016-08-20 18:45 | 45865.2932 | 659.988
Devonshire Building | 2016-08-20 19:00 | 45865.4532 | 640.008
Devonshire Building | 2016-08-20 19:15 | 45865.6182 | 659.988
Devonshire Building | 2016-08-20 19:30 | 45865.7782 | 640.008
Devonshire Building | 2016-08-20 19:45 | 45865.9432 | 659.988
Devonshire Building | 2016-08-20 20:00 | 45866.1032 | 640.008
Devonshire Building | 2016-08-20 20:15 | 45866.2682 | 659.988
Devonshire Building | 2016-08-20 20:30 | 45866.4332 | 659.988
Devonshire Building | 2016-08-20 20:45 | 45866.5982 | 659.988
Devonshire Building | 2016-08-20 21:00 | 45866.7682 | 680.004
Devonshire Building | 2016-08-20 21:15 | 45866.9332 | 659.988
Devonshire Building | 2016-08-20 21:30 | 45867.0982 | 659.988
Devonshire Building | 2016-08-20 21:45 | 45867.2632 | 659.988
Devonshire Building | 2016-08-20 22:00 | 45867.4282 | 659.988
Devonshire Building | 2016-08-20 22:15 | 45867.5932 | 659.988
Devonshire Building | 2016-08-20 22:30 | 45867.7582 | 659.988
Devonshire Building | 2016-08-20 22:45 | 45867.9182 | 640.008
Devonshire Building | 2016-08-20 23:00 | 45868.0832 | 659.988
Devonshire Building | 2016-08-20 23:15 | 45868.2482 | 659.988
Devonshire Building | 2016-08-20 23:30 | 45868.4132 | 659.988
Devonshire Building | 2016-08-20 23:45 | 45868.5782 | 659.988 | 640.008
Devonshire Building | 2016-08-21 | 45868.7461 | 659.988
Devonshire Building | 2016-08-21 00:15 | 45868.9111 | 659.988
Devonshire Building | 2016-08-21 00:30 | 45869.0761 | 659.988
Devonshire Building | 2016-08-21 00:45 | 45869.2411 | 659.988
Devonshire Building | 2016-08-21 01:00 | 45869.4011 | 640.008
Devonshire Building | 2016-08-21 01:15 | 45869.5711 | 680.004
Devonshire Building | 2016-08-21 01:30 | 45869.7311 | 640.008
Devonshire Building | 2016-08-21 01:45 | 45869.8961 | 659.988
Devonshire Building | 2016-08-21 02:00 | 45870.0661 | 680.004
Devonshire Building | 2016-08-21 02:15 | 45870.2311 | 659.988
Devonshire Building | 2016-08-21 02:30 | 45870.3961 | 659.988
Devonshire Building | 2016-08-21 02:45 | 45870.5611 | 659.988
Devonshire Building | 2016-08-21 03:00 | 45870.7261 | 659.988
Devonshire Building | 2016-08-21 03:15 | 45870.8911 | 659.988
Devonshire Building | 2016-08-21 03:30 | 45871.0561 | 659.988
Devonshire Building | 2016-08-21 03:45 | 45871.2211 | 659.988
Devonshire Building | 2016-08-21 04:00 | 45871.3861 | 659.988
Devonshire Building | 2016-08-21 04:15 | 45871.5561 | 680.004
Devonshire Building | 2016-08-21 04:30 | 45871.7211 | 659.988
Devonshire Building | 2016-08-21 04:45 | 45871.8861 | 659.988
Devonshire Building | 2016-08-21 05:00 | 45872.0511 | 659.988
Devonshire Building | 2016-08-21 05:15 | 45872.2211 | 680.004
Devonshire Building | 2016-08-21 05:30 | 45872.3861 | 659.988
Devonshire Building | 2016-08-21 05:45 | 45872.551 | 659.988
Devonshire Building | 2016-08-21 06:00 | 45872.716 | 659.988
Devonshire Building | 2016-08-21 06:15 | 45872.881 | 659.988
Devonshire Building | 2016-08-21 06:30 | 45873.046 | 659.988
Devonshire Building | 2016-08-21 06:45 | 45873.211 | 659.988
Devonshire Building | 2016-08-21 07:00 | 45873.376 | 659.988
Devonshire Building | 2016-08-21 07:15 | 45873.541 | 659.988
Devonshire Building | 2016-08-21 07:30 | 45873.706 | 659.988
Devonshire Building | 2016-08-21 07:45 | 45873.871 | 659.988
Devonshire Building | 2016-08-21 08:00 | 45874.036 | 659.988
Devonshire Building | 2016-08-21 08:15 | 45874.201 | 659.988
Devonshire Building | 2016-08-21 08:30 | 45874.366 | 659.988
Devonshire Building | 2016-08-21 08:45 | 45874.531 | 659.988
Devonshire Building | 2016-08-21 09:00 | 45874.691 | 640.008
Devonshire Building | 2016-08-21 09:15 | 45874.856 | 659.988
Devonshire Building | 2016-08-21 09:30 | 45875.016 | 640.008
Devonshire Building | 2016-08-21 09:45 | 45875.181 | 659.988
Devonshire Building | 2016-08-21 10:00 | 45875.346 | 659.988
Devonshire Building | 2016-08-21 10:15 | 45875.506 | 640.008
Devonshire Building | 2016-08-21 10:30 | 45875.671 | 659.988
Devonshire Building | 2016-08-21 10:45 | 45875.831 | 640.008
Devonshire Building | 2016-08-21 11:00 | 45875.996 | 659.988
Devonshire Building | 2016-08-21 11:15 | 45876.161 | 659.988
Devonshire Building | 2016-08-21 11:30 | 45876.326 | 659.988
Devonshire Building | 2016-08-21 11:45 | 45876.491 | 659.988
Devonshire Building | 2016-08-21 12:00 | 45876.656 | 659.988
Devonshire Building | 2016-08-21 12:15 | 45876.821 | 659.988
Devonshire Building | 2016-08-21 12:30 | 45876.986 | 659.988
Devonshire Building | 2016-08-21 12:45 | 45877.151 | 659.988
Devonshire Building | 2016-08-21 13:00 | 45877.316 | 659.988
Devonshire Building | 2016-08-21 13:15 | 45877.726 | 1640.016
Devonshire Building | 2016-08-21 13:30 | 45877.901 | 699.984
Devonshire Building | 2016-08-21 13:45 | 45878.081 | 720
Devonshire Building | 2016-08-21 14:00 | 45878.266 | 740.016
Devonshire Building | 2016-08-21 14:15 | 45878.446 | 720
Devonshire Building | 2016-08-21 14:30 | 45878.626 | 720
Devonshire Building | 2016-08-21 14:45 | 45878.806 | 720
Devonshire Building | 2016-08-21 15:00 | 45878.986 | 720
Devonshire Building | 2016-08-21 15:15 | 45879.166 | 720
Devonshire Building | 2016-08-21 15:30 | 45879.346 | 720
Devonshire Building | 2016-08-21 15:45 | 45879.516 | 680.004
Devonshire Building | 2016-08-21 16:00 | 45879.681 | 659.988
Devonshire Building | 2016-08-21 16:15 | 45879.846 | 659.988
Devonshire Building | 2016-08-21 16:30 | 45880.006 | 640.008
Devonshire Building | 2016-08-21 16:45 | 45880.171 | 659.988
Devonshire Building | 2016-08-21 17:00 | 45880.336 | 659.988
Devonshire Building | 2016-08-21 17:15 | 45880.496 | 640.008
Devonshire Building | 2016-08-21 17:30 | 45880.661 | 659.988
Devonshire Building | 2016-08-21 17:45 | 45880.821 | 640.008
Devonshire Building | 2016-08-21 18:00 | 45880.986 | 659.988
Devonshire Building | 2016-08-21 18:15 | 45881.151 | 659.988
Devonshire Building | 2016-08-21 18:30 | 45881.311 | 640.008
Devonshire Building | 2016-08-21 18:45 | 45881.476 | 659.988
Devonshire Building | 2016-08-21 19:00 | 45881.641 | 659.988
Devonshire Building | 2016-08-21 19:15 | 45881.801 | 640.008
Devonshire Building | 2016-08-21 19:30 | 45881.966 | 659.988
Devonshire Building | 2016-08-21 19:45 | 45882.131 | 659.988
Devonshire Building | 2016-08-21 20:00 | 45882.296 | 659.988
Devonshire Building | 2016-08-21 20:15 | 45882.456 | 640.008
Devonshire Building | 2016-08-21 20:30 | 45882.621 | 659.988
Devonshire Building | 2016-08-21 20:45 | 45882.786 | 659.988
Devonshire Building | 2016-08-21 21:00 | 45882.961 | 699.984
Devonshire Building | 2016-08-21 21:15 | 45883.1259 | 659.988
Devonshire Building | 2016-08-21 21:30 | 45883.2909 | 659.988
Devonshire Building | 2016-08-21 21:45 | 45883.4559 | 659.988
Devonshire Building | 2016-08-21 22:00 | 45883.6209 | 659.988
Devonshire Building | 2016-08-21 22:15 | 45883.7859 | 659.988
Devonshire Building | 2016-08-21 22:30 | 45883.9509 | 659.988
Devonshire Building | 2016-08-21 22:45 | 45884.1159 | 659.988
Devonshire Building | 2016-08-21 23:00 | 45884.2809 | 659.988
Devonshire Building | 2016-08-21 23:15 | 45884.4509 | 680.004
Devonshire Building | 2016-08-21 23:30 | 45884.6159 | 659.988
Devonshire Building | 2016-08-21 23:45 | 45884.7809 | 659.988 | 640.008
Devonshire Building | 2016-08-22 | 45884.9453 | 659.988
Devonshire Building | 2016-08-22 00:15 | 45885.1103 | 659.988
Devonshire Building | 2016-08-22 00:30 | 45885.2753 | 659.988
Devonshire Building | 2016-08-22 00:45 | 45885.4403 | 659.988
Devonshire Building | 2016-08-22 01:00 | 45885.6103 | 680.004
Devonshire Building | 2016-08-22 01:15 | 45885.7753 | 659.988
Devonshire Building | 2016-08-22 01:30 | 45885.9403 | 659.988
Devonshire Building | 2016-08-22 01:45 | 45886.1053 | 659.988
Devonshire Building | 2016-08-22 02:00 | 45886.2753 | 680.004
Devonshire Building | 2016-08-22 02:15 | 45886.4403 | 659.988
Devonshire Building | 2016-08-22 02:30 | 45886.6053 | 659.988
Devonshire Building | 2016-08-22 02:45 | 45886.7753 | 680.004
Devonshire Building | 2016-08-22 03:00 | 45886.9403 | 659.988
Devonshire Building | 2016-08-22 03:15 | 45887.1103 | 680.004
Devonshire Building | 2016-08-22 03:30 | 45887.2753 | 659.988
Devonshire Building | 2016-08-22 03:45 | 45887.4453 | 680.004
Devonshire Building | 2016-08-22 04:00 | 45887.6153 | 680.004
Devonshire Building | 2016-08-22 04:15 | 45887.7803 | 659.988
Devonshire Building | 2016-08-22 04:30 | 45887.9503 | 680.004
Devonshire Building | 2016-08-22 04:45 | 45888.1153 | 659.988
Devonshire Building | 2016-08-22 05:00 | 45888.2803 | 659.988
Devonshire Building | 2016-08-22 05:15 | 45888.4503 | 680.004
Devonshire Building | 2016-08-22 05:30 | 45888.6203 | 680.004
Devonshire Building | 2016-08-22 05:45 | 45888.7853 | 659.988
Devonshire Building | 2016-08-22 06:00 | 45888.9503 | 659.988
Devonshire Building | 2016-08-22 06:15 | 45889.1203 | 680.004
Devonshire Building | 2016-08-22 06:30 | 45889.2903 | 680.004
Devonshire Building | 2016-08-22 06:45 | 45889.4603 | 680.004
Devonshire Building | 2016-08-22 07:00 | 45889.6303 | 680.004
Devonshire Building | 2016-08-22 07:15 | 45889.8003 | 680.004
Devonshire Building | 2016-08-22 07:30 | 45889.9753 | 699.984
Devonshire Building | 2016-08-22 07:45 | 45890.3753 | 1599.984
Devonshire Building | 2016-08-22 08:00 | 45890.5553 | 720
Devonshire Building | 2016-08-22 08:15 | 45890.7403 | 740.016
Devonshire Building | 2016-08-22 08:30 | 45890.9303 | 759.996
Devonshire Building | 2016-08-22 08:45 | 45891.1153 | 740.016
Devonshire Building | 2016-08-22 09:00 | 45891.3003 | 740.016
Devonshire Building | 2016-08-22 09:15 | 45891.4953 | 780.012
Devonshire Building | 2016-08-22 09:30 | 45891.7653 | 1080
Devonshire Building | 2016-08-22 09:45 | 45892.2303 | 1860.012
Devonshire Building | 2016-08-22 10:00 | 45892.8303 | 2400.012
Devonshire Building | 2016-08-22 10:15 | 45893.1203 | 1159.992
Devonshire Building | 2016-08-22 10:30 | 45893.3653 | 979.992
Devonshire Building | 2016-08-22 10:45 | 45893.5803 | 860.004
Devonshire Building | 2016-08-22 11:00 | 45893.7753 | 780.012
Devonshire Building | 2016-08-22 11:15 | 45893.9653 | 759.996
Devonshire Building | 2016-08-22 11:30 | 45894.1503 | 740.016
Devonshire Building | 2016-08-22 11:45 | 45894.3353 | 740.016
Devonshire Building | 2016-08-22 12:00 | 45894.5153 | 720
Devonshire Building | 2016-08-22 12:15 | 45894.9403 | 1699.992
Devonshire Building | 2016-08-22 12:30 | 45895.1103 | 680.004
Devonshire Building | 2016-08-22 12:45 | 45895.2803 | 680.004
Devonshire Building | 2016-08-22 13:00 | 45895.4553 | 699.984
Devonshire Building | 2016-08-22 13:15 | 45895.6303 | 699.984
Devonshire Building | 2016-08-22 13:30 | 45895.8003 | 680.004
Devonshire Building | 2016-08-22 13:45 | 45895.9703 | 680.004
Devonshire Building | 2016-08-22 14:00 | 45896.3153 | 1379.988
Devonshire Building | 2016-08-22 14:15 | 45896.5703 | 1019.988
Devonshire Building | 2016-08-22 14:30 | 45896.7503 | 720
Devonshire Building | 2016-08-22 14:45 | 45896.9303 | 720
Devonshire Building | 2016-08-22 15:00 | 45897.1003 | 680.004
Devonshire Building | 2016-08-22 15:15 | 45897.2853 | 740.016
Devonshire Building | 2016-08-22 15:30 | 45897.4653 | 720
Devonshire Building | 2016-08-22 15:45 | 45897.7103 | 979.992
Devonshire Building | 2016-08-22 16:00 | 45897.9903 | 1119.996
Devonshire Building | 2016-08-22 16:15 | 45898.2403 | 1000.008
Devonshire Building | 2016-08-22 16:30 | 45898.4653 | 900
Devonshire Building | 2016-08-22 16:45 | 45898.6753 | 839.988
Devonshire Building | 2016-08-22 17:00 | 45898.8753 | 799.992
Devonshire Building | 2016-08-22 17:15 | 45899.2953 | 1680.012
Devonshire Building | 2016-08-22 17:30 | 45899.4703 | 699.984
Devonshire Building | 2016-08-22 17:45 | 45899.6403 | 680.004
Devonshire Building | 2016-08-22 18:00 | 45899.8153 | 699.984
Devonshire Building | 2016-08-22 18:15 | 45899.9853 | 680.004
Devonshire Building | 2016-08-22 18:30 | 45900.1603 | 699.984
Devonshire Building | 2016-08-22 18:45 | 45900.3303 | 680.004
Devonshire Building | 2016-08-22 19:00 | 45900.5053 | 699.984
Devonshire Building | 2016-08-22 19:15 | 45900.6753 | 680.004
Devonshire Building | 2016-08-22 19:30 | 45900.8503 | 699.984
Devonshire Building | 2016-08-22 19:45 | 45901.0203 | 680.004
Devonshire Building | 2016-08-22 20:00 | 45901.1953 | 699.984
Devonshire Building | 2016-08-22 20:15 | 45901.3653 | 680.004
Devonshire Building | 2016-08-22 20:30 | 45901.5353 | 680.004
Devonshire Building | 2016-08-22 20:45 | 45901.7103 | 699.984
Devonshire Building | 2016-08-22 21:00 | 45901.8853 | 699.984
Devonshire Building | 2016-08-22 21:15 | 45902.0553 | 680.004
Devonshire Building | 2016-08-22 21:30 | 45902.2203 | 659.988
Devonshire Building | 2016-08-22 21:45 | 45902.3903 | 680.004
Devonshire Building | 2016-08-22 22:00 | 45902.5603 | 680.004
Devonshire Building | 2016-08-22 22:15 | 45902.7303 | 680.004
Devonshire Building | 2016-08-22 22:30 | 45902.8953 | 659.988
Devonshire Building | 2016-08-22 22:45 | 45903.0653 | 680.004
Devonshire Building | 2016-08-22 23:00 | 45903.2353 | 680.004
Devonshire Building | 2016-08-22 23:15 | 45903.4053 | 680.004
Devonshire Building | 2016-08-22 23:30 | 45903.5753 | 680.004
Devonshire Building | 2016-08-22 23:45 | 45903.7453 | 680.004 | 659.988
Devonshire Building | 2016-08-23 | 45903.9141 | 680.004
Devonshire Building | 2016-08-23 00:15 | 45904.0841 | 680.004
Devonshire Building | 2016-08-23 00:30 | 45904.2591 | 699.984
Devonshire Building | 2016-08-23 00:45 | 45904.4291 | 680.004
Devonshire Building | 2016-08-23 01:00 | 45904.5991 | 680.004
Devonshire Building | 2016-08-23 01:15 | 45904.7691 | 680.004
Devonshire Building | 2016-08-23 01:30 | 45904.9391 | 680.004
Devonshire Building | 2016-08-23 01:45 | 45905.1091 | 680.004
Devonshire Building | 2016-08-23 02:00 | 45905.2791 | 680.004
Devonshire Building | 2016-08-23 02:15 | 45905.4491 | 680.004
Devonshire Building | 2016-08-23 02:30 | 45905.6191 | 680.004
Devonshire Building | 2016-08-23 02:45 | 45905.7891 | 680.004
Devonshire Building | 2016-08-23 03:00 | 45905.9591 | 680.004
Devonshire Building | 2016-08-23 03:15 | 45906.1291 | 680.004
Devonshire Building | 2016-08-23 03:30 | 45906.2991 | 680.004
Devonshire Building | 2016-08-23 03:45 | 45906.4691 | 680.004
Devonshire Building | 2016-08-23 04:00 | 45906.6391 | 680.004
Devonshire Building | 2016-08-23 04:15 | 45906.8091 | 680.004
Devonshire Building | 2016-08-23 04:30 | 45906.9791 | 680.004
Devonshire Building | 2016-08-23 04:45 | 45907.1491 | 680.004
Devonshire Building | 2016-08-23 05:00 | 45907.3191 | 680.004
Devonshire Building | 2016-08-23 05:15 | 45907.4891 | 680.004
Devonshire Building | 2016-08-23 05:30 | 45907.6541 | 659.988
Devonshire Building | 2016-08-23 05:45 | 45907.8241 | 680.004
Devonshire Building | 2016-08-23 06:00 | 45907.9941 | 680.004
Devonshire Building | 2016-08-23 06:15 | 45908.1641 | 680.004
Devonshire Building | 2016-08-23 06:30 | 45908.3291 | 659.988
Devonshire Building | 2016-08-23 06:45 | 45908.4991 | 680.004
Devonshire Building | 2016-08-23 07:00 | 45908.6741 | 699.984
Devonshire Building | 2016-08-23 07:15 | 45908.8441 | 680.004
Devonshire Building | 2016-08-23 07:30 | 45909.0241 | 720
Devonshire Building | 2016-08-23 07:45 | 45909.2641 | 960.012
Devonshire Building | 2016-08-23 08:00 | 45909.6441 | 1519.992
Devonshire Building | 2016-08-23 08:15 | 45909.8341 | 759.996
Devonshire Building | 2016-08-23 08:30 | 45910.0191 | 740.016
Devonshire Building | 2016-08-23 08:45 | 45910.2291 | 839.988
Devonshire Building | 2016-08-23 09:00 | 45910.4391 | 839.988
Devonshire Building | 2016-08-23 09:15 | 45910.7491 | 1239.984
Devonshire Building | 2016-08-23 09:30 | 45911.1941 | 1779.984
Devonshire Building | 2016-08-23 09:45 | 45911.5991 | 1620
Devonshire Building | 2016-08-23 10:00 | 45912.1841 | 2340
Devonshire Building | 2016-08-23 10:15 | 45912.4741 | 1159.992
Devonshire Building | 2016-08-23 10:30 | 45912.7241 | 1000.008
Devonshire Building | 2016-08-23 10:45 | 45912.9641 | 960.012
Devonshire Building | 2016-08-23 11:00 | 45913.1891 | 900
Devonshire Building | 2016-08-23 11:15 | 45913.4091 | 879.984
Devonshire Building | 2016-08-23 11:30 | 45913.6191 | 839.988
Devonshire Building | 2016-08-23 11:45 | 45913.8241 | 820.008
Devonshire Building | 2016-08-23 12:00 | 45914.2591 | 1739.988
Devonshire Building | 2016-08-23 12:15 | 45914.4541 | 780.012
Devonshire Building | 2016-08-23 12:30 | 45914.6441 | 759.996
Devonshire Building | 2016-08-23 12:45 | 45914.8391 | 780.012
Devonshire Building | 2016-08-23 13:00 | 45915.0341 | 780.012
Devonshire Building | 2016-08-23 13:15 | 45915.2341 | 799.992
Devonshire Building | 2016-08-23 13:30 | 45915.4291 | 780.012
Devonshire Building | 2016-08-23 13:45 | 45915.6191 | 759.996
Devonshire Building | 2016-08-23 14:00 | 45915.9091 | 1159.992
Devonshire Building | 2016-08-23 14:15 | 45916.2741 | 1460.016
Devonshire Building | 2016-08-23 14:30 | 45916.5041 | 920.016
Devonshire Building | 2016-08-23 14:45 | 45916.7341 | 920.016
Devonshire Building | 2016-08-23 15:00 | 45916.9541 | 879.984
Devonshire Building | 2016-08-23 15:15 | 45917.1791 | 900
Devonshire Building | 2016-08-23 15:30 | 45917.3941 | 860.004
Devonshire Building | 2016-08-23 15:45 | 45917.6141 | 879.984
Devonshire Building | 2016-08-23 16:00 | 45917.8591 | 979.992
Devonshire Building | 2016-08-23 16:15 | 45918.1041 | 979.992
Devonshire Building | 2016-08-23 16:30 | 45918.5941 | 1959.984
Devonshire Building | 2016-08-23 16:45 | 45918.8641 | 1080
Devonshire Building | 2016-08-23 17:00 | 45919.1191 | 1019.988
Devonshire Building | 2016-08-23 17:15 | 45919.3441 | 900
Devonshire Building | 2016-08-23 17:30 | 45919.5591 | 860.004
Devonshire Building | 2016-08-23 17:45 | 45919.7591 | 799.992
Devonshire Building | 2016-08-23 18:00 | 45919.9541 | 780.012
Devonshire Building | 2016-08-23 18:15 | 45920.1441 | 759.996
Devonshire Building | 2016-08-23 18:30 | 45920.3291 | 740.016
Devonshire Building | 2016-08-23 18:45 | 45920.5091 | 720
Devonshire Building | 2016-08-23 19:00 | 45920.6891 | 720
Devonshire Building | 2016-08-23 19:15 | 45920.8641 | 699.984
Devonshire Building | 2016-08-23 19:30 | 45921.0441 | 720
Devonshire Building | 2016-08-23 19:45 | 45921.2191 | 699.984
Devonshire Building | 2016-08-23 20:00 | 45921.394 | 699.984
Devonshire Building | 2016-08-23 20:15 | 45921.569 | 699.984
Devonshire Building | 2016-08-23 20:30 | 45921.744 | 699.984
Devonshire Building | 2016-08-23 20:45 | 45921.919 | 699.984
Devonshire Building | 2016-08-23 21:00 | 45922.099 | 720
Devonshire Building | 2016-08-23 21:15 | 45922.269 | 680.004
Devonshire Building | 2016-08-23 21:30 | 45922.439 | 680.004
Devonshire Building | 2016-08-23 21:45 | 45922.609 | 680.004
Devonshire Building | 2016-08-23 22:00 | 45922.774 | 659.988
Devonshire Building | 2016-08-23 22:15 | 45922.944 | 680.004
Devonshire Building | 2016-08-23 22:30 | 45923.114 | 680.004
Devonshire Building | 2016-08-23 22:45 | 45923.284 | 680.004
Devonshire Building | 2016-08-23 23:00 | 45923.454 | 680.004
Devonshire Building | 2016-08-23 23:15 | 45923.624 | 680.004
Devonshire Building | 2016-08-23 23:30 | 45923.789 | 659.988
Devonshire Building | 2016-08-23 23:45 | 45923.959 | 680.004 | 659.988
Devonshire Building | 2016-08-24 | 45924.1289 | 680.004
Devonshire Building | 2016-08-24 00:15 | 45924.2989 | 680.004
Devonshire Building | 2016-08-24 00:30 | 45924.4689 | 680.004
Devonshire Building | 2016-08-24 00:45 | 45924.6389 | 680.004
Devonshire Building | 2016-08-24 01:00 | 45924.8089 | 680.004
Devonshire Building | 2016-08-24 01:15 | 45924.9789 | 680.004
Devonshire Building | 2016-08-24 01:30 | 45925.1489 | 680.004
Devonshire Building | 2016-08-24 01:45 | 45925.3189 | 680.004
Devonshire Building | 2016-08-24 02:00 | 45925.4889 | 680.004
Devonshire Building | 2016-08-24 02:15 | 45925.6639 | 699.984
Devonshire Building | 2016-08-24 02:30 | 45925.8339 | 680.004
Devonshire Building | 2016-08-24 02:45 | 45926.0039 | 680.004
Devonshire Building | 2016-08-24 03:00 | 45926.1689 | 659.988
Devonshire Building | 2016-08-24 03:15 | 45926.3389 | 680.004
Devonshire Building | 2016-08-24 03:30 | 45926.5089 | 680.004
Devonshire Building | 2016-08-24 03:45 | 45926.6789 | 680.004
Devonshire Building | 2016-08-24 04:00 | 45926.8489 | 680.004
Devonshire Building | 2016-08-24 04:15 | 45927.0189 | 680.004
Devonshire Building | 2016-08-24 04:30 | 45927.1889 | 680.004
Devonshire Building | 2016-08-24 04:45 | 45927.3589 | 680.004
Devonshire Building | 2016-08-24 05:00 | 45927.5289 | 680.004
Devonshire Building | 2016-08-24 05:15 | 45927.6989 | 680.004
Devonshire Building | 2016-08-24 05:30 | 45927.8689 | 680.004
Devonshire Building | 2016-08-24 05:45 | 45928.0389 | 680.004
Devonshire Building | 2016-08-24 06:00 | 45928.2089 | 680.004
Devonshire Building | 2016-08-24 06:15 | 45928.3789 | 680.004
Devonshire Building | 2016-08-24 06:30 | 45928.5439 | 659.988
Devonshire Building | 2016-08-24 06:45 | 45928.7189 | 699.984
Devonshire Building | 2016-08-24 07:00 | 45928.8839 | 659.988
Devonshire Building | 2016-08-24 07:15 | 45929.0539 | 680.004
Devonshire Building | 2016-08-24 07:30 | 45929.2239 | 680.004
Devonshire Building | 2016-08-24 07:45 | 45929.4089 | 740.016
Devonshire Building | 2016-08-24 08:00 | 45929.8489 | 1760.004
Devonshire Building | 2016-08-24 08:15 | 45930.0339 | 740.016
Devonshire Building | 2016-08-24 08:30 | 45930.2239 | 759.996
Devonshire Building | 2016-08-24 08:45 | 45930.4139 | 759.996
Devonshire Building | 2016-08-24 09:00 | 45930.6039 | 759.996
Devonshire Building | 2016-08-24 09:15 | 45930.7889 | 740.016
Devonshire Building | 2016-08-24 09:30 | 45930.9739 | 740.016
Devonshire Building | 2016-08-24 09:45 | 45931.3539 | 1519.992
Devonshire Building | 2016-08-24 10:00 | 45931.6189 | 1059.984
Devonshire Building | 2016-08-24 10:15 | 45931.7889 | 680.004
Devonshire Building | 2016-08-24 10:30 | 45931.9789 | 759.996
Devonshire Building | 2016-08-24 10:45 | 45932.1789 | 799.992
Devonshire Building | 2016-08-24 11:00 | 45932.3739 | 780.012
Devonshire Building | 2016-08-24 11:15 | 45932.5739 | 799.992
Devonshire Building | 2016-08-24 11:30 | 45932.7739 | 799.992
Devonshire Building | 2016-08-24 11:45 | 45932.9689 | 780.012
Devonshire Building | 2016-08-24 12:00 | 45933.1639 | 780.012
Devonshire Building | 2016-08-24 12:15 | 45933.3539 | 759.996
Devonshire Building | 2016-08-24 12:30 | 45933.7889 | 1739.988
Devonshire Building | 2016-08-24 12:45 | 45933.9739 | 740.016
Devonshire Building | 2016-08-24 13:00 | 45934.1539 | 720
Devonshire Building | 2016-08-24 13:15 | 45934.3389 | 740.016
Devonshire Building | 2016-08-24 13:30 | 45934.5339 | 780.012
Devonshire Building | 2016-08-24 13:45 | 45934.7189 | 740.016
Devonshire Building | 2016-08-24 14:00 | 45934.9039 | 740.016
Devonshire Building | 2016-08-24 14:15 | 45935.0889 | 740.016
Devonshire Building | 2016-08-24 14:30 | 45935.274 | 740.016
Devonshire Building | 2016-08-24 14:45 | 45935.464 | 759.996
Devonshire Building | 2016-08-24 15:00 | 45935.9089 | 1779.984
Devonshire Building | 2016-08-24 15:15 | 45936.094 | 740.016
Devonshire Building | 2016-08-24 15:30 | 45936.274 | 720
Devonshire Building | 2016-08-24 15:45 | 45936.459 | 740.016
Devonshire Building | 2016-08-24 16:00 | 45936.644 | 740.016
Devonshire Building | 2016-08-24 16:15 | 45936.829 | 740.016
Devonshire Building | 2016-08-24 16:30 | 45937.019 | 759.996
Devonshire Building | 2016-08-24 16:45 | 45937.204 | 740.016
Devonshire Building | 2016-08-24 17:00 | 45937.384 | 720
Devonshire Building | 2016-08-24 17:15 | 45937.569 | 740.016
Devonshire Building | 2016-08-24 17:30 | 45937.749 | 720
Devonshire Building | 2016-08-24 17:45 | 45937.929 | 720
Devonshire Building | 2016-08-24 18:00 | 45938.109 | 720
Devonshire Building | 2016-08-24 18:15 | 45938.289 | 720
Devonshire Building | 2016-08-24 18:30 | 45938.469 | 720
Devonshire Building | 2016-08-24 18:45 | 45938.644 | 699.984
Devonshire Building | 2016-08-24 19:00 | 45938.824 | 720
Devonshire Building | 2016-08-24 19:15 | 45938.999 | 699.984
Devonshire Building | 2016-08-24 19:30 | 45939.179 | 720
Devonshire Building | 2016-08-24 19:45 | 45939.354 | 699.984
Devonshire Building | 2016-08-24 20:00 | 45939.529 | 699.984
Devonshire Building | 2016-08-24 20:15 | 45939.704 | 699.984
Devonshire Building | 2016-08-24 20:30 | 45939.8789 | 699.984
Devonshire Building | 2016-08-24 20:45 | 45940.0489 | 680.004
Devonshire Building | 2016-08-24 21:00 | 45940.2439 | 780.012
Devonshire Building | 2016-08-24 21:15 | 45940.414 | 680.004
Devonshire Building | 2016-08-24 21:30 | 45940.5789 | 659.988
Devonshire Building | 2016-08-24 21:45 | 45940.7489 | 680.004
Devonshire Building | 2016-08-24 22:00 | 45940.9189 | 680.004
Devonshire Building | 2016-08-24 22:15 | 45941.0839 | 659.988
Devonshire Building | 2016-08-24 22:30 | 45941.2539 | 680.004
Devonshire Building | 2016-08-24 22:45 | 45941.4239 | 680.004
Devonshire Building | 2016-08-24 23:00 | 45941.5889 | 659.988
Devonshire Building | 2016-08-24 23:15 | 45941.7589 | 680.004
Devonshire Building | 2016-08-24 23:30 | 45941.9289 | 680.004
Devonshire Building | 2016-08-24 23:45 | 45942.0939 | 659.988 | 659.988
Devonshire Building | 2016-08-25 | 45942.2656 | 680.004
Devonshire Building | 2016-08-25 00:15 | 45942.4356 | 680.004
Devonshire Building | 2016-08-25 00:30 | 45942.6056 | 680.004
Devonshire Building | 2016-08-25 00:45 | 45942.7756 | 680.004
Devonshire Building | 2016-08-25 01:00 | 45942.9406 | 659.988
Devonshire Building | 2016-08-25 01:15 | 45943.1106 | 680.004
Devonshire Building | 2016-08-25 01:30 | 45943.2806 | 680.004
Devonshire Building | 2016-08-25 01:45 | 45943.4506 | 680.004
Devonshire Building | 2016-08-25 02:00 | 45943.6206 | 680.004
Devonshire Building | 2016-08-25 02:15 | 45943.7906 | 680.004
Devonshire Building | 2016-08-25 02:30 | 45943.9606 | 680.004
Devonshire Building | 2016-08-25 02:45 | 45944.1256 | 659.988
Devonshire Building | 2016-08-25 03:00 | 45944.2956 | 680.004
Devonshire Building | 2016-08-25 03:15 | 45944.4656 | 680.004
Devonshire Building | 2016-08-25 03:30 | 45944.6306 | 659.988
Devonshire Building | 2016-08-25 03:45 | 45945.0356 | 1620
Devonshire Building | 2016-08-25 04:00 | 45945.2056 | 680.004
Devonshire Building | 2016-08-25 04:15 | 45945.3706 | 659.988
Devonshire Building | 2016-08-25 04:30 | 45945.5356 | 659.988
Devonshire Building | 2016-08-25 04:45 | 45945.7056 | 680.004
Devonshire Building | 2016-08-25 05:00 | 45945.8706 | 659.988
Devonshire Building | 2016-08-25 05:15 | 45946.0356 | 659.988
Devonshire Building | 2016-08-25 05:30 | 45946.2056 | 680.004
Devonshire Building | 2016-08-25 05:45 | 45946.3706 | 659.988
Devonshire Building | 2016-08-25 06:00 | 45946.5356 | 659.988
Devonshire Building | 2016-08-25 06:15 | 45946.7056 | 680.004
Devonshire Building | 2016-08-25 06:30 | 45946.8806 | 699.984
Devonshire Building | 2016-08-25 06:45 | 45947.0456 | 659.988
Devonshire Building | 2016-08-25 07:00 | 45947.2106 | 659.988
Devonshire Building | 2016-08-25 07:15 | 45947.3756 | 659.988
Devonshire Building | 2016-08-25 07:30 | 45947.5506 | 699.984
Devonshire Building | 2016-08-25 07:45 | 45947.7306 | 720
Devonshire Building | 2016-08-25 08:00 | 45947.9206 | 759.996
Devonshire Building | 2016-08-25 08:15 | 45948.1056 | 740.016
Devonshire Building | 2016-08-25 08:30 | 45948.2906 | 740.016
Devonshire Building | 2016-08-25 08:45 | 45948.4756 | 740.016
Devonshire Building | 2016-08-25 09:00 | 45948.6556 | 720
Devonshire Building | 2016-08-25 09:15 | 45949.0956 | 1760.004
Devonshire Building | 2016-08-25 09:30 | 45949.2756 | 720
Devonshire Building | 2016-08-25 09:45 | 45949.4606 | 740.016
Devonshire Building | 2016-08-25 10:00 | 45949.6756 | 860.004
Devonshire Building | 2016-08-25 10:15 | 45949.8756 | 799.992
Devonshire Building | 2016-08-25 10:30 | 45950.0756 | 799.992
Devonshire Building | 2016-08-25 10:45 | 45950.3556 | 1119.996
Devonshire Building | 2016-08-25 11:00 | 45950.7406 | 1540.008
Devonshire Building | 2016-08-25 11:15 | 45950.9456 | 820.008
Devonshire Building | 2016-08-25 11:30 | 45951.1506 | 820.008
Devonshire Building | 2016-08-25 11:45 | 45951.3506 | 799.992
Devonshire Building | 2016-08-25 12:00 | 45951.5506 | 799.992
Devonshire Building | 2016-08-25 12:15 | 45951.7506 | 799.992
Devonshire Building | 2016-08-25 12:30 | 45952.1906 | 1760.004
Devonshire Building | 2016-08-25 12:45 | 45952.3756 | 740.016
Devonshire Building | 2016-08-25 13:00 | 45952.5606 | 740.016
Devonshire Building | 2016-08-25 13:15 | 45952.7556 | 780.012
Devonshire Building | 2016-08-25 13:30 | 45952.9406 | 740.016
Devonshire Building | 2016-08-25 13:45 | 45953.1256 | 740.016
Devonshire Building | 2016-08-25 14:00 | 45953.3156 | 759.996
Devonshire Building | 2016-08-25 14:15 | 45953.5006 | 740.016
Devonshire Building | 2016-08-25 14:30 | 45953.9456 | 1779.984
Devonshire Building | 2016-08-25 14:45 | 45954.1356 | 759.996
Devonshire Building | 2016-08-25 15:00 | 45954.3256 | 759.996
Devonshire Building | 2016-08-25 15:15 | 45954.5156 | 759.996
Devonshire Building | 2016-08-25 15:30 | 45954.7056 | 759.996
Devonshire Building | 2016-08-25 15:45 | 45954.9006 | 780.012
Devonshire Building | 2016-08-25 16:00 | 45955.0856 | 740.016
Devonshire Building | 2016-08-25 16:15 | 45955.2756 | 759.996
Devonshire Building | 2016-08-25 16:30 | 45955.4606 | 740.016
Devonshire Building | 2016-08-25 16:45 | 45955.6456 | 740.016
Devonshire Building | 2016-08-25 17:00 | 45955.8256 | 720
Devonshire Building | 2016-08-25 17:15 | 45956.2556 | 1720.008
Devonshire Building | 2016-08-25 17:30 | 45956.4306 | 699.984
Devonshire Building | 2016-08-25 17:45 | 45956.6156 | 740.016
Devonshire Building | 2016-08-25 18:00 | 45956.7956 | 720
Devonshire Building | 2016-08-25 18:15 | 45956.9756 | 720
Devonshire Building | 2016-08-25 18:30 | 45957.1556 | 720
Devonshire Building | 2016-08-25 18:45 | 45957.3356 | 720
Devonshire Building | 2016-08-25 19:00 | 45957.5156 | 720
Devonshire Building | 2016-08-25 19:15 | 45957.6906 | 699.984
Devonshire Building | 2016-08-25 19:30 | 45957.8706 | 720
Devonshire Building | 2016-08-25 19:45 | 45958.0456 | 699.984
Devonshire Building | 2016-08-25 20:00 | 45958.2206 | 699.984
Devonshire Building | 2016-08-25 20:15 | 45958.3906 | 680.004
Devonshire Building | 2016-08-25 20:30 | 45958.5656 | 699.984
Devonshire Building | 2016-08-25 20:45 | 45958.7356 | 680.004
Devonshire Building | 2016-08-25 21:00 | 45958.9156 | 720
Devonshire Building | 2016-08-25 21:15 | 45959.0806 | 659.988
Devonshire Building | 2016-08-25 21:30 | 45959.2456 | 659.988
Devonshire Building | 2016-08-25 21:45 | 45959.4106 | 659.988
Devonshire Building | 2016-08-25 22:00 | 45959.5756 | 659.988
Devonshire Building | 2016-08-25 22:15 | 45959.7406 | 659.988
Devonshire Building | 2016-08-25 22:30 | 45959.9056 | 659.988
Devonshire Building | 2016-08-25 22:45 | 45960.0706 | 659.988
Devonshire Building | 2016-08-25 23:00 | 45960.2356 | 659.988
Devonshire Building | 2016-08-25 23:15 | 45960.4006 | 659.988
Devonshire Building | 2016-08-25 23:30 | 45960.5706 | 680.004
Devonshire Building | 2016-08-25 23:45 | 45960.7356 | 659.988 | 659.988
Devonshire Building | 2016-08-26 | 45960.8984 | 659.988
Devonshire Building | 2016-08-26 00:15 | 45961.0634 | 659.988
Devonshire Building | 2016-08-26 00:30 | 45961.2284 | 659.988
Devonshire Building | 2016-08-26 00:45 | 45961.3934 | 659.988
Devonshire Building | 2016-08-26 01:00 | 45961.5584 | 659.988
Devonshire Building | 2016-08-26 01:15 | 45961.7234 | 659.988
Devonshire Building | 2016-08-26 01:30 | 45961.8934 | 680.004
Devonshire Building | 2016-08-26 01:45 | 45962.0584 | 659.988
Devonshire Building | 2016-08-26 02:00 | 45962.2234 | 659.988
Devonshire Building | 2016-08-26 02:15 | 45962.3884 | 659.988
Devonshire Building | 2016-08-26 02:30 | 45962.5534 | 659.988
Devonshire Building | 2016-08-26 02:45 | 45962.7184 | 659.988
Devonshire Building | 2016-08-26 03:00 | 45962.8834 | 659.988
Devonshire Building | 2016-08-26 03:15 | 45963.0484 | 659.988
Devonshire Building | 2016-08-26 03:30 | 45963.2134 | 659.988
Devonshire Building | 2016-08-26 03:45 | 45963.3784 | 659.988
Devonshire Building | 2016-08-26 04:00 | 45963.5434 | 659.988
Devonshire Building | 2016-08-26 04:15 | 45963.7084 | 659.988
Devonshire Building | 2016-08-26 04:30 | 45963.8734 | 659.988
Devonshire Building | 2016-08-26 04:45 | 45964.0384 | 659.988
Devonshire Building | 2016-08-26 05:00 | 45964.2034 | 659.988
Devonshire Building | 2016-08-26 05:15 | 45964.3684 | 659.988
Devonshire Building | 2016-08-26 05:30 | 45964.5334 | 659.988
Devonshire Building | 2016-08-26 05:45 | 45964.6934 | 640.008
Devonshire Building | 2016-08-26 06:00 | 45964.8584 | 659.988
Devonshire Building | 2016-08-26 06:15 | 45965.0234 | 659.988
Devonshire Building | 2016-08-26 06:30 | 45965.1884 | 659.988
Devonshire Building | 2016-08-26 06:45 | 45965.3534 | 659.988
Devonshire Building | 2016-08-26 07:00 | 45965.5134 | 640.008
Devonshire Building | 2016-08-26 07:15 | 45965.6884 | 699.984
Devonshire Building | 2016-08-26 07:30 | 45965.8584 | 680.004
Devonshire Building | 2016-08-26 07:45 | 45966.2684 | 1640.016
Devonshire Building | 2016-08-26 08:00 | 45966.4434 | 699.984
Devonshire Building | 2016-08-26 08:15 | 45966.6234 | 720
Devonshire Building | 2016-08-26 08:30 | 45966.8034 | 720
Devonshire Building | 2016-08-26 08:45 | 45966.9834 | 720
Devonshire Building | 2016-08-26 09:00 | 45967.1584 | 699.984
Devonshire Building | 2016-08-26 09:15 | 45967.3384 | 720
Devonshire Building | 2016-08-26 09:30 | 45967.5184 | 720
Devonshire Building | 2016-08-26 09:45 | 45967.6934 | 699.984
Devonshire Building | 2016-08-26 10:00 | 45968.1234 | 1720.008
Devonshire Building | 2016-08-26 10:15 | 45968.2934 | 680.004
Devonshire Building | 2016-08-26 10:30 | 45968.4684 | 699.984
Devonshire Building | 2016-08-26 10:45 | 45968.6484 | 720
Devonshire Building | 2016-08-26 11:00 | 45968.8334 | 740.016
Devonshire Building | 2016-08-26 11:15 | 45969.0284 | 780.012
Devonshire Building | 2016-08-26 11:30 | 45969.2234 | 780.012
Devonshire Building | 2016-08-26 11:45 | 45969.5884 | 1460.016
Devonshire Building | 2016-08-26 12:00 | 45969.8634 | 1100.016
Devonshire Building | 2016-08-26 12:15 | 45970.0534 | 759.996
Devonshire Building | 2016-08-26 12:30 | 45970.2434 | 759.996
Devonshire Building | 2016-08-26 12:45 | 45970.4334 | 759.996
Devonshire Building | 2016-08-26 13:00 | 45970.6284 | 780.012
Devonshire Building | 2016-08-26 13:15 | 45970.8384 | 839.988
Devonshire Building | 2016-08-26 13:30 | 45971.0484 | 839.988
Devonshire Building | 2016-08-26 13:45 | 45971.2534 | 820.008
Devonshire Building | 2016-08-26 14:00 | 45971.4684 | 860.004
Devonshire Building | 2016-08-26 14:15 | 45971.6784 | 839.988
Devonshire Building | 2016-08-26 14:30 | 45972.1434 | 1860.012
Devonshire Building | 2016-08-26 14:45 | 45972.3734 | 920.016
Devonshire Building | 2016-08-26 15:00 | 45972.5984 | 900
Devonshire Building | 2016-08-26 15:15 | 45972.8134 | 860.004
Devonshire Building | 2016-08-26 15:30 | 45973.0134 | 799.992
Devonshire Building | 2016-08-26 15:45 | 45973.2034 | 759.996
Devonshire Building | 2016-08-26 16:00 | 45973.3934 | 759.996
Devonshire Building | 2016-08-26 16:15 | 45973.5784 | 740.016
Devonshire Building | 2016-08-26 16:30 | 45973.7584 | 720
Devonshire Building | 2016-08-26 16:45 | 45973.9334 | 699.984
Devonshire Building | 2016-08-26 17:00 | 45974.1084 | 699.984
Devonshire Building | 2016-08-26 17:15 | 45974.2784 | 680.004
Devonshire Building | 2016-08-26 17:30 | 45974.4484 | 680.004
Devonshire Building | 2016-08-26 17:45 | 45974.6184 | 680.004
Devonshire Building | 2016-08-26 18:00 | 45974.7834 | 659.988
Devonshire Building | 2016-08-26 18:15 | 45974.9534 | 680.004
Devonshire Building | 2016-08-26 18:30 | 45975.1184 | 659.988
Devonshire Building | 2016-08-26 18:45 | 45975.5134 | 1580.004
Devonshire Building | 2016-08-26 19:00 | 45975.6734 | 640.008
Devonshire Building | 2016-08-26 19:15 | 45975.8334 | 640.008
Devonshire Building | 2016-08-26 19:30 | 45975.9934 | 640.008
Devonshire Building | 2016-08-26 19:45 | 45976.1534 | 640.008
Devonshire Building | 2016-08-26 20:00 | 45976.3134 | 640.008
Devonshire Building | 2016-08-26 20:15 | 45976.4734 | 640.008
Devonshire Building | 2016-08-26 20:30 | 45976.6334 | 640.008
Devonshire Building | 2016-08-26 20:45 | 45976.7984 | 659.988
Devonshire Building | 2016-08-26 21:00 | 45976.9734 | 699.984
Devonshire Building | 2016-08-26 21:15 | 45977.1334 | 640.008
Devonshire Building | 2016-08-26 21:30 | 45977.2934 | 640.008
Devonshire Building | 2016-08-26 21:45 | 45977.4534 | 640.008
Devonshire Building | 2016-08-26 22:00 | 45977.6134 | 640.008
Devonshire Building | 2016-08-26 22:15 | 45977.7784 | 659.988
Devonshire Building | 2016-08-26 22:30 | 45977.9384 | 640.008
Devonshire Building | 2016-08-26 22:45 | 45978.0984 | 640.008
Devonshire Building | 2016-08-26 23:00 | 45978.2634 | 659.988
Devonshire Building | 2016-08-26 23:15 | 45978.4234 | 640.008
Devonshire Building | 2016-08-26 23:30 | 45978.5834 | 640.008
Devonshire Building | 2016-08-26 23:45 | 45978.7484 | 659.988 | 640.008
Devonshire Building | 2016-08-27 | 45978.9102 | 640.008
Devonshire Building | 2016-08-27 00:15 | 45979.0752 | 659.988
Devonshire Building | 2016-08-27 00:30 | 45979.2352 | 640.008
Devonshire Building | 2016-08-27 00:45 | 45979.4002 | 659.988
Devonshire Building | 2016-08-27 01:00 | 45979.5602 | 640.008
Devonshire Building | 2016-08-27 01:15 | 45979.7252 | 659.988
Devonshire Building | 2016-08-27 01:30 | 45979.8852 | 640.008
Devonshire Building | 2016-08-27 01:45 | 45980.0502 | 659.988
Devonshire Building | 2016-08-27 02:00 | 45980.2102 | 640.008
Devonshire Building | 2016-08-27 02:15 | 45980.3752 | 659.988
Devonshire Building | 2016-08-27 02:30 | 45980.5352 | 640.008
Devonshire Building | 2016-08-27 02:45 | 45980.7002 | 659.988
Devonshire Building | 2016-08-27 03:00 | 45980.8602 | 640.008
Devonshire Building | 2016-08-27 03:15 | 45981.0252 | 659.988
Devonshire Building | 2016-08-27 03:30 | 45981.1852 | 640.008
Devonshire Building | 2016-08-27 03:45 | 45981.3452 | 640.008
Devonshire Building | 2016-08-27 04:00 | 45981.5102 | 659.988
Devonshire Building | 2016-08-27 04:15 | 45981.6702 | 640.008
Devonshire Building | 2016-08-27 04:30 | 45981.8352 | 659.988
Devonshire Building | 2016-08-27 04:45 | 45982.0001 | 659.988
Devonshire Building | 2016-08-27 05:00 | 45982.1602 | 640.008
Devonshire Building | 2016-08-27 05:15 | 45982.3251 | 659.988
Devonshire Building | 2016-08-27 05:30 | 45982.4851 | 640.008
Devonshire Building | 2016-08-27 05:45 | 45982.6501 | 659.988
Devonshire Building | 2016-08-27 06:00 | 45982.8101 | 640.008
Devonshire Building | 2016-08-27 06:15 | 45982.9702 | 640.008
Devonshire Building | 2016-08-27 06:30 | 45983.1351 | 659.988
Devonshire Building | 2016-08-27 06:45 | 45983.2951 | 640.008
Devonshire Building | 2016-08-27 07:00 | 45983.4552 | 640.008
Devonshire Building | 2016-08-27 07:15 | 45983.6201 | 659.988
Devonshire Building | 2016-08-27 07:30 | 45983.7801 | 640.008
Devonshire Building | 2016-08-27 07:45 | 45983.9551 | 699.984
Devonshire Building | 2016-08-27 08:00 | 45984.1301 | 699.984
Devonshire Building | 2016-08-27 08:15 | 45984.3051 | 699.984
Devonshire Building | 2016-08-27 08:30 | 45984.4851 | 720
Devonshire Building | 2016-08-27 08:45 | 45984.6601 | 699.984
Devonshire Building | 2016-08-27 09:00 | 45984.8351 | 699.984
Devonshire Building | 2016-08-27 09:15 | 45985.0101 | 699.984
Devonshire Building | 2016-08-27 09:30 | 45985.1851 | 699.984
Devonshire Building | 2016-08-27 09:45 | 45985.3451 | 640.008
Devonshire Building | 2016-08-27 10:00 | 45985.5051 | 640.008
Devonshire Building | 2016-08-27 10:15 | 45985.6651 | 640.008
Devonshire Building | 2016-08-27 10:30 | 45985.8251 | 640.008
Devonshire Building | 2016-08-27 10:45 | 45985.9851 | 640.008
Devonshire Building | 2016-08-27 11:00 | 45986.1451 | 640.008
Devonshire Building | 2016-08-27 11:15 | 45986.3051 | 640.008
Devonshire Building | 2016-08-27 11:30 | 45986.4651 | 640.008
Devonshire Building | 2016-08-27 11:45 | 45986.6251 | 640.008
Devonshire Building | 2016-08-27 12:00 | 45986.7851 | 640.008
Devonshire Building | 2016-08-27 12:15 | 45986.9501 | 659.988
Devonshire Building | 2016-08-27 12:30 | 45987.1101 | 640.008
Devonshire Building | 2016-08-27 12:45 | 45987.2701 | 640.008
Devonshire Building | 2016-08-27 13:00 | 45987.4301 | 640.008
Devonshire Building | 2016-08-27 13:15 | 45987.5901 | 640.008
Devonshire Building | 2016-08-27 13:30 | 45987.7501 | 640.008
Devonshire Building | 2016-08-27 13:45 | 45987.9151 | 659.988
Devonshire Building | 2016-08-27 14:00 | 45988.0751 | 640.008
Devonshire Building | 2016-08-27 14:15 | 45988.2401 | 659.988
Devonshire Building | 2016-08-27 14:30 | 45988.4001 | 640.008
Devonshire Building | 2016-08-27 14:45 | 45988.5601 | 640.008
Devonshire Building | 2016-08-27 15:00 | 45988.7251 | 659.988
Devonshire Building | 2016-08-27 15:15 | 45988.8851 | 640.008
Devonshire Building | 2016-08-27 15:30 | 45989.0501 | 659.988
Devonshire Building | 2016-08-27 15:45 | 45989.2101 | 640.008
Devonshire Building | 2016-08-27 16:00 | 45989.3701 | 640.008
Devonshire Building | 2016-08-27 16:15 | 45989.5302 | 640.008
Devonshire Building | 2016-08-27 16:30 | 45989.6951 | 659.988
Devonshire Building | 2016-08-27 16:45 | 45989.8552 | 640.008
Devonshire Building | 2016-08-27 17:00 | 45990.2602 | 1620
Devonshire Building | 2016-08-27 17:15 | 45990.4251 | 659.988
Devonshire Building | 2016-08-27 17:30 | 45990.5801 | 619.992
Devonshire Building | 2016-08-27 17:45 | 45990.7401 | 640.008
Devonshire Building | 2016-08-27 18:00 | 45990.9051 | 659.988
Devonshire Building | 2016-08-27 18:15 | 45991.0651 | 640.008
Devonshire Building | 2016-08-27 18:30 | 45991.2251 | 640.008
Devonshire Building | 2016-08-27 18:45 | 45991.3852 | 640.008
Devonshire Building | 2016-08-27 19:00 | 45991.5452 | 640.008
Devonshire Building | 2016-08-27 19:15 | 45991.7052 | 640.008
Devonshire Building | 2016-08-27 19:30 | 45991.8652 | 640.008
Devonshire Building | 2016-08-27 19:45 | 45992.0252 | 640.008
Devonshire Building | 2016-08-27 20:00 | 45992.1852 | 640.008
Devonshire Building | 2016-08-27 20:15 | 45992.3452 | 640.008
Devonshire Building | 2016-08-27 20:30 | 45992.5052 | 640.008
Devonshire Building | 2016-08-27 20:45 | 45992.6702 | 659.988
Devonshire Building | 2016-08-27 21:00 | 45992.8352 | 659.988
Devonshire Building | 2016-08-27 21:15 | 45992.9952 | 640.008
Devonshire Building | 2016-08-27 21:30 | 45993.1552 | 640.008
Devonshire Building | 2016-08-27 21:45 | 45993.3202 | 659.988
Devonshire Building | 2016-08-27 22:00 | 45993.4802 | 640.008
Devonshire Building | 2016-08-27 22:15 | 45993.6402 | 640.008
Devonshire Building | 2016-08-27 22:30 | 45993.8002 | 640.008
Devonshire Building | 2016-08-27 22:45 | 45993.9652 | 659.988
Devonshire Building | 2016-08-27 23:00 | 45994.1252 | 640.008
Devonshire Building | 2016-08-27 23:15 | 45994.2902 | 659.988
Devonshire Building | 2016-08-27 23:30 | 45994.4502 | 640.008
Devonshire Building | 2016-08-27 23:45 | 45994.6102 | 640.008 | 619.992
Devonshire Building | 2016-08-28 | 45994.7734 | 659.988
Devonshire Building | 2016-08-28 00:15 | 45994.9334 | 640.008
Devonshire Building | 2016-08-28 00:30 | 45995.0984 | 659.988
Devonshire Building | 2016-08-28 00:45 | 45995.2584 | 640.008
Devonshire Building | 2016-08-28 01:00 | 45995.4234 | 659.988
Devonshire Building | 2016-08-28 01:15 | 45995.5834 | 640.008
Devonshire Building | 2016-08-28 01:30 | 45995.7484 | 659.988
Devonshire Building | 2016-08-28 01:45 | 45995.9084 | 640.008
Devonshire Building | 2016-08-28 02:00 | 45996.0734 | 659.988
Devonshire Building | 2016-08-28 02:15 | 45996.2334 | 640.008
Devonshire Building | 2016-08-28 02:30 | 45996.3984 | 659.988
Devonshire Building | 2016-08-28 02:45 | 45996.5584 | 640.008
Devonshire Building | 2016-08-28 03:00 | 45996.7234 | 659.988
Devonshire Building | 2016-08-28 03:15 | 45996.8884 | 659.988
Devonshire Building | 2016-08-28 03:30 | 45997.0484 | 640.008
Devonshire Building | 2016-08-28 03:45 | 45997.2134 | 659.988
Devonshire Building | 2016-08-28 04:00 | 45997.3734 | 640.008
Devonshire Building | 2016-08-28 04:15 | 45997.5384 | 659.988
Devonshire Building | 2016-08-28 04:30 | 45997.7034 | 659.988
Devonshire Building | 2016-08-28 04:45 | 45997.8634 | 640.008
Devonshire Building | 2016-08-28 05:00 | 45998.0284 | 659.988
Devonshire Building | 2016-08-28 05:15 | 45998.1934 | 659.988
Devonshire Building | 2016-08-28 05:30 | 45998.3534 | 640.008
Devonshire Building | 2016-08-28 05:45 | 45998.5184 | 659.988
Devonshire Building | 2016-08-28 06:00 | 45998.6784 | 640.008
Devonshire Building | 2016-08-28 06:15 | 45998.8434 | 659.988
Devonshire Building | 2016-08-28 06:30 | 45999.0034 | 640.008
Devonshire Building | 2016-08-28 06:45 | 45999.1684 | 659.988
Devonshire Building | 2016-08-28 07:00 | 45999.3284 | 640.008
Devonshire Building | 2016-08-28 07:15 | 45999.4934 | 659.988
Devonshire Building | 2016-08-28 07:30 | 45999.6534 | 640.008
Devonshire Building | 2016-08-28 07:45 | 45999.8284 | 699.984
Devonshire Building | 2016-08-28 08:00 | 46000.0084 | 720
Devonshire Building | 2016-08-28 08:15 | 46000.1884 | 720
Devonshire Building | 2016-08-28 08:30 | 46000.3634 | 699.984
Devonshire Building | 2016-08-28 08:45 | 46000.5434 | 720
Devonshire Building | 2016-08-28 09:00 | 46000.7184 | 699.984
Devonshire Building | 2016-08-28 09:15 | 46000.8984 | 720
Devonshire Building | 2016-08-28 09:30 | 46001.0734 | 699.984
Devonshire Building | 2016-08-28 09:45 | 46001.2334 | 640.008
Devonshire Building | 2016-08-28 10:00 | 46001.3934 | 640.008
Devonshire Building | 2016-08-28 10:15 | 46001.5584 | 659.988
Devonshire Building | 2016-08-28 10:30 | 46001.7184 | 640.008
Devonshire Building | 2016-08-28 10:45 | 46001.8784 | 640.008
Devonshire Building | 2016-08-28 11:00 | 46002.0384 | 640.008
Devonshire Building | 2016-08-28 11:15 | 46002.1984 | 640.008
Devonshire Building | 2016-08-28 11:30 | 46002.3584 | 640.008
Devonshire Building | 2016-08-28 11:45 | 46002.5184 | 640.008
Devonshire Building | 2016-08-28 12:00 | 46002.6834 | 659.988
Devonshire Building | 2016-08-28 12:15 | 46002.8434 | 640.008
Devonshire Building | 2016-08-28 12:30 | 46003.0084 | 659.988
Devonshire Building | 2016-08-28 12:45 | 46003.1684 | 640.008
Devonshire Building | 2016-08-28 13:00 | 46003.3334 | 659.988
Devonshire Building | 2016-08-28 13:15 | 46003.4984 | 659.988
Devonshire Building | 2016-08-28 13:30 | 46003.6584 | 640.008
Devonshire Building | 2016-08-28 13:45 | 46003.8234 | 659.988
Devonshire Building | 2016-08-28 14:00 | 46003.9834 | 640.008
Devonshire Building | 2016-08-28 14:15 | 46004.1484 | 659.988
Devonshire Building | 2016-08-28 14:30 | 46004.3134 | 659.988
Devonshire Building | 2016-08-28 14:45 | 46004.4734 | 640.008
Devonshire Building | 2016-08-28 15:00 | 46004.6334 | 640.008
Devonshire Building | 2016-08-28 15:15 | 46004.7984 | 659.988
Devonshire Building | 2016-08-28 15:30 | 46004.9584 | 640.008
Devonshire Building | 2016-08-28 15:45 | 46005.1184 | 640.008
Devonshire Building | 2016-08-28 16:00 | 46005.2784 | 640.008
Devonshire Building | 2016-08-28 16:15 | 46005.4434 | 659.988
Devonshire Building | 2016-08-28 16:30 | 46005.6034 | 640.008
Devonshire Building | 2016-08-28 16:45 | 46005.7634 | 640.008
Devonshire Building | 2016-08-28 17:00 | 46005.9234 | 640.008
Devonshire Building | 2016-08-28 17:15 | 46006.0834 | 640.008
Devonshire Building | 2016-08-28 17:30 | 46006.2434 | 640.008
Devonshire Building | 2016-08-28 17:45 | 46006.6284 | 1540.008
Devonshire Building | 2016-08-28 18:00 | 46006.7884 | 640.008
Devonshire Building | 2016-08-28 18:15 | 46006.9484 | 640.008
Devonshire Building | 2016-08-28 18:30 | 46007.1134 | 659.988
Devonshire Building | 2016-08-28 18:45 | 46007.2734 | 640.008
Devonshire Building | 2016-08-28 19:00 | 46007.4334 | 640.008
Devonshire Building | 2016-08-28 19:15 | 46007.5934 | 640.008
Devonshire Building | 2016-08-28 19:30 | 46007.7584 | 659.988
Devonshire Building | 2016-08-28 19:45 | 46007.9184 | 640.008
Devonshire Building | 2016-08-28 20:00 | 46008.0784 | 640.008
Devonshire Building | 2016-08-28 20:15 | 46008.2384 | 640.008
Devonshire Building | 2016-08-28 20:30 | 46008.4034 | 659.988
Devonshire Building | 2016-08-28 20:45 | 46008.5634 | 640.008
Devonshire Building | 2016-08-28 21:00 | 46008.7434 | 720
Devonshire Building | 2016-08-28 21:15 | 46008.9034 | 640.008
Devonshire Building | 2016-08-28 21:30 | 46009.0684 | 659.988
Devonshire Building | 2016-08-28 21:45 | 46009.2284 | 640.008
Devonshire Building | 2016-08-28 22:00 | 46009.3884 | 640.008
Devonshire Building | 2016-08-28 22:15 | 46009.5534 | 659.988
Devonshire Building | 2016-08-28 22:30 | 46009.7134 | 640.008
Devonshire Building | 2016-08-28 22:45 | 46009.8784 | 659.988
Devonshire Building | 2016-08-28 23:00 | 46010.0384 | 640.008
Devonshire Building | 2016-08-28 23:15 | 46010.2034 | 659.988
Devonshire Building | 2016-08-28 23:30 | 46010.3634 | 640.008
Devonshire Building | 2016-08-28 23:45 | 46010.5284 | 659.988 | 640.008
Devonshire Building | 2016-08-29 | 46010.6914 | 640.008
Devonshire Building | 2016-08-29 00:15 | 46010.8564 | 659.988
Devonshire Building | 2016-08-29 00:30 | 46011.0214 | 659.988
Devonshire Building | 2016-08-29 00:45 | 46011.1814 | 640.008
Devonshire Building | 2016-08-29 01:00 | 46011.3464 | 659.988
Devonshire Building | 2016-08-29 01:15 | 46011.5064 | 640.008
Devonshire Building | 2016-08-29 01:30 | 46011.6764 | 680.004
Devonshire Building | 2016-08-29 01:45 | 46011.8564 | 720
Devonshire Building | 2016-08-29 02:00 | 46012.0364 | 720
Devonshire Building | 2016-08-29 02:15 | 46012.2164 | 720
Devonshire Building | 2016-08-29 02:30 | 46012.3964 | 720
Devonshire Building | 2016-08-29 02:45 | 46012.5814 | 740.016
Devonshire Building | 2016-08-29 03:00 | 46012.7614 | 720
Devonshire Building | 2016-08-29 03:15 | 46012.9414 | 720
Devonshire Building | 2016-08-29 03:30 | 46013.1064 | 659.988
Devonshire Building | 2016-08-29 03:45 | 46013.2714 | 659.988
Devonshire Building | 2016-08-29 04:00 | 46013.4314 | 640.008
Devonshire Building | 2016-08-29 04:15 | 46013.5964 | 659.988
Devonshire Building | 2016-08-29 04:30 | 46013.7614 | 659.988
Devonshire Building | 2016-08-29 04:45 | 46013.9214 | 640.008
Devonshire Building | 2016-08-29 05:00 | 46014.0864 | 659.988
Devonshire Building | 2016-08-29 05:15 | 46014.2514 | 659.988
Devonshire Building | 2016-08-29 05:30 | 46014.4114 | 640.008
Devonshire Building | 2016-08-29 05:45 | 46014.5764 | 659.988
Devonshire Building | 2016-08-29 06:00 | 46014.7414 | 659.988
Devonshire Building | 2016-08-29 06:15 | 46014.9014 | 640.008
Devonshire Building | 2016-08-29 06:30 | 46015.0664 | 659.988
Devonshire Building | 2016-08-29 06:45 | 46015.2264 | 640.008
Devonshire Building | 2016-08-29 07:00 | 46015.3914 | 659.988
Devonshire Building | 2016-08-29 07:15 | 46015.5514 | 640.008
Devonshire Building | 2016-08-29 07:30 | 46015.7164 | 659.988
Devonshire Building | 2016-08-29 07:45 | 46015.8764 | 640.008
Devonshire Building | 2016-08-29 08:00 | 46016.0364 | 640.008
Devonshire Building | 2016-08-29 08:15 | 46016.1964 | 640.008
Devonshire Building | 2016-08-29 08:30 | 46016.3614 | 659.988
Devonshire Building | 2016-08-29 08:45 | 46016.5214 | 640.008
Devonshire Building | 2016-08-29 09:00 | 46016.6814 | 640.008
Devonshire Building | 2016-08-29 09:15 | 46016.8414 | 640.008
Devonshire Building | 2016-08-29 09:30 | 46017.0014 | 640.008
Devonshire Building | 2016-08-29 09:45 | 46017.1664 | 659.988
Devonshire Building | 2016-08-29 10:00 | 46017.3264 | 640.008
Devonshire Building | 2016-08-29 10:15 | 46017.4864 | 640.008
Devonshire Building | 2016-08-29 10:30 | 46017.6464 | 640.008
Devonshire Building | 2016-08-29 10:45 | 46017.8064 | 640.008
Devonshire Building | 2016-08-29 11:00 | 46017.9714 | 659.988
Devonshire Building | 2016-08-29 11:15 | 46018.1464 | 699.984
Devonshire Building | 2016-08-29 11:30 | 46018.3214 | 699.984
Devonshire Building | 2016-08-29 11:45 | 46018.5014 | 720
Devonshire Building | 2016-08-29 12:00 | 46018.6814 | 720
Devonshire Building | 2016-08-29 12:15 | 46018.8664 | 740.016
Devonshire Building | 2016-08-29 12:30 | 46019.0464 | 720
Devonshire Building | 2016-08-29 12:45 | 46019.2264 | 720
Devonshire Building | 2016-08-29 13:00 | 46019.4064 | 720
Devonshire Building | 2016-08-29 13:15 | 46019.5814 | 699.984
Devonshire Building | 2016-08-29 13:30 | 46019.7464 | 659.988
Devonshire Building | 2016-08-29 13:45 | 46019.9114 | 659.988
Devonshire Building | 2016-08-29 14:00 | 46020.0764 | 659.988
Devonshire Building | 2016-08-29 14:15 | 46020.2364 | 640.008
Devonshire Building | 2016-08-29 14:30 | 46020.4014 | 659.988
Devonshire Building | 2016-08-29 14:45 | 46020.5664 | 659.988
Devonshire Building | 2016-08-29 15:00 | 46020.7314 | 659.988
Devonshire Building | 2016-08-29 15:15 | 46020.8914 | 640.008
Devonshire Building | 2016-08-29 15:30 | 46021.0564 | 659.988
Devonshire Building | 2016-08-29 15:45 | 46021.2164 | 640.008
Devonshire Building | 2016-08-29 16:00 | 46021.3814 | 659.988
Devonshire Building | 2016-08-29 16:15 | 46021.5414 | 640.008
Devonshire Building | 2016-08-29 16:30 | 46021.7064 | 659.988
Devonshire Building | 2016-08-29 16:45 | 46021.8664 | 640.008
Devonshire Building | 2016-08-29 17:00 | 46022.0314 | 659.988
Devonshire Building | 2016-08-29 17:15 | 46022.1914 | 640.008
Devonshire Building | 2016-08-29 17:30 | 46022.3514 | 640.008
Devonshire Building | 2016-08-29 17:45 | 46022.7414 | 1559.988
Devonshire Building | 2016-08-29 18:00 | 46022.9014 | 640.008
Devonshire Building | 2016-08-29 18:15 | 46023.0614 | 640.008
Devonshire Building | 2016-08-29 18:30 | 46023.2264 | 659.988
Devonshire Building | 2016-08-29 18:45 | 46023.3864 | 640.008
Devonshire Building | 2016-08-29 19:00 | 46023.5464 | 640.008
Devonshire Building | 2016-08-29 19:15 | 46023.7064 | 640.008
Devonshire Building | 2016-08-29 19:30 | 46023.8714 | 659.988
Devonshire Building | 2016-08-29 19:45 | 46024.0314 | 640.008
Devonshire Building | 2016-08-29 20:00 | 46024.1964 | 659.988
Devonshire Building | 2016-08-29 20:15 | 46024.3564 | 640.008
Devonshire Building | 2016-08-29 20:30 | 46024.5214 | 659.988
Devonshire Building | 2016-08-29 20:45 | 46024.6814 | 640.008
Devonshire Building | 2016-08-29 21:00 | 46024.8614 | 720
Devonshire Building | 2016-08-29 21:15 | 46025.0214 | 640.008
Devonshire Building | 2016-08-29 21:30 | 46025.1864 | 659.988
Devonshire Building | 2016-08-29 21:45 | 46025.3514 | 659.988
Devonshire Building | 2016-08-29 22:00 | 46025.5114 | 640.008
Devonshire Building | 2016-08-29 22:15 | 46025.6764 | 659.988
Devonshire Building | 2016-08-29 22:30 | 46025.8414 | 659.988
Devonshire Building | 2016-08-29 22:45 | 46026.0014 | 640.008
Devonshire Building | 2016-08-29 23:00 | 46026.1664 | 659.988
Devonshire Building | 2016-08-29 23:15 | 46026.3314 | 659.988
Devonshire Building | 2016-08-29 23:30 | 46026.4914 | 640.008
Devonshire Building | 2016-08-29 23:45 | 46026.6564 | 659.988 | 640.008
Devonshire Building | 2016-08-30 | 46026.8203 | 659.988
Devonshire Building | 2016-08-30 00:15 | 46026.9853 | 659.988
Devonshire Building | 2016-08-30 00:30 | 46027.1453 | 640.008
Devonshire Building | 2016-08-30 00:45 | 46027.3103 | 659.988
Devonshire Building | 2016-08-30 01:00 | 46027.4753 | 659.988
Devonshire Building | 2016-08-30 01:15 | 46027.6403 | 659.988
Devonshire Building | 2016-08-30 01:30 | 46027.8053 | 659.988
Devonshire Building | 2016-08-30 01:45 | 46027.9703 | 659.988
Devonshire Building | 2016-08-30 02:00 | 46028.1353 | 659.988
Devonshire Building | 2016-08-30 02:15 | 46028.3003 | 659.988
Devonshire Building | 2016-08-30 02:30 | 46028.4603 | 640.008
Devonshire Building | 2016-08-30 02:45 | 46028.6253 | 659.988
Devonshire Building | 2016-08-30 03:00 | 46028.7903 | 659.988
Devonshire Building | 2016-08-30 03:15 | 46028.9553 | 659.988
Devonshire Building | 2016-08-30 03:30 | 46029.1203 | 659.988
Devonshire Building | 2016-08-30 03:45 | 46029.2853 | 659.988
Devonshire Building | 2016-08-30 04:00 | 46029.4503 | 659.988
Devonshire Building | 2016-08-30 04:15 | 46029.6153 | 659.988
Devonshire Building | 2016-08-30 04:30 | 46029.7803 | 659.988
Devonshire Building | 2016-08-30 04:45 | 46029.9453 | 659.988
Devonshire Building | 2016-08-30 05:00 | 46030.1103 | 659.988
Devonshire Building | 2016-08-30 05:15 | 46030.2703 | 640.008
Devonshire Building | 2016-08-30 05:30 | 46030.4353 | 659.988
Devonshire Building | 2016-08-30 05:45 | 46030.6003 | 659.988
Devonshire Building | 2016-08-30 06:00 | 46030.7653 | 659.988
Devonshire Building | 2016-08-30 06:15 | 46030.9353 | 680.004
Devonshire Building | 2016-08-30 06:30 | 46031.1003 | 659.988
Devonshire Building | 2016-08-30 06:45 | 46031.2652 | 659.988
Devonshire Building | 2016-08-30 07:00 | 46031.4302 | 659.988
Devonshire Building | 2016-08-30 07:15 | 46031.6052 | 699.984
Devonshire Building | 2016-08-30 07:30 | 46031.7702 | 659.988
Devonshire Building | 2016-08-30 07:45 | 46031.9552 | 740.016
Devonshire Building | 2016-08-30 08:00 | 46032.1352 | 720
Devonshire Building | 2016-08-30 08:15 | 46032.3202 | 740.016
Devonshire Building | 2016-08-30 08:30 | 46032.5002 | 720
Devonshire Building | 2016-08-30 08:45 | 46032.6853 | 740.016
Devonshire Building | 2016-08-30 09:00 | 46033.1153 | 1720.008
Devonshire Building | 2016-08-30 09:15 | 46033.2953 | 720
Devonshire Building | 2016-08-30 09:30 | 46033.5103 | 860.004
Devonshire Building | 2016-08-30 09:45 | 46033.7453 | 939.996
Devonshire Building | 2016-08-30 10:00 | 46033.9753 | 920.016
Devonshire Building | 2016-08-30 10:15 | 46034.2153 | 960.012
Devonshire Building | 2016-08-30 10:30 | 46034.6803 | 1860.012
Devonshire Building | 2016-08-30 10:45 | 46034.9003 | 879.984
Devonshire Building | 2016-08-30 11:00 | 46035.1153 | 860.004
Devonshire Building | 2016-08-30 11:15 | 46035.3203 | 820.008
Devonshire Building | 2016-08-30 11:30 | 46035.5203 | 799.992
Devonshire Building | 2016-08-30 11:45 | 46035.7103 | 759.996
Devonshire Building | 2016-08-30 12:00 | 46035.8953 | 740.016
Devonshire Building | 2016-08-30 12:15 | 46036.0753 | 720
Devonshire Building | 2016-08-30 12:30 | 46036.2553 | 720
Devonshire Building | 2016-08-30 12:45 | 46036.6903 | 1739.988
Devonshire Building | 2016-08-30 13:00 | 46036.8753 | 740.016
Devonshire Building | 2016-08-30 13:15 | 46037.0653 | 759.996
Devonshire Building | 2016-08-30 13:30 | 46037.2603 | 780.012
Devonshire Building | 2016-08-30 13:45 | 46037.4553 | 780.012
Devonshire Building | 2016-08-30 14:00 | 46037.6453 | 759.996
Devonshire Building | 2016-08-30 14:15 | 46037.8403 | 780.012
Devonshire Building | 2016-08-30 14:30 | 46038.0353 | 780.012
Devonshire Building | 2016-08-30 14:45 | 46038.2703 | 939.996
Devonshire Building | 2016-08-30 15:00 | 46038.4653 | 780.012
Devonshire Building | 2016-08-30 15:15 | 46038.6553 | 759.996
Devonshire Building | 2016-08-30 15:30 | 46038.8453 | 759.996
Devonshire Building | 2016-08-30 15:45 | 46039.3053 | 1839.996
Devonshire Building | 2016-08-30 16:00 | 46039.4953 | 759.996
Devonshire Building | 2016-08-30 16:15 | 46039.6853 | 759.996
Devonshire Building | 2016-08-30 16:30 | 46039.8753 | 759.996
Devonshire Building | 2016-08-30 16:45 | 46040.0603 | 740.016
Devonshire Building | 2016-08-30 17:00 | 46040.2453 | 740.016
Devonshire Building | 2016-08-30 17:15 | 46040.4303 | 740.016
Devonshire Building | 2016-08-30 17:30 | 46040.6103 | 720
Devonshire Building | 2016-08-30 17:45 | 46040.7853 | 699.984
Devonshire Building | 2016-08-30 18:00 | 46040.9603 | 699.984
Devonshire Building | 2016-08-30 18:15 | 46041.1303 | 680.004
Devonshire Building | 2016-08-30 18:30 | 46041.3053 | 699.984
Devonshire Building | 2016-08-30 18:45 | 46041.4753 | 680.004
Devonshire Building | 2016-08-30 19:00 | 46041.6453 | 680.004
Devonshire Building | 2016-08-30 19:15 | 46041.8103 | 659.988
Devonshire Building | 2016-08-30 19:30 | 46041.9803 | 680.004
Devonshire Building | 2016-08-30 19:45 | 46042.1503 | 680.004
Devonshire Building | 2016-08-30 20:00 | 46042.3153 | 659.988
Devonshire Building | 2016-08-30 20:15 | 46042.4803 | 659.988
Devonshire Building | 2016-08-30 20:30 | 46042.6503 | 680.004
Devonshire Building | 2016-08-30 20:45 | 46042.8153 | 659.988
Devonshire Building | 2016-08-30 21:00 | 46043.0053 | 759.996
Devonshire Building | 2016-08-30 21:15 | 46043.1653 | 640.008
Devonshire Building | 2016-08-30 21:30 | 46043.3303 | 659.988
Devonshire Building | 2016-08-30 21:45 | 46043.4953 | 659.988
Devonshire Building | 2016-08-30 22:00 | 46043.6603 | 659.988
Devonshire Building | 2016-08-30 22:15 | 46043.8203 | 640.008
Devonshire Building | 2016-08-30 22:30 | 46043.9853 | 659.988
Devonshire Building | 2016-08-30 22:45 | 46044.1503 | 659.988
Devonshire Building | 2016-08-30 23:00 | 46044.3152 | 659.988
Devonshire Building | 2016-08-30 23:15 | 46044.4802 | 659.988
Devonshire Building | 2016-08-30 23:30 | 46044.6452 | 659.988
Devonshire Building | 2016-08-30 23:45 | 46044.8052 | 640.008 | 640.008
Devonshire Building | 2016-08-31 | 46044.9688 | 659.988
Devonshire Building | 2016-08-31 00:15 | 46045.1337 | 659.988
Devonshire Building | 2016-08-31 00:30 | 46045.2987 | 659.988
Devonshire Building | 2016-08-31 00:45 | 46045.4637 | 659.988
Devonshire Building | 2016-08-31 01:00 | 46045.6287 | 659.988
Devonshire Building | 2016-08-31 01:15 | 46045.7937 | 659.988
Devonshire Building | 2016-08-31 01:30 | 46045.9537 | 640.008
Devonshire Building | 2016-08-31 01:45 | 46046.1187 | 659.988
Devonshire Building | 2016-08-31 02:00 | 46046.2837 | 659.988
Devonshire Building | 2016-08-31 02:15 | 46046.4487 | 659.988
Devonshire Building | 2016-08-31 02:30 | 46046.6137 | 659.988
Devonshire Building | 2016-08-31 02:45 | 46046.7787 | 659.988
Devonshire Building | 2016-08-31 03:00 | 46046.9387 | 640.008
Devonshire Building | 2016-08-31 03:15 | 46047.1037 | 659.988
Devonshire Building | 2016-08-31 03:30 | 46047.2687 | 659.988
Devonshire Building | 2016-08-31 03:45 | 46047.4337 | 659.988
Devonshire Building | 2016-08-31 04:00 | 46047.5987 | 659.988
Devonshire Building | 2016-08-31 04:15 | 46047.7637 | 659.988
Devonshire Building | 2016-08-31 04:30 | 46047.9287 | 659.988
Devonshire Building | 2016-08-31 04:45 | 46048.0937 | 659.988
Devonshire Building | 2016-08-31 05:00 | 46048.2587 | 659.988
Devonshire Building | 2016-08-31 05:15 | 46048.4237 | 659.988
Devonshire Building | 2016-08-31 05:30 | 46048.5887 | 659.988
Devonshire Building | 2016-08-31 05:45 | 46048.7487 | 640.008
Devonshire Building | 2016-08-31 06:00 | 46048.9137 | 659.988
Devonshire Building | 2016-08-31 06:15 | 46049.0787 | 659.988
Devonshire Building | 2016-08-31 06:30 | 46049.2437 | 659.988
Devonshire Building | 2016-08-31 06:45 | 46049.6487 | 1620
Devonshire Building | 2016-08-31 07:00 | 46049.8187 | 680.004
Devonshire Building | 2016-08-31 07:15 | 46049.9837 | 659.988
Devonshire Building | 2016-08-31 07:30 | 46050.1437 | 640.008
Devonshire Building | 2016-08-31 07:45 | 46050.3237 | 720
Devonshire Building | 2016-08-31 08:00 | 46050.5087 | 740.016
Devonshire Building | 2016-08-31 08:15 | 46050.6887 | 720
Devonshire Building | 2016-08-31 08:30 | 46050.8687 | 720
Devonshire Building | 2016-08-31 08:45 | 46051.0437 | 699.984
Devonshire Building | 2016-08-31 09:00 | 46051.2237 | 720
Devonshire Building | 2016-08-31 09:15 | 46051.4087 | 740.016
Devonshire Building | 2016-08-31 09:30 | 46051.5887 | 720
Devonshire Building | 2016-08-31 09:45 | 46051.9137 | 1299.996
Devonshire Building | 2016-08-31 10:00 | 46052.1787 | 1059.984
Devonshire Building | 2016-08-31 10:15 | 46052.3487 | 680.004
Devonshire Building | 2016-08-31 10:30 | 46052.5937 | 979.992
Devonshire Building | 2016-08-31 10:45 | 46052.8787 | 1140.012
Devonshire Building | 2016-08-31 11:00 | 46053.1687 | 1159.992
Devonshire Building | 2016-08-31 11:15 | 46053.4337 | 1059.984
Devonshire Building | 2016-08-31 11:30 | 46053.6837 | 1000.008
Devonshire Building | 2016-08-31 11:45 | 46053.9387 | 1019.988
Devonshire Building | 2016-08-31 12:00 | 46054.1937 | 1019.988
Devonshire Building | 2016-08-31 12:15 | 46054.4287 | 939.996
Devonshire Building | 2016-08-31 12:30 | 46054.8737 | 1779.984
Devonshire Building | 2016-08-31 12:45 | 46055.0687 | 780.012
Devonshire Building | 2016-08-31 13:00 | 46055.2587 | 759.996
Devonshire Building | 2016-08-31 13:15 | 46055.4487 | 759.996
Devonshire Building | 2016-08-31 13:30 | 46055.6337 | 740.016
Devonshire Building | 2016-08-31 13:45 | 46055.8387 | 820.008
Devonshire Building | 2016-08-31 14:00 | 46056.0187 | 720
Devonshire Building | 2016-08-31 14:15 | 46056.1937 | 699.984
Devonshire Building | 2016-08-31 14:30 | 46056.3737 | 720
Devonshire Building | 2016-08-31 14:45 | 46056.5437 | 680.004
Devonshire Building | 2016-08-31 15:00 | 46056.7237 | 720
Devonshire Building | 2016-08-31 15:15 | 46057.1387 | 1659.996
Devonshire Building | 2016-08-31 15:30 | 46057.3137 | 699.984
Devonshire Building | 2016-08-31 15:45 | 46057.4887 | 699.984
Devonshire Building | 2016-08-31 16:00 | 46057.6637 | 699.984
Devonshire Building | 2016-08-31 16:15 | 46057.8387 | 699.984
Devonshire Building | 2016-08-31 16:30 | 46058.0087 | 680.004
Devonshire Building | 2016-08-31 16:45 | 46058.1837 | 699.984
Devonshire Building | 2016-08-31 17:00 | 46058.3587 | 699.984
Devonshire Building | 2016-08-31 17:15 | 46058.5287 | 680.004
Devonshire Building | 2016-08-31 17:30 | 46058.7037 | 699.984
Devonshire Building | 2016-08-31 17:45 | 46058.8737 | 680.004
Devonshire Building | 2016-08-31 18:00 | 46059.0437 | 680.004
Devonshire Building | 2016-08-31 18:15 | 46059.2186 | 699.984
Devonshire Building | 2016-08-31 18:30 | 46059.3886 | 680.004
Devonshire Building | 2016-08-31 18:45 | 46059.5586 | 680.004
Devonshire Building | 2016-08-31 19:00 | 46059.7287 | 680.004
Devonshire Building | 2016-08-31 19:15 | 46059.8987 | 680.004
Devonshire Building | 2016-08-31 19:30 | 46060.0687 | 680.004
Devonshire Building | 2016-08-31 19:45 | 46060.2387 | 680.004
Devonshire Building | 2016-08-31 20:00 | 46060.4087 | 680.004
Devonshire Building | 2016-08-31 20:15 | 46060.5787 | 680.004
Devonshire Building | 2016-08-31 20:30 | 46060.7437 | 659.988
Devonshire Building | 2016-08-31 20:45 | 46060.9137 | 680.004
Devonshire Building | 2016-08-31 21:00 | 46061.1037 | 759.996
Devonshire Building | 2016-08-31 21:15 | 46061.2637 | 640.008
Devonshire Building | 2016-08-31 21:30 | 46061.4237 | 640.008
Devonshire Building | 2016-08-31 21:45 | 46061.5887 | 659.988
Devonshire Building | 2016-08-31 22:00 | 46061.7487 | 640.008
Devonshire Building | 2016-08-31 22:15 | 46061.9137 | 659.988
Devonshire Building | 2016-08-31 22:30 | 46062.0737 | 640.008
Devonshire Building | 2016-08-31 22:45 | 46062.2387 | 659.988
Devonshire Building | 2016-08-31 23:00 | 46062.4036 | 659.988
Devonshire Building | 2016-08-31 23:15 | 46062.5637 | 640.008
Devonshire Building | 2016-08-31 23:30 | 46062.7286 | 659.988
Devonshire Building | 2016-08-31 23:45 | 46062.8936 | 659.988 | 640.008
Devonshire Building | 2016-09-01 | 46063.0586 | 659.988
Devonshire Building | 2016-09-01 00:15 | 46063.2186 | 640.008
Devonshire Building | 2016-09-01 00:30 | 46063.3836 | 659.988
Devonshire Building | 2016-09-01 00:45 | 46063.5486 | 659.988
Devonshire Building | 2016-09-01 01:00 | 46063.7136 | 659.988
Devonshire Building | 2016-09-01 01:15 | 46063.8786 | 659.988
Devonshire Building | 2016-09-01 01:30 | 46064.0386 | 640.008
Devonshire Building | 2016-09-01 01:45 | 46064.2036 | 659.988
Devonshire Building | 2016-09-01 02:00 | 46064.3686 | 659.988
Devonshire Building | 2016-09-01 02:15 | 46064.5336 | 659.988
Devonshire Building | 2016-09-01 02:30 | 46064.6986 | 659.988
Devonshire Building | 2016-09-01 02:45 | 46064.8636 | 659.988
Devonshire Building | 2016-09-01 03:00 | 46065.0236 | 640.008
Devonshire Building | 2016-09-01 03:15 | 46065.1886 | 659.988
Devonshire Building | 2016-09-01 03:30 | 46065.3536 | 659.988
Devonshire Building | 2016-09-01 03:45 | 46065.5186 | 659.988
Devonshire Building | 2016-09-01 04:00 | 46065.6786 | 640.008
Devonshire Building | 2016-09-01 04:15 | 46065.8436 | 659.988
Devonshire Building | 2016-09-01 04:30 | 46066.0086 | 659.988
Devonshire Building | 2016-09-01 04:45 | 46066.1686 | 640.008
Devonshire Building | 2016-09-01 05:00 | 46066.3336 | 659.988
Devonshire Building | 2016-09-01 05:15 | 46066.4986 | 659.988
Devonshire Building | 2016-09-01 05:30 | 46066.6586 | 640.008
Devonshire Building | 2016-09-01 05:45 | 46066.8236 | 659.988
Devonshire Building | 2016-09-01 06:00 | 46066.9836 | 640.008
Devonshire Building | 2016-09-01 06:15 | 46067.2386 | 1019.988
Devonshire Building | 2016-09-01 06:30 | 46067.5436 | 1220.004
Devonshire Building | 2016-09-01 06:45 | 46067.7185 | 699.984
Devonshire Building | 2016-09-01 07:00 | 46067.8935 | 699.984
Devonshire Building | 2016-09-01 07:15 | 46068.0535 | 640.008
Devonshire Building | 2016-09-01 07:30 | 46068.2135 | 640.008
Devonshire Building | 2016-09-01 07:45 | 46068.3935 | 720
Devonshire Building | 2016-09-01 08:00 | 46068.5735 | 720
Devonshire Building | 2016-09-01 08:15 | 46068.7535 | 720
Devonshire Building | 2016-09-01 08:30 | 46068.9386 | 740.016
Devonshire Building | 2016-09-01 08:45 | 46069.1186 | 720
Devonshire Building | 2016-09-01 09:00 | 46069.3036 | 740.016
Devonshire Building | 2016-09-01 09:15 | 46069.4986 | 780.012
Devonshire Building | 2016-09-01 09:30 | 46069.9436 | 1779.984
Devonshire Building | 2016-09-01 09:45 | 46070.1686 | 900
Devonshire Building | 2016-09-01 10:00 | 46070.4336 | 1059.984
Devonshire Building | 2016-09-01 10:15 | 46070.6836 | 1000.008
Devonshire Building | 2016-09-01 10:30 | 46070.9285 | 979.992
Devonshire Building | 2016-09-01 10:45 | 46071.1536 | 900
Devonshire Building | 2016-09-01 11:00 | 46071.6286 | 1900.008
Devonshire Building | 2016-09-01 11:15 | 46071.8086 | 720
Devonshire Building | 2016-09-01 11:30 | 46071.9936 | 740.016
Devonshire Building | 2016-09-01 11:45 | 46072.1786 | 740.016
Devonshire Building | 2016-09-01 12:00 | 46072.3636 | 740.016
Devonshire Building | 2016-09-01 12:15 | 46072.5436 | 720
Devonshire Building | 2016-09-01 12:30 | 46072.7586 | 860.004
Devonshire Building | 2016-09-01 12:45 | 46073.0136 | 1019.988
Devonshire Building | 2016-09-01 13:00 | 46073.2886 | 1100.016
Devonshire Building | 2016-09-01 13:15 | 46073.8236 | 2139.984
Devonshire Building | 2016-09-01 13:30 | 46074.0786 | 1019.988
Devonshire Building | 2016-09-01 13:45 | 46074.3086 | 920.016
Devonshire Building | 2016-09-01 14:00 | 46074.5186 | 839.988
Devonshire Building | 2016-09-01 14:15 | 46074.7186 | 799.992
Devonshire Building | 2016-09-01 14:30 | 46074.9186 | 799.992
Devonshire Building | 2016-09-01 14:45 | 46075.1136 | 780.012
Devonshire Building | 2016-09-01 15:00 | 46075.3086 | 780.012
Devonshire Building | 2016-09-01 15:15 | 46075.4986 | 759.996
Devonshire Building | 2016-09-01 15:30 | 46075.7036 | 820.008
Devonshire Building | 2016-09-01 15:45 | 46075.9586 | 1019.988
Devonshire Building | 2016-09-01 16:00 | 46076.4736 | 2059.992
Devonshire Building | 2016-09-01 16:15 | 46076.7386 | 1059.984
Devonshire Building | 2016-09-01 16:30 | 46076.9736 | 939.996
Devonshire Building | 2016-09-01 16:45 | 46077.1886 | 860.004
Devonshire Building | 2016-09-01 17:00 | 46077.3886 | 799.992
Devonshire Building | 2016-09-01 17:15 | 46077.5836 | 780.012
Devonshire Building | 2016-09-01 17:30 | 46077.7636 | 720
Devonshire Building | 2016-09-01 17:45 | 46077.9436 | 720
Devonshire Building | 2016-09-01 18:00 | 46078.1186 | 699.984
Devonshire Building | 2016-09-01 18:15 | 46078.2935 | 699.984
Devonshire Building | 2016-09-01 18:30 | 46078.4635 | 680.004
Devonshire Building | 2016-09-01 18:45 | 46078.6335 | 680.004
Devonshire Building | 2016-09-01 19:00 | 46078.8035 | 680.004
Devonshire Building | 2016-09-01 19:15 | 46078.9685 | 659.988
Devonshire Building | 2016-09-01 19:30 | 46079.1385 | 680.004
Devonshire Building | 2016-09-01 19:45 | 46079.3035 | 659.988
Devonshire Building | 2016-09-01 20:00 | 46079.4785 | 699.984
Devonshire Building | 2016-09-01 20:15 | 46079.6435 | 659.988
Devonshire Building | 2016-09-01 20:30 | 46079.8085 | 659.988
Devonshire Building | 2016-09-01 20:45 | 46079.9735 | 659.988
Devonshire Building | 2016-09-01 21:00 | 46080.1485 | 699.984
Devonshire Building | 2016-09-01 21:15 | 46080.3085 | 640.008
Devonshire Building | 2016-09-01 21:30 | 46080.4685 | 640.008
Devonshire Building | 2016-09-01 21:45 | 46080.6335 | 659.988
Devonshire Building | 2016-09-01 22:00 | 46080.7935 | 640.008
Devonshire Building | 2016-09-01 22:15 | 46080.9535 | 640.008
Devonshire Building | 2016-09-01 22:30 | 46081.1185 | 659.988
Devonshire Building | 2016-09-01 22:45 | 46081.2785 | 640.008
Devonshire Building | 2016-09-01 23:00 | 46081.4435 | 659.988
Devonshire Building | 2016-09-01 23:15 | 46081.6035 | 640.008
Devonshire Building | 2016-09-01 23:30 | 46081.7685 | 659.988
Devonshire Building | 2016-09-01 23:45 | 46081.9285 | 640.008 | 640.008
Devonshire Building | 2016-09-02 | 46082.0938 | 659.988
Devonshire Building | 2016-09-02 00:15 | 46082.2538 | 640.008
Devonshire Building | 2016-09-02 00:30 | 46082.4187 | 659.988
Devonshire Building | 2016-09-02 00:45 | 46082.5788 | 640.008
Devonshire Building | 2016-09-02 01:00 | 46082.7437 | 659.988
Devonshire Building | 2016-09-02 01:15 | 46082.9087 | 659.988
Devonshire Building | 2016-09-02 01:30 | 46083.0687 | 640.008
Devonshire Building | 2016-09-02 01:45 | 46083.2337 | 659.988
Devonshire Building | 2016-09-02 02:00 | 46083.3987 | 659.988
Devonshire Building | 2016-09-02 02:15 | 46083.5587 | 640.008
Devonshire Building | 2016-09-02 02:30 | 46083.7237 | 659.988
Devonshire Building | 2016-09-02 02:45 | 46083.8887 | 659.988
Devonshire Building | 2016-09-02 03:00 | 46084.0487 | 640.008
Devonshire Building | 2016-09-02 03:15 | 46084.2137 | 659.988
Devonshire Building | 2016-09-02 03:30 | 46084.3737 | 640.008
Devonshire Building | 2016-09-02 03:45 | 46084.5387 | 659.988
Devonshire Building | 2016-09-02 04:00 | 46084.6987 | 640.008
Devonshire Building | 2016-09-02 04:15 | 46084.8637 | 659.988
Devonshire Building | 2016-09-02 04:30 | 46085.0237 | 640.008
Devonshire Building | 2016-09-02 04:45 | 46085.1887 | 659.988
Devonshire Building | 2016-09-02 05:00 | 46085.3487 | 640.008
Devonshire Building | 2016-09-02 05:15 | 46085.5137 | 659.988
Devonshire Building | 2016-09-02 05:30 | 46085.6737 | 640.008
Devonshire Building | 2016-09-02 05:45 | 46085.8387 | 659.988
Devonshire Building | 2016-09-02 06:00 | 46085.9987 | 640.008
Devonshire Building | 2016-09-02 06:15 | 46086.1587 | 640.008
Devonshire Building | 2016-09-02 06:30 | 46086.3237 | 659.988
Devonshire Building | 2016-09-02 06:45 | 46086.4837 | 640.008
Devonshire Building | 2016-09-02 07:00 | 46086.6837 | 799.992
Devonshire Building | 2016-09-02 07:15 | 46087.0787 | 1580.004
Devonshire Building | 2016-09-02 07:30 | 46087.2437 | 659.988
Devonshire Building | 2016-09-02 07:45 | 46087.4237 | 720
Devonshire Building | 2016-09-02 08:00 | 46087.6037 | 720
Devonshire Building | 2016-09-02 08:15 | 46087.7837 | 720
Devonshire Building | 2016-09-02 08:30 | 46087.9637 | 720
Devonshire Building | 2016-09-02 08:45 | 46088.1437 | 720
Devonshire Building | 2016-09-02 09:00 | 46088.3237 | 720
Devonshire Building | 2016-09-02 09:15 | 46088.5137 | 759.996
Devonshire Building | 2016-09-02 09:30 | 46088.7187 | 820.008
Devonshire Building | 2016-09-02 09:45 | 46089.1987 | 1919.988
Devonshire Building | 2016-09-02 10:00 | 46089.4837 | 1140.012
Devonshire Building | 2016-09-02 10:15 | 46089.7587 | 1100.016
Devonshire Building | 2016-09-02 10:30 | 46090.0037 | 979.992
Devonshire Building | 2016-09-02 10:45 | 46090.2287 | 900
Devonshire Building | 2016-09-02 11:00 | 46090.4437 | 860.004
Devonshire Building | 2016-09-02 11:15 | 46090.6537 | 839.988
Devonshire Building | 2016-09-02 11:30 | 46090.8537 | 799.992
Devonshire Building | 2016-09-02 11:45 | 46091.2687 | 1659.996
Devonshire Building | 2016-09-02 12:00 | 46091.4337 | 659.988
Devonshire Building | 2016-09-02 12:15 | 46091.6037 | 680.004
Devonshire Building | 2016-09-02 12:30 | 46091.7687 | 659.988
Devonshire Building | 2016-09-02 12:45 | 46091.9437 | 699.984
Devonshire Building | 2016-09-02 13:00 | 46092.1087 | 659.988
Devonshire Building | 2016-09-02 13:15 | 46092.2737 | 659.988
Devonshire Building | 2016-09-02 13:30 | 46092.4487 | 699.984
Devonshire Building | 2016-09-02 13:45 | 46092.6137 | 659.988
Devonshire Building | 2016-09-02 14:00 | 46092.7887 | 699.984
Devonshire Building | 2016-09-02 14:15 | 46092.9537 | 659.988
Devonshire Building | 2016-09-02 14:30 | 46093.1237 | 680.004
Devonshire Building | 2016-09-02 14:45 | 46093.5387 | 1659.996
Devonshire Building | 2016-09-02 15:00 | 46093.7087 | 680.004
Devonshire Building | 2016-09-02 15:15 | 46093.8787 | 680.004
Devonshire Building | 2016-09-02 15:30 | 46094.0487 | 680.004
Devonshire Building | 2016-09-02 15:45 | 46094.2237 | 699.984
Devonshire Building | 2016-09-02 16:00 | 46094.3987 | 699.984
Devonshire Building | 2016-09-02 16:15 | 46094.5687 | 680.004
Devonshire Building | 2016-09-02 16:30 | 46094.7387 | 680.004
Devonshire Building | 2016-09-02 16:45 | 46094.9087 | 680.004
Devonshire Building | 2016-09-02 17:00 | 46095.0787 | 680.004
Devonshire Building | 2016-09-02 17:15 | 46095.2487 | 680.004
Devonshire Building | 2016-09-02 17:30 | 46095.4137 | 659.988
Devonshire Building | 2016-09-02 17:45 | 46095.5837 | 680.004
Devonshire Building | 2016-09-02 18:00 | 46095.7537 | 680.004
Devonshire Building | 2016-09-02 18:15 | 46095.9237 | 680.004
Devonshire Building | 2016-09-02 18:30 | 46096.0887 | 659.988
Devonshire Building | 2016-09-02 18:45 | 46096.2587 | 680.004
Devonshire Building | 2016-09-02 19:00 | 46096.4237 | 659.988
Devonshire Building | 2016-09-02 19:15 | 46096.5937 | 680.004
Devonshire Building | 2016-09-02 19:30 | 46096.7587 | 659.988
Devonshire Building | 2016-09-02 19:45 | 46096.9237 | 659.988
Devonshire Building | 2016-09-02 20:00 | 46097.0937 | 680.004
Devonshire Building | 2016-09-02 20:15 | 46097.2587 | 659.988
Devonshire Building | 2016-09-02 20:30 | 46097.4287 | 680.004
Devonshire Building | 2016-09-02 20:45 | 46097.5937 | 659.988
Devonshire Building | 2016-09-02 21:00 | 46097.7837 | 759.996
Devonshire Building | 2016-09-02 21:15 | 46097.9487 | 659.988
Devonshire Building | 2016-09-02 21:30 | 46098.1137 | 659.988
Devonshire Building | 2016-09-02 21:45 | 46098.2787 | 659.988
Devonshire Building | 2016-09-02 22:00 | 46098.4437 | 659.988
Devonshire Building | 2016-09-02 22:15 | 46098.6087 | 659.988
Devonshire Building | 2016-09-02 22:30 | 46098.7737 | 659.988
Devonshire Building | 2016-09-02 22:45 | 46098.9437 | 680.004
Devonshire Building | 2016-09-02 23:00 | 46099.1087 | 659.988
Devonshire Building | 2016-09-02 23:15 | 46099.2737 | 659.988
Devonshire Building | 2016-09-02 23:30 | 46099.4387 | 659.988
Devonshire Building | 2016-09-02 23:45 | 46099.6037 | 659.988 | 640.008
Devonshire Building | 2016-09-03 | 46099.7695 | 659.988
Devonshire Building | 2016-09-03 00:15 | 46099.9345 | 659.988
Devonshire Building | 2016-09-03 00:30 | 46100.1045 | 680.004
Devonshire Building | 2016-09-03 00:45 | 46100.2695 | 659.988
Devonshire Building | 2016-09-03 01:00 | 46100.4345 | 659.988
Devonshire Building | 2016-09-03 01:15 | 46100.5995 | 659.988
Devonshire Building | 2016-09-03 01:30 | 46100.7645 | 659.988
Devonshire Building | 2016-09-03 01:45 | 46101.1645 | 1599.984
Devonshire Building | 2016-09-03 02:00 | 46101.3295 | 659.988
Devonshire Building | 2016-09-03 02:15 | 46101.4945 | 659.988
Devonshire Building | 2016-09-03 02:30 | 46101.6595 | 659.988
Devonshire Building | 2016-09-03 02:45 | 46101.8195 | 640.008
Devonshire Building | 2016-09-03 03:00 | 46101.9845 | 659.988
Devonshire Building | 2016-09-03 03:15 | 46102.1495 | 659.988
Devonshire Building | 2016-09-03 03:30 | 46102.3145 | 659.988
Devonshire Building | 2016-09-03 03:45 | 46102.4795 | 659.988
Devonshire Building | 2016-09-03 04:00 | 46102.6445 | 659.988
Devonshire Building | 2016-09-03 04:15 | 46102.8095 | 659.988
Devonshire Building | 2016-09-03 04:30 | 46102.9745 | 659.988
Devonshire Building | 2016-09-03 04:45 | 46103.1395 | 659.988
Devonshire Building | 2016-09-03 05:00 | 46103.3045 | 659.988
Devonshire Building | 2016-09-03 05:15 | 46103.4695 | 659.988
Devonshire Building | 2016-09-03 05:30 | 46103.6295 | 640.008
Devonshire Building | 2016-09-03 05:45 | 46103.7945 | 659.988
Devonshire Building | 2016-09-03 06:00 | 46103.9595 | 659.988
Devonshire Building | 2016-09-03 06:15 | 46104.1245 | 659.988
Devonshire Building | 2016-09-03 06:30 | 46104.2895 | 659.988
Devonshire Building | 2016-09-03 06:45 | 46104.4545 | 659.988
Devonshire Building | 2016-09-03 07:00 | 46104.6145 | 640.008
Devonshire Building | 2016-09-03 07:15 | 46104.7795 | 659.988
Devonshire Building | 2016-09-03 07:30 | 46104.9445 | 659.988
Devonshire Building | 2016-09-03 07:45 | 46105.1245 | 720
Devonshire Building | 2016-09-03 08:00 | 46105.3045 | 720
Devonshire Building | 2016-09-03 08:15 | 46105.4845 | 720
Devonshire Building | 2016-09-03 08:30 | 46105.6645 | 720
Devonshire Building | 2016-09-03 08:45 | 46105.8445 | 720
Devonshire Building | 2016-09-03 09:00 | 46106.0245 | 720
Devonshire Building | 2016-09-03 09:15 | 46106.2045 | 720
Devonshire Building | 2016-09-03 09:30 | 46106.3845 | 720
Devonshire Building | 2016-09-03 09:45 | 46106.5595 | 699.984
Devonshire Building | 2016-09-03 10:00 | 46106.7245 | 659.988
Devonshire Building | 2016-09-03 10:15 | 46106.8845 | 640.008
Devonshire Building | 2016-09-03 10:30 | 46107.0494 | 659.988
Devonshire Building | 2016-09-03 10:45 | 46107.2095 | 640.008
Devonshire Building | 2016-09-03 11:00 | 46107.3744 | 659.988
Devonshire Building | 2016-09-03 11:15 | 46107.5345 | 640.008
Devonshire Building | 2016-09-03 11:30 | 46107.7045 | 680.004
Devonshire Building | 2016-09-03 11:45 | 46107.8694 | 659.988
Devonshire Building | 2016-09-03 12:00 | 46108.0344 | 659.988
Devonshire Building | 2016-09-03 12:15 | 46108.1994 | 659.988
Devonshire Building | 2016-09-03 12:30 | 46108.3644 | 659.988
Devonshire Building | 2016-09-03 12:45 | 46108.5294 | 659.988
Devonshire Building | 2016-09-03 13:00 | 46108.6944 | 659.988
Devonshire Building | 2016-09-03 13:15 | 46108.8544 | 640.008
Devonshire Building | 2016-09-03 13:30 | 46109.0194 | 659.988
Devonshire Building | 2016-09-03 13:45 | 46109.1844 | 659.988
Devonshire Building | 2016-09-03 14:00 | 46109.3494 | 659.988
Devonshire Building | 2016-09-03 14:15 | 46109.5144 | 659.988
Devonshire Building | 2016-09-03 14:30 | 46109.6794 | 659.988
Devonshire Building | 2016-09-03 14:45 | 46109.8394 | 640.008
Devonshire Building | 2016-09-03 15:00 | 46110.0094 | 680.004
Devonshire Building | 2016-09-03 15:15 | 46110.1694 | 640.008
Devonshire Building | 2016-09-03 15:30 | 46110.3344 | 659.988
Devonshire Building | 2016-09-03 15:45 | 46110.4994 | 659.988
Devonshire Building | 2016-09-03 16:00 | 46110.6644 | 659.988
Devonshire Building | 2016-09-03 16:15 | 46110.8294 | 659.988
Devonshire Building | 2016-09-03 16:30 | 46110.9944 | 659.988
Devonshire Building | 2016-09-03 16:45 | 46111.1594 | 659.988
Devonshire Building | 2016-09-03 17:00 | 46111.3244 | 659.988
Devonshire Building | 2016-09-03 17:15 | 46111.4894 | 659.988
Devonshire Building | 2016-09-03 17:30 | 46111.6544 | 659.988
Devonshire Building | 2016-09-03 17:45 | 46111.8144 | 640.008
Devonshire Building | 2016-09-03 18:00 | 46111.9794 | 659.988
Devonshire Building | 2016-09-03 18:15 | 46112.1444 | 659.988
Devonshire Building | 2016-09-03 18:30 | 46112.3144 | 680.004
Devonshire Building | 2016-09-03 18:45 | 46112.4794 | 659.988
Devonshire Building | 2016-09-03 19:00 | 46112.6444 | 659.988
Devonshire Building | 2016-09-03 19:15 | 46112.8094 | 659.988
Devonshire Building | 2016-09-03 19:30 | 46113.2044 | 1580.004
Devonshire Building | 2016-09-03 19:45 | 46113.3694 | 659.988
Devonshire Building | 2016-09-03 20:00 | 46113.5344 | 659.988
Devonshire Building | 2016-09-03 20:15 | 46113.6994 | 659.988
Devonshire Building | 2016-09-03 20:30 | 46113.8644 | 659.988
Devonshire Building | 2016-09-03 20:45 | 46114.0294 | 659.988
Devonshire Building | 2016-09-03 21:00 | 46114.2144 | 740.016
Devonshire Building | 2016-09-03 21:15 | 46114.3794 | 659.988
Devonshire Building | 2016-09-03 21:30 | 46114.5444 | 659.988
Devonshire Building | 2016-09-03 21:45 | 46114.7094 | 659.988
Devonshire Building | 2016-09-03 22:00 | 46114.8744 | 659.988
Devonshire Building | 2016-09-03 22:15 | 46115.0394 | 659.988
Devonshire Building | 2016-09-03 22:30 | 46115.2044 | 659.988
Devonshire Building | 2016-09-03 22:45 | 46115.3744 | 680.004
Devonshire Building | 2016-09-03 23:00 | 46115.5394 | 659.988
Devonshire Building | 2016-09-03 23:15 | 46115.7044 | 659.988
Devonshire Building | 2016-09-03 23:30 | 46115.8744 | 680.004
Devonshire Building | 2016-09-03 23:45 | 46116.0394 | 659.988 | 640.008
Devonshire Building | 2016-09-04 | 46116.2031 | 659.988
Devonshire Building | 2016-09-04 00:15 | 46116.3731 | 680.004
Devonshire Building | 2016-09-04 00:30 | 46116.5381 | 659.988
Devonshire Building | 2016-09-04 00:45 | 46116.7081 | 680.004
Devonshire Building | 2016-09-04 01:00 | 46116.8731 | 659.988
Devonshire Building | 2016-09-04 01:15 | 46117.0431 | 680.004
Devonshire Building | 2016-09-04 01:30 | 46117.2081 | 659.988
Devonshire Building | 2016-09-04 01:45 | 46117.3781 | 680.004
Devonshire Building | 2016-09-04 02:00 | 46117.5431 | 659.988
Devonshire Building | 2016-09-04 02:15 | 46117.7131 | 680.004
Devonshire Building | 2016-09-04 02:30 | 46117.8831 | 680.004
Devonshire Building | 2016-09-04 02:45 | 46118.0481 | 659.988
Devonshire Building | 2016-09-04 03:00 | 46118.2181 | 680.004
Devonshire Building | 2016-09-04 03:15 | 46118.3831 | 659.988
Devonshire Building | 2016-09-04 03:30 | 46118.5531 | 680.004
Devonshire Building | 2016-09-04 03:45 | 46118.7231 | 680.004
Devonshire Building | 2016-09-04 04:00 | 46118.8881 | 659.988
Devonshire Building | 2016-09-04 04:15 | 46119.0581 | 680.004
Devonshire Building | 2016-09-04 04:30 | 46119.2231 | 659.988
Devonshire Building | 2016-09-04 04:45 | 46119.3931 | 680.004
Devonshire Building | 2016-09-04 05:00 | 46119.5631 | 680.004
Devonshire Building | 2016-09-04 05:15 | 46119.7281 | 659.988
Devonshire Building | 2016-09-04 05:30 | 46119.8981 | 680.004
Devonshire Building | 2016-09-04 05:45 | 46120.0681 | 680.004
Devonshire Building | 2016-09-04 06:00 | 46120.2331 | 659.988
Devonshire Building | 2016-09-04 06:15 | 46120.4031 | 680.004
Devonshire Building | 2016-09-04 06:30 | 46120.5681 | 659.988
Devonshire Building | 2016-09-04 06:45 | 46120.7381 | 680.004
Devonshire Building | 2016-09-04 07:00 | 46120.9031 | 659.988
Devonshire Building | 2016-09-04 07:15 | 46121.0731 | 680.004
Devonshire Building | 2016-09-04 07:30 | 46121.2381 | 659.988
Devonshire Building | 2016-09-04 07:45 | 46121.4231 | 740.016
Devonshire Building | 2016-09-04 08:00 | 46121.6081 | 740.016
Devonshire Building | 2016-09-04 08:15 | 46121.7931 | 740.016
Devonshire Building | 2016-09-04 08:30 | 46121.9731 | 720
Devonshire Building | 2016-09-04 08:45 | 46122.1581 | 740.016
Devonshire Building | 2016-09-04 09:00 | 46122.3431 | 740.016
Devonshire Building | 2016-09-04 09:15 | 46122.5231 | 720
Devonshire Building | 2016-09-04 09:30 | 46122.7081 | 740.016
Devonshire Building | 2016-09-04 09:45 | 46122.8781 | 680.004
Devonshire Building | 2016-09-04 10:00 | 46123.0481 | 680.004
Devonshire Building | 2016-09-04 10:15 | 46123.2131 | 659.988
Devonshire Building | 2016-09-04 10:30 | 46123.3781 | 659.988
Devonshire Building | 2016-09-04 10:45 | 46123.5431 | 659.988
Devonshire Building | 2016-09-04 11:00 | 46123.7081 | 659.988
Devonshire Building | 2016-09-04 11:15 | 46123.8731 | 659.988
Devonshire Building | 2016-09-04 11:30 | 46124.0381 | 659.988
Devonshire Building | 2016-09-04 11:45 | 46124.2031 | 659.988
Devonshire Building | 2016-09-04 12:00 | 46124.3731 | 680.004
Devonshire Building | 2016-09-04 12:15 | 46124.5381 | 659.988
Devonshire Building | 2016-09-04 12:30 | 46124.7031 | 659.988
Devonshire Building | 2016-09-04 12:45 | 46124.8731 | 680.004
Devonshire Building | 2016-09-04 13:00 | 46125.0431 | 680.004
Devonshire Building | 2016-09-04 13:15 | 46125.2081 | 659.988
Devonshire Building | 2016-09-04 13:30 | 46125.3781 | 680.004
Devonshire Building | 2016-09-04 13:45 | 46125.5481 | 680.004
Devonshire Building | 2016-09-04 14:00 | 46125.7181 | 680.004
Devonshire Building | 2016-09-04 14:15 | 46125.8831 | 659.988
Devonshire Building | 2016-09-04 14:30 | 46126.0531 | 680.004
Devonshire Building | 2016-09-04 14:45 | 46126.2231 | 680.004
Devonshire Building | 2016-09-04 15:00 | 46126.3881 | 659.988
Devonshire Building | 2016-09-04 15:15 | 46126.5631 | 699.984
Devonshire Building | 2016-09-04 15:30 | 46126.7281 | 659.988
Devonshire Building | 2016-09-04 15:45 | 46126.8981 | 680.004
Devonshire Building | 2016-09-04 16:00 | 46127.0631 | 659.988
Devonshire Building | 2016-09-04 16:15 | 46127.2331 | 680.004
Devonshire Building | 2016-09-04 16:30 | 46127.4031 | 680.004
Devonshire Building | 2016-09-04 16:45 | 46127.7931 | 1559.988
Devonshire Building | 2016-09-04 17:00 | 46127.9581 | 659.988
Devonshire Building | 2016-09-04 17:15 | 46128.1281 | 680.004
Devonshire Building | 2016-09-04 17:30 | 46128.2981 | 680.004
Devonshire Building | 2016-09-04 17:45 | 46128.4631 | 659.988
Devonshire Building | 2016-09-04 18:00 | 46128.6331 | 680.004
Devonshire Building | 2016-09-04 18:15 | 46128.8031 | 680.004
Devonshire Building | 2016-09-04 18:30 | 46128.9681 | 659.988
Devonshire Building | 2016-09-04 18:45 | 46129.1381 | 680.004
Devonshire Building | 2016-09-04 19:00 | 46129.3081 | 680.004
Devonshire Building | 2016-09-04 19:15 | 46129.4781 | 680.004
Devonshire Building | 2016-09-04 19:30 | 46129.6431 | 659.988
Devonshire Building | 2016-09-04 19:45 | 46129.8131 | 680.004
Devonshire Building | 2016-09-04 20:00 | 46129.9831 | 680.004
Devonshire Building | 2016-09-04 20:15 | 46130.1531 | 680.004
Devonshire Building | 2016-09-04 20:30 | 46130.3281 | 699.984
Devonshire Building | 2016-09-04 20:45 | 46130.4981 | 680.004
Devonshire Building | 2016-09-04 21:00 | 46130.6831 | 740.016
Devonshire Building | 2016-09-04 21:15 | 46130.8531 | 680.004
Devonshire Building | 2016-09-04 21:30 | 46131.0231 | 680.004
Devonshire Building | 2016-09-04 21:45 | 46131.1931 | 680.004
Devonshire Building | 2016-09-04 22:00 | 46131.3631 | 680.004
Devonshire Building | 2016-09-04 22:15 | 46131.5331 | 680.004
Devonshire Building | 2016-09-04 22:30 | 46131.7031 | 680.004
Devonshire Building | 2016-09-04 22:45 | 46131.8731 | 680.004
Devonshire Building | 2016-09-04 23:00 | 46132.0431 | 680.004
Devonshire Building | 2016-09-04 23:15 | 46132.2131 | 680.004
Devonshire Building | 2016-09-04 23:30 | 46132.3881 | 699.984
Devonshire Building | 2016-09-04 23:45 | 46132.5581 | 680.004 | 659.988
Devonshire Building | 2016-09-05 | 46132.7305 | 680.004
Devonshire Building | 2016-09-05 00:15 | 46132.9005 | 680.004
Devonshire Building | 2016-09-05 00:30 | 46133.0755 | 699.984
Devonshire Building | 2016-09-05 00:45 | 46133.2455 | 680.004
Devonshire Building | 2016-09-05 01:00 | 46133.4155 | 680.004
Devonshire Building | 2016-09-05 01:15 | 46133.5905 | 699.984
Devonshire Building | 2016-09-05 01:30 | 46133.7605 | 680.004
Devonshire Building | 2016-09-05 01:45 | 46133.9305 | 680.004
Devonshire Building | 2016-09-05 02:00 | 46134.1055 | 699.984
Devonshire Building | 2016-09-05 02:15 | 46134.2755 | 680.004
Devonshire Building | 2016-09-05 02:30 | 46134.4455 | 680.004
Devonshire Building | 2016-09-05 02:45 | 46134.6205 | 699.984
Devonshire Building | 2016-09-05 03:00 | 46134.7905 | 680.004
Devonshire Building | 2016-09-05 03:15 | 46134.9605 | 680.004
Devonshire Building | 2016-09-05 03:30 | 46135.1355 | 699.984
Devonshire Building | 2016-09-05 03:45 | 46135.3055 | 680.004
Devonshire Building | 2016-09-05 04:00 | 46135.4755 | 680.004
Devonshire Building | 2016-09-05 04:15 | 46135.6455 | 680.004
Devonshire Building | 2016-09-05 04:30 | 46135.8205 | 699.984
Devonshire Building | 2016-09-05 04:45 | 46135.9905 | 680.004
Devonshire Building | 2016-09-05 05:00 | 46136.1605 | 680.004
Devonshire Building | 2016-09-05 05:15 | 46136.3355 | 699.984
Devonshire Building | 2016-09-05 05:30 | 46136.5055 | 680.004
Devonshire Building | 2016-09-05 05:45 | 46136.6805 | 699.984
Devonshire Building | 2016-09-05 06:00 | 46136.8505 | 680.004
Devonshire Building | 2016-09-05 06:15 | 46137.0255 | 699.984
Devonshire Building | 2016-09-05 06:30 | 46137.1955 | 680.004
Devonshire Building | 2016-09-05 06:45 | 46137.3805 | 740.016
Devonshire Building | 2016-09-05 07:00 | 46137.5505 | 680.004
Devonshire Building | 2016-09-05 07:15 | 46137.7205 | 680.004
Devonshire Building | 2016-09-05 07:30 | 46138.1205 | 1599.984
Devonshire Building | 2016-09-05 07:45 | 46138.3355 | 860.004
Devonshire Building | 2016-09-05 08:00 | 46138.5305 | 780.012
Devonshire Building | 2016-09-05 08:15 | 46138.7305 | 799.992
Devonshire Building | 2016-09-05 08:30 | 46138.9405 | 839.988
Devonshire Building | 2016-09-05 08:45 | 46139.1604 | 879.984
Devonshire Building | 2016-09-05 09:00 | 46139.3754 | 860.004
Devonshire Building | 2016-09-05 09:15 | 46139.5954 | 879.984
Devonshire Building | 2016-09-05 09:30 | 46140.0754 | 1919.988
Devonshire Building | 2016-09-05 09:45 | 46140.3404 | 1059.984
Devonshire Building | 2016-09-05 10:00 | 46140.6104 | 1080
Devonshire Building | 2016-09-05 10:15 | 46140.8604 | 1000.008
Devonshire Building | 2016-09-05 10:30 | 46141.0854 | 900
Devonshire Building | 2016-09-05 10:45 | 46141.5504 | 1860.012
Devonshire Building | 2016-09-05 11:00 | 46141.7854 | 939.996
Devonshire Building | 2016-09-05 11:15 | 46142.0154 | 920.016
Devonshire Building | 2016-09-05 11:30 | 46142.2354 | 879.984
Devonshire Building | 2016-09-05 11:45 | 46142.4504 | 860.004
Devonshire Building | 2016-09-05 12:00 | 46142.6654 | 860.004
Devonshire Building | 2016-09-05 12:15 | 46142.8754 | 839.988
Devonshire Building | 2016-09-05 12:30 | 46143.3554 | 1919.988
Devonshire Building | 2016-09-05 12:45 | 46143.5804 | 900
Devonshire Building | 2016-09-05 13:00 | 46143.7954 | 860.004
Devonshire Building | 2016-09-05 13:15 | 46144.0104 | 860.004
Devonshire Building | 2016-09-05 13:30 | 46144.2204 | 839.988
Devonshire Building | 2016-09-05 13:45 | 46144.4304 | 839.988
Devonshire Building | 2016-09-05 14:00 | 46144.6454 | 860.004
Devonshire Building | 2016-09-05 14:15 | 46144.8554 | 839.988
Devonshire Building | 2016-09-05 14:30 | 46145.3104 | 1820.016
Devonshire Building | 2016-09-05 14:45 | 46145.5004 | 759.996
Devonshire Building | 2016-09-05 15:00 | 46145.6954 | 780.012
Devonshire Building | 2016-09-05 15:15 | 46145.8954 | 799.992
Devonshire Building | 2016-09-05 15:30 | 46146.0954 | 799.992
Devonshire Building | 2016-09-05 15:45 | 46146.2904 | 780.012
Devonshire Building | 2016-09-05 16:00 | 46146.4804 | 759.996
Devonshire Building | 2016-09-05 16:15 | 46146.9354 | 1820.016
Devonshire Building | 2016-09-05 16:30 | 46147.1304 | 780.012
Devonshire Building | 2016-09-05 16:45 | 46147.3304 | 799.992
Devonshire Building | 2016-09-05 17:00 | 46147.5304 | 799.992
Devonshire Building | 2016-09-05 17:15 | 46147.7254 | 780.012
Devonshire Building | 2016-09-05 17:30 | 46147.9254 | 799.992
Devonshire Building | 2016-09-05 17:45 | 46148.1204 | 780.012
Devonshire Building | 2016-09-05 18:00 | 46148.3154 | 780.012
Devonshire Building | 2016-09-05 18:15 | 46148.5054 | 759.996
Devonshire Building | 2016-09-05 18:30 | 46148.6954 | 759.996
Devonshire Building | 2016-09-05 18:45 | 46148.8854 | 759.996
Devonshire Building | 2016-09-05 19:00 | 46149.0754 | 759.996
Devonshire Building | 2016-09-05 19:15 | 46149.2604 | 740.016
Devonshire Building | 2016-09-05 19:30 | 46149.4454 | 740.016
Devonshire Building | 2016-09-05 19:45 | 46149.6305 | 740.016
Devonshire Building | 2016-09-05 20:00 | 46149.8105 | 720
Devonshire Building | 2016-09-05 20:15 | 46149.9955 | 740.016
Devonshire Building | 2016-09-05 20:30 | 46150.1805 | 740.016
Devonshire Building | 2016-09-05 20:45 | 46150.3655 | 740.016
Devonshire Building | 2016-09-05 21:00 | 46150.5705 | 820.008
Devonshire Building | 2016-09-05 21:15 | 46150.7605 | 759.996
Devonshire Building | 2016-09-05 21:30 | 46150.9455 | 740.016
Devonshire Building | 2016-09-05 21:45 | 46151.1355 | 759.996
Devonshire Building | 2016-09-05 22:00 | 46151.3205 | 740.016
Devonshire Building | 2016-09-05 22:15 | 46151.5105 | 759.996
Devonshire Building | 2016-09-05 22:30 | 46151.6955 | 740.016
Devonshire Building | 2016-09-05 22:45 | 46151.8805 | 740.016
Devonshire Building | 2016-09-05 23:00 | 46152.0655 | 740.016
Devonshire Building | 2016-09-05 23:15 | 46152.2555 | 759.996
Devonshire Building | 2016-09-05 23:30 | 46152.4405 | 740.016
Devonshire Building | 2016-09-05 23:45 | 46152.6255 | 740.016 | 680.004
Devonshire Building | 2016-09-06 | 46152.8047 | 720
Devonshire Building | 2016-09-06 00:15 | 46152.9897 | 740.016
Devonshire Building | 2016-09-06 00:30 | 46153.1747 | 740.016
Devonshire Building | 2016-09-06 00:45 | 46153.3547 | 720
Devonshire Building | 2016-09-06 01:00 | 46153.5347 | 720
Devonshire Building | 2016-09-06 01:15 | 46153.7147 | 720
Devonshire Building | 2016-09-06 01:30 | 46153.8947 | 720
Devonshire Building | 2016-09-06 01:45 | 46154.0747 | 720
Devonshire Building | 2016-09-06 02:00 | 46154.2547 | 720
Devonshire Building | 2016-09-06 02:15 | 46154.4347 | 720
Devonshire Building | 2016-09-06 02:30 | 46154.6097 | 699.984
Devonshire Building | 2016-09-06 02:45 | 46154.7897 | 720
Devonshire Building | 2016-09-06 03:00 | 46154.9647 | 699.984
Devonshire Building | 2016-09-06 03:15 | 46155.1447 | 720
Devonshire Building | 2016-09-06 03:30 | 46155.3247 | 720
Devonshire Building | 2016-09-06 03:45 | 46155.4997 | 699.984
Devonshire Building | 2016-09-06 04:00 | 46155.6797 | 720
Devonshire Building | 2016-09-06 04:15 | 46155.8547 | 699.984
Devonshire Building | 2016-09-06 04:30 | 46156.0297 | 699.984
Devonshire Building | 2016-09-06 04:45 | 46156.2097 | 720
Devonshire Building | 2016-09-06 05:00 | 46156.3847 | 699.984
Devonshire Building | 2016-09-06 05:15 | 46156.5597 | 699.984
Devonshire Building | 2016-09-06 05:30 | 46156.7347 | 699.984
Devonshire Building | 2016-09-06 05:45 | 46156.9097 | 699.984
Devonshire Building | 2016-09-06 06:00 | 46157.0847 | 699.984
Devonshire Building | 2016-09-06 06:15 | 46157.2597 | 699.984
Devonshire Building | 2016-09-06 06:30 | 46157.4347 | 699.984
Devonshire Building | 2016-09-06 06:45 | 46157.8747 | 1760.004
Devonshire Building | 2016-09-06 07:00 | 46158.0447 | 680.004
Devonshire Building | 2016-09-06 07:15 | 46158.2196 | 699.984
Devonshire Building | 2016-09-06 07:30 | 46158.3946 | 699.984
Devonshire Building | 2016-09-06 07:45 | 46158.5946 | 799.992
Devonshire Building | 2016-09-06 08:00 | 46158.7846 | 759.996
Devonshire Building | 2016-09-06 08:15 | 46158.9796 | 780.012
Devonshire Building | 2016-09-06 08:30 | 46159.1746 | 780.012
Devonshire Building | 2016-09-06 08:45 | 46159.3697 | 780.012
Devonshire Building | 2016-09-06 09:00 | 46159.5647 | 780.012
Devonshire Building | 2016-09-06 09:15 | 46160.0397 | 1900.008
Devonshire Building | 2016-09-06 09:30 | 46160.2347 | 780.012
Devonshire Building | 2016-09-06 09:45 | 46160.4297 | 780.012
Devonshire Building | 2016-09-06 10:00 | 46160.6447 | 860.004
Devonshire Building | 2016-09-06 10:15 | 46160.8397 | 780.012
Devonshire Building | 2016-09-06 10:30 | 46161.0447 | 820.008
Devonshire Building | 2016-09-06 10:45 | 46161.5297 | 1940.004
Devonshire Building | 2016-09-06 11:00 | 46161.7397 | 839.988
Devonshire Building | 2016-09-06 11:15 | 46161.9497 | 839.988
Devonshire Building | 2016-09-06 11:30 | 46162.1597 | 839.988
Devonshire Building | 2016-09-06 11:45 | 46162.3647 | 820.008
Devonshire Building | 2016-09-06 12:00 | 46162.5697 | 820.008
Devonshire Building | 2016-09-06 12:15 | 46162.7697 | 799.992
Devonshire Building | 2016-09-06 12:30 | 46163.2247 | 1820.016
Devonshire Building | 2016-09-06 12:45 | 46163.4347 | 839.988
Devonshire Building | 2016-09-06 13:00 | 46163.6497 | 860.004
Devonshire Building | 2016-09-06 13:15 | 46163.8547 | 820.008
Devonshire Building | 2016-09-06 13:30 | 46164.0547 | 799.992
Devonshire Building | 2016-09-06 13:45 | 46164.2597 | 820.008
Devonshire Building | 2016-09-06 14:00 | 46164.4697 | 839.988
Devonshire Building | 2016-09-06 14:15 | 46164.6697 | 799.992
Devonshire Building | 2016-09-06 14:30 | 46165.1047 | 1739.988
Devonshire Building | 2016-09-06 14:45 | 46165.2947 | 759.996
Devonshire Building | 2016-09-06 15:00 | 46165.4797 | 740.016
Devonshire Building | 2016-09-06 15:15 | 46165.6997 | 879.984
Devonshire Building | 2016-09-06 15:30 | 46165.9647 | 1059.984
Devonshire Building | 2016-09-06 15:45 | 46166.2296 | 1059.984
Devonshire Building | 2016-09-06 16:00 | 46166.4896 | 1040.004
Devonshire Building | 2016-09-06 16:15 | 46166.7397 | 1000.008
Devonshire Building | 2016-09-06 16:30 | 46167.1347 | 1580.004
Devonshire Building | 2016-09-06 16:45 | 46167.5097 | 1500.012
Devonshire Building | 2016-09-06 17:00 | 46167.7647 | 1019.988
Devonshire Building | 2016-09-06 17:15 | 46167.9947 | 920.016
Devonshire Building | 2016-09-06 17:30 | 46168.2097 | 860.004
Devonshire Building | 2016-09-06 17:45 | 46168.4147 | 820.008
Devonshire Building | 2016-09-06 18:00 | 46168.6097 | 780.012
Devonshire Building | 2016-09-06 18:15 | 46168.7997 | 759.996
Devonshire Building | 2016-09-06 18:30 | 46168.9847 | 740.016
Devonshire Building | 2016-09-06 18:45 | 46169.1697 | 740.016
Devonshire Building | 2016-09-06 19:00 | 46169.3547 | 740.016
Devonshire Building | 2016-09-06 19:15 | 46169.5347 | 720
Devonshire Building | 2016-09-06 19:30 | 46169.7147 | 720
Devonshire Building | 2016-09-06 19:45 | 46169.8947 | 720
Devonshire Building | 2016-09-06 20:00 | 46170.0697 | 699.984
Devonshire Building | 2016-09-06 20:15 | 46170.2497 | 720
Devonshire Building | 2016-09-06 20:30 | 46170.4297 | 720
Devonshire Building | 2016-09-06 20:45 | 46170.6047 | 699.984
Devonshire Building | 2016-09-06 21:00 | 46170.7947 | 759.996
Devonshire Building | 2016-09-06 21:15 | 46170.9647 | 680.004
Devonshire Building | 2016-09-06 21:30 | 46171.1347 | 680.004
Devonshire Building | 2016-09-06 21:45 | 46171.3097 | 699.984
Devonshire Building | 2016-09-06 22:00 | 46171.4797 | 680.004
Devonshire Building | 2016-09-06 22:15 | 46171.6497 | 680.004
Devonshire Building | 2016-09-06 22:30 | 46171.8197 | 680.004
Devonshire Building | 2016-09-06 22:45 | 46171.9947 | 699.984
Devonshire Building | 2016-09-06 23:00 | 46172.1647 | 680.004
Devonshire Building | 2016-09-06 23:15 | 46172.3347 | 680.004
Devonshire Building | 2016-09-06 23:30 | 46172.5097 | 699.984
Devonshire Building | 2016-09-06 23:45 | 46172.6797 | 680.004 | 680.004
Devonshire Building | 2016-09-07 | 46172.8555 | 699.984
Devonshire Building | 2016-09-07 00:15 | 46173.0255 | 680.004
Devonshire Building | 2016-09-07 00:30 | 46173.2005 | 699.984
Devonshire Building | 2016-09-07 00:45 | 46173.3705 | 680.004
Devonshire Building | 2016-09-07 01:00 | 46173.5505 | 720
Devonshire Building | 2016-09-07 01:15 | 46173.7205 | 680.004
Devonshire Building | 2016-09-07 01:30 | 46173.8955 | 699.984
Devonshire Building | 2016-09-07 01:45 | 46174.0655 | 680.004
Devonshire Building | 2016-09-07 02:00 | 46174.2405 | 699.984
Devonshire Building | 2016-09-07 02:15 | 46174.4105 | 680.004
Devonshire Building | 2016-09-07 02:30 | 46174.5855 | 699.984
Devonshire Building | 2016-09-07 02:45 | 46174.7555 | 680.004
Devonshire Building | 2016-09-07 03:00 | 46174.9305 | 699.984
Devonshire Building | 2016-09-07 03:15 | 46175.1055 | 699.984
Devonshire Building | 2016-09-07 03:30 | 46175.2755 | 680.004
Devonshire Building | 2016-09-07 03:45 | 46175.4504 | 699.984
Devonshire Building | 2016-09-07 04:00 | 46175.6205 | 680.004
Devonshire Building | 2016-09-07 04:15 | 46175.7954 | 699.984
Devonshire Building | 2016-09-07 04:30 | 46175.9654 | 680.004
Devonshire Building | 2016-09-07 04:45 | 46176.1404 | 699.984
Devonshire Building | 2016-09-07 05:00 | 46176.3104 | 680.004
Devonshire Building | 2016-09-07 05:15 | 46176.4854 | 699.984
Devonshire Building | 2016-09-07 05:30 | 46176.6554 | 680.004
Devonshire Building | 2016-09-07 05:45 | 46176.8254 | 680.004
Devonshire Building | 2016-09-07 06:00 | 46176.9954 | 680.004
Devonshire Building | 2016-09-07 06:15 | 46177.1654 | 680.004
Devonshire Building | 2016-09-07 06:30 | 46177.3404 | 699.984
Devonshire Building | 2016-09-07 06:45 | 46177.5204 | 720
Devonshire Building | 2016-09-07 07:00 | 46177.6954 | 699.984
Devonshire Building | 2016-09-07 07:15 | 46178.1054 | 1640.016
Devonshire Building | 2016-09-07 07:30 | 46178.2754 | 680.004
Devonshire Building | 2016-09-07 07:45 | 46178.4654 | 759.996
Devonshire Building | 2016-09-07 08:00 | 46178.6504 | 740.016
Devonshire Building | 2016-09-07 08:15 | 46178.8454 | 780.012
Devonshire Building | 2016-09-07 08:30 | 46179.0354 | 759.996
Devonshire Building | 2016-09-07 08:45 | 46179.2304 | 780.012
Devonshire Building | 2016-09-07 09:00 | 46179.4204 | 759.996
Devonshire Building | 2016-09-07 09:15 | 46179.6055 | 740.016
Devonshire Building | 2016-09-07 09:30 | 46180.0854 | 1919.988
Devonshire Building | 2016-09-07 09:45 | 46180.2754 | 759.996
Devonshire Building | 2016-09-07 10:00 | 46180.4705 | 780.012
Devonshire Building | 2016-09-07 10:15 | 46180.6704 | 799.992
Devonshire Building | 2016-09-07 10:30 | 46180.8755 | 820.008
Devonshire Building | 2016-09-07 10:45 | 46181.0854 | 839.988
Devonshire Building | 2016-09-07 11:00 | 46181.2954 | 839.988
Devonshire Building | 2016-09-07 11:15 | 46181.7504 | 1820.016
Devonshire Building | 2016-09-07 11:30 | 46181.9555 | 820.008
Devonshire Building | 2016-09-07 11:45 | 46182.1505 | 780.012
Devonshire Building | 2016-09-07 12:00 | 46182.3555 | 820.008
Devonshire Building | 2016-09-07 12:15 | 46182.5555 | 799.992
Devonshire Building | 2016-09-07 12:30 | 46182.7555 | 799.992
Devonshire Building | 2016-09-07 12:45 | 46182.9555 | 799.992
Devonshire Building | 2016-09-07 13:00 | 46183.3454 | 1559.988
Devonshire Building | 2016-09-07 13:15 | 46183.6104 | 1059.984
Devonshire Building | 2016-09-07 13:30 | 46183.8154 | 820.008
Devonshire Building | 2016-09-07 13:45 | 46184.0204 | 820.008
Devonshire Building | 2016-09-07 14:00 | 46184.2254 | 820.008
Devonshire Building | 2016-09-07 14:15 | 46184.4354 | 839.988
Devonshire Building | 2016-09-07 14:30 | 46184.6404 | 820.008
Devonshire Building | 2016-09-07 14:45 | 46184.8455 | 820.008
Devonshire Building | 2016-09-07 15:00 | 46185.2954 | 1800
Devonshire Building | 2016-09-07 15:15 | 46185.4954 | 799.992
Devonshire Building | 2016-09-07 15:30 | 46185.6954 | 799.992
Devonshire Building | 2016-09-07 15:45 | 46185.8954 | 799.992
Devonshire Building | 2016-09-07 16:00 | 46186.0954 | 799.992
Devonshire Building | 2016-09-07 16:15 | 46186.2854 | 759.996
Devonshire Building | 2016-09-07 16:30 | 46186.4754 | 759.996
Devonshire Building | 2016-09-07 16:45 | 46186.6654 | 759.996
Devonshire Building | 2016-09-07 17:00 | 46186.8504 | 740.016
Devonshire Building | 2016-09-07 17:15 | 46187.0304 | 720
Devonshire Building | 2016-09-07 17:30 | 46187.2104 | 720
Devonshire Building | 2016-09-07 17:45 | 46187.3854 | 699.984
Devonshire Building | 2016-09-07 18:00 | 46187.5604 | 699.984
Devonshire Building | 2016-09-07 18:15 | 46187.7354 | 699.984
Devonshire Building | 2016-09-07 18:30 | 46187.9104 | 699.984
Devonshire Building | 2016-09-07 18:45 | 46188.0804 | 680.004
Devonshire Building | 2016-09-07 19:00 | 46188.2554 | 699.984
Devonshire Building | 2016-09-07 19:15 | 46188.4254 | 680.004
Devonshire Building | 2016-09-07 19:30 | 46188.5954 | 680.004
Devonshire Building | 2016-09-07 19:45 | 46188.7654 | 680.004
Devonshire Building | 2016-09-07 20:00 | 46188.9354 | 680.004
Devonshire Building | 2016-09-07 20:15 | 46189.1054 | 680.004
Devonshire Building | 2016-09-07 20:30 | 46189.2804 | 699.984
Devonshire Building | 2016-09-07 20:45 | 46189.4504 | 680.004
Devonshire Building | 2016-09-07 21:00 | 46189.6404 | 759.996
Devonshire Building | 2016-09-07 21:15 | 46189.8104 | 680.004
Devonshire Building | 2016-09-07 21:30 | 46189.9754 | 659.988
Devonshire Building | 2016-09-07 21:45 | 46190.1454 | 680.004
Devonshire Building | 2016-09-07 22:00 | 46190.3154 | 680.004
Devonshire Building | 2016-09-07 22:15 | 46190.4804 | 659.988
Devonshire Building | 2016-09-07 22:30 | 46190.6504 | 680.004
Devonshire Building | 2016-09-07 22:45 | 46190.8204 | 680.004
Devonshire Building | 2016-09-07 23:00 | 46190.9854 | 659.988
Devonshire Building | 2016-09-07 23:15 | 46191.1554 | 680.004
Devonshire Building | 2016-09-07 23:30 | 46191.3254 | 680.004
Devonshire Building | 2016-09-07 23:45 | 46191.4954 | 680.004 | 659.988
Devonshire Building | 2016-09-08 | 46191.6641 | 680.004
Devonshire Building | 2016-09-08 00:15 | 46191.8291 | 659.988
Devonshire Building | 2016-09-08 00:30 | 46192.2291 | 1599.984
Devonshire Building | 2016-09-08 00:45 | 46192.3991 | 680.004
Devonshire Building | 2016-09-08 01:00 | 46192.5691 | 680.004
Devonshire Building | 2016-09-08 01:15 | 46192.7391 | 680.004
Devonshire Building | 2016-09-08 01:30 | 46192.9091 | 680.004
Devonshire Building | 2016-09-08 01:45 | 46193.0791 | 680.004
Devonshire Building | 2016-09-08 02:00 | 46193.2491 | 680.004
Devonshire Building | 2016-09-08 02:15 | 46193.4191 | 680.004
Devonshire Building | 2016-09-08 02:30 | 46193.5891 | 680.004
Devonshire Building | 2016-09-08 02:45 | 46193.7591 | 680.004
Devonshire Building | 2016-09-08 03:00 | 46193.9241 | 659.988
Devonshire Building | 2016-09-08 03:15 | 46194.0941 | 680.004
Devonshire Building | 2016-09-08 03:30 | 46194.2641 | 680.004
Devonshire Building | 2016-09-08 03:45 | 46194.4341 | 680.004
Devonshire Building | 2016-09-08 04:00 | 46194.6041 | 680.004
Devonshire Building | 2016-09-08 04:15 | 46194.7741 | 680.004
Devonshire Building | 2016-09-08 04:30 | 46194.9391 | 659.988
Devonshire Building | 2016-09-08 04:45 | 46195.1091 | 680.004
Devonshire Building | 2016-09-08 05:00 | 46195.2791 | 680.004
Devonshire Building | 2016-09-08 05:15 | 46195.4491 | 680.004
Devonshire Building | 2016-09-08 05:30 | 46195.6141 | 659.988
Devonshire Building | 2016-09-08 05:45 | 46195.7841 | 680.004
Devonshire Building | 2016-09-08 06:00 | 46195.9541 | 680.004
Devonshire Building | 2016-09-08 06:15 | 46196.1191 | 659.988
Devonshire Building | 2016-09-08 06:30 | 46196.2891 | 680.004
Devonshire Building | 2016-09-08 06:45 | 46196.4791 | 759.996
Devonshire Building | 2016-09-08 07:00 | 46196.6441 | 659.988
Devonshire Building | 2016-09-08 07:15 | 46196.8141 | 680.004
Devonshire Building | 2016-09-08 07:30 | 46196.9941 | 720
Devonshire Building | 2016-09-08 07:45 | 46197.1841 | 759.996
Devonshire Building | 2016-09-08 08:00 | 46197.3791 | 780.012
Devonshire Building | 2016-09-08 08:15 | 46197.5841 | 820.008
Devonshire Building | 2016-09-08 08:30 | 46197.7891 | 820.008
Devonshire Building | 2016-09-08 08:45 | 46198.2591 | 1879.992
Devonshire Building | 2016-09-08 09:00 | 46198.4941 | 939.996
Devonshire Building | 2016-09-08 09:15 | 46198.7341 | 960.012
Devonshire Building | 2016-09-08 09:30 | 46198.9641 | 920.016
Devonshire Building | 2016-09-08 09:45 | 46199.1991 | 939.996
Devonshire Building | 2016-09-08 10:00 | 46199.4141 | 860.004
Devonshire Building | 2016-09-08 10:15 | 46199.8291 | 1659.996
Devonshire Building | 2016-09-08 10:30 | 46200.0741 | 979.992
Devonshire Building | 2016-09-08 10:45 | 46200.2791 | 820.008
Devonshire Building | 2016-09-08 11:00 | 46200.4791 | 799.992
Devonshire Building | 2016-09-08 11:15 | 46200.6841 | 820.008
Devonshire Building | 2016-09-08 11:30 | 46200.8841 | 799.992
Devonshire Building | 2016-09-08 11:45 | 46201.0741 | 759.996
Devonshire Building | 2016-09-08 12:00 | 46201.2641 | 759.996
Devonshire Building | 2016-09-08 12:15 | 46201.7141 | 1800
Devonshire Building | 2016-09-08 12:30 | 46201.8941 | 720
Devonshire Building | 2016-09-08 12:45 | 46202.0741 | 720
Devonshire Building | 2016-09-08 13:00 | 46202.2591 | 740.016
Devonshire Building | 2016-09-08 13:15 | 46202.4541 | 780.012
Devonshire Building | 2016-09-08 13:30 | 46202.6491 | 780.012
Devonshire Building | 2016-09-08 13:45 | 46202.8441 | 780.012
Devonshire Building | 2016-09-08 14:00 | 46203.3141 | 1879.992
Devonshire Building | 2016-09-08 14:15 | 46203.5041 | 759.996
Devonshire Building | 2016-09-08 14:30 | 46203.6991 | 780.012
Devonshire Building | 2016-09-08 14:45 | 46203.8891 | 759.996
Devonshire Building | 2016-09-08 15:00 | 46204.0791 | 759.996
Devonshire Building | 2016-09-08 15:15 | 46204.2641 | 740.016
Devonshire Building | 2016-09-08 15:30 | 46204.4491 | 740.016
Devonshire Building | 2016-09-08 15:45 | 46204.6441 | 780.012
Devonshire Building | 2016-09-08 16:00 | 46204.8291 | 740.016
Devonshire Building | 2016-09-08 16:15 | 46205.2641 | 1739.988
Devonshire Building | 2016-09-08 16:30 | 46205.4541 | 759.996
Devonshire Building | 2016-09-08 16:45 | 46205.6391 | 740.016
Devonshire Building | 2016-09-08 17:00 | 46205.8241 | 740.016
Devonshire Building | 2016-09-08 17:15 | 46206.0141 | 759.996
Devonshire Building | 2016-09-08 17:30 | 46206.1991 | 740.016
Devonshire Building | 2016-09-08 17:45 | 46206.3791 | 720
Devonshire Building | 2016-09-08 18:00 | 46206.5641 | 740.016
Devonshire Building | 2016-09-08 18:15 | 46206.7441 | 720
Devonshire Building | 2016-09-08 18:30 | 46206.9241 | 720
Devonshire Building | 2016-09-08 18:45 | 46207.1041 | 720
Devonshire Building | 2016-09-08 19:00 | 46207.2791 | 699.984
Devonshire Building | 2016-09-08 19:15 | 46207.4541 | 699.984
Devonshire Building | 2016-09-08 19:30 | 46207.6241 | 680.004
Devonshire Building | 2016-09-08 19:45 | 46207.7991 | 699.984
Devonshire Building | 2016-09-08 20:00 | 46207.9691 | 680.004
Devonshire Building | 2016-09-08 20:15 | 46208.1441 | 699.984
Devonshire Building | 2016-09-08 20:30 | 46208.3141 | 680.004
Devonshire Building | 2016-09-08 20:45 | 46208.4841 | 680.004
Devonshire Building | 2016-09-08 21:00 | 46208.6791 | 780.012
Devonshire Building | 2016-09-08 21:15 | 46208.8491 | 680.004
Devonshire Building | 2016-09-08 21:30 | 46209.0241 | 699.984
Devonshire Building | 2016-09-08 21:45 | 46209.1991 | 699.984
Devonshire Building | 2016-09-08 22:00 | 46209.3691 | 680.004
Devonshire Building | 2016-09-08 22:15 | 46209.5441 | 699.984
Devonshire Building | 2016-09-08 22:30 | 46209.7141 | 680.004
Devonshire Building | 2016-09-08 22:45 | 46209.8891 | 699.984
Devonshire Building | 2016-09-08 23:00 | 46210.0641 | 699.984
Devonshire Building | 2016-09-08 23:15 | 46210.2341 | 680.004
Devonshire Building | 2016-09-08 23:30 | 46210.4091 | 699.984
Devonshire Building | 2016-09-08 23:45 | 46210.5841 | 699.984 | 659.988
Devonshire Building | 2016-09-09 | 46210.7539 | 680.004
Devonshire Building | 2016-09-09 00:15 | 46210.9289 | 699.984
Devonshire Building | 2016-09-09 00:30 | 46211.0989 | 680.004
Devonshire Building | 2016-09-09 00:45 | 46211.2739 | 699.984
Devonshire Building | 2016-09-09 01:00 | 46211.4439 | 680.004
Devonshire Building | 2016-09-09 01:15 | 46211.6189 | 699.984
Devonshire Building | 2016-09-09 01:30 | 46211.7889 | 680.004
Devonshire Building | 2016-09-09 01:45 | 46211.9589 | 680.004
Devonshire Building | 2016-09-09 02:00 | 46212.1339 | 699.984
Devonshire Building | 2016-09-09 02:15 | 46212.3039 | 680.004
Devonshire Building | 2016-09-09 02:30 | 46212.4739 | 680.004
Devonshire Building | 2016-09-09 02:45 | 46212.6439 | 680.004
Devonshire Building | 2016-09-09 03:00 | 46212.8139 | 680.004
Devonshire Building | 2016-09-09 03:15 | 46212.9839 | 680.004
Devonshire Building | 2016-09-09 03:30 | 46213.1539 | 680.004
Devonshire Building | 2016-09-09 03:45 | 46213.3239 | 680.004
Devonshire Building | 2016-09-09 04:00 | 46213.4939 | 680.004
Devonshire Building | 2016-09-09 04:15 | 46213.6639 | 680.004
Devonshire Building | 2016-09-09 04:30 | 46213.8339 | 680.004
Devonshire Building | 2016-09-09 04:45 | 46213.9989 | 659.988
Devonshire Building | 2016-09-09 05:00 | 46214.1689 | 680.004
Devonshire Building | 2016-09-09 05:15 | 46214.3389 | 680.004
Devonshire Building | 2016-09-09 05:30 | 46214.5039 | 659.988
Devonshire Building | 2016-09-09 05:45 | 46214.6689 | 659.988
Devonshire Building | 2016-09-09 06:00 | 46214.8389 | 680.004
Devonshire Building | 2016-09-09 06:15 | 46215.0039 | 659.988
Devonshire Building | 2016-09-09 06:30 | 46215.1689 | 659.988
Devonshire Building | 2016-09-09 06:45 | 46215.6039 | 1739.988
Devonshire Building | 2016-09-09 07:00 | 46215.7689 | 659.988
Devonshire Building | 2016-09-09 07:15 | 46215.9339 | 659.988
Devonshire Building | 2016-09-09 07:30 | 46216.1039 | 680.004
Devonshire Building | 2016-09-09 07:45 | 46216.2739 | 680.004
Devonshire Building | 2016-09-09 08:00 | 46216.4389 | 659.988
Devonshire Building | 2016-09-09 08:15 | 46216.6039 | 659.988
Devonshire Building | 2016-09-09 08:30 | 46216.7789 | 699.984
Devonshire Building | 2016-09-09 08:45 | 46216.9539 | 699.984
Devonshire Building | 2016-09-09 09:00 | 46217.1289 | 699.984
Devonshire Building | 2016-09-09 09:15 | 46217.3089 | 720
Devonshire Building | 2016-09-09 09:30 | 46217.4889 | 720
Devonshire Building | 2016-09-09 09:45 | 46217.6889 | 799.992
Devonshire Building | 2016-09-09 10:00 | 46218.1839 | 1980
Devonshire Building | 2016-09-09 10:15 | 46218.4339 | 1000.008
Devonshire Building | 2016-09-09 10:30 | 46218.6739 | 960.012
Devonshire Building | 2016-09-09 10:45 | 46218.8989 | 900
Devonshire Building | 2016-09-09 11:00 | 46219.1239 | 900
Devonshire Building | 2016-09-09 11:15 | 46219.3389 | 860.004
Devonshire Building | 2016-09-09 11:30 | 46219.5539 | 860.004
Devonshire Building | 2016-09-09 11:45 | 46219.7539 | 799.992
Devonshire Building | 2016-09-09 12:00 | 46220.1989 | 1779.984
Devonshire Building | 2016-09-09 12:15 | 46220.3739 | 699.984
Devonshire Building | 2016-09-09 12:30 | 46220.5539 | 720
Devonshire Building | 2016-09-09 12:45 | 46220.7339 | 720
Devonshire Building | 2016-09-09 13:00 | 46220.9139 | 720
Devonshire Building | 2016-09-09 13:15 | 46221.0939 | 720
Devonshire Building | 2016-09-09 13:30 | 46221.2689 | 699.984
Devonshire Building | 2016-09-09 13:45 | 46221.4539 | 740.016
Devonshire Building | 2016-09-09 14:00 | 46221.6439 | 759.996
Devonshire Building | 2016-09-09 14:15 | 46221.8339 | 759.996
Devonshire Building | 2016-09-09 14:30 | 46222.0689 | 939.996
Devonshire Building | 2016-09-09 14:45 | 46222.5639 | 1980
Devonshire Building | 2016-09-09 15:00 | 46222.8289 | 1059.984
Devonshire Building | 2016-09-09 15:15 | 46223.1039 | 1100.016
Devonshire Building | 2016-09-09 15:30 | 46223.4339 | 1320.012
Devonshire Building | 2016-09-09 15:45 | 46223.7439 | 1239.984
Devonshire Building | 2016-09-09 16:00 | 46224.0089 | 1059.984
Devonshire Building | 2016-09-09 16:15 | 46224.2339 | 900
Devonshire Building | 2016-09-09 16:30 | 46224.4439 | 839.988
Devonshire Building | 2016-09-09 16:45 | 46224.6489 | 820.008
Devonshire Building | 2016-09-09 17:00 | 46224.8439 | 780.012
Devonshire Building | 2016-09-09 17:15 | 46225.2739 | 1720.008
Devonshire Building | 2016-09-09 17:30 | 46225.4789 | 820.008
Devonshire Building | 2016-09-09 17:45 | 46225.6789 | 799.992
Devonshire Building | 2016-09-09 18:00 | 46225.8839 | 820.008
Devonshire Building | 2016-09-09 18:15 | 46226.1289 | 979.992
Devonshire Building | 2016-09-09 18:30 | 46226.3739 | 979.992
Devonshire Building | 2016-09-09 18:45 | 46226.6139 | 960.012
Devonshire Building | 2016-09-09 19:00 | 46226.8339 | 879.984
Devonshire Building | 2016-09-09 19:15 | 46227.0389 | 820.008
Devonshire Building | 2016-09-09 19:30 | 46227.2389 | 799.992
Devonshire Building | 2016-09-09 19:45 | 46227.4289 | 759.996
Devonshire Building | 2016-09-09 20:00 | 46227.6089 | 720
Devonshire Building | 2016-09-09 20:15 | 46227.7939 | 740.016
Devonshire Building | 2016-09-09 20:30 | 46227.9689 | 699.984
Devonshire Building | 2016-09-09 20:45 | 46228.1439 | 699.984
Devonshire Building | 2016-09-09 21:00 | 46228.3339 | 759.996
Devonshire Building | 2016-09-09 21:15 | 46228.4989 | 659.988
Devonshire Building | 2016-09-09 21:30 | 46228.6589 | 640.008
Devonshire Building | 2016-09-09 21:45 | 46228.8238 | 659.988
Devonshire Building | 2016-09-09 22:00 | 46228.9888 | 659.988
Devonshire Building | 2016-09-09 22:15 | 46229.1538 | 659.988
Devonshire Building | 2016-09-09 22:30 | 46229.3188 | 659.988
Devonshire Building | 2016-09-09 22:45 | 46229.4838 | 659.988
Devonshire Building | 2016-09-09 23:00 | 46229.6488 | 659.988
Devonshire Building | 2016-09-09 23:15 | 46229.8138 | 659.988
Devonshire Building | 2016-09-09 23:30 | 46229.9788 | 659.988
Devonshire Building | 2016-09-09 23:45 | 46230.1438 | 659.988 | 640.008
Devonshire Building | 2016-09-10 | 46230.3086 | 659.988
Devonshire Building | 2016-09-10 00:15 | 46230.4686 | 640.008
Devonshire Building | 2016-09-10 00:30 | 46230.6386 | 680.004
Devonshire Building | 2016-09-10 00:45 | 46230.8036 | 659.988
Devonshire Building | 2016-09-10 01:00 | 46230.9686 | 659.988
Devonshire Building | 2016-09-10 01:15 | 46231.1336 | 659.988
Devonshire Building | 2016-09-10 01:30 | 46231.2986 | 659.988
Devonshire Building | 2016-09-10 01:45 | 46231.4636 | 659.988
Devonshire Building | 2016-09-10 02:00 | 46231.6286 | 659.988
Devonshire Building | 2016-09-10 02:15 | 46231.7936 | 659.988
Devonshire Building | 2016-09-10 02:30 | 46231.9586 | 659.988
Devonshire Building | 2016-09-10 02:45 | 46232.1236 | 659.988
Devonshire Building | 2016-09-10 03:00 | 46232.2886 | 659.988
Devonshire Building | 2016-09-10 03:15 | 46232.4536 | 659.988
Devonshire Building | 2016-09-10 03:30 | 46232.6186 | 659.988
Devonshire Building | 2016-09-10 03:45 | 46232.7836 | 659.988
Devonshire Building | 2016-09-10 04:00 | 46232.9486 | 659.988
Devonshire Building | 2016-09-10 04:15 | 46233.1135 | 659.988
Devonshire Building | 2016-09-10 04:30 | 46233.2785 | 659.988
Devonshire Building | 2016-09-10 04:45 | 46233.4435 | 659.988
Devonshire Building | 2016-09-10 05:00 | 46233.6185 | 699.984
Devonshire Building | 2016-09-10 05:15 | 46233.7785 | 640.008
Devonshire Building | 2016-09-10 05:30 | 46233.9485 | 680.004
Devonshire Building | 2016-09-10 05:45 | 46234.1135 | 659.988
Devonshire Building | 2016-09-10 06:00 | 46234.2785 | 659.988
Devonshire Building | 2016-09-10 06:15 | 46234.4385 | 640.008
Devonshire Building | 2016-09-10 06:30 | 46234.6035 | 659.988
Devonshire Building | 2016-09-10 06:45 | 46234.7685 | 659.988
Devonshire Building | 2016-09-10 07:00 | 46234.9335 | 659.988
Devonshire Building | 2016-09-10 07:15 | 46235.0935 | 640.008
Devonshire Building | 2016-09-10 07:30 | 46235.2585 | 659.988
Devonshire Building | 2016-09-10 07:45 | 46235.4185 | 640.008
Devonshire Building | 2016-09-10 08:00 | 46235.5835 | 659.988
Devonshire Building | 2016-09-10 08:15 | 46235.7435 | 640.008
Devonshire Building | 2016-09-10 08:30 | 46235.9035 | 640.008
Devonshire Building | 2016-09-10 08:45 | 46236.0635 | 640.008
Devonshire Building | 2016-09-10 09:00 | 46236.2285 | 659.988
Devonshire Building | 2016-09-10 09:15 | 46236.3885 | 640.008
Devonshire Building | 2016-09-10 09:30 | 46236.5485 | 640.008
Devonshire Building | 2016-09-10 09:45 | 46236.7085 | 640.008
Devonshire Building | 2016-09-10 10:00 | 46236.8735 | 659.988
Devonshire Building | 2016-09-10 10:15 | 46237.0335 | 640.008
Devonshire Building | 2016-09-10 10:30 | 46237.1935 | 640.008
Devonshire Building | 2016-09-10 10:45 | 46237.3535 | 640.008
Devonshire Building | 2016-09-10 11:00 | 46237.5185 | 659.988
Devonshire Building | 2016-09-10 11:15 | 46237.6785 | 640.008
Devonshire Building | 2016-09-10 11:30 | 46237.8435 | 659.988
Devonshire Building | 2016-09-10 11:45 | 46238.0035 | 640.008
Devonshire Building | 2016-09-10 12:00 | 46238.1685 | 659.988
Devonshire Building | 2016-09-10 12:15 | 46238.3285 | 640.008
Devonshire Building | 2016-09-10 12:30 | 46238.4935 | 659.988
Devonshire Building | 2016-09-10 12:45 | 46238.6535 | 640.008
Devonshire Building | 2016-09-10 13:00 | 46238.8185 | 659.988
Devonshire Building | 2016-09-10 13:15 | 46238.9785 | 640.008
Devonshire Building | 2016-09-10 13:30 | 46239.1435 | 659.988
Devonshire Building | 2016-09-10 13:45 | 46239.3085 | 659.988
Devonshire Building | 2016-09-10 14:00 | 46239.7135 | 1620
Devonshire Building | 2016-09-10 14:15 | 46239.8785 | 659.988
Devonshire Building | 2016-09-10 14:30 | 46240.0435 | 659.988
Devonshire Building | 2016-09-10 14:45 | 46240.2085 | 659.988
Devonshire Building | 2016-09-10 15:00 | 46240.3735 | 659.988
Devonshire Building | 2016-09-10 15:15 | 46240.5335 | 640.008
Devonshire Building | 2016-09-10 15:30 | 46240.6985 | 659.988
Devonshire Building | 2016-09-10 15:45 | 46240.8585 | 640.008
Devonshire Building | 2016-09-10 16:00 | 46241.0235 | 659.988
Devonshire Building | 2016-09-10 16:15 | 46241.1885 | 659.988
Devonshire Building | 2016-09-10 16:30 | 46241.3485 | 640.008
Devonshire Building | 2016-09-10 16:45 | 46241.5135 | 659.988
Devonshire Building | 2016-09-10 17:00 | 46241.6735 | 640.008
Devonshire Building | 2016-09-10 17:15 | 46241.8385 | 659.988
Devonshire Building | 2016-09-10 17:30 | 46242.0035 | 659.988
Devonshire Building | 2016-09-10 17:45 | 46242.1635 | 640.008
Devonshire Building | 2016-09-10 18:00 | 46242.3285 | 659.988
Devonshire Building | 2016-09-10 18:15 | 46242.4935 | 659.988
Devonshire Building | 2016-09-10 18:30 | 46242.6585 | 659.988
Devonshire Building | 2016-09-10 18:45 | 46242.8235 | 659.988
Devonshire Building | 2016-09-10 19:00 | 46242.9835 | 640.008
Devonshire Building | 2016-09-10 19:15 | 46243.1485 | 659.988
Devonshire Building | 2016-09-10 19:30 | 46243.3135 | 659.988
Devonshire Building | 2016-09-10 19:45 | 46243.4785 | 659.988
Devonshire Building | 2016-09-10 20:00 | 46243.6435 | 659.988
Devonshire Building | 2016-09-10 20:15 | 46243.8035 | 640.008
Devonshire Building | 2016-09-10 20:30 | 46243.9685 | 659.988
Devonshire Building | 2016-09-10 20:45 | 46244.1335 | 659.988
Devonshire Building | 2016-09-10 21:00 | 46244.3185 | 740.016
Devonshire Building | 2016-09-10 21:15 | 46244.4835 | 659.988
Devonshire Building | 2016-09-10 21:30 | 46244.6535 | 680.004
Devonshire Building | 2016-09-10 21:45 | 46244.8185 | 659.988
Devonshire Building | 2016-09-10 22:00 | 46244.9835 | 659.988
Devonshire Building | 2016-09-10 22:15 | 46245.1485 | 659.988
Devonshire Building | 2016-09-10 22:30 | 46245.3135 | 659.988
Devonshire Building | 2016-09-10 22:45 | 46245.4785 | 659.988
Devonshire Building | 2016-09-10 23:00 | 46245.6435 | 659.988
Devonshire Building | 2016-09-10 23:15 | 46245.8085 | 659.988
Devonshire Building | 2016-09-10 23:30 | 46245.9735 | 659.988
Devonshire Building | 2016-09-10 23:45 | 46246.1385 | 659.988 | 640.008
Devonshire Building | 2016-09-11 | 46246.3086 | 680.004
Devonshire Building | 2016-09-11 00:15 | 46246.4736 | 659.988
Devonshire Building | 2016-09-11 00:30 | 46246.6386 | 659.988
Devonshire Building | 2016-09-11 00:45 | 46246.8036 | 659.988
Devonshire Building | 2016-09-11 01:00 | 46246.9686 | 659.988
Devonshire Building | 2016-09-11 01:15 | 46247.1336 | 659.988
Devonshire Building | 2016-09-11 01:30 | 46247.2986 | 659.988
Devonshire Building | 2016-09-11 01:45 | 46247.4636 | 659.988
Devonshire Building | 2016-09-11 02:00 | 46247.6286 | 659.988
Devonshire Building | 2016-09-11 02:15 | 46247.7986 | 680.004
Devonshire Building | 2016-09-11 02:30 | 46247.9636 | 659.988
Devonshire Building | 2016-09-11 02:45 | 46248.1286 | 659.988
Devonshire Building | 2016-09-11 03:00 | 46248.2986 | 680.004
Devonshire Building | 2016-09-11 03:15 | 46248.4636 | 659.988
Devonshire Building | 2016-09-11 03:30 | 46248.6286 | 659.988
Devonshire Building | 2016-09-11 03:45 | 46248.7936 | 659.988
Devonshire Building | 2016-09-11 04:00 | 46248.9586 | 659.988
Devonshire Building | 2016-09-11 04:15 | 46249.1286 | 680.004
Devonshire Building | 2016-09-11 04:30 | 46249.2935 | 659.988
Devonshire Building | 2016-09-11 04:45 | 46249.4585 | 659.988
Devonshire Building | 2016-09-11 05:00 | 46249.6235 | 659.988
Devonshire Building | 2016-09-11 05:15 | 46249.7935 | 680.004
Devonshire Building | 2016-09-11 05:30 | 46249.9585 | 659.988
Devonshire Building | 2016-09-11 05:45 | 46250.1235 | 659.988
Devonshire Building | 2016-09-11 06:00 | 46250.2885 | 659.988
Devonshire Building | 2016-09-11 06:15 | 46250.4585 | 680.004
Devonshire Building | 2016-09-11 06:30 | 46250.6235 | 659.988
Devonshire Building | 2016-09-11 06:45 | 46250.7885 | 659.988
Devonshire Building | 2016-09-11 07:00 | 46250.9535 | 659.988
Devonshire Building | 2016-09-11 07:15 | 46251.1185 | 659.988
Devonshire Building | 2016-09-11 07:30 | 46251.2835 | 659.988
Devonshire Building | 2016-09-11 07:45 | 46251.4485 | 659.988
Devonshire Building | 2016-09-11 08:00 | 46251.6135 | 659.988
Devonshire Building | 2016-09-11 08:15 | 46252.0135 | 1599.984
Devonshire Building | 2016-09-11 08:30 | 46252.1785 | 659.988
Devonshire Building | 2016-09-11 08:45 | 46252.3435 | 659.988
Devonshire Building | 2016-09-11 09:00 | 46252.5035 | 640.008
Devonshire Building | 2016-09-11 09:15 | 46252.6685 | 659.988
Devonshire Building | 2016-09-11 09:30 | 46252.8285 | 640.008
Devonshire Building | 2016-09-11 09:45 | 46252.9935 | 659.988
Devonshire Building | 2016-09-11 10:00 | 46253.1585 | 659.988
Devonshire Building | 2016-09-11 10:15 | 46253.3185 | 640.008
Devonshire Building | 2016-09-11 10:30 | 46253.4835 | 659.988
Devonshire Building | 2016-09-11 10:45 | 46253.6485 | 659.988
Devonshire Building | 2016-09-11 11:00 | 46253.8085 | 640.008
Devonshire Building | 2016-09-11 11:15 | 46253.9735 | 659.988
Devonshire Building | 2016-09-11 11:30 | 46254.1385 | 659.988
Devonshire Building | 2016-09-11 11:45 | 46254.3035 | 659.988
Devonshire Building | 2016-09-11 12:00 | 46254.4685 | 659.988
Devonshire Building | 2016-09-11 12:15 | 46254.6335 | 659.988
Devonshire Building | 2016-09-11 12:30 | 46254.7985 | 659.988
Devonshire Building | 2016-09-11 12:45 | 46254.9635 | 659.988
Devonshire Building | 2016-09-11 13:00 | 46255.1285 | 659.988
Devonshire Building | 2016-09-11 13:15 | 46255.2935 | 659.988
Devonshire Building | 2016-09-11 13:30 | 46255.4585 | 659.988
Devonshire Building | 2016-09-11 13:45 | 46255.6235 | 659.988
Devonshire Building | 2016-09-11 14:00 | 46255.7935 | 680.004
Devonshire Building | 2016-09-11 14:15 | 46255.9585 | 659.988
Devonshire Building | 2016-09-11 14:30 | 46256.1235 | 659.988
Devonshire Building | 2016-09-11 14:45 | 46256.2885 | 659.988
Devonshire Building | 2016-09-11 15:00 | 46256.4535 | 659.988
Devonshire Building | 2016-09-11 15:15 | 46256.6235 | 680.004
Devonshire Building | 2016-09-11 15:30 | 46257.0235 | 1599.984
Devonshire Building | 2016-09-11 15:45 | 46257.1935 | 680.004
Devonshire Building | 2016-09-11 16:00 | 46257.3584 | 659.988
Devonshire Building | 2016-09-11 16:15 | 46257.5234 | 659.988
Devonshire Building | 2016-09-11 16:30 | 46257.6884 | 659.988
Devonshire Building | 2016-09-11 16:45 | 46257.8584 | 680.004
Devonshire Building | 2016-09-11 17:00 | 46258.0234 | 659.988
Devonshire Building | 2016-09-11 17:15 | 46258.1884 | 659.988
Devonshire Building | 2016-09-11 17:30 | 46258.3534 | 659.988
Devonshire Building | 2016-09-11 17:45 | 46258.5184 | 659.988
Devonshire Building | 2016-09-11 18:00 | 46258.6834 | 659.988
Devonshire Building | 2016-09-11 18:15 | 46258.8484 | 659.988
Devonshire Building | 2016-09-11 18:30 | 46259.0134 | 659.988
Devonshire Building | 2016-09-11 18:45 | 46259.1784 | 659.988
Devonshire Building | 2016-09-11 19:00 | 46259.3434 | 659.988
Devonshire Building | 2016-09-11 19:15 | 46259.5134 | 680.004
Devonshire Building | 2016-09-11 19:30 | 46259.6784 | 659.988
Devonshire Building | 2016-09-11 19:45 | 46259.8434 | 659.988
Devonshire Building | 2016-09-11 20:00 | 46260.0134 | 680.004
Devonshire Building | 2016-09-11 20:15 | 46260.1784 | 659.988
Devonshire Building | 2016-09-11 20:30 | 46260.3434 | 659.988
Devonshire Building | 2016-09-11 20:45 | 46260.5134 | 680.004
Devonshire Building | 2016-09-11 21:00 | 46260.6934 | 720
Devonshire Building | 2016-09-11 21:15 | 46260.8634 | 680.004
Devonshire Building | 2016-09-11 21:30 | 46261.0334 | 680.004
Devonshire Building | 2016-09-11 21:45 | 46261.2034 | 680.004
Devonshire Building | 2016-09-11 22:00 | 46261.3734 | 680.004
Devonshire Building | 2016-09-11 22:15 | 46261.5384 | 659.988
Devonshire Building | 2016-09-11 22:30 | 46261.7084 | 680.004
Devonshire Building | 2016-09-11 22:45 | 46261.8784 | 680.004
Devonshire Building | 2016-09-11 23:00 | 46262.0534 | 699.984
Devonshire Building | 2016-09-11 23:15 | 46262.2234 | 680.004
Devonshire Building | 2016-09-11 23:30 | 46262.3934 | 680.004
Devonshire Building | 2016-09-11 23:45 | 46262.5634 | 680.004 | 640.008
Devonshire Building | 2016-09-12 | 46262.7344 | 680.004
Devonshire Building | 2016-09-12 00:15 | 46262.9094 | 699.984
Devonshire Building | 2016-09-12 00:30 | 46263.0794 | 680.004
Devonshire Building | 2016-09-12 00:45 | 46263.2494 | 680.004
Devonshire Building | 2016-09-12 01:00 | 46263.4194 | 680.004
Devonshire Building | 2016-09-12 01:15 | 46263.5944 | 699.984
Devonshire Building | 2016-09-12 01:30 | 46263.7644 | 680.004
Devonshire Building | 2016-09-12 01:45 | 46263.9344 | 680.004
Devonshire Building | 2016-09-12 02:00 | 46264.1094 | 699.984
Devonshire Building | 2016-09-12 02:15 | 46264.2794 | 680.004
Devonshire Building | 2016-09-12 02:30 | 46264.4494 | 680.004
Devonshire Building | 2016-09-12 02:45 | 46264.6244 | 699.984
Devonshire Building | 2016-09-12 03:00 | 46264.7944 | 680.004
Devonshire Building | 2016-09-12 03:15 | 46264.9644 | 680.004
Devonshire Building | 2016-09-12 03:30 | 46265.1344 | 680.004
Devonshire Building | 2016-09-12 03:45 | 46265.3044 | 680.004
Devonshire Building | 2016-09-12 04:00 | 46265.4744 | 680.004
Devonshire Building | 2016-09-12 04:15 | 46265.6494 | 699.984
Devonshire Building | 2016-09-12 04:30 | 46265.8194 | 680.004
Devonshire Building | 2016-09-12 04:45 | 46265.9894 | 680.004
Devonshire Building | 2016-09-12 05:00 | 46266.1594 | 680.004
Devonshire Building | 2016-09-12 05:15 | 46266.3294 | 680.004
Devonshire Building | 2016-09-12 05:30 | 46266.4994 | 680.004
Devonshire Building | 2016-09-12 05:45 | 46266.6694 | 680.004
Devonshire Building | 2016-09-12 06:00 | 46266.8394 | 680.004
Devonshire Building | 2016-09-12 06:15 | 46267.0094 | 680.004
Devonshire Building | 2016-09-12 06:30 | 46267.1744 | 659.988
Devonshire Building | 2016-09-12 06:45 | 46267.3644 | 759.996
Devonshire Building | 2016-09-12 07:00 | 46267.5444 | 720
Devonshire Building | 2016-09-12 07:15 | 46267.7094 | 659.988
Devonshire Building | 2016-09-12 07:30 | 46267.8844 | 699.984
Devonshire Building | 2016-09-12 07:45 | 46268.3094 | 1699.992
Devonshire Building | 2016-09-12 08:00 | 46268.5094 | 799.992
Devonshire Building | 2016-09-12 08:15 | 46268.7294 | 879.984
Devonshire Building | 2016-09-12 08:30 | 46268.9494 | 879.984
Devonshire Building | 2016-09-12 08:45 | 46269.1794 | 920.016
Devonshire Building | 2016-09-12 09:00 | 46269.4094 | 920.016
Devonshire Building | 2016-09-12 09:15 | 46269.6394 | 920.016
Devonshire Building | 2016-09-12 09:30 | 46269.8644 | 900
Devonshire Building | 2016-09-12 09:45 | 46270.3794 | 2059.992
Devonshire Building | 2016-09-12 10:00 | 46270.6044 | 900
Devonshire Building | 2016-09-12 10:15 | 46270.8394 | 939.996
Devonshire Building | 2016-09-12 10:30 | 46271.0694 | 920.016
Devonshire Building | 2016-09-12 10:45 | 46271.2994 | 920.016
Devonshire Building | 2016-09-12 11:00 | 46271.7944 | 1980
Devonshire Building | 2016-09-12 11:15 | 46272.0794 | 1140.012
Devonshire Building | 2016-09-12 11:30 | 46272.3644 | 1140.012
Devonshire Building | 2016-09-12 11:45 | 46272.6494 | 1140.012
Devonshire Building | 2016-09-12 12:00 | 46272.9144 | 1059.984
Devonshire Building | 2016-09-12 12:15 | 46273.1794 | 1059.984
Devonshire Building | 2016-09-12 12:30 | 46273.4194 | 960.012
Devonshire Building | 2016-09-12 12:45 | 46273.8994 | 1919.988
Devonshire Building | 2016-09-12 13:00 | 46274.1044 | 820.008
Devonshire Building | 2016-09-12 13:15 | 46274.3094 | 820.008
Devonshire Building | 2016-09-12 13:30 | 46274.5144 | 820.008
Devonshire Building | 2016-09-12 13:45 | 46274.7194 | 820.008
Devonshire Building | 2016-09-12 14:00 | 46274.9244 | 820.008
Devonshire Building | 2016-09-12 14:15 | 46275.1244 | 799.992
Devonshire Building | 2016-09-12 14:30 | 46275.3444 | 879.984
Devonshire Building | 2016-09-12 14:45 | 46275.5544 | 839.988
Devonshire Building | 2016-09-12 15:00 | 46275.9744 | 1680.012
Devonshire Building | 2016-09-12 15:15 | 46276.2744 | 1199.988
Devonshire Building | 2016-09-12 15:30 | 46276.5144 | 960.012
Devonshire Building | 2016-09-12 15:45 | 46276.7694 | 1019.988
Devonshire Building | 2016-09-12 16:00 | 46277.0194 | 1000.008
Devonshire Building | 2016-09-12 16:15 | 46277.2744 | 1019.988
Devonshire Building | 2016-09-12 16:30 | 46277.5294 | 1019.988
Devonshire Building | 2016-09-12 16:45 | 46277.7694 | 960.012
Devonshire Building | 2016-09-12 17:00 | 46277.9944 | 900
Devonshire Building | 2016-09-12 17:15 | 46278.4394 | 1779.984
Devonshire Building | 2016-09-12 17:30 | 46278.6294 | 759.996
Devonshire Building | 2016-09-12 17:45 | 46278.8144 | 740.016
Devonshire Building | 2016-09-12 18:00 | 46279.0044 | 759.996
Devonshire Building | 2016-09-12 18:15 | 46279.1894 | 740.016
Devonshire Building | 2016-09-12 18:30 | 46279.3744 | 740.016
Devonshire Building | 2016-09-12 18:45 | 46279.5544 | 720
Devonshire Building | 2016-09-12 19:00 | 46279.7394 | 740.016
Devonshire Building | 2016-09-12 19:15 | 46279.9144 | 699.984
Devonshire Building | 2016-09-12 19:30 | 46280.0944 | 720
Devonshire Building | 2016-09-12 19:45 | 46280.2694 | 699.984
Devonshire Building | 2016-09-12 20:00 | 46280.4494 | 720
Devonshire Building | 2016-09-12 20:15 | 46280.6244 | 699.984
Devonshire Building | 2016-09-12 20:30 | 46280.7994 | 699.984
Devonshire Building | 2016-09-12 20:45 | 46280.9744 | 699.984
Devonshire Building | 2016-09-12 21:00 | 46281.1644 | 759.996
Devonshire Building | 2016-09-12 21:15 | 46281.3344 | 680.004
Devonshire Building | 2016-09-12 21:30 | 46281.5044 | 680.004
Devonshire Building | 2016-09-12 21:45 | 46281.6744 | 680.004
Devonshire Building | 2016-09-12 22:00 | 46281.8444 | 680.004
Devonshire Building | 2016-09-12 22:15 | 46282.0194 | 699.984
Devonshire Building | 2016-09-12 22:30 | 46282.1894 | 680.004
Devonshire Building | 2016-09-12 22:45 | 46282.3594 | 680.004
Devonshire Building | 2016-09-12 23:00 | 46282.5294 | 680.004
Devonshire Building | 2016-09-12 23:15 | 46282.7044 | 699.984
Devonshire Building | 2016-09-12 23:30 | 46282.8744 | 680.004
Devonshire Building | 2016-09-12 23:45 | 46283.0494 | 699.984 | 659.988
Devonshire Building | 2016-09-13 | 46283.2188 | 680.004
Devonshire Building | 2016-09-13 00:15 | 46283.3888 | 680.004
Devonshire Building | 2016-09-13 00:30 | 46283.5637 | 699.984
Devonshire Building | 2016-09-13 00:45 | 46283.7337 | 680.004
Devonshire Building | 2016-09-13 01:00 | 46283.9037 | 680.004
Devonshire Building | 2016-09-13 01:15 | 46284.0787 | 699.984
Devonshire Building | 2016-09-13 01:30 | 46284.2487 | 680.004
Devonshire Building | 2016-09-13 01:45 | 46284.4187 | 680.004
Devonshire Building | 2016-09-13 02:00 | 46284.5937 | 699.984
Devonshire Building | 2016-09-13 02:15 | 46284.7637 | 680.004
Devonshire Building | 2016-09-13 02:30 | 46284.9387 | 699.984
Devonshire Building | 2016-09-13 02:45 | 46285.1087 | 680.004
Devonshire Building | 2016-09-13 03:00 | 46285.2787 | 680.004
Devonshire Building | 2016-09-13 03:15 | 46285.4537 | 699.984
Devonshire Building | 2016-09-13 03:30 | 46285.6237 | 680.004
Devonshire Building | 2016-09-13 03:45 | 46285.7987 | 699.984
Devonshire Building | 2016-09-13 04:00 | 46285.9687 | 680.004
Devonshire Building | 2016-09-13 04:15 | 46286.1437 | 699.984
Devonshire Building | 2016-09-13 04:30 | 46286.3137 | 680.004
Devonshire Building | 2016-09-13 04:45 | 46286.4837 | 680.004
Devonshire Building | 2016-09-13 05:00 | 46286.6587 | 699.984
Devonshire Building | 2016-09-13 05:15 | 46286.8287 | 680.004
Devonshire Building | 2016-09-13 05:30 | 46287.0037 | 699.984
Devonshire Building | 2016-09-13 05:45 | 46287.1737 | 680.004
Devonshire Building | 2016-09-13 06:00 | 46287.3437 | 680.004
Devonshire Building | 2016-09-13 06:15 | 46287.5137 | 680.004
Devonshire Building | 2016-09-13 06:30 | 46287.7037 | 759.996
Devonshire Building | 2016-09-13 06:45 | 46287.8787 | 699.984
Devonshire Building | 2016-09-13 07:00 | 46288.0537 | 699.984
Devonshire Building | 2016-09-13 07:15 | 46288.2237 | 680.004
Devonshire Building | 2016-09-13 07:30 | 46288.3987 | 699.984
Devonshire Building | 2016-09-13 07:45 | 46288.5787 | 720
Devonshire Building | 2016-09-13 08:00 | 46288.7587 | 720
Devonshire Building | 2016-09-13 08:15 | 46289.1937 | 1739.988
Devonshire Building | 2016-09-13 08:30 | 46289.4037 | 839.988
Devonshire Building | 2016-09-13 08:45 | 46289.6287 | 900
Devonshire Building | 2016-09-13 09:00 | 46289.8737 | 979.992
Devonshire Building | 2016-09-13 09:15 | 46290.1137 | 960.012
Devonshire Building | 2016-09-13 09:30 | 46290.3487 | 939.996
Devonshire Building | 2016-09-13 09:45 | 46290.8337 | 1940.004
Devonshire Building | 2016-09-13 10:00 | 46291.0487 | 860.004
Devonshire Building | 2016-09-13 10:15 | 46291.2687 | 879.984
Devonshire Building | 2016-09-13 10:30 | 46291.4837 | 860.004
Devonshire Building | 2016-09-13 10:45 | 46291.6937 | 839.988
Devonshire Building | 2016-09-13 11:00 | 46291.9087 | 860.004
Devonshire Building | 2016-09-13 11:15 | 46292.2387 | 1320.012
Devonshire Building | 2016-09-13 11:30 | 46292.5937 | 1419.984
Devonshire Building | 2016-09-13 11:45 | 46292.8037 | 839.988
Devonshire Building | 2016-09-13 12:00 | 46293.0137 | 839.988
Devonshire Building | 2016-09-13 12:15 | 46293.2187 | 820.008
Devonshire Building | 2016-09-13 12:30 | 46293.4187 | 799.992
Devonshire Building | 2016-09-13 12:45 | 46293.6187 | 799.992
Devonshire Building | 2016-09-13 13:00 | 46293.8137 | 780.012
Devonshire Building | 2016-09-13 13:15 | 46294.2537 | 1760.004
Devonshire Building | 2016-09-13 13:30 | 46294.4487 | 780.012
Devonshire Building | 2016-09-13 13:45 | 46294.6487 | 799.992
Devonshire Building | 2016-09-13 14:00 | 46294.8487 | 799.992
Devonshire Building | 2016-09-13 14:15 | 46295.0687 | 879.984
Devonshire Building | 2016-09-13 14:30 | 46295.2987 | 920.016
Devonshire Building | 2016-09-13 14:45 | 46295.5237 | 900
Devonshire Building | 2016-09-13 15:00 | 46295.9837 | 1839.996
Devonshire Building | 2016-09-13 15:15 | 46296.1987 | 860.004
Devonshire Building | 2016-09-13 15:30 | 46296.4087 | 839.988
Devonshire Building | 2016-09-13 15:45 | 46296.6187 | 839.988
Devonshire Building | 2016-09-13 16:00 | 46296.8237 | 820.008
Devonshire Building | 2016-09-13 16:15 | 46297.0187 | 780.012
Devonshire Building | 2016-09-13 16:30 | 46297.2087 | 759.996
Devonshire Building | 2016-09-13 16:45 | 46297.3987 | 759.996
Devonshire Building | 2016-09-13 17:00 | 46297.5887 | 759.996
Devonshire Building | 2016-09-13 17:15 | 46297.7687 | 720
Devonshire Building | 2016-09-13 17:30 | 46298.1887 | 1680.012
Devonshire Building | 2016-09-13 17:45 | 46298.3587 | 680.004
Devonshire Building | 2016-09-13 18:00 | 46298.5337 | 699.984
Devonshire Building | 2016-09-13 18:15 | 46298.7087 | 699.984
Devonshire Building | 2016-09-13 18:30 | 46298.8837 | 699.984
Devonshire Building | 2016-09-13 18:45 | 46299.0537 | 680.004
Devonshire Building | 2016-09-13 19:00 | 46299.2287 | 699.984
Devonshire Building | 2016-09-13 19:15 | 46299.4037 | 699.984
Devonshire Building | 2016-09-13 19:30 | 46299.5787 | 699.984
Devonshire Building | 2016-09-13 19:45 | 46299.7537 | 699.984
Devonshire Building | 2016-09-13 20:00 | 46299.9287 | 699.984
Devonshire Building | 2016-09-13 20:15 | 46300.0987 | 680.004
Devonshire Building | 2016-09-13 20:30 | 46300.2737 | 699.984
Devonshire Building | 2016-09-13 20:45 | 46300.4487 | 699.984
Devonshire Building | 2016-09-13 21:00 | 46300.6387 | 759.996
Devonshire Building | 2016-09-13 21:15 | 46300.8137 | 699.984
Devonshire Building | 2016-09-13 21:30 | 46300.9887 | 699.984
Devonshire Building | 2016-09-13 21:45 | 46301.1637 | 699.984
Devonshire Building | 2016-09-13 22:00 | 46301.3386 | 699.984
Devonshire Building | 2016-09-13 22:15 | 46301.5136 | 699.984
Devonshire Building | 2016-09-13 22:30 | 46301.6886 | 699.984
Devonshire Building | 2016-09-13 22:45 | 46301.8636 | 699.984
Devonshire Building | 2016-09-13 23:00 | 46302.0386 | 699.984
Devonshire Building | 2016-09-13 23:15 | 46302.2136 | 699.984
Devonshire Building | 2016-09-13 23:30 | 46302.3886 | 699.984
Devonshire Building | 2016-09-13 23:45 | 46302.5636 | 699.984 | 680.004
Devonshire Building | 2016-09-14 | 46302.7383 | 699.984
Devonshire Building | 2016-09-14 00:15 | 46302.9133 | 699.984
Devonshire Building | 2016-09-14 00:30 | 46303.0883 | 699.984
Devonshire Building | 2016-09-14 00:45 | 46303.2633 | 699.984
Devonshire Building | 2016-09-14 01:00 | 46303.4383 | 699.984
Devonshire Building | 2016-09-14 01:15 | 46303.6133 | 699.984
Devonshire Building | 2016-09-14 01:30 | 46303.7883 | 699.984
Devonshire Building | 2016-09-14 01:45 | 46303.9633 | 699.984
Devonshire Building | 2016-09-14 02:00 | 46304.1382 | 699.984
Devonshire Building | 2016-09-14 02:15 | 46304.3132 | 699.984
Devonshire Building | 2016-09-14 02:30 | 46304.4882 | 699.984
Devonshire Building | 2016-09-14 02:45 | 46304.6632 | 699.984
Devonshire Building | 2016-09-14 03:00 | 46304.8382 | 699.984
Devonshire Building | 2016-09-14 03:15 | 46305.0132 | 699.984
Devonshire Building | 2016-09-14 03:30 | 46305.1882 | 699.984
Devonshire Building | 2016-09-14 03:45 | 46305.3632 | 699.984
Devonshire Building | 2016-09-14 04:00 | 46305.5382 | 699.984
Devonshire Building | 2016-09-14 04:15 | 46305.7132 | 699.984
Devonshire Building | 2016-09-14 04:30 | 46305.8882 | 699.984
Devonshire Building | 2016-09-14 04:45 | 46306.0632 | 699.984
Devonshire Building | 2016-09-14 05:00 | 46306.2332 | 680.004
Devonshire Building | 2016-09-14 05:15 | 46306.4082 | 699.984
Devonshire Building | 2016-09-14 05:30 | 46306.5832 | 699.984
Devonshire Building | 2016-09-14 05:45 | 46306.7582 | 699.984
Devonshire Building | 2016-09-14 06:00 | 46306.9282 | 680.004
Devonshire Building | 2016-09-14 06:15 | 46307.1032 | 699.984
Devonshire Building | 2016-09-14 06:30 | 46307.2782 | 699.984
Devonshire Building | 2016-09-14 06:45 | 46307.4482 | 680.004
Devonshire Building | 2016-09-14 07:00 | 46307.6382 | 759.996
Devonshire Building | 2016-09-14 07:15 | 46307.8132 | 699.984
Devonshire Building | 2016-09-14 07:30 | 46307.9882 | 699.984
Devonshire Building | 2016-09-14 07:45 | 46308.1682 | 720
Devonshire Building | 2016-09-14 08:00 | 46308.5982 | 1720.008
Devonshire Building | 2016-09-14 08:15 | 46308.7932 | 780.012
Devonshire Building | 2016-09-14 08:30 | 46308.9832 | 759.996
Devonshire Building | 2016-09-14 08:45 | 46309.1682 | 740.016
Devonshire Building | 2016-09-14 09:00 | 46309.3582 | 759.996
Devonshire Building | 2016-09-14 09:15 | 46309.5632 | 820.008
Devonshire Building | 2016-09-14 09:30 | 46310.0532 | 1959.984
Devonshire Building | 2016-09-14 09:45 | 46310.3032 | 1000.008
Devonshire Building | 2016-09-14 10:00 | 46310.5682 | 1059.984
Devonshire Building | 2016-09-14 10:15 | 46310.8682 | 1199.988
Devonshire Building | 2016-09-14 10:30 | 46311.1832 | 1260
Devonshire Building | 2016-09-14 10:45 | 46311.4582 | 1100.016
Devonshire Building | 2016-09-14 11:00 | 46311.8132 | 1419.984
Devonshire Building | 2016-09-14 11:15 | 46312.1832 | 1479.996
Devonshire Building | 2016-09-14 11:30 | 46312.3932 | 839.988
Devonshire Building | 2016-09-14 11:45 | 46312.6032 | 839.988
Devonshire Building | 2016-09-14 12:00 | 46312.8382 | 939.996
Devonshire Building | 2016-09-14 12:15 | 46313.0482 | 839.988
Devonshire Building | 2016-09-14 12:30 | 46313.5282 | 1919.988
Devonshire Building | 2016-09-14 12:45 | 46313.7482 | 879.984
Devonshire Building | 2016-09-14 13:00 | 46313.9732 | 900
Devonshire Building | 2016-09-14 13:15 | 46314.1882 | 860.004
Devonshire Building | 2016-09-14 13:30 | 46314.4132 | 900
Devonshire Building | 2016-09-14 13:45 | 46314.6282 | 860.004
Devonshire Building | 2016-09-14 14:00 | 46315.0932 | 1860.012
Devonshire Building | 2016-09-14 14:15 | 46315.3182 | 900
Devonshire Building | 2016-09-14 14:30 | 46315.5382 | 879.984
Devonshire Building | 2016-09-14 14:45 | 46315.7582 | 879.984
Devonshire Building | 2016-09-14 15:00 | 46316.0132 | 1019.988
Devonshire Building | 2016-09-14 15:15 | 46316.3632 | 1400.004
Devonshire Building | 2016-09-14 15:30 | 46316.6932 | 1320.012
Devonshire Building | 2016-09-14 15:45 | 46317.2182 | 2099.988
Devonshire Building | 2016-09-14 16:00 | 46317.4782 | 1040.004
Devonshire Building | 2016-09-14 16:15 | 46317.7482 | 1080
Devonshire Building | 2016-09-14 16:30 | 46318.0132 | 1059.984
Devonshire Building | 2016-09-14 16:45 | 46318.2732 | 1040.004
Devonshire Building | 2016-09-14 17:00 | 46318.5132 | 960.012
Devonshire Building | 2016-09-14 17:15 | 46318.7282 | 860.004
Devonshire Building | 2016-09-14 17:30 | 46318.9332 | 820.008
Devonshire Building | 2016-09-14 17:45 | 46319.1232 | 759.996
Devonshire Building | 2016-09-14 18:00 | 46319.3132 | 759.996
Devonshire Building | 2016-09-14 18:15 | 46319.4932 | 720
Devonshire Building | 2016-09-14 18:30 | 46319.6732 | 720
Devonshire Building | 2016-09-14 18:45 | 46319.8532 | 720
Devonshire Building | 2016-09-14 19:00 | 46320.0282 | 699.984
Devonshire Building | 2016-09-14 19:15 | 46320.2031 | 699.984
Devonshire Building | 2016-09-14 19:30 | 46320.3781 | 699.984
Devonshire Building | 2016-09-14 19:45 | 46320.5531 | 699.984
Devonshire Building | 2016-09-14 20:00 | 46320.7281 | 699.984
Devonshire Building | 2016-09-14 20:15 | 46320.8981 | 680.004
Devonshire Building | 2016-09-14 20:30 | 46321.0681 | 680.004
Devonshire Building | 2016-09-14 20:45 | 46321.2431 | 699.984
Devonshire Building | 2016-09-14 21:00 | 46321.4331 | 759.996
Devonshire Building | 2016-09-14 21:15 | 46321.6031 | 680.004
Devonshire Building | 2016-09-14 21:30 | 46321.7731 | 680.004
Devonshire Building | 2016-09-14 21:45 | 46321.9381 | 659.988
Devonshire Building | 2016-09-14 22:00 | 46322.1081 | 680.004
Devonshire Building | 2016-09-14 22:15 | 46322.2781 | 680.004
Devonshire Building | 2016-09-14 22:30 | 46322.4481 | 680.004
Devonshire Building | 2016-09-14 22:45 | 46322.6131 | 659.988
Devonshire Building | 2016-09-14 23:00 | 46322.7831 | 680.004
Devonshire Building | 2016-09-14 23:15 | 46322.9531 | 680.004
Devonshire Building | 2016-09-14 23:30 | 46323.1231 | 680.004
Devonshire Building | 2016-09-14 23:45 | 46323.2931 | 680.004 | 659.988
Devonshire Building | 2016-09-15 | 46323.4688 | 699.984
Devonshire Building | 2016-09-15 00:15 | 46323.6388 | 680.004
Devonshire Building | 2016-09-15 00:30 | 46323.8088 | 680.004
Devonshire Building | 2016-09-15 00:45 | 46323.9837 | 699.984
Devonshire Building | 2016-09-15 01:00 | 46324.1537 | 680.004
Devonshire Building | 2016-09-15 01:15 | 46324.3287 | 699.984
Devonshire Building | 2016-09-15 01:30 | 46324.4987 | 680.004
Devonshire Building | 2016-09-15 01:45 | 46324.6737 | 699.984
Devonshire Building | 2016-09-15 02:00 | 46324.8437 | 680.004
Devonshire Building | 2016-09-15 02:15 | 46325.0187 | 699.984
Devonshire Building | 2016-09-15 02:30 | 46325.1887 | 680.004
Devonshire Building | 2016-09-15 02:45 | 46325.3587 | 680.004
Devonshire Building | 2016-09-15 03:00 | 46325.5337 | 699.984
Devonshire Building | 2016-09-15 03:15 | 46325.7037 | 680.004
Devonshire Building | 2016-09-15 03:30 | 46325.8737 | 680.004
Devonshire Building | 2016-09-15 03:45 | 46326.0487 | 699.984
Devonshire Building | 2016-09-15 04:00 | 46326.2187 | 680.004
Devonshire Building | 2016-09-15 04:15 | 46326.3887 | 680.004
Devonshire Building | 2016-09-15 04:30 | 46326.5537 | 659.988
Devonshire Building | 2016-09-15 04:45 | 46326.7237 | 680.004
Devonshire Building | 2016-09-15 05:00 | 46326.8937 | 680.004
Devonshire Building | 2016-09-15 05:15 | 46327.0637 | 680.004
Devonshire Building | 2016-09-15 05:30 | 46327.2337 | 680.004
Devonshire Building | 2016-09-15 05:45 | 46327.6387 | 1620
Devonshire Building | 2016-09-15 06:00 | 46327.8087 | 680.004
Devonshire Building | 2016-09-15 06:15 | 46327.9787 | 680.004
Devonshire Building | 2016-09-15 06:30 | 46328.1437 | 659.988
Devonshire Building | 2016-09-15 06:45 | 46328.3137 | 680.004
Devonshire Building | 2016-09-15 07:00 | 46328.4787 | 659.988
Devonshire Building | 2016-09-15 07:15 | 46328.6487 | 680.004
Devonshire Building | 2016-09-15 07:30 | 46328.8187 | 680.004
Devonshire Building | 2016-09-15 07:45 | 46328.9937 | 699.984
Devonshire Building | 2016-09-15 08:00 | 46329.1637 | 680.004
Devonshire Building | 2016-09-15 08:15 | 46329.3337 | 680.004
Devonshire Building | 2016-09-15 08:30 | 46329.5087 | 699.984
Devonshire Building | 2016-09-15 08:45 | 46329.6787 | 680.004
Devonshire Building | 2016-09-15 09:00 | 46330.1237 | 1779.984
Devonshire Building | 2016-09-15 09:15 | 46330.3937 | 1080
Devonshire Building | 2016-09-15 09:30 | 46330.6887 | 1180.008
Devonshire Building | 2016-09-15 09:45 | 46330.9687 | 1119.996
Devonshire Building | 2016-09-15 10:00 | 46331.2437 | 1100.016
Devonshire Building | 2016-09-15 10:15 | 46331.7437 | 2000.016
Devonshire Building | 2016-09-15 10:30 | 46331.9937 | 1000.008
Devonshire Building | 2016-09-15 10:45 | 46332.2237 | 920.016
Devonshire Building | 2016-09-15 11:00 | 46332.4437 | 879.984
Devonshire Building | 2016-09-15 11:15 | 46332.6587 | 860.004
Devonshire Building | 2016-09-15 11:30 | 46332.8687 | 839.988
Devonshire Building | 2016-09-15 11:45 | 46333.2987 | 1720.008
Devonshire Building | 2016-09-15 12:00 | 46333.4787 | 720
Devonshire Building | 2016-09-15 12:15 | 46333.6587 | 720
Devonshire Building | 2016-09-15 12:30 | 46333.8387 | 720
Devonshire Building | 2016-09-15 12:45 | 46334.0237 | 740.016
Devonshire Building | 2016-09-15 13:00 | 46334.2137 | 759.996
Devonshire Building | 2016-09-15 13:15 | 46334.4137 | 799.992
Devonshire Building | 2016-09-15 13:30 | 46334.9087 | 1980
Devonshire Building | 2016-09-15 13:45 | 46335.1387 | 920.016
Devonshire Building | 2016-09-15 14:00 | 46335.3687 | 920.016
Devonshire Building | 2016-09-15 14:15 | 46335.6188 | 1000.008
Devonshire Building | 2016-09-15 14:30 | 46335.8488 | 920.016
Devonshire Building | 2016-09-15 14:45 | 46336.0788 | 920.016
Devonshire Building | 2016-09-15 15:00 | 46336.5588 | 1919.988
Devonshire Building | 2016-09-15 15:15 | 46336.7738 | 860.004
Devonshire Building | 2016-09-15 15:30 | 46336.9888 | 860.004
Devonshire Building | 2016-09-15 15:45 | 46337.2038 | 860.004
Devonshire Building | 2016-09-15 16:00 | 46337.4188 | 860.004
Devonshire Building | 2016-09-15 16:15 | 46337.6338 | 860.004
Devonshire Building | 2016-09-15 16:30 | 46337.8438 | 839.988
Devonshire Building | 2016-09-15 16:45 | 46338.0638 | 879.984
Devonshire Building | 2016-09-15 17:00 | 46338.2788 | 860.004
Devonshire Building | 2016-09-15 17:15 | 46338.4838 | 820.008
Devonshire Building | 2016-09-15 17:30 | 46338.6838 | 799.992
Devonshire Building | 2016-09-15 17:45 | 46338.8788 | 780.012
Devonshire Building | 2016-09-15 18:00 | 46339.0638 | 740.016
Devonshire Building | 2016-09-15 18:15 | 46339.2488 | 740.016
Devonshire Building | 2016-09-15 18:30 | 46339.4288 | 720
Devonshire Building | 2016-09-15 18:45 | 46339.6088 | 720
Devonshire Building | 2016-09-15 19:00 | 46339.7838 | 699.984
Devonshire Building | 2016-09-15 19:15 | 46340.1938 | 1640.016
Devonshire Building | 2016-09-15 19:30 | 46340.3588 | 659.988
Devonshire Building | 2016-09-15 19:45 | 46340.5238 | 659.988
Devonshire Building | 2016-09-15 20:00 | 46340.6938 | 680.004
Devonshire Building | 2016-09-15 20:15 | 46340.8588 | 659.988
Devonshire Building | 2016-09-15 20:30 | 46341.0238 | 659.988
Devonshire Building | 2016-09-15 20:45 | 46341.1888 | 659.988
Devonshire Building | 2016-09-15 21:00 | 46341.3688 | 720
Devonshire Building | 2016-09-15 21:15 | 46341.5337 | 659.988
Devonshire Building | 2016-09-15 21:30 | 46341.6987 | 659.988
Devonshire Building | 2016-09-15 21:45 | 46341.8637 | 659.988
Devonshire Building | 2016-09-15 22:00 | 46342.0287 | 659.988
Devonshire Building | 2016-09-15 22:15 | 46342.1937 | 659.988
Devonshire Building | 2016-09-15 22:30 | 46342.3587 | 659.988
Devonshire Building | 2016-09-15 22:45 | 46342.5237 | 659.988
Devonshire Building | 2016-09-15 23:00 | 46342.6887 | 659.988
Devonshire Building | 2016-09-15 23:15 | 46342.8587 | 680.004
Devonshire Building | 2016-09-15 23:30 | 46343.0237 | 659.988
Devonshire Building | 2016-09-15 23:45 | 46343.1887 | 659.988 | 659.988
Devonshire Building | 2016-09-16 | 46343.3555 | 659.988
Devonshire Building | 2016-09-16 00:15 | 46343.5255 | 680.004
Devonshire Building | 2016-09-16 00:30 | 46343.6955 | 680.004
Devonshire Building | 2016-09-16 00:45 | 46343.8605 | 659.988
Devonshire Building | 2016-09-16 01:00 | 46344.0305 | 680.004
Devonshire Building | 2016-09-16 01:15 | 46344.2005 | 680.004
Devonshire Building | 2016-09-16 01:30 | 46344.3655 | 659.988
Devonshire Building | 2016-09-16 01:45 | 46344.5355 | 680.004
Devonshire Building | 2016-09-16 02:00 | 46344.7055 | 680.004
Devonshire Building | 2016-09-16 02:15 | 46344.8705 | 659.988
Devonshire Building | 2016-09-16 02:30 | 46345.0405 | 680.004
Devonshire Building | 2016-09-16 02:45 | 46345.2105 | 680.004
Devonshire Building | 2016-09-16 03:00 | 46345.3805 | 680.004
Devonshire Building | 2016-09-16 03:15 | 46345.5505 | 680.004
Devonshire Building | 2016-09-16 03:30 | 46345.7205 | 680.004
Devonshire Building | 2016-09-16 03:45 | 46345.8855 | 659.988
Devonshire Building | 2016-09-16 04:00 | 46346.0555 | 680.004
Devonshire Building | 2016-09-16 04:15 | 46346.2255 | 680.004
Devonshire Building | 2016-09-16 04:30 | 46346.3955 | 680.004
Devonshire Building | 2016-09-16 04:45 | 46346.5605 | 659.988
Devonshire Building | 2016-09-16 05:00 | 46346.7305 | 680.004
Devonshire Building | 2016-09-16 05:15 | 46346.9005 | 680.004
Devonshire Building | 2016-09-16 05:30 | 46347.0655 | 659.988
Devonshire Building | 2016-09-16 05:45 | 46347.2355 | 680.004
Devonshire Building | 2016-09-16 06:00 | 46347.4005 | 659.988
Devonshire Building | 2016-09-16 06:15 | 46347.5705 | 680.004
Devonshire Building | 2016-09-16 06:30 | 46347.7355 | 659.988
Devonshire Building | 2016-09-16 06:45 | 46347.9005 | 659.988
Devonshire Building | 2016-09-16 07:00 | 46348.0705 | 680.004
Devonshire Building | 2016-09-16 07:15 | 46348.2455 | 699.984
Devonshire Building | 2016-09-16 07:30 | 46348.4155 | 680.004
Devonshire Building | 2016-09-16 07:45 | 46348.5955 | 720
Devonshire Building | 2016-09-16 08:00 | 46348.7705 | 699.984
Devonshire Building | 2016-09-16 08:15 | 46349.0505 | 1119.996
Devonshire Building | 2016-09-16 08:30 | 46349.3855 | 1339.992
Devonshire Building | 2016-09-16 08:45 | 46349.5905 | 820.008
Devonshire Building | 2016-09-16 09:00 | 46349.8755 | 1140.012
Devonshire Building | 2016-09-16 09:15 | 46350.1955 | 1280.016
Devonshire Building | 2016-09-16 09:30 | 46350.4855 | 1159.992
Devonshire Building | 2016-09-16 09:45 | 46350.8005 | 1260
Devonshire Building | 2016-09-16 10:00 | 46351.3955 | 2379.996
Devonshire Building | 2016-09-16 10:15 | 46351.6805 | 1140.012
Devonshire Building | 2016-09-16 10:30 | 46351.9355 | 1019.988
Devonshire Building | 2016-09-16 10:45 | 46352.1705 | 939.996
Devonshire Building | 2016-09-16 11:00 | 46352.3955 | 900
Devonshire Building | 2016-09-16 11:15 | 46352.6205 | 900
Devonshire Building | 2016-09-16 11:30 | 46352.8405 | 879.984
Devonshire Building | 2016-09-16 11:45 | 46353.3005 | 1839.996
Devonshire Building | 2016-09-16 12:00 | 46353.4855 | 740.016
Devonshire Building | 2016-09-16 12:15 | 46353.6755 | 759.996
Devonshire Building | 2016-09-16 12:30 | 46353.8805 | 820.008
Devonshire Building | 2016-09-16 12:45 | 46354.1255 | 979.992
Devonshire Building | 2016-09-16 13:00 | 46354.3755 | 1000.008
Devonshire Building | 2016-09-16 13:15 | 46354.6255 | 1000.008
Devonshire Building | 2016-09-16 13:30 | 46355.0155 | 1559.988
Devonshire Building | 2016-09-16 13:45 | 46355.3655 | 1400.004
Devonshire Building | 2016-09-16 14:00 | 46355.5855 | 879.984
Devonshire Building | 2016-09-16 14:15 | 46355.8105 | 900
Devonshire Building | 2016-09-16 14:30 | 46356.0255 | 860.004
Devonshire Building | 2016-09-16 14:45 | 46356.2455 | 879.984
Devonshire Building | 2016-09-16 15:00 | 46356.4605 | 860.004
Devonshire Building | 2016-09-16 15:15 | 46356.6755 | 860.004
Devonshire Building | 2016-09-16 15:30 | 46357.1654 | 1959.984
Devonshire Building | 2016-09-16 15:45 | 46357.3904 | 900
Devonshire Building | 2016-09-16 16:00 | 46357.6254 | 939.996
Devonshire Building | 2016-09-16 16:15 | 46357.8504 | 900
Devonshire Building | 2016-09-16 16:30 | 46358.0654 | 860.004
Devonshire Building | 2016-09-16 16:45 | 46358.2754 | 839.988
Devonshire Building | 2016-09-16 17:00 | 46358.4804 | 820.008
Devonshire Building | 2016-09-16 17:15 | 46358.6755 | 780.012
Devonshire Building | 2016-09-16 17:30 | 46358.8654 | 759.996
Devonshire Building | 2016-09-16 17:45 | 46359.0505 | 740.016
Devonshire Building | 2016-09-16 18:00 | 46359.2305 | 720
Devonshire Building | 2016-09-16 18:15 | 46359.4105 | 720
Devonshire Building | 2016-09-16 18:30 | 46359.5905 | 720
Devonshire Building | 2016-09-16 18:45 | 46359.7654 | 699.984
Devonshire Building | 2016-09-16 19:00 | 46359.9404 | 699.984
Devonshire Building | 2016-09-16 19:15 | 46360.1154 | 699.984
Devonshire Building | 2016-09-16 19:30 | 46360.2854 | 680.004
Devonshire Building | 2016-09-16 19:45 | 46360.4604 | 699.984
Devonshire Building | 2016-09-16 20:00 | 46360.6304 | 680.004
Devonshire Building | 2016-09-16 20:15 | 46360.8004 | 680.004
Devonshire Building | 2016-09-16 20:30 | 46360.9754 | 699.984
Devonshire Building | 2016-09-16 20:45 | 46361.1454 | 680.004
Devonshire Building | 2016-09-16 21:00 | 46361.3404 | 780.012
Devonshire Building | 2016-09-16 21:15 | 46361.5054 | 659.988
Devonshire Building | 2016-09-16 21:30 | 46361.6704 | 659.988
Devonshire Building | 2016-09-16 21:45 | 46361.8404 | 680.004
Devonshire Building | 2016-09-16 22:00 | 46362.0054 | 659.988
Devonshire Building | 2016-09-16 22:15 | 46362.1704 | 659.988
Devonshire Building | 2016-09-16 22:30 | 46362.3404 | 680.004
Devonshire Building | 2016-09-16 22:45 | 46362.5054 | 659.988
Devonshire Building | 2016-09-16 23:00 | 46362.6754 | 680.004
Devonshire Building | 2016-09-16 23:15 | 46362.8404 | 659.988
Devonshire Building | 2016-09-16 23:30 | 46363.0104 | 680.004
Devonshire Building | 2016-09-16 23:45 | 46363.1804 | 680.004 | 659.988
Devonshire Building | 2016-09-17 | 46363.3438 | 659.988
Devonshire Building | 2016-09-17 00:15 | 46363.5138 | 680.004
Devonshire Building | 2016-09-17 00:30 | 46363.6838 | 680.004
Devonshire Building | 2016-09-17 00:45 | 46363.8487 | 659.988
Devonshire Building | 2016-09-17 01:00 | 46364.0188 | 680.004
Devonshire Building | 2016-09-17 01:15 | 46364.1888 | 680.004
Devonshire Building | 2016-09-17 01:30 | 46364.3537 | 659.988
Devonshire Building | 2016-09-17 01:45 | 46364.5237 | 680.004
Devonshire Building | 2016-09-17 02:00 | 46364.6937 | 680.004
Devonshire Building | 2016-09-17 02:15 | 46364.8587 | 659.988
Devonshire Building | 2016-09-17 02:30 | 46365.0287 | 680.004
Devonshire Building | 2016-09-17 02:45 | 46365.1987 | 680.004
Devonshire Building | 2016-09-17 03:00 | 46365.3637 | 659.988
Devonshire Building | 2016-09-17 03:15 | 46365.5337 | 680.004
Devonshire Building | 2016-09-17 03:30 | 46365.7037 | 680.004
Devonshire Building | 2016-09-17 03:45 | 46365.8737 | 680.004
Devonshire Building | 2016-09-17 04:00 | 46366.0387 | 659.988
Devonshire Building | 2016-09-17 04:15 | 46366.2087 | 680.004
Devonshire Building | 2016-09-17 04:30 | 46366.3787 | 680.004
Devonshire Building | 2016-09-17 04:45 | 46366.5487 | 680.004
Devonshire Building | 2016-09-17 05:00 | 46366.7188 | 680.004
Devonshire Building | 2016-09-17 05:15 | 46366.8837 | 659.988
Devonshire Building | 2016-09-17 05:30 | 46367.0537 | 680.004
Devonshire Building | 2016-09-17 05:45 | 46367.3137 | 1040.004
Devonshire Building | 2016-09-17 06:00 | 46367.6237 | 1239.984
Devonshire Building | 2016-09-17 06:15 | 46367.7937 | 680.004
Devonshire Building | 2016-09-17 06:30 | 46367.9637 | 680.004
Devonshire Building | 2016-09-17 06:45 | 46368.1287 | 659.988
Devonshire Building | 2016-09-17 07:00 | 46368.2987 | 680.004
Devonshire Building | 2016-09-17 07:15 | 46368.4687 | 680.004
Devonshire Building | 2016-09-17 07:30 | 46368.6337 | 659.988
Devonshire Building | 2016-09-17 07:45 | 46368.7987 | 659.988
Devonshire Building | 2016-09-17 08:00 | 46368.9687 | 680.004
Devonshire Building | 2016-09-17 08:15 | 46369.1337 | 659.988
Devonshire Building | 2016-09-17 08:30 | 46369.2987 | 659.988
Devonshire Building | 2016-09-17 08:45 | 46369.4637 | 659.988
Devonshire Building | 2016-09-17 09:00 | 46369.6287 | 659.988
Devonshire Building | 2016-09-17 09:15 | 46369.7937 | 659.988
Devonshire Building | 2016-09-17 09:30 | 46369.9587 | 659.988
Devonshire Building | 2016-09-17 09:45 | 46370.1237 | 659.988
Devonshire Building | 2016-09-17 10:00 | 46370.2837 | 640.008
Devonshire Building | 2016-09-17 10:15 | 46370.4487 | 659.988
Devonshire Building | 2016-09-17 10:30 | 46370.6137 | 659.988
Devonshire Building | 2016-09-17 10:45 | 46370.7787 | 659.988
Devonshire Building | 2016-09-17 11:00 | 46370.9437 | 659.988
Devonshire Building | 2016-09-17 11:15 | 46371.1037 | 640.008
Devonshire Building | 2016-09-17 11:30 | 46371.2687 | 659.988
Devonshire Building | 2016-09-17 11:45 | 46371.4337 | 659.988
Devonshire Building | 2016-09-17 12:00 | 46371.5987 | 659.988
Devonshire Building | 2016-09-17 12:15 | 46371.7687 | 680.004
Devonshire Building | 2016-09-17 12:30 | 46371.9337 | 659.988
Devonshire Building | 2016-09-17 12:45 | 46372.0987 | 659.988
Devonshire Building | 2016-09-17 13:00 | 46372.2637 | 659.988
Devonshire Building | 2016-09-17 13:15 | 46372.4287 | 659.988
Devonshire Building | 2016-09-17 13:30 | 46372.8237 | 1580.004
Devonshire Building | 2016-09-17 13:45 | 46372.9887 | 659.988
Devonshire Building | 2016-09-17 14:00 | 46373.1537 | 659.988
Devonshire Building | 2016-09-17 14:15 | 46373.3187 | 659.988
Devonshire Building | 2016-09-17 14:30 | 46373.4887 | 680.004
Devonshire Building | 2016-09-17 14:45 | 46373.6537 | 659.988
Devonshire Building | 2016-09-17 15:00 | 46373.8187 | 659.988
Devonshire Building | 2016-09-17 15:15 | 46373.9887 | 680.004
Devonshire Building | 2016-09-17 15:30 | 46374.1537 | 659.988
Devonshire Building | 2016-09-17 15:45 | 46374.3187 | 659.988
Devonshire Building | 2016-09-17 16:00 | 46374.4887 | 680.004
Devonshire Building | 2016-09-17 16:15 | 46374.6537 | 659.988
Devonshire Building | 2016-09-17 16:30 | 46374.8187 | 659.988
Devonshire Building | 2016-09-17 16:45 | 46374.9887 | 680.004
Devonshire Building | 2016-09-17 17:00 | 46375.1537 | 659.988
Devonshire Building | 2016-09-17 17:15 | 46375.3187 | 659.988
Devonshire Building | 2016-09-17 17:30 | 46375.4887 | 680.004
Devonshire Building | 2016-09-17 17:45 | 46375.6537 | 659.988
Devonshire Building | 2016-09-17 18:00 | 46375.8237 | 680.004
Devonshire Building | 2016-09-17 18:15 | 46375.9887 | 659.988
Devonshire Building | 2016-09-17 18:30 | 46376.1537 | 659.988
Devonshire Building | 2016-09-17 18:45 | 46376.3237 | 680.004
Devonshire Building | 2016-09-17 19:00 | 46376.4887 | 659.988
Devonshire Building | 2016-09-17 19:15 | 46376.6587 | 680.004
Devonshire Building | 2016-09-17 19:30 | 46376.8237 | 659.988
Devonshire Building | 2016-09-17 19:45 | 46376.9937 | 680.004
Devonshire Building | 2016-09-17 20:00 | 46377.1587 | 659.988
Devonshire Building | 2016-09-17 20:15 | 46377.3287 | 680.004
Devonshire Building | 2016-09-17 20:30 | 46377.4936 | 659.988
Devonshire Building | 2016-09-17 20:45 | 46377.6637 | 680.004
Devonshire Building | 2016-09-17 21:00 | 46377.8536 | 759.996
Devonshire Building | 2016-09-17 21:15 | 46378.0237 | 680.004
Devonshire Building | 2016-09-17 21:30 | 46378.1886 | 659.988
Devonshire Building | 2016-09-17 21:45 | 46378.3586 | 680.004
Devonshire Building | 2016-09-17 22:00 | 46378.5286 | 680.004
Devonshire Building | 2016-09-17 22:15 | 46378.6936 | 659.988
Devonshire Building | 2016-09-17 22:30 | 46378.8636 | 680.004
Devonshire Building | 2016-09-17 22:45 | 46379.0336 | 680.004
Devonshire Building | 2016-09-17 23:00 | 46379.2036 | 680.004
Devonshire Building | 2016-09-17 23:15 | 46379.3737 | 680.004
Devonshire Building | 2016-09-17 23:30 | 46379.5437 | 680.004
Devonshire Building | 2016-09-17 23:45 | 46379.7137 | 680.004 | 640.008
Devonshire Building | 2016-09-18 | 46379.8828 | 680.004
Devonshire Building | 2016-09-18 00:15 | 46380.0528 | 680.004
Devonshire Building | 2016-09-18 00:30 | 46380.2228 | 680.004
Devonshire Building | 2016-09-18 00:45 | 46380.3928 | 680.004
Devonshire Building | 2016-09-18 01:00 | 46380.5628 | 680.004
Devonshire Building | 2016-09-18 01:15 | 46380.7328 | 680.004
Devonshire Building | 2016-09-18 01:30 | 46380.9028 | 680.004
Devonshire Building | 2016-09-18 01:45 | 46381.0778 | 699.984
Devonshire Building | 2016-09-18 02:00 | 46381.2478 | 680.004
Devonshire Building | 2016-09-18 02:15 | 46381.4178 | 680.004
Devonshire Building | 2016-09-18 02:30 | 46381.5878 | 680.004
Devonshire Building | 2016-09-18 02:45 | 46381.7578 | 680.004
Devonshire Building | 2016-09-18 03:00 | 46381.9278 | 680.004
Devonshire Building | 2016-09-18 03:15 | 46382.0978 | 680.004
Devonshire Building | 2016-09-18 03:30 | 46382.2678 | 680.004
Devonshire Building | 2016-09-18 03:45 | 46382.4378 | 680.004
Devonshire Building | 2016-09-18 04:00 | 46382.6078 | 680.004
Devonshire Building | 2016-09-18 04:15 | 46382.7778 | 680.004
Devonshire Building | 2016-09-18 04:30 | 46382.9528 | 699.984
Devonshire Building | 2016-09-18 04:45 | 46383.1228 | 680.004
Devonshire Building | 2016-09-18 05:00 | 46383.2928 | 680.004
Devonshire Building | 2016-09-18 05:15 | 46383.4628 | 680.004
Devonshire Building | 2016-09-18 05:30 | 46383.6328 | 680.004
Devonshire Building | 2016-09-18 05:45 | 46383.8028 | 680.004
Devonshire Building | 2016-09-18 06:00 | 46383.9728 | 680.004
Devonshire Building | 2016-09-18 06:15 | 46384.1478 | 699.984
Devonshire Building | 2016-09-18 06:30 | 46384.3178 | 680.004
Devonshire Building | 2016-09-18 06:45 | 46384.4878 | 680.004
Devonshire Building | 2016-09-18 07:00 | 46384.6578 | 680.004
Devonshire Building | 2016-09-18 07:15 | 46384.8278 | 680.004
Devonshire Building | 2016-09-18 07:30 | 46384.9978 | 680.004
Devonshire Building | 2016-09-18 07:45 | 46385.1678 | 680.004
Devonshire Building | 2016-09-18 08:00 | 46385.3378 | 680.004
Devonshire Building | 2016-09-18 08:15 | 46385.5028 | 659.988
Devonshire Building | 2016-09-18 08:30 | 46385.6728 | 680.004
Devonshire Building | 2016-09-18 08:45 | 46385.8428 | 680.004
Devonshire Building | 2016-09-18 09:00 | 46386.0078 | 659.988
Devonshire Building | 2016-09-18 09:15 | 46386.1778 | 680.004
Devonshire Building | 2016-09-18 09:30 | 46386.3478 | 680.004
Devonshire Building | 2016-09-18 09:45 | 46386.5128 | 659.988
Devonshire Building | 2016-09-18 10:00 | 46386.9128 | 1599.984
Devonshire Building | 2016-09-18 10:15 | 46387.0828 | 680.004
Devonshire Building | 2016-09-18 10:30 | 46387.2478 | 659.988
Devonshire Building | 2016-09-18 10:45 | 46387.4178 | 680.004
Devonshire Building | 2016-09-18 11:00 | 46387.5878 | 680.004
Devonshire Building | 2016-09-18 11:15 | 46387.7578 | 680.004
Devonshire Building | 2016-09-18 11:30 | 46387.9278 | 680.004
Devonshire Building | 2016-09-18 11:45 | 46388.0978 | 680.004
Devonshire Building | 2016-09-18 12:00 | 46388.2628 | 659.988
Devonshire Building | 2016-09-18 12:15 | 46388.4378 | 699.984
Devonshire Building | 2016-09-18 12:30 | 46388.6078 | 680.004
Devonshire Building | 2016-09-18 12:45 | 46388.7778 | 680.004
Devonshire Building | 2016-09-18 13:00 | 46388.9478 | 680.004
Devonshire Building | 2016-09-18 13:15 | 46389.1178 | 680.004
Devonshire Building | 2016-09-18 13:30 | 46389.2878 | 680.004
Devonshire Building | 2016-09-18 13:45 | 46389.4578 | 680.004
Devonshire Building | 2016-09-18 14:00 | 46389.6278 | 680.004
Devonshire Building | 2016-09-18 14:15 | 46389.7978 | 680.004
Devonshire Building | 2016-09-18 14:30 | 46389.9778 | 720
Devonshire Building | 2016-09-18 14:45 | 46390.1478 | 680.004
Devonshire Building | 2016-09-18 15:00 | 46390.3178 | 680.004
Devonshire Building | 2016-09-18 15:15 | 46390.4878 | 680.004
Devonshire Building | 2016-09-18 15:30 | 46390.6578 | 680.004
Devonshire Building | 2016-09-18 15:45 | 46390.8278 | 680.004
Devonshire Building | 2016-09-18 16:00 | 46391.0028 | 699.984
Devonshire Building | 2016-09-18 16:15 | 46391.1728 | 680.004
Devonshire Building | 2016-09-18 16:30 | 46391.3428 | 680.004
Devonshire Building | 2016-09-18 16:45 | 46391.5128 | 680.004
Devonshire Building | 2016-09-18 17:00 | 46391.6828 | 680.004
Devonshire Building | 2016-09-18 17:15 | 46391.8528 | 680.004
Devonshire Building | 2016-09-18 17:30 | 46392.0178 | 659.988
Devonshire Building | 2016-09-18 17:45 | 46392.1928 | 699.984
Devonshire Building | 2016-09-18 18:00 | 46392.3628 | 680.004
Devonshire Building | 2016-09-18 18:15 | 46392.5278 | 659.988
Devonshire Building | 2016-09-18 18:30 | 46392.6978 | 680.004
Devonshire Building | 2016-09-18 18:45 | 46392.8678 | 680.004
Devonshire Building | 2016-09-18 19:00 | 46393.0378 | 680.004
Devonshire Building | 2016-09-18 19:15 | 46393.2128 | 699.984
Devonshire Building | 2016-09-18 19:30 | 46393.3828 | 680.004
Devonshire Building | 2016-09-18 19:45 | 46393.5528 | 680.004
Devonshire Building | 2016-09-18 20:00 | 46393.7228 | 680.004
Devonshire Building | 2016-09-18 20:15 | 46393.8978 | 699.984
Devonshire Building | 2016-09-18 20:30 | 46394.0678 | 680.004
Devonshire Building | 2016-09-18 20:45 | 46394.2378 | 680.004
Devonshire Building | 2016-09-18 21:00 | 46394.4328 | 780.012
Devonshire Building | 2016-09-18 21:15 | 46394.6078 | 699.984
Devonshire Building | 2016-09-18 21:30 | 46394.7778 | 680.004
Devonshire Building | 2016-09-18 21:45 | 46394.9528 | 699.984
Devonshire Building | 2016-09-18 22:00 | 46395.1228 | 680.004
Devonshire Building | 2016-09-18 22:15 | 46395.2978 | 699.984
Devonshire Building | 2016-09-18 22:30 | 46395.4678 | 680.004
Devonshire Building | 2016-09-18 22:45 | 46395.6428 | 699.984
Devonshire Building | 2016-09-18 23:00 | 46395.8128 | 680.004
Devonshire Building | 2016-09-18 23:15 | 46395.9878 | 699.984
Devonshire Building | 2016-09-18 23:30 | 46396.1578 | 680.004
Devonshire Building | 2016-09-18 23:45 | 46396.3328 | 699.984 | 659.988
Devonshire Building | 2016-09-19 | 46396.5078 | 699.984
Devonshire Building | 2016-09-19 00:15 | 46396.6778 | 680.004
Devonshire Building | 2016-09-19 00:30 | 46396.8528 | 699.984
Devonshire Building | 2016-09-19 00:45 | 46397.0278 | 699.984
Devonshire Building | 2016-09-19 01:00 | 46397.2028 | 699.984
Devonshire Building | 2016-09-19 01:15 | 46397.3778 | 699.984
Devonshire Building | 2016-09-19 01:30 | 46397.5478 | 680.004
Devonshire Building | 2016-09-19 01:45 | 46397.7228 | 699.984
Devonshire Building | 2016-09-19 02:00 | 46397.8978 | 699.984
Devonshire Building | 2016-09-19 02:15 | 46398.0728 | 699.984
Devonshire Building | 2016-09-19 02:30 | 46398.2428 | 680.004
Devonshire Building | 2016-09-19 02:45 | 46398.4178 | 699.984
Devonshire Building | 2016-09-19 03:00 | 46398.5928 | 699.984
Devonshire Building | 2016-09-19 03:15 | 46398.7628 | 680.004
Devonshire Building | 2016-09-19 03:30 | 46398.9378 | 699.984
Devonshire Building | 2016-09-19 03:45 | 46399.1128 | 699.984
Devonshire Building | 2016-09-19 04:00 | 46399.2878 | 699.984
Devonshire Building | 2016-09-19 04:15 | 46399.4578 | 680.004
Devonshire Building | 2016-09-19 04:30 | 46399.6328 | 699.984
Devonshire Building | 2016-09-19 04:45 | 46399.8078 | 699.984
Devonshire Building | 2016-09-19 05:00 | 46399.9828 | 699.984
Devonshire Building | 2016-09-19 05:15 | 46400.1578 | 699.984
Devonshire Building | 2016-09-19 05:30 | 46400.3327 | 699.984
Devonshire Building | 2016-09-19 05:45 | 46400.5077 | 699.984
Devonshire Building | 2016-09-19 06:00 | 46400.6777 | 680.004
Devonshire Building | 2016-09-19 06:15 | 46400.8527 | 699.984
Devonshire Building | 2016-09-19 06:30 | 46401.2627 | 1640.016
Devonshire Building | 2016-09-19 06:45 | 46401.4377 | 699.984
Devonshire Building | 2016-09-19 07:00 | 46401.6127 | 699.984
Devonshire Building | 2016-09-19 07:15 | 46401.7927 | 720
Devonshire Building | 2016-09-19 07:30 | 46401.9627 | 680.004
Devonshire Building | 2016-09-19 07:45 | 46402.1427 | 720
Devonshire Building | 2016-09-19 08:00 | 46402.3427 | 799.992
Devonshire Building | 2016-09-19 08:15 | 46402.5227 | 720
Devonshire Building | 2016-09-19 08:30 | 46402.6977 | 699.984
Devonshire Building | 2016-09-19 08:45 | 46402.8677 | 680.004
Devonshire Building | 2016-09-19 09:00 | 46403.0427 | 699.984
Devonshire Building | 2016-09-19 09:15 | 46403.4827 | 1760.004
Devonshire Building | 2016-09-19 09:30 | 46403.6627 | 720
Devonshire Building | 2016-09-19 09:45 | 46403.8777 | 860.004
Devonshire Building | 2016-09-19 10:00 | 46404.1377 | 1040.004
Devonshire Building | 2016-09-19 10:15 | 46404.5227 | 1540.008
Devonshire Building | 2016-09-19 10:30 | 46404.9127 | 1559.988
Devonshire Building | 2016-09-19 10:45 | 46405.1877 | 1100.016
Devonshire Building | 2016-09-19 11:00 | 46405.4977 | 1239.984
Devonshire Building | 2016-09-19 11:15 | 46405.7877 | 1159.992
Devonshire Building | 2016-09-19 11:30 | 46406.0477 | 1040.004
Devonshire Building | 2016-09-19 11:45 | 46406.4727 | 1699.992
Devonshire Building | 2016-09-19 12:00 | 46406.7377 | 1059.984
Devonshire Building | 2016-09-19 12:15 | 46406.9427 | 820.008
Devonshire Building | 2016-09-19 12:30 | 46407.1477 | 820.008
Devonshire Building | 2016-09-19 12:45 | 46407.3527 | 820.008
Devonshire Building | 2016-09-19 13:00 | 46407.5577 | 820.008
Devonshire Building | 2016-09-19 13:15 | 46407.7577 | 799.992
Devonshire Building | 2016-09-19 13:30 | 46407.9577 | 799.992
Devonshire Building | 2016-09-19 13:45 | 46408.4077 | 1800
Devonshire Building | 2016-09-19 14:00 | 46408.5977 | 759.996
Devonshire Building | 2016-09-19 14:15 | 46408.7827 | 740.016
Devonshire Building | 2016-09-19 14:30 | 46408.9727 | 759.996
Devonshire Building | 2016-09-19 14:45 | 46409.1627 | 759.996
Devonshire Building | 2016-09-19 15:00 | 46409.3777 | 860.004
Devonshire Building | 2016-09-19 15:15 | 46409.6027 | 900
Devonshire Building | 2016-09-19 15:30 | 46410.0727 | 1879.992
Devonshire Building | 2016-09-19 15:45 | 46410.3327 | 1040.004
Devonshire Building | 2016-09-19 16:00 | 46410.5877 | 1019.988
Devonshire Building | 2016-09-19 16:15 | 46410.8677 | 1119.996
Devonshire Building | 2016-09-19 16:30 | 46411.1527 | 1140.012
Devonshire Building | 2016-09-19 16:45 | 46411.4177 | 1059.984
Devonshire Building | 2016-09-19 17:00 | 46411.6527 | 939.996
Devonshire Building | 2016-09-19 17:15 | 46411.8727 | 879.984
Devonshire Building | 2016-09-19 17:30 | 46412.0777 | 820.008
Devonshire Building | 2016-09-19 17:45 | 46412.2777 | 799.992
Devonshire Building | 2016-09-19 18:00 | 46412.4727 | 780.012
Devonshire Building | 2016-09-19 18:15 | 46412.6677 | 780.012
Devonshire Building | 2016-09-19 18:30 | 46412.8527 | 740.016
Devonshire Building | 2016-09-19 18:45 | 46413.0377 | 740.016
Devonshire Building | 2016-09-19 19:00 | 46413.2227 | 740.016
Devonshire Building | 2016-09-19 19:15 | 46413.4027 | 720
Devonshire Building | 2016-09-19 19:30 | 46413.5827 | 720
Devonshire Building | 2016-09-19 19:45 | 46413.7627 | 720
Devonshire Building | 2016-09-19 20:00 | 46413.9427 | 720
Devonshire Building | 2016-09-19 20:15 | 46414.1227 | 720
Devonshire Building | 2016-09-19 20:30 | 46414.3027 | 720
Devonshire Building | 2016-09-19 20:45 | 46414.4827 | 720
Devonshire Building | 2016-09-19 21:00 | 46414.6827 | 799.992
Devonshire Building | 2016-09-19 21:15 | 46414.8577 | 699.984
Devonshire Building | 2016-09-19 21:30 | 46415.0327 | 699.984
Devonshire Building | 2016-09-19 21:45 | 46415.2077 | 699.984
Devonshire Building | 2016-09-19 22:00 | 46415.3827 | 699.984
Devonshire Building | 2016-09-19 22:15 | 46415.5577 | 699.984
Devonshire Building | 2016-09-19 22:30 | 46415.7327 | 699.984
Devonshire Building | 2016-09-19 22:45 | 46415.9077 | 699.984
Devonshire Building | 2016-09-19 23:00 | 46416.0827 | 699.984
Devonshire Building | 2016-09-19 23:15 | 46416.2577 | 699.984
Devonshire Building | 2016-09-19 23:30 | 46416.4377 | 720
Devonshire Building | 2016-09-19 23:45 | 46416.6127 | 699.984 | 680.004
Devonshire Building | 2016-09-20 | 46416.7891 | 699.984
Devonshire Building | 2016-09-20 00:15 | 46416.9691 | 720
Devonshire Building | 2016-09-20 00:30 | 46417.1441 | 699.984
Devonshire Building | 2016-09-20 00:45 | 46417.3241 | 720
Devonshire Building | 2016-09-20 01:00 | 46417.4991 | 699.984
Devonshire Building | 2016-09-20 01:15 | 46417.6791 | 720
Devonshire Building | 2016-09-20 01:30 | 46417.854 | 699.984
Devonshire Building | 2016-09-20 01:45 | 46418.269 | 1659.996
Devonshire Building | 2016-09-20 02:00 | 46418.449 | 720
Devonshire Building | 2016-09-20 02:15 | 46418.624 | 699.984
Devonshire Building | 2016-09-20 02:30 | 46418.804 | 720
Devonshire Building | 2016-09-20 02:45 | 46418.979 | 699.984
Devonshire Building | 2016-09-20 03:00 | 46419.154 | 699.984
Devonshire Building | 2016-09-20 03:15 | 46419.334 | 720
Devonshire Building | 2016-09-20 03:30 | 46419.509 | 699.984
Devonshire Building | 2016-09-20 03:45 | 46419.684 | 699.984
Devonshire Building | 2016-09-20 04:00 | 46419.864 | 720
Devonshire Building | 2016-09-20 04:15 | 46420.039 | 699.984
Devonshire Building | 2016-09-20 04:30 | 46420.214 | 699.984
Devonshire Building | 2016-09-20 04:45 | 46420.389 | 699.984
Devonshire Building | 2016-09-20 05:00 | 46420.564 | 699.984
Devonshire Building | 2016-09-20 05:15 | 46420.739 | 699.984
Devonshire Building | 2016-09-20 05:30 | 46420.919 | 720
Devonshire Building | 2016-09-20 05:45 | 46421.094 | 699.984
Devonshire Building | 2016-09-20 06:00 | 46421.269 | 699.984
Devonshire Building | 2016-09-20 06:15 | 46421.449 | 720
Devonshire Building | 2016-09-20 06:30 | 46421.624 | 699.984
Devonshire Building | 2016-09-20 06:45 | 46421.799 | 699.984
Devonshire Building | 2016-09-20 07:00 | 46421.974 | 699.984
Devonshire Building | 2016-09-20 07:15 | 46422.149 | 699.984
Devonshire Building | 2016-09-20 07:30 | 46422.329 | 720
Devonshire Building | 2016-09-20 07:45 | 46422.519 | 759.996
Devonshire Building | 2016-09-20 08:00 | 46422.694 | 699.984
Devonshire Building | 2016-09-20 08:15 | 46422.874 | 720
Devonshire Building | 2016-09-20 08:30 | 46423.054 | 720
Devonshire Building | 2016-09-20 08:45 | 46423.494 | 1760.004
Devonshire Building | 2016-09-20 09:00 | 46423.674 | 720
Devonshire Building | 2016-09-20 09:15 | 46423.869 | 780.012
Devonshire Building | 2016-09-20 09:30 | 46424.099 | 920.016
Devonshire Building | 2016-09-20 09:45 | 46424.354 | 1019.988
Devonshire Building | 2016-09-20 10:00 | 46424.894 | 2160
Devonshire Building | 2016-09-20 10:15 | 46425.184 | 1159.992
Devonshire Building | 2016-09-20 10:30 | 46425.459 | 1100.016
Devonshire Building | 2016-09-20 10:45 | 46425.719 | 1040.004
Devonshire Building | 2016-09-20 11:00 | 46425.964 | 979.992
Devonshire Building | 2016-09-20 11:15 | 46426.199 | 939.996
Devonshire Building | 2016-09-20 11:30 | 46426.694 | 1980
Devonshire Building | 2016-09-20 11:45 | 46426.919 | 900
Devonshire Building | 2016-09-20 12:00 | 46427.149 | 920.016
Devonshire Building | 2016-09-20 12:15 | 46427.374 | 900
Devonshire Building | 2016-09-20 12:30 | 46427.604 | 920.016
Devonshire Building | 2016-09-20 12:45 | 46427.839 | 939.996
Devonshire Building | 2016-09-20 13:00 | 46428.064 | 900
Devonshire Building | 2016-09-20 13:15 | 46428.554 | 1959.984
Devonshire Building | 2016-09-20 13:30 | 46428.774 | 879.984
Devonshire Building | 2016-09-20 13:45 | 46428.989 | 860.004
Devonshire Building | 2016-09-20 14:00 | 46429.214 | 900
Devonshire Building | 2016-09-20 14:15 | 46429.434 | 879.984
Devonshire Building | 2016-09-20 14:30 | 46429.659 | 900
Devonshire Building | 2016-09-20 14:45 | 46429.884 | 900
Devonshire Building | 2016-09-20 15:00 | 46430.109 | 900
Devonshire Building | 2016-09-20 15:15 | 46430.614 | 2019.996
Devonshire Building | 2016-09-20 15:30 | 46430.869 | 1019.988
Devonshire Building | 2016-09-20 15:45 | 46431.124 | 1019.988
Devonshire Building | 2016-09-20 16:00 | 46431.384 | 1040.004
Devonshire Building | 2016-09-20 16:15 | 46431.649 | 1059.984
Devonshire Building | 2016-09-20 16:30 | 46431.909 | 1040.004
Devonshire Building | 2016-09-20 16:45 | 46432.164 | 1019.988
Devonshire Building | 2016-09-20 17:00 | 46432.399 | 939.996
Devonshire Building | 2016-09-20 17:15 | 46432.619 | 879.984
Devonshire Building | 2016-09-20 17:30 | 46432.829 | 839.988
Devonshire Building | 2016-09-20 17:45 | 46433.029 | 799.992
Devonshire Building | 2016-09-20 18:00 | 46433.229 | 799.992
Devonshire Building | 2016-09-20 18:15 | 46433.419 | 759.996
Devonshire Building | 2016-09-20 18:30 | 46433.609 | 759.996
Devonshire Building | 2016-09-20 18:45 | 46433.799 | 759.996
Devonshire Building | 2016-09-20 19:00 | 46433.984 | 740.016
Devonshire Building | 2016-09-20 19:15 | 46434.169 | 740.016
Devonshire Building | 2016-09-20 19:30 | 46434.354 | 740.016
Devonshire Building | 2016-09-20 19:45 | 46434.539 | 740.016
Devonshire Building | 2016-09-20 20:00 | 46434.719 | 720
Devonshire Building | 2016-09-20 20:15 | 46434.904 | 740.016
Devonshire Building | 2016-09-20 20:30 | 46435.084 | 720
Devonshire Building | 2016-09-20 20:45 | 46435.269 | 740.016
Devonshire Building | 2016-09-20 21:00 | 46435.469 | 799.992
Devonshire Building | 2016-09-20 21:15 | 46435.644 | 699.984
Devonshire Building | 2016-09-20 21:30 | 46435.824 | 720
Devonshire Building | 2016-09-20 21:45 | 46435.999 | 699.984
Devonshire Building | 2016-09-20 22:00 | 46436.174 | 699.984
Devonshire Building | 2016-09-20 22:15 | 46436.354 | 720
Devonshire Building | 2016-09-20 22:30 | 46436.529 | 699.984
Devonshire Building | 2016-09-20 22:45 | 46436.709 | 720
Devonshire Building | 2016-09-20 23:00 | 46436.884 | 699.984
Devonshire Building | 2016-09-20 23:15 | 46437.064 | 720
Devonshire Building | 2016-09-20 23:30 | 46437.2389 | 699.984
Devonshire Building | 2016-09-20 23:45 | 46437.4189 | 720 | 699.984
Devonshire Building | 2016-09-21 | 46437.5938 | 699.984
Devonshire Building | 2016-09-21 00:15 | 46437.7738 | 720
Devonshire Building | 2016-09-21 00:30 | 46437.9487 | 699.984
Devonshire Building | 2016-09-21 00:45 | 46438.1287 | 720
Devonshire Building | 2016-09-21 01:00 | 46438.5437 | 1659.996
Devonshire Building | 2016-09-21 01:15 | 46438.7187 | 699.984
Devonshire Building | 2016-09-21 01:30 | 46438.8987 | 720
Devonshire Building | 2016-09-21 01:45 | 46439.0787 | 720
Devonshire Building | 2016-09-21 02:00 | 46439.2587 | 720
Devonshire Building | 2016-09-21 02:15 | 46439.4387 | 720
Devonshire Building | 2016-09-21 02:30 | 46439.6187 | 720
Devonshire Building | 2016-09-21 02:45 | 46439.7987 | 720
Devonshire Building | 2016-09-21 03:00 | 46439.9787 | 720
Devonshire Building | 2016-09-21 03:15 | 46440.1537 | 699.984
Devonshire Building | 2016-09-21 03:30 | 46440.3337 | 720
Devonshire Building | 2016-09-21 03:45 | 46440.5137 | 720
Devonshire Building | 2016-09-21 04:00 | 46440.6937 | 720
Devonshire Building | 2016-09-21 04:15 | 46440.8737 | 720
Devonshire Building | 2016-09-21 04:30 | 46441.0537 | 720
Devonshire Building | 2016-09-21 04:45 | 46441.2287 | 699.984
Devonshire Building | 2016-09-21 05:00 | 46441.4087 | 720
Devonshire Building | 2016-09-21 05:15 | 46441.5887 | 720
Devonshire Building | 2016-09-21 05:30 | 46441.7687 | 720
Devonshire Building | 2016-09-21 05:45 | 46441.9437 | 699.984
Devonshire Building | 2016-09-21 06:00 | 46442.1237 | 720
Devonshire Building | 2016-09-21 06:15 | 46442.2987 | 699.984
Devonshire Building | 2016-09-21 06:30 | 46442.4787 | 720
Devonshire Building | 2016-09-21 06:45 | 46442.6537 | 699.984
Devonshire Building | 2016-09-21 07:00 | 46442.8337 | 720
Devonshire Building | 2016-09-21 07:15 | 46443.0187 | 740.016
Devonshire Building | 2016-09-21 07:30 | 46443.1987 | 720
Devonshire Building | 2016-09-21 07:45 | 46443.3787 | 720
Devonshire Building | 2016-09-21 08:00 | 46443.5587 | 720
Devonshire Building | 2016-09-21 08:15 | 46443.7437 | 740.016
Devonshire Building | 2016-09-21 08:30 | 46444.1787 | 1739.988
Devonshire Building | 2016-09-21 08:45 | 46444.3537 | 699.984
Devonshire Building | 2016-09-21 09:00 | 46444.5287 | 699.984
Devonshire Building | 2016-09-21 09:15 | 46444.7087 | 720
Devonshire Building | 2016-09-21 09:30 | 46444.9087 | 799.992
Devonshire Building | 2016-09-21 09:45 | 46445.1387 | 920.016
Devonshire Building | 2016-09-21 10:00 | 46445.6687 | 2120.004
Devonshire Building | 2016-09-21 10:15 | 46445.9987 | 1320.012
Devonshire Building | 2016-09-21 10:30 | 46446.3337 | 1339.992
Devonshire Building | 2016-09-21 10:45 | 46446.6287 | 1180.008
Devonshire Building | 2016-09-21 11:00 | 46446.8887 | 1040.004
Devonshire Building | 2016-09-21 11:15 | 46447.4087 | 2080.008
Devonshire Building | 2016-09-21 11:30 | 46447.6387 | 920.016
Devonshire Building | 2016-09-21 11:45 | 46447.8587 | 879.984
Devonshire Building | 2016-09-21 12:00 | 46448.0837 | 900
Devonshire Building | 2016-09-21 12:15 | 46448.3187 | 939.996
Devonshire Building | 2016-09-21 12:30 | 46448.5537 | 939.996
Devonshire Building | 2016-09-21 12:45 | 46448.7987 | 979.992
Devonshire Building | 2016-09-21 13:00 | 46449.0387 | 960.012
Devonshire Building | 2016-09-21 13:15 | 46449.5437 | 2019.996
Devonshire Building | 2016-09-21 13:30 | 46449.7837 | 960.012
Devonshire Building | 2016-09-21 13:45 | 46450.0287 | 979.992
Devonshire Building | 2016-09-21 14:00 | 46450.2687 | 960.012
Devonshire Building | 2016-09-21 14:15 | 46450.5087 | 960.012
Devonshire Building | 2016-09-21 14:30 | 46450.7437 | 939.996
Devonshire Building | 2016-09-21 14:45 | 46450.9737 | 920.016
Devonshire Building | 2016-09-21 15:00 | 46451.2037 | 920.016
Devonshire Building | 2016-09-21 15:15 | 46451.6937 | 1959.984
Devonshire Building | 2016-09-21 15:30 | 46451.9037 | 839.988
Devonshire Building | 2016-09-21 15:45 | 46452.1187 | 860.004
Devonshire Building | 2016-09-21 16:00 | 46452.3437 | 900
Devonshire Building | 2016-09-21 16:15 | 46452.5937 | 1000.008
Devonshire Building | 2016-09-21 16:30 | 46452.8387 | 979.992
Devonshire Building | 2016-09-21 16:45 | 46453.0937 | 1019.988
Devonshire Building | 2016-09-21 17:00 | 46453.3637 | 1080
Devonshire Building | 2016-09-21 17:15 | 46453.6287 | 1059.984
Devonshire Building | 2016-09-21 17:30 | 46453.8837 | 1019.988
Devonshire Building | 2016-09-21 17:45 | 46454.1337 | 1000.008
Devonshire Building | 2016-09-21 18:00 | 46454.3637 | 920.016
Devonshire Building | 2016-09-21 18:15 | 46454.5837 | 879.984
Devonshire Building | 2016-09-21 18:30 | 46454.9037 | 1280.016
Devonshire Building | 2016-09-21 18:45 | 46455.2137 | 1239.984
Devonshire Building | 2016-09-21 19:00 | 46455.3937 | 720
Devonshire Building | 2016-09-21 19:15 | 46455.5737 | 720
Devonshire Building | 2016-09-21 19:30 | 46455.7537 | 720
Devonshire Building | 2016-09-21 19:45 | 46455.9337 | 720
Devonshire Building | 2016-09-21 20:00 | 46456.1137 | 720
Devonshire Building | 2016-09-21 20:15 | 46456.2937 | 720
Devonshire Building | 2016-09-21 20:30 | 46456.4737 | 720
Devonshire Building | 2016-09-21 20:45 | 46456.6537 | 720
Devonshire Building | 2016-09-21 21:00 | 46456.8437 | 759.996
Devonshire Building | 2016-09-21 21:15 | 46457.0187 | 699.984
Devonshire Building | 2016-09-21 21:30 | 46457.1987 | 720
Devonshire Building | 2016-09-21 21:45 | 46457.3737 | 699.984
Devonshire Building | 2016-09-21 22:00 | 46457.5537 | 720
Devonshire Building | 2016-09-21 22:15 | 46457.7287 | 699.984
Devonshire Building | 2016-09-21 22:30 | 46457.9087 | 720
Devonshire Building | 2016-09-21 22:45 | 46458.0837 | 699.984
Devonshire Building | 2016-09-21 23:00 | 46458.2637 | 720
Devonshire Building | 2016-09-21 23:15 | 46458.4387 | 699.984
Devonshire Building | 2016-09-21 23:30 | 46458.6187 | 720
Devonshire Building | 2016-09-21 23:45 | 46458.7987 | 720 | 699.984
Devonshire Building | 2016-09-22 | 46458.9805 | 720
Devonshire Building | 2016-09-22 00:15 | 46459.1555 | 699.984
Devonshire Building | 2016-09-22 00:30 | 46459.3355 | 720
Devonshire Building | 2016-09-22 00:45 | 46459.5155 | 720
Devonshire Building | 2016-09-22 01:00 | 46459.6955 | 720
Devonshire Building | 2016-09-22 01:15 | 46459.8755 | 720
Devonshire Building | 2016-09-22 01:30 | 46460.0555 | 720
Devonshire Building | 2016-09-22 01:45 | 46460.2355 | 720
Devonshire Building | 2016-09-22 02:00 | 46460.4155 | 720
Devonshire Building | 2016-09-22 02:15 | 46460.5955 | 720
Devonshire Building | 2016-09-22 02:30 | 46460.7755 | 720
Devonshire Building | 2016-09-22 02:45 | 46460.9555 | 720
Devonshire Building | 2016-09-22 03:00 | 46461.1355 | 720
Devonshire Building | 2016-09-22 03:15 | 46461.3155 | 720
Devonshire Building | 2016-09-22 03:30 | 46461.4955 | 720
Devonshire Building | 2016-09-22 03:45 | 46461.6705 | 699.984
Devonshire Building | 2016-09-22 04:00 | 46461.8505 | 720
Devonshire Building | 2016-09-22 04:15 | 46462.0255 | 699.984
Devonshire Building | 2016-09-22 04:30 | 46462.2005 | 699.984
Devonshire Building | 2016-09-22 04:45 | 46462.3754 | 699.984
Devonshire Building | 2016-09-22 05:00 | 46462.5504 | 699.984
Devonshire Building | 2016-09-22 05:15 | 46462.7304 | 720
Devonshire Building | 2016-09-22 05:30 | 46462.9054 | 699.984
Devonshire Building | 2016-09-22 05:45 | 46463.0804 | 699.984
Devonshire Building | 2016-09-22 06:00 | 46463.2554 | 699.984
Devonshire Building | 2016-09-22 06:15 | 46463.4254 | 680.004
Devonshire Building | 2016-09-22 06:30 | 46463.6004 | 699.984
Devonshire Building | 2016-09-22 06:45 | 46463.7754 | 699.984
Devonshire Building | 2016-09-22 07:00 | 46463.9504 | 699.984
Devonshire Building | 2016-09-22 07:15 | 46464.1254 | 699.984
Devonshire Building | 2016-09-22 07:30 | 46464.3054 | 720
Devonshire Building | 2016-09-22 07:45 | 46464.4854 | 720
Devonshire Building | 2016-09-22 08:00 | 46464.6704 | 740.016
Devonshire Building | 2016-09-22 08:15 | 46464.8454 | 699.984
Devonshire Building | 2016-09-22 08:30 | 46465.2504 | 1620
Devonshire Building | 2016-09-22 08:45 | 46465.4304 | 720
Devonshire Building | 2016-09-22 09:00 | 46465.6104 | 720
Devonshire Building | 2016-09-22 09:15 | 46465.7854 | 699.984
Devonshire Building | 2016-09-22 09:30 | 46465.9604 | 699.984
Devonshire Building | 2016-09-22 09:45 | 46466.1354 | 699.984
Devonshire Building | 2016-09-22 10:00 | 46466.3554 | 879.984
Devonshire Building | 2016-09-22 10:15 | 46466.8104 | 1820.016
Devonshire Building | 2016-09-22 10:30 | 46467.0304 | 879.984
Devonshire Building | 2016-09-22 10:45 | 46467.2554 | 900
Devonshire Building | 2016-09-22 11:00 | 46467.4704 | 860.004
Devonshire Building | 2016-09-22 11:15 | 46467.6904 | 879.984
Devonshire Building | 2016-09-22 11:30 | 46467.9054 | 860.004
Devonshire Building | 2016-09-22 11:45 | 46468.1154 | 839.988
Devonshire Building | 2016-09-22 12:00 | 46468.3304 | 860.004
Devonshire Building | 2016-09-22 12:15 | 46468.8104 | 1919.988
Devonshire Building | 2016-09-22 12:30 | 46469.0154 | 820.008
Devonshire Building | 2016-09-22 12:45 | 46469.2254 | 839.988
Devonshire Building | 2016-09-22 13:00 | 46469.4354 | 839.988
Devonshire Building | 2016-09-22 13:15 | 46469.6404 | 820.008
Devonshire Building | 2016-09-22 13:30 | 46469.8554 | 860.004
Devonshire Building | 2016-09-22 13:45 | 46470.0604 | 820.008
Devonshire Building | 2016-09-22 14:00 | 46470.2654 | 820.008
Devonshire Building | 2016-09-22 14:15 | 46470.7354 | 1879.992
Devonshire Building | 2016-09-22 14:30 | 46470.9404 | 820.008
Devonshire Building | 2016-09-22 14:45 | 46471.1404 | 799.992
Devonshire Building | 2016-09-22 15:00 | 46471.3454 | 820.008
Devonshire Building | 2016-09-22 15:15 | 46471.5554 | 839.988
Devonshire Building | 2016-09-22 15:30 | 46471.7654 | 839.988
Devonshire Building | 2016-09-22 15:45 | 46471.9704 | 820.008
Devonshire Building | 2016-09-22 16:00 | 46472.1754 | 820.008
Devonshire Building | 2016-09-22 16:15 | 46472.5154 | 1360.008
Devonshire Building | 2016-09-22 16:30 | 46472.8604 | 1379.988
Devonshire Building | 2016-09-22 16:45 | 46473.0754 | 860.004
Devonshire Building | 2016-09-22 17:00 | 46473.2904 | 860.004
Devonshire Building | 2016-09-22 17:15 | 46473.5054 | 860.004
Devonshire Building | 2016-09-22 17:30 | 46473.7204 | 860.004
Devonshire Building | 2016-09-22 17:45 | 46473.9254 | 820.008
Devonshire Building | 2016-09-22 18:00 | 46474.1304 | 820.008
Devonshire Building | 2016-09-22 18:15 | 46474.3304 | 799.992
Devonshire Building | 2016-09-22 18:30 | 46474.5154 | 740.016
Devonshire Building | 2016-09-22 18:45 | 46474.7004 | 740.016
Devonshire Building | 2016-09-22 19:00 | 46474.8804 | 720
Devonshire Building | 2016-09-22 19:15 | 46475.0654 | 740.016
Devonshire Building | 2016-09-22 19:30 | 46475.2454 | 720
Devonshire Building | 2016-09-22 19:45 | 46475.4254 | 720
Devonshire Building | 2016-09-22 20:00 | 46475.6054 | 720
Devonshire Building | 2016-09-22 20:15 | 46475.7854 | 720
Devonshire Building | 2016-09-22 20:30 | 46475.9604 | 699.984
Devonshire Building | 2016-09-22 20:45 | 46476.1404 | 720
Devonshire Building | 2016-09-22 21:00 | 46476.3354 | 780.012
Devonshire Building | 2016-09-22 21:15 | 46476.5104 | 699.984
Devonshire Building | 2016-09-22 21:30 | 46476.6804 | 680.004
Devonshire Building | 2016-09-22 21:45 | 46476.8554 | 699.984
Devonshire Building | 2016-09-22 22:00 | 46477.0304 | 699.984
Devonshire Building | 2016-09-22 22:15 | 46477.2054 | 699.984
Devonshire Building | 2016-09-22 22:30 | 46477.3804 | 699.984
Devonshire Building | 2016-09-22 22:45 | 46477.5554 | 699.984
Devonshire Building | 2016-09-22 23:00 | 46477.7304 | 699.984
Devonshire Building | 2016-09-22 23:15 | 46477.9054 | 699.984
Devonshire Building | 2016-09-22 23:30 | 46478.0854 | 720
Devonshire Building | 2016-09-22 23:45 | 46478.2604 | 699.984 | 680.004
Devonshire Building | 2016-09-23 | 46478.4336 | 699.984
Devonshire Building | 2016-09-23 00:15 | 46478.6136 | 720
Devonshire Building | 2016-09-23 00:30 | 46478.7936 | 720
Devonshire Building | 2016-09-23 00:45 | 46478.9686 | 699.984
Devonshire Building | 2016-09-23 01:00 | 46479.1486 | 720
Devonshire Building | 2016-09-23 01:15 | 46479.3286 | 720
Devonshire Building | 2016-09-23 01:30 | 46479.5036 | 699.984
Devonshire Building | 2016-09-23 01:45 | 46479.6836 | 720
Devonshire Building | 2016-09-23 02:00 | 46479.8636 | 720
Devonshire Building | 2016-09-23 02:15 | 46480.0436 | 720
Devonshire Building | 2016-09-23 02:30 | 46480.2186 | 699.984
Devonshire Building | 2016-09-23 02:45 | 46480.3986 | 720
Devonshire Building | 2016-09-23 03:00 | 46480.5786 | 720
Devonshire Building | 2016-09-23 03:15 | 46480.7536 | 699.984
Devonshire Building | 2016-09-23 03:30 | 46480.9336 | 720
Devonshire Building | 2016-09-23 03:45 | 46481.1086 | 699.984
Devonshire Building | 2016-09-23 04:00 | 46481.2886 | 720
Devonshire Building | 2016-09-23 04:15 | 46481.4636 | 699.984
Devonshire Building | 2016-09-23 04:30 | 46481.6436 | 720
Devonshire Building | 2016-09-23 04:45 | 46481.8186 | 699.984
Devonshire Building | 2016-09-23 05:00 | 46481.9936 | 699.984
Devonshire Building | 2016-09-23 05:15 | 46482.1736 | 720
Devonshire Building | 2016-09-23 05:30 | 46482.3486 | 699.984
Devonshire Building | 2016-09-23 05:45 | 46482.5235 | 699.984
Devonshire Building | 2016-09-23 06:00 | 46482.6985 | 699.984
Devonshire Building | 2016-09-23 06:15 | 46482.8735 | 699.984
Devonshire Building | 2016-09-23 06:30 | 46483.0435 | 680.004
Devonshire Building | 2016-09-23 06:45 | 46483.2185 | 699.984
Devonshire Building | 2016-09-23 07:00 | 46483.6335 | 1659.996
Devonshire Building | 2016-09-23 07:15 | 46483.8285 | 780.012
Devonshire Building | 2016-09-23 07:30 | 46483.9985 | 680.004
Devonshire Building | 2016-09-23 07:45 | 46484.1735 | 699.984
Devonshire Building | 2016-09-23 08:00 | 46484.3635 | 759.996
Devonshire Building | 2016-09-23 08:15 | 46484.5435 | 720
Devonshire Building | 2016-09-23 08:30 | 46484.7235 | 720
Devonshire Building | 2016-09-23 08:45 | 46484.8985 | 699.984
Devonshire Building | 2016-09-23 09:00 | 46485.0785 | 720
Devonshire Building | 2016-09-23 09:15 | 46485.2635 | 740.016
Devonshire Building | 2016-09-23 09:30 | 46485.4585 | 780.012
Devonshire Building | 2016-09-23 09:45 | 46485.9435 | 1940.004
Devonshire Building | 2016-09-23 10:00 | 46486.1735 | 920.016
Devonshire Building | 2016-09-23 10:15 | 46486.4035 | 920.016
Devonshire Building | 2016-09-23 10:30 | 46486.6235 | 879.984
Devonshire Building | 2016-09-23 10:45 | 46486.8385 | 860.004
Devonshire Building | 2016-09-23 11:00 | 46487.0435 | 820.008
Devonshire Building | 2016-09-23 11:15 | 46487.2635 | 879.984
Devonshire Building | 2016-09-23 11:30 | 46487.6135 | 1400.004
Devonshire Building | 2016-09-23 11:45 | 46487.9335 | 1280.016
Devonshire Building | 2016-09-23 12:00 | 46488.1435 | 839.988
Devonshire Building | 2016-09-23 12:15 | 46488.3735 | 920.016
Devonshire Building | 2016-09-23 12:30 | 46488.6136 | 960.012
Devonshire Building | 2016-09-23 12:45 | 46488.8536 | 960.012
Devonshire Building | 2016-09-23 13:00 | 46489.0936 | 960.012
Devonshire Building | 2016-09-23 13:15 | 46489.3186 | 900
Devonshire Building | 2016-09-23 13:30 | 46489.5286 | 839.988
Devonshire Building | 2016-09-23 13:45 | 46489.7386 | 839.988
Devonshire Building | 2016-09-23 14:00 | 46489.9436 | 820.008
Devonshire Building | 2016-09-23 14:15 | 46490.3986 | 1820.016
Devonshire Building | 2016-09-23 14:30 | 46490.5936 | 780.012
Devonshire Building | 2016-09-23 14:45 | 46490.7936 | 799.992
Devonshire Building | 2016-09-23 15:00 | 46491.0286 | 939.996
Devonshire Building | 2016-09-23 15:15 | 46491.2736 | 979.992
Devonshire Building | 2016-09-23 15:30 | 46491.5186 | 979.992
Devonshire Building | 2016-09-23 15:45 | 46491.8886 | 1479.996
Devonshire Building | 2016-09-23 16:00 | 46492.3136 | 1699.992
Devonshire Building | 2016-09-23 16:15 | 46492.7935 | 1919.988
Devonshire Building | 2016-09-23 16:30 | 46493.0436 | 1000.008
Devonshire Building | 2016-09-23 16:45 | 46493.2686 | 900
Devonshire Building | 2016-09-23 17:00 | 46493.4785 | 839.988
Devonshire Building | 2016-09-23 17:15 | 46493.6836 | 820.008
Devonshire Building | 2016-09-23 17:30 | 46493.8786 | 780.012
Devonshire Building | 2016-09-23 17:45 | 46494.0736 | 780.012
Devonshire Building | 2016-09-23 18:00 | 46494.2636 | 759.996
Devonshire Building | 2016-09-23 18:15 | 46494.4536 | 759.996
Devonshire Building | 2016-09-23 18:30 | 46494.6436 | 759.996
Devonshire Building | 2016-09-23 18:45 | 46494.8336 | 759.996
Devonshire Building | 2016-09-23 19:00 | 46495.0186 | 740.016
Devonshire Building | 2016-09-23 19:15 | 46495.2036 | 740.016
Devonshire Building | 2016-09-23 19:30 | 46495.3886 | 740.016
Devonshire Building | 2016-09-23 19:45 | 46495.5736 | 740.016
Devonshire Building | 2016-09-23 20:00 | 46495.7586 | 740.016
Devonshire Building | 2016-09-23 20:15 | 46495.9436 | 740.016
Devonshire Building | 2016-09-23 20:30 | 46496.1286 | 740.016
Devonshire Building | 2016-09-23 20:45 | 46496.3136 | 740.016
Devonshire Building | 2016-09-23 21:00 | 46496.5186 | 820.008
Devonshire Building | 2016-09-23 21:15 | 46496.6986 | 720
Devonshire Building | 2016-09-23 21:30 | 46496.8836 | 740.016
Devonshire Building | 2016-09-23 21:45 | 46497.0636 | 720
Devonshire Building | 2016-09-23 22:00 | 46497.2536 | 759.996
Devonshire Building | 2016-09-23 22:15 | 46497.4536 | 799.992
Devonshire Building | 2016-09-23 22:30 | 46497.6486 | 780.012
Devonshire Building | 2016-09-23 22:45 | 46497.8486 | 799.992
Devonshire Building | 2016-09-23 23:00 | 46498.0486 | 799.992
Devonshire Building | 2016-09-23 23:15 | 46498.2486 | 799.992
Devonshire Building | 2016-09-23 23:30 | 46498.4486 | 799.992
Devonshire Building | 2016-09-23 23:45 | 46498.6486 | 799.992 | 680.004
Devonshire Building | 2016-09-24 | 46498.8516 | 799.992
Devonshire Building | 2016-09-24 00:15 | 46499.0416 | 759.996
Devonshire Building | 2016-09-24 00:30 | 46499.2266 | 740.016
Devonshire Building | 2016-09-24 00:45 | 46499.4116 | 740.016
Devonshire Building | 2016-09-24 01:00 | 46499.5916 | 720
Devonshire Building | 2016-09-24 01:15 | 46499.7766 | 740.016
Devonshire Building | 2016-09-24 01:30 | 46499.9616 | 740.016
Devonshire Building | 2016-09-24 01:45 | 46500.1466 | 740.016
Devonshire Building | 2016-09-24 02:00 | 46500.3266 | 720
Devonshire Building | 2016-09-24 02:15 | 46500.5116 | 740.016
Devonshire Building | 2016-09-24 02:30 | 46500.6966 | 740.016
Devonshire Building | 2016-09-24 02:45 | 46500.8816 | 740.016
Devonshire Building | 2016-09-24 03:00 | 46501.0666 | 740.016
Devonshire Building | 2016-09-24 03:15 | 46501.2516 | 740.016
Devonshire Building | 2016-09-24 03:30 | 46501.4366 | 740.016
Devonshire Building | 2016-09-24 03:45 | 46501.6216 | 740.016
Devonshire Building | 2016-09-24 04:00 | 46501.8016 | 720
Devonshire Building | 2016-09-24 04:15 | 46501.9866 | 740.016
Devonshire Building | 2016-09-24 04:30 | 46502.1716 | 740.016
Devonshire Building | 2016-09-24 04:45 | 46502.3566 | 740.016
Devonshire Building | 2016-09-24 05:00 | 46502.5416 | 740.016
Devonshire Building | 2016-09-24 05:15 | 46502.7216 | 720
Devonshire Building | 2016-09-24 05:30 | 46502.9066 | 740.016
Devonshire Building | 2016-09-24 05:45 | 46503.0916 | 740.016
Devonshire Building | 2016-09-24 06:00 | 46503.2766 | 740.016
Devonshire Building | 2016-09-24 06:15 | 46503.4616 | 740.016
Devonshire Building | 2016-09-24 06:30 | 46503.6416 | 720
Devonshire Building | 2016-09-24 06:45 | 46503.8266 | 740.016
Devonshire Building | 2016-09-24 07:00 | 46504.0066 | 720
Devonshire Building | 2016-09-24 07:15 | 46504.1916 | 740.016
Devonshire Building | 2016-09-24 07:30 | 46504.3716 | 720
Devonshire Building | 2016-09-24 07:45 | 46504.5516 | 720
Devonshire Building | 2016-09-24 08:00 | 46504.7367 | 740.016
Devonshire Building | 2016-09-24 08:15 | 46504.9167 | 720
Devonshire Building | 2016-09-24 08:30 | 46505.0967 | 720
Devonshire Building | 2016-09-24 08:45 | 46505.2817 | 740.016
Devonshire Building | 2016-09-24 09:00 | 46505.4617 | 720
Devonshire Building | 2016-09-24 09:15 | 46505.6417 | 720
Devonshire Building | 2016-09-24 09:30 | 46505.8267 | 740.016
Devonshire Building | 2016-09-24 09:45 | 46506.0067 | 720
Devonshire Building | 2016-09-24 10:00 | 46506.1867 | 720
Devonshire Building | 2016-09-24 10:15 | 46506.3717 | 740.016
Devonshire Building | 2016-09-24 10:30 | 46506.5517 | 720
Devonshire Building | 2016-09-24 10:45 | 46506.7367 | 740.016
Devonshire Building | 2016-09-24 11:00 | 46506.9217 | 740.016
Devonshire Building | 2016-09-24 11:15 | 46507.1017 | 720
Devonshire Building | 2016-09-24 11:30 | 46507.2867 | 740.016
Devonshire Building | 2016-09-24 11:45 | 46507.4667 | 720
Devonshire Building | 2016-09-24 12:00 | 46507.6517 | 740.016
Devonshire Building | 2016-09-24 12:15 | 46507.8317 | 720
Devonshire Building | 2016-09-24 12:30 | 46508.2517 | 1680.012
Devonshire Building | 2016-09-24 12:45 | 46508.4367 | 740.016
Devonshire Building | 2016-09-24 13:00 | 46508.6167 | 720
Devonshire Building | 2016-09-24 13:15 | 46508.8017 | 740.016
Devonshire Building | 2016-09-24 13:30 | 46508.9867 | 740.016
Devonshire Building | 2016-09-24 13:45 | 46509.1667 | 720
Devonshire Building | 2016-09-24 14:00 | 46509.3517 | 740.016
Devonshire Building | 2016-09-24 14:15 | 46509.5317 | 720
Devonshire Building | 2016-09-24 14:30 | 46509.7167 | 740.016
Devonshire Building | 2016-09-24 14:45 | 46509.8967 | 720
Devonshire Building | 2016-09-24 15:00 | 46510.0817 | 740.016
Devonshire Building | 2016-09-24 15:15 | 46510.2667 | 740.016
Devonshire Building | 2016-09-24 15:30 | 46510.4517 | 740.016
Devonshire Building | 2016-09-24 15:45 | 46510.6317 | 720
Devonshire Building | 2016-09-24 16:00 | 46510.8167 | 740.016
Devonshire Building | 2016-09-24 16:15 | 46511.0017 | 740.016
Devonshire Building | 2016-09-24 16:30 | 46511.1867 | 740.016
Devonshire Building | 2016-09-24 16:45 | 46511.3667 | 720
Devonshire Building | 2016-09-24 17:00 | 46511.5517 | 740.016
Devonshire Building | 2016-09-24 17:15 | 46511.7367 | 740.016
Devonshire Building | 2016-09-24 17:30 | 46511.9217 | 740.016
Devonshire Building | 2016-09-24 17:45 | 46512.1067 | 740.016
Devonshire Building | 2016-09-24 18:00 | 46512.2917 | 740.016
Devonshire Building | 2016-09-24 18:15 | 46512.4768 | 740.016
Devonshire Building | 2016-09-24 18:30 | 46512.6568 | 720
Devonshire Building | 2016-09-24 18:45 | 46512.8418 | 740.016
Devonshire Building | 2016-09-24 19:00 | 46513.0268 | 740.016
Devonshire Building | 2016-09-24 19:15 | 46513.2118 | 740.016
Devonshire Building | 2016-09-24 19:30 | 46513.3968 | 740.016
Devonshire Building | 2016-09-24 19:45 | 46513.5868 | 759.996
Devonshire Building | 2016-09-24 20:00 | 46513.7718 | 740.016
Devonshire Building | 2016-09-24 20:15 | 46513.9568 | 740.016
Devonshire Building | 2016-09-24 20:30 | 46514.1418 | 740.016
Devonshire Building | 2016-09-24 20:45 | 46514.3268 | 740.016
Devonshire Building | 2016-09-24 21:00 | 46514.5368 | 839.988
Devonshire Building | 2016-09-24 21:15 | 46514.7218 | 740.016
Devonshire Building | 2016-09-24 21:30 | 46514.9068 | 740.016
Devonshire Building | 2016-09-24 21:45 | 46515.0918 | 740.016
Devonshire Building | 2016-09-24 22:00 | 46515.2918 | 799.992
Devonshire Building | 2016-09-24 22:15 | 46515.4918 | 799.992
Devonshire Building | 2016-09-24 22:30 | 46515.6968 | 820.008
Devonshire Building | 2016-09-24 22:45 | 46515.9018 | 820.008
Devonshire Building | 2016-09-24 23:00 | 46516.1018 | 799.992
Devonshire Building | 2016-09-24 23:15 | 46516.3068 | 820.008
Devonshire Building | 2016-09-24 23:30 | 46516.5118 | 820.008
Devonshire Building | 2016-09-24 23:45 | 46516.7168 | 820.008 | 720
Devonshire Building | 2016-09-25 | 46516.9141 | 799.992
Devonshire Building | 2016-09-25 00:15 | 46517.1041 | 759.996
Devonshire Building | 2016-09-25 00:30 | 46517.2891 | 740.016
Devonshire Building | 2016-09-25 00:45 | 46517.4791 | 759.996
Devonshire Building | 2016-09-25 01:00 | 46517.6691 | 759.996
Devonshire Building | 2016-09-25 01:15 | 46517.8591 | 759.996
Devonshire Building | 2016-09-25 01:30 | 46518.0491 | 759.996
Devonshire Building | 2016-09-25 01:45 | 46518.2391 | 759.996
Devonshire Building | 2016-09-25 02:00 | 46518.4241 | 740.016
Devonshire Building | 2016-09-25 02:15 | 46518.6141 | 759.996
Devonshire Building | 2016-09-25 02:30 | 46518.8041 | 759.996
Devonshire Building | 2016-09-25 02:45 | 46518.9941 | 759.996
Devonshire Building | 2016-09-25 03:00 | 46519.1841 | 759.996
Devonshire Building | 2016-09-25 03:15 | 46519.3741 | 759.996
Devonshire Building | 2016-09-25 03:30 | 46519.5591 | 740.016
Devonshire Building | 2016-09-25 03:45 | 46519.7491 | 759.996
Devonshire Building | 2016-09-25 04:00 | 46519.9391 | 759.996
Devonshire Building | 2016-09-25 04:15 | 46520.1291 | 759.996
Devonshire Building | 2016-09-25 04:30 | 46520.3191 | 759.996
Devonshire Building | 2016-09-25 04:45 | 46520.5091 | 759.996
Devonshire Building | 2016-09-25 05:00 | 46520.6991 | 759.996
Devonshire Building | 2016-09-25 05:15 | 46520.8891 | 759.996
Devonshire Building | 2016-09-25 05:30 | 46521.0791 | 759.996
Devonshire Building | 2016-09-25 05:45 | 46521.2691 | 759.996
Devonshire Building | 2016-09-25 06:00 | 46521.4591 | 759.996
Devonshire Building | 2016-09-25 06:15 | 46521.649 | 759.996
Devonshire Building | 2016-09-25 06:30 | 46521.8341 | 740.016
Devonshire Building | 2016-09-25 06:45 | 46522.0241 | 759.996
Devonshire Building | 2016-09-25 07:00 | 46522.2141 | 759.996
Devonshire Building | 2016-09-25 07:15 | 46522.4041 | 759.996
Devonshire Building | 2016-09-25 07:30 | 46522.5891 | 740.016
Devonshire Building | 2016-09-25 07:45 | 46522.7791 | 759.996
Devonshire Building | 2016-09-25 08:00 | 46522.9641 | 740.016
Devonshire Building | 2016-09-25 08:15 | 46523.1541 | 759.996
Devonshire Building | 2016-09-25 08:30 | 46523.3391 | 740.016
Devonshire Building | 2016-09-25 08:45 | 46523.5241 | 740.016
Devonshire Building | 2016-09-25 09:00 | 46523.7141 | 759.996
Devonshire Building | 2016-09-25 09:15 | 46523.8991 | 740.016
Devonshire Building | 2016-09-25 09:30 | 46524.0841 | 740.016
Devonshire Building | 2016-09-25 09:45 | 46524.2691 | 740.016
Devonshire Building | 2016-09-25 10:00 | 46524.4591 | 759.996
Devonshire Building | 2016-09-25 10:15 | 46524.6441 | 740.016
Devonshire Building | 2016-09-25 10:30 | 46524.8291 | 740.016
Devonshire Building | 2016-09-25 10:45 | 46525.0141 | 740.016
Devonshire Building | 2016-09-25 11:00 | 46525.2041 | 759.996
Devonshire Building | 2016-09-25 11:15 | 46525.3891 | 740.016
Devonshire Building | 2016-09-25 11:30 | 46525.5791 | 759.996
Devonshire Building | 2016-09-25 11:45 | 46525.7691 | 759.996
Devonshire Building | 2016-09-25 12:00 | 46525.9541 | 740.016
Devonshire Building | 2016-09-25 12:15 | 46526.1441 | 759.996
Devonshire Building | 2016-09-25 12:30 | 46526.3341 | 759.996
Devonshire Building | 2016-09-25 12:45 | 46526.7591 | 1699.992
Devonshire Building | 2016-09-25 13:00 | 46526.9491 | 759.996
Devonshire Building | 2016-09-25 13:15 | 46527.1391 | 759.996
Devonshire Building | 2016-09-25 13:30 | 46527.3291 | 759.996
Devonshire Building | 2016-09-25 13:45 | 46527.5141 | 740.016
Devonshire Building | 2016-09-25 14:00 | 46527.7041 | 759.996
Devonshire Building | 2016-09-25 14:15 | 46527.8941 | 759.996
Devonshire Building | 2016-09-25 14:30 | 46528.0841 | 759.996
Devonshire Building | 2016-09-25 14:45 | 46528.2741 | 759.996
Devonshire Building | 2016-09-25 15:00 | 46528.4641 | 759.996
Devonshire Building | 2016-09-25 15:15 | 46528.6541 | 759.996
Devonshire Building | 2016-09-25 15:30 | 46528.8441 | 759.996
Devonshire Building | 2016-09-25 15:45 | 46529.0291 | 740.016
Devonshire Building | 2016-09-25 16:00 | 46529.2141 | 740.016
Devonshire Building | 2016-09-25 16:15 | 46529.3991 | 740.016
Devonshire Building | 2016-09-25 16:30 | 46529.5891 | 759.996
Devonshire Building | 2016-09-25 16:45 | 46529.7741 | 740.016
Devonshire Building | 2016-09-25 17:00 | 46529.9591 | 740.016
Devonshire Building | 2016-09-25 17:15 | 46530.1441 | 740.016
Devonshire Building | 2016-09-25 17:30 | 46530.3291 | 740.016
Devonshire Building | 2016-09-25 17:45 | 46530.5141 | 740.016
Devonshire Building | 2016-09-25 18:00 | 46530.6991 | 740.016
Devonshire Building | 2016-09-25 18:15 | 46530.8841 | 740.016
Devonshire Building | 2016-09-25 18:30 | 46531.0691 | 740.016
Devonshire Building | 2016-09-25 18:45 | 46531.2541 | 740.016
Devonshire Building | 2016-09-25 19:00 | 46531.4391 | 740.016
Devonshire Building | 2016-09-25 19:15 | 46531.6241 | 740.016
Devonshire Building | 2016-09-25 19:30 | 46531.8141 | 759.996
Devonshire Building | 2016-09-25 19:45 | 46531.9991 | 740.016
Devonshire Building | 2016-09-25 20:00 | 46532.1841 | 740.016
Devonshire Building | 2016-09-25 20:15 | 46532.3741 | 759.996
Devonshire Building | 2016-09-25 20:30 | 46532.5591 | 740.016
Devonshire Building | 2016-09-25 20:45 | 46532.7491 | 759.996
Devonshire Building | 2016-09-25 21:00 | 46532.9541 | 820.008
Devonshire Building | 2016-09-25 21:15 | 46533.1392 | 740.016
Devonshire Building | 2016-09-25 21:30 | 46533.3242 | 740.016
Devonshire Building | 2016-09-25 21:45 | 46533.5142 | 759.996
Devonshire Building | 2016-09-25 22:00 | 46533.7042 | 759.996
Devonshire Building | 2016-09-25 22:15 | 46533.9092 | 820.008
Devonshire Building | 2016-09-25 22:30 | 46534.1142 | 820.008
Devonshire Building | 2016-09-25 22:45 | 46534.3192 | 820.008
Devonshire Building | 2016-09-25 23:00 | 46534.5242 | 820.008
Devonshire Building | 2016-09-25 23:15 | 46534.7292 | 820.008
Devonshire Building | 2016-09-25 23:30 | 46534.9342 | 820.008
Devonshire Building | 2016-09-25 23:45 | 46535.1392 | 820.008 | 740.016
Devonshire Building | 2016-09-26 | 46535.3398 | 799.992
Devonshire Building | 2016-09-26 00:15 | 46535.5298 | 759.996
Devonshire Building | 2016-09-26 00:30 | 46535.7198 | 759.996
Devonshire Building | 2016-09-26 00:45 | 46535.9148 | 780.012
Devonshire Building | 2016-09-26 01:00 | 46536.1048 | 759.996
Devonshire Building | 2016-09-26 01:15 | 46536.2998 | 780.012
Devonshire Building | 2016-09-26 01:30 | 46536.4898 | 759.996
Devonshire Building | 2016-09-26 01:45 | 46536.6848 | 780.012
Devonshire Building | 2016-09-26 02:00 | 46536.8748 | 759.996
Devonshire Building | 2016-09-26 02:15 | 46537.0648 | 759.996
Devonshire Building | 2016-09-26 02:30 | 46537.2598 | 780.012
Devonshire Building | 2016-09-26 02:45 | 46537.4498 | 759.996
Devonshire Building | 2016-09-26 03:00 | 46537.6448 | 780.012
Devonshire Building | 2016-09-26 03:15 | 46537.8348 | 759.996
Devonshire Building | 2016-09-26 03:30 | 46538.0298 | 780.012
Devonshire Building | 2016-09-26 03:45 | 46538.2249 | 780.012
Devonshire Building | 2016-09-26 04:00 | 46538.4149 | 759.996
Devonshire Building | 2016-09-26 04:15 | 46538.6099 | 780.012
Devonshire Building | 2016-09-26 04:30 | 46538.8049 | 780.012
Devonshire Building | 2016-09-26 04:45 | 46538.9949 | 759.996
Devonshire Building | 2016-09-26 05:00 | 46539.1849 | 759.996
Devonshire Building | 2016-09-26 05:15 | 46539.3799 | 780.012
Devonshire Building | 2016-09-26 05:30 | 46539.8049 | 1699.992
Devonshire Building | 2016-09-26 05:45 | 46539.9949 | 759.996
Devonshire Building | 2016-09-26 06:00 | 46540.1849 | 759.996
Devonshire Building | 2016-09-26 06:15 | 46540.3699 | 740.016
Devonshire Building | 2016-09-26 06:30 | 46540.5649 | 780.012
Devonshire Building | 2016-09-26 06:45 | 46540.7599 | 780.012
Devonshire Building | 2016-09-26 07:00 | 46540.9499 | 759.996
Devonshire Building | 2016-09-26 07:15 | 46541.1449 | 780.012
Devonshire Building | 2016-09-26 07:30 | 46541.3499 | 820.008
Devonshire Building | 2016-09-26 07:45 | 46541.5349 | 740.016
Devonshire Building | 2016-09-26 08:00 | 46541.7299 | 780.012
Devonshire Building | 2016-09-26 08:15 | 46541.9199 | 759.996
Devonshire Building | 2016-09-26 08:30 | 46542.1049 | 740.016
Devonshire Building | 2016-09-26 08:45 | 46542.2949 | 759.996
Devonshire Building | 2016-09-26 09:00 | 46542.7449 | 1800
Devonshire Building | 2016-09-26 09:15 | 46542.9399 | 780.012
Devonshire Building | 2016-09-26 09:30 | 46543.1349 | 780.012
Devonshire Building | 2016-09-26 09:45 | 46543.3799 | 979.992
Devonshire Building | 2016-09-26 10:00 | 46543.7049 | 1299.996
Devonshire Building | 2016-09-26 10:15 | 46544.2399 | 2139.984
Devonshire Building | 2016-09-26 10:30 | 46544.5349 | 1180.008
Devonshire Building | 2016-09-26 10:45 | 46544.8199 | 1140.012
Devonshire Building | 2016-09-26 11:00 | 46545.0849 | 1059.984
Devonshire Building | 2016-09-26 11:15 | 46545.3299 | 979.992
Devonshire Building | 2016-09-26 11:30 | 46545.5599 | 920.016
Devonshire Building | 2016-09-26 11:45 | 46545.8949 | 1339.992
Devonshire Building | 2016-09-26 12:00 | 46546.2199 | 1299.996
Devonshire Building | 2016-09-26 12:15 | 46546.4249 | 820.008
Devonshire Building | 2016-09-26 12:30 | 46546.6249 | 799.992
Devonshire Building | 2016-09-26 12:45 | 46546.8249 | 799.992
Devonshire Building | 2016-09-26 13:00 | 46547.0249 | 799.992
Devonshire Building | 2016-09-26 13:15 | 46547.2249 | 799.992
Devonshire Building | 2016-09-26 13:30 | 46547.4249 | 799.992
Devonshire Building | 2016-09-26 13:45 | 46547.6249 | 799.992
Devonshire Building | 2016-09-26 14:00 | 46548.0749 | 1800
Devonshire Building | 2016-09-26 14:15 | 46548.2899 | 860.004
Devonshire Building | 2016-09-26 14:30 | 46548.5049 | 860.004
Devonshire Building | 2016-09-26 14:45 | 46548.7349 | 920.016
Devonshire Building | 2016-09-26 15:00 | 46548.9449 | 839.988
Devonshire Building | 2016-09-26 15:15 | 46549.1599 | 860.004
Devonshire Building | 2016-09-26 15:30 | 46549.3699 | 839.988
Devonshire Building | 2016-09-26 15:45 | 46549.5799 | 839.988
Devonshire Building | 2016-09-26 16:00 | 46549.7949 | 860.004
Devonshire Building | 2016-09-26 16:15 | 46550.2799 | 1940.004
Devonshire Building | 2016-09-26 16:30 | 46550.4849 | 820.008
Devonshire Building | 2016-09-26 16:45 | 46550.6849 | 799.992
Devonshire Building | 2016-09-26 17:00 | 46550.8849 | 799.992
Devonshire Building | 2016-09-26 17:15 | 46551.0849 | 799.992
Devonshire Building | 2016-09-26 17:30 | 46551.2849 | 799.992
Devonshire Building | 2016-09-26 17:45 | 46551.4849 | 799.992
Devonshire Building | 2016-09-26 18:00 | 46551.6799 | 780.012
Devonshire Building | 2016-09-26 18:15 | 46551.8799 | 799.992
Devonshire Building | 2016-09-26 18:30 | 46552.0749 | 780.012
Devonshire Building | 2016-09-26 18:45 | 46552.2699 | 780.012
Devonshire Building | 2016-09-26 19:00 | 46552.4649 | 780.012
Devonshire Building | 2016-09-26 19:15 | 46552.6599 | 780.012
Devonshire Building | 2016-09-26 19:30 | 46552.8549 | 780.012
Devonshire Building | 2016-09-26 19:45 | 46553.0499 | 780.012
Devonshire Building | 2016-09-26 20:00 | 46553.2399 | 759.996
Devonshire Building | 2016-09-26 20:15 | 46553.4349 | 780.012
Devonshire Building | 2016-09-26 20:30 | 46553.6249 | 759.996
Devonshire Building | 2016-09-26 20:45 | 46553.8199 | 780.012
Devonshire Building | 2016-09-26 21:00 | 46554.0299 | 839.988
Devonshire Building | 2016-09-26 21:15 | 46554.2149 | 740.016
Devonshire Building | 2016-09-26 21:30 | 46554.4049 | 759.996
Devonshire Building | 2016-09-26 21:45 | 46554.5949 | 759.996
Devonshire Building | 2016-09-26 22:00 | 46554.7799 | 740.016
Devonshire Building | 2016-09-26 22:15 | 46554.9699 | 759.996
Devonshire Building | 2016-09-26 22:30 | 46555.1599 | 759.996
Devonshire Building | 2016-09-26 22:45 | 46555.3549 | 780.012
Devonshire Building | 2016-09-26 23:00 | 46555.5449 | 759.996
Devonshire Building | 2016-09-26 23:15 | 46555.7349 | 759.996
Devonshire Building | 2016-09-26 23:30 | 46555.9299 | 780.012
Devonshire Building | 2016-09-26 23:45 | 46556.1199 | 759.996 | 740.016
Devonshire Building | 2016-09-27 | 46556.3086 | 759.996
Devonshire Building | 2016-09-27 00:15 | 46556.5036 | 780.012
Devonshire Building | 2016-09-27 00:30 | 46556.6936 | 759.996
Devonshire Building | 2016-09-27 00:45 | 46556.8886 | 780.012
Devonshire Building | 2016-09-27 01:00 | 46557.0836 | 780.012
Devonshire Building | 2016-09-27 01:15 | 46557.2786 | 780.012
Devonshire Building | 2016-09-27 01:30 | 46557.4736 | 780.012
Devonshire Building | 2016-09-27 01:45 | 46557.6636 | 759.996
Devonshire Building | 2016-09-27 02:00 | 46557.8586 | 780.012
Devonshire Building | 2016-09-27 02:15 | 46558.0536 | 780.012
Devonshire Building | 2016-09-27 02:30 | 46558.2486 | 780.012
Devonshire Building | 2016-09-27 02:45 | 46558.4436 | 780.012
Devonshire Building | 2016-09-27 03:00 | 46558.6386 | 780.012
Devonshire Building | 2016-09-27 03:15 | 46558.8336 | 780.012
Devonshire Building | 2016-09-27 03:30 | 46559.0286 | 780.012
Devonshire Building | 2016-09-27 03:45 | 46559.2236 | 780.012
Devonshire Building | 2016-09-27 04:00 | 46559.4186 | 780.012
Devonshire Building | 2016-09-27 04:15 | 46559.6136 | 780.012
Devonshire Building | 2016-09-27 04:30 | 46559.8086 | 780.012
Devonshire Building | 2016-09-27 04:45 | 46560.0036 | 780.012
Devonshire Building | 2016-09-27 05:00 | 46560.1986 | 780.012
Devonshire Building | 2016-09-27 05:15 | 46560.3936 | 780.012
Devonshire Building | 2016-09-27 05:30 | 46560.5886 | 780.012
Devonshire Building | 2016-09-27 05:45 | 46560.7837 | 780.012
Devonshire Building | 2016-09-27 06:00 | 46560.9736 | 759.996
Devonshire Building | 2016-09-27 06:15 | 46561.1687 | 780.012
Devonshire Building | 2016-09-27 06:30 | 46561.3587 | 759.996
Devonshire Building | 2016-09-27 06:45 | 46561.5586 | 799.992
Devonshire Building | 2016-09-27 07:00 | 46561.7486 | 759.996
Devonshire Building | 2016-09-27 07:15 | 46562.0636 | 1260
Devonshire Building | 2016-09-27 07:30 | 46562.3736 | 1239.984
Devonshire Building | 2016-09-27 07:45 | 46562.5686 | 780.012
Devonshire Building | 2016-09-27 08:00 | 46562.7586 | 759.996
Devonshire Building | 2016-09-27 08:15 | 46562.9537 | 780.012
Devonshire Building | 2016-09-27 08:30 | 46563.1436 | 759.996
Devonshire Building | 2016-09-27 08:45 | 46563.3387 | 780.012
Devonshire Building | 2016-09-27 09:00 | 46563.5287 | 759.996
Devonshire Building | 2016-09-27 09:15 | 46563.7237 | 780.012
Devonshire Building | 2016-09-27 09:30 | 46564.1937 | 1879.992
Devonshire Building | 2016-09-27 09:45 | 46564.3887 | 780.012
Devonshire Building | 2016-09-27 10:00 | 46564.5787 | 759.996
Devonshire Building | 2016-09-27 10:15 | 46564.7787 | 799.992
Devonshire Building | 2016-09-27 10:30 | 46564.9737 | 780.012
Devonshire Building | 2016-09-27 10:45 | 46565.1737 | 799.992
Devonshire Building | 2016-09-27 11:00 | 46565.4037 | 920.016
Devonshire Building | 2016-09-27 11:15 | 46565.7637 | 1440
Devonshire Building | 2016-09-27 11:30 | 46566.1737 | 1640.016
Devonshire Building | 2016-09-27 11:45 | 46566.4537 | 1119.996
Devonshire Building | 2016-09-27 12:00 | 46566.7287 | 1100.016
Devonshire Building | 2016-09-27 12:15 | 46566.9987 | 1080
Devonshire Building | 2016-09-27 12:30 | 46567.2787 | 1119.996
Devonshire Building | 2016-09-27 12:45 | 46567.5437 | 1059.984
Devonshire Building | 2016-09-27 13:00 | 46567.7937 | 1000.008
Devonshire Building | 2016-09-27 13:15 | 46568.2887 | 1980
Devonshire Building | 2016-09-27 13:30 | 46568.5037 | 860.004
Devonshire Building | 2016-09-27 13:45 | 46568.7237 | 879.984
Devonshire Building | 2016-09-27 14:00 | 46568.9487 | 900
Devonshire Building | 2016-09-27 14:15 | 46569.1687 | 879.984
Devonshire Building | 2016-09-27 14:30 | 46569.3887 | 879.984
Devonshire Building | 2016-09-27 14:45 | 46569.6086 | 879.984
Devonshire Building | 2016-09-27 15:00 | 46569.8286 | 879.984
Devonshire Building | 2016-09-27 15:15 | 46570.0536 | 900
Devonshire Building | 2016-09-27 15:30 | 46570.2786 | 900
Devonshire Building | 2016-09-27 15:45 | 46570.7886 | 2040.012
Devonshire Building | 2016-09-27 16:00 | 46571.0286 | 960.012
Devonshire Building | 2016-09-27 16:15 | 46571.2836 | 1019.988
Devonshire Building | 2016-09-27 16:30 | 46571.5336 | 1000.008
Devonshire Building | 2016-09-27 16:45 | 46571.7886 | 1019.988
Devonshire Building | 2016-09-27 17:00 | 46572.0336 | 979.992
Devonshire Building | 2016-09-27 17:15 | 46572.2686 | 939.996
Devonshire Building | 2016-09-27 17:30 | 46572.4936 | 900
Devonshire Building | 2016-09-27 17:45 | 46572.7186 | 900
Devonshire Building | 2016-09-27 18:00 | 46572.9336 | 860.004
Devonshire Building | 2016-09-27 18:15 | 46573.1486 | 860.004
Devonshire Building | 2016-09-27 18:30 | 46573.3586 | 839.988
Devonshire Building | 2016-09-27 18:45 | 46573.5636 | 820.008
Devonshire Building | 2016-09-27 19:00 | 46573.7736 | 839.988
Devonshire Building | 2016-09-27 19:15 | 46573.9736 | 799.992
Devonshire Building | 2016-09-27 19:30 | 46574.1786 | 820.008
Devonshire Building | 2016-09-27 19:45 | 46574.3836 | 820.008
Devonshire Building | 2016-09-27 20:00 | 46574.5886 | 820.008
Devonshire Building | 2016-09-27 20:15 | 46574.7886 | 799.992
Devonshire Building | 2016-09-27 20:30 | 46574.9886 | 799.992
Devonshire Building | 2016-09-27 20:45 | 46575.1936 | 820.008
Devonshire Building | 2016-09-27 21:00 | 46575.4136 | 879.984
Devonshire Building | 2016-09-27 21:15 | 46575.6136 | 799.992
Devonshire Building | 2016-09-27 21:30 | 46575.8136 | 799.992
Devonshire Building | 2016-09-27 21:45 | 46576.0086 | 780.012
Devonshire Building | 2016-09-27 22:00 | 46576.2386 | 920.016
Devonshire Building | 2016-09-27 22:15 | 46576.6486 | 1640.016
Devonshire Building | 2016-09-27 22:30 | 46576.8486 | 799.992
Devonshire Building | 2016-09-27 22:45 | 46577.0436 | 780.012
Devonshire Building | 2016-09-27 23:00 | 46577.2486 | 820.008
Devonshire Building | 2016-09-27 23:15 | 46577.4437 | 780.012
Devonshire Building | 2016-09-27 23:30 | 46577.6436 | 799.992
Devonshire Building | 2016-09-27 23:45 | 46577.8436 | 799.992 | 759.996
Devonshire Building | 2016-09-28 | 46578.043 | 799.992
Devonshire Building | 2016-09-28 00:15 | 46578.243 | 799.992
Devonshire Building | 2016-09-28 00:30 | 46578.443 | 799.992
Devonshire Building | 2016-09-28 00:45 | 46578.643 | 799.992
Devonshire Building | 2016-09-28 01:00 | 46578.843 | 799.992
Devonshire Building | 2016-09-28 01:15 | 46579.043 | 799.992
Devonshire Building | 2016-09-28 01:30 | 46579.243 | 799.992
Devonshire Building | 2016-09-28 01:45 | 46579.443 | 799.992
Devonshire Building | 2016-09-28 02:00 | 46579.643 | 799.992
Devonshire Building | 2016-09-28 02:15 | 46579.843 | 799.992
Devonshire Building | 2016-09-28 02:30 | 46580.043 | 799.992
Devonshire Building | 2016-09-28 02:45 | 46580.2429 | 799.992
Devonshire Building | 2016-09-28 03:00 | 46580.4429 | 799.992
Devonshire Building | 2016-09-28 03:15 | 46580.6429 | 799.992
Devonshire Building | 2016-09-28 03:30 | 46580.8429 | 799.992
Devonshire Building | 2016-09-28 03:45 | 46581.0429 | 799.992
Devonshire Building | 2016-09-28 04:00 | 46581.2429 | 799.992
Devonshire Building | 2016-09-28 04:15 | 46581.4429 | 799.992
Devonshire Building | 2016-09-28 04:30 | 46581.6429 | 799.992
Devonshire Building | 2016-09-28 04:45 | 46581.8429 | 799.992
Devonshire Building | 2016-09-28 05:00 | 46582.0429 | 799.992
Devonshire Building | 2016-09-28 05:15 | 46582.2379 | 780.012
Devonshire Building | 2016-09-28 05:30 | 46582.4379 | 799.992
Devonshire Building | 2016-09-28 05:45 | 46582.6379 | 799.992
Devonshire Building | 2016-09-28 06:00 | 46582.8379 | 799.992
Devonshire Building | 2016-09-28 06:15 | 46583.0379 | 799.992
Devonshire Building | 2016-09-28 06:30 | 46583.2329 | 780.012
Devonshire Building | 2016-09-28 06:45 | 46583.4329 | 799.992
Devonshire Building | 2016-09-28 07:00 | 46583.6329 | 799.992
Devonshire Building | 2016-09-28 07:15 | 46583.8329 | 799.992
Devonshire Building | 2016-09-28 07:30 | 46584.0329 | 799.992
Devonshire Building | 2016-09-28 07:45 | 46584.2329 | 799.992
Devonshire Building | 2016-09-28 08:00 | 46584.6779 | 1779.984
Devonshire Building | 2016-09-28 08:15 | 46584.8879 | 839.988
Devonshire Building | 2016-09-28 08:30 | 46585.0879 | 799.992
Devonshire Building | 2016-09-28 08:45 | 46585.2829 | 780.012
Devonshire Building | 2016-09-28 09:00 | 46585.4879 | 820.008
Devonshire Building | 2016-09-28 09:15 | 46585.6829 | 780.012
Devonshire Building | 2016-09-28 09:30 | 46586.1529 | 1879.992
Devonshire Building | 2016-09-28 09:45 | 46586.4029 | 1000.008
Devonshire Building | 2016-09-28 10:00 | 46586.6729 | 1080
Devonshire Building | 2016-09-28 10:15 | 46586.9529 | 1119.996
Devonshire Building | 2016-09-28 10:30 | 46587.2779 | 1299.996
Devonshire Building | 2016-09-28 10:45 | 46587.5929 | 1260
Devonshire Building | 2016-09-28 11:00 | 46588.1279 | 2139.984
Devonshire Building | 2016-09-28 11:15 | 46588.3779 | 1000.008
Devonshire Building | 2016-09-28 11:30 | 46588.6429 | 1059.984
Devonshire Building | 2016-09-28 11:45 | 46588.9229 | 1119.996
Devonshire Building | 2016-09-28 12:00 | 46589.1979 | 1100.016
Devonshire Building | 2016-09-28 12:15 | 46589.4729 | 1100.016
Devonshire Building | 2016-09-28 12:30 | 46589.7529 | 1119.996
Devonshire Building | 2016-09-28 12:45 | 46590.0279 | 1100.016
Devonshire Building | 2016-09-28 13:00 | 46590.5529 | 2099.988
Devonshire Building | 2016-09-28 13:15 | 46590.8129 | 1040.004
Devonshire Building | 2016-09-28 13:30 | 46591.0779 | 1059.984
Devonshire Building | 2016-09-28 13:45 | 46591.3379 | 1040.004
Devonshire Building | 2016-09-28 14:00 | 46591.6079 | 1080
Devonshire Building | 2016-09-28 14:15 | 46591.8629 | 1019.988
Devonshire Building | 2016-09-28 14:30 | 46592.1179 | 1019.988
Devonshire Building | 2016-09-28 14:45 | 46592.3679 | 1000.008
Devonshire Building | 2016-09-28 15:00 | 46592.6029 | 939.996
Devonshire Building | 2016-09-28 15:15 | 46593.0779 | 1900.008
Devonshire Building | 2016-09-28 15:30 | 46593.2879 | 839.988
Devonshire Building | 2016-09-28 15:45 | 46593.5079 | 879.984
Devonshire Building | 2016-09-28 16:00 | 46593.7229 | 860.004
Devonshire Building | 2016-09-28 16:15 | 46593.9329 | 839.988
Devonshire Building | 2016-09-28 16:30 | 46594.1429 | 839.988
Devonshire Building | 2016-09-28 16:45 | 46594.3529 | 839.988
Devonshire Building | 2016-09-28 17:00 | 46594.5629 | 839.988
Devonshire Building | 2016-09-28 17:15 | 46594.7679 | 820.008
Devonshire Building | 2016-09-28 17:30 | 46594.9779 | 839.988
Devonshire Building | 2016-09-28 17:45 | 46595.1879 | 839.988
Devonshire Building | 2016-09-28 18:00 | 46595.3929 | 820.008
Devonshire Building | 2016-09-28 18:15 | 46595.5979 | 820.008
Devonshire Building | 2016-09-28 18:30 | 46595.8029 | 820.008
Devonshire Building | 2016-09-28 18:45 | 46596.0079 | 820.008
Devonshire Building | 2016-09-28 19:00 | 46596.4479 | 1760.004
Devonshire Building | 2016-09-28 19:15 | 46596.6579 | 839.988
Devonshire Building | 2016-09-28 19:30 | 46596.8629 | 820.008
Devonshire Building | 2016-09-28 19:45 | 46597.0679 | 820.008
Devonshire Building | 2016-09-28 20:00 | 46597.2729 | 820.008
Devonshire Building | 2016-09-28 20:15 | 46597.4779 | 820.008
Devonshire Building | 2016-09-28 20:30 | 46597.6829 | 820.008
Devonshire Building | 2016-09-28 20:45 | 46597.8879 | 820.008
Devonshire Building | 2016-09-28 21:00 | 46598.1079 | 879.984
Devonshire Building | 2016-09-28 21:15 | 46598.3129 | 820.008
Devonshire Building | 2016-09-28 21:30 | 46598.5129 | 799.992
Devonshire Building | 2016-09-28 21:45 | 46598.7179 | 820.008
Devonshire Building | 2016-09-28 22:00 | 46598.9179 | 799.992
Devonshire Building | 2016-09-28 22:15 | 46599.1229 | 820.008
Devonshire Building | 2016-09-28 22:30 | 46599.3229 | 799.992
Devonshire Building | 2016-09-28 22:45 | 46599.5279 | 820.008
Devonshire Building | 2016-09-28 23:00 | 46599.7329 | 820.008
Devonshire Building | 2016-09-28 23:15 | 46599.9379 | 820.008
Devonshire Building | 2016-09-28 23:30 | 46600.1429 | 820.008
Devonshire Building | 2016-09-28 23:45 | 46600.3479 | 820.008 | 780.012
Devonshire Building | 2016-09-29 | 46600.5547 | 820.008
Devonshire Building | 2016-09-29 00:15 | 46600.7597 | 820.008
Devonshire Building | 2016-09-29 00:30 | 46600.9647 | 820.008
Devonshire Building | 2016-09-29 00:45 | 46601.1697 | 820.008
Devonshire Building | 2016-09-29 01:00 | 46601.3747 | 820.008
Devonshire Building | 2016-09-29 01:15 | 46601.5797 | 820.008
Devonshire Building | 2016-09-29 01:30 | 46601.7847 | 820.008
Devonshire Building | 2016-09-29 01:45 | 46601.9847 | 799.992
Devonshire Building | 2016-09-29 02:00 | 46602.1897 | 820.008
Devonshire Building | 2016-09-29 02:15 | 46602.3947 | 820.008
Devonshire Building | 2016-09-29 02:30 | 46602.5997 | 820.008
Devonshire Building | 2016-09-29 02:45 | 46602.8047 | 820.008
Devonshire Building | 2016-09-29 03:00 | 46603.0097 | 820.008
Devonshire Building | 2016-09-29 03:15 | 46603.2097 | 799.992
Devonshire Building | 2016-09-29 03:30 | 46603.4147 | 820.008
Devonshire Building | 2016-09-29 03:45 | 46603.6197 | 820.008
Devonshire Building | 2016-09-29 04:00 | 46603.8247 | 820.008
Devonshire Building | 2016-09-29 04:15 | 46604.0297 | 820.008
Devonshire Building | 2016-09-29 04:30 | 46604.2297 | 799.992
Devonshire Building | 2016-09-29 04:45 | 46604.4347 | 820.008
Devonshire Building | 2016-09-29 05:00 | 46604.6347 | 799.992
Devonshire Building | 2016-09-29 05:15 | 46604.8397 | 820.008
Devonshire Building | 2016-09-29 05:30 | 46605.0397 | 799.992
Devonshire Building | 2016-09-29 05:45 | 46605.2447 | 820.008
Devonshire Building | 2016-09-29 06:00 | 46605.4447 | 799.992
Devonshire Building | 2016-09-29 06:15 | 46605.6447 | 799.992
Devonshire Building | 2016-09-29 06:30 | 46605.8447 | 799.992
Devonshire Building | 2016-09-29 06:45 | 46606.0447 | 799.992
Devonshire Building | 2016-09-29 07:00 | 46606.2447 | 799.992
Devonshire Building | 2016-09-29 07:15 | 46606.4497 | 820.008
Devonshire Building | 2016-09-29 07:30 | 46606.6547 | 820.008
Devonshire Building | 2016-09-29 07:45 | 46606.8647 | 839.988
Devonshire Building | 2016-09-29 08:00 | 46607.0647 | 799.992
Devonshire Building | 2016-09-29 08:15 | 46607.5197 | 1820.016
Devonshire Building | 2016-09-29 08:30 | 46607.7247 | 820.008
Devonshire Building | 2016-09-29 08:45 | 46607.9247 | 799.992
Devonshire Building | 2016-09-29 09:00 | 46608.1297 | 820.008
Devonshire Building | 2016-09-29 09:15 | 46608.3297 | 799.992
Devonshire Building | 2016-09-29 09:30 | 46608.7097 | 1519.992
Devonshire Building | 2016-09-29 09:45 | 46608.9847 | 1100.016
Devonshire Building | 2016-09-29 10:00 | 46609.1997 | 860.004
Devonshire Building | 2016-09-29 10:15 | 46609.4247 | 900
Devonshire Building | 2016-09-29 10:30 | 46609.6847 | 1040.004
Devonshire Building | 2016-09-29 10:45 | 46609.9497 | 1059.984
Devonshire Building | 2016-09-29 11:00 | 46610.2147 | 1059.984
Devonshire Building | 2016-09-29 11:15 | 46610.4847 | 1080
Devonshire Building | 2016-09-29 11:30 | 46611.0247 | 2160
Devonshire Building | 2016-09-29 11:45 | 46611.2847 | 1040.004
Devonshire Building | 2016-09-29 12:00 | 46611.5447 | 1040.004
Devonshire Building | 2016-09-29 12:15 | 46611.8147 | 1080
Devonshire Building | 2016-09-29 12:30 | 46612.0747 | 1040.004
Devonshire Building | 2016-09-29 12:45 | 46612.3247 | 1000.008
Devonshire Building | 2016-09-29 13:00 | 46612.5697 | 979.992
Devonshire Building | 2016-09-29 13:15 | 46612.8247 | 1019.988
Devonshire Building | 2016-09-29 13:30 | 46613.3397 | 2059.992
Devonshire Building | 2016-09-29 13:45 | 46613.5797 | 960.012
Devonshire Building | 2016-09-29 14:00 | 46613.8297 | 1000.008
Devonshire Building | 2016-09-29 14:15 | 46614.1047 | 1100.016
Devonshire Building | 2016-09-29 14:30 | 46614.4147 | 1239.984
Devonshire Building | 2016-09-29 14:45 | 46614.7497 | 1339.992
Devonshire Building | 2016-09-29 15:00 | 46615.0897 | 1360.008
Devonshire Building | 2016-09-29 15:15 | 46615.4047 | 1260
Devonshire Building | 2016-09-29 15:30 | 46615.6947 | 1159.992
Devonshire Building | 2016-09-29 15:45 | 46616.2297 | 2139.984
Devonshire Building | 2016-09-29 16:00 | 46616.5247 | 1180.008
Devonshire Building | 2016-09-29 16:15 | 46616.7947 | 1080
Devonshire Building | 2016-09-29 16:30 | 46617.0447 | 1000.008
Devonshire Building | 2016-09-29 16:45 | 46617.2897 | 979.992
Devonshire Building | 2016-09-29 17:00 | 46617.5297 | 960.012
Devonshire Building | 2016-09-29 17:15 | 46617.7647 | 939.996
Devonshire Building | 2016-09-29 17:30 | 46617.9997 | 939.996
Devonshire Building | 2016-09-29 17:45 | 46618.2347 | 939.996
Devonshire Building | 2016-09-29 18:00 | 46618.4747 | 960.012
Devonshire Building | 2016-09-29 18:15 | 46618.7047 | 920.016
Devonshire Building | 2016-09-29 18:30 | 46618.9397 | 939.996
Devonshire Building | 2016-09-29 18:45 | 46619.1597 | 879.984
Devonshire Building | 2016-09-29 19:00 | 46619.3797 | 879.984
Devonshire Building | 2016-09-29 19:15 | 46619.5947 | 860.004
Devonshire Building | 2016-09-29 19:30 | 46619.8097 | 860.004
Devonshire Building | 2016-09-29 19:45 | 46620.0197 | 839.988
Devonshire Building | 2016-09-29 20:00 | 46620.2297 | 839.988
Devonshire Building | 2016-09-29 20:15 | 46620.4397 | 839.988
Devonshire Building | 2016-09-29 20:30 | 46620.6497 | 839.988
Devonshire Building | 2016-09-29 20:45 | 46620.8597 | 839.988
Devonshire Building | 2016-09-29 21:00 | 46621.0897 | 920.016
Devonshire Building | 2016-09-29 21:15 | 46621.2897 | 799.992
Devonshire Building | 2016-09-29 21:30 | 46621.4897 | 799.992
Devonshire Building | 2016-09-29 21:45 | 46621.6947 | 820.008
Devonshire Building | 2016-09-29 22:00 | 46621.8997 | 820.008
Devonshire Building | 2016-09-29 22:15 | 46622.0997 | 799.992
Devonshire Building | 2016-09-29 22:30 | 46622.3047 | 820.008
Devonshire Building | 2016-09-29 22:45 | 46622.5047 | 799.992
Devonshire Building | 2016-09-29 23:00 | 46622.7097 | 820.008
Devonshire Building | 2016-09-29 23:15 | 46622.9147 | 820.008
Devonshire Building | 2016-09-29 23:30 | 46623.1197 | 820.008
Devonshire Building | 2016-09-29 23:45 | 46623.3247 | 820.008 | 799.992
Devonshire Building | 2016-09-30 | 46623.5312 | 820.008
Devonshire Building | 2016-09-30 00:15 | 46623.7363 | 820.008
Devonshire Building | 2016-09-30 00:30 | 46623.9413 | 820.008
Devonshire Building | 2016-09-30 00:45 | 46624.1463 | 820.008
Devonshire Building | 2016-09-30 01:00 | 46624.3513 | 820.008
Devonshire Building | 2016-09-30 01:15 | 46624.5563 | 820.008
Devonshire Building | 2016-09-30 01:30 | 46624.7613 | 820.008
Devonshire Building | 2016-09-30 01:45 | 46624.9663 | 820.008
Devonshire Building | 2016-09-30 02:00 | 46625.1763 | 839.988
Devonshire Building | 2016-09-30 02:15 | 46625.3813 | 820.008
Devonshire Building | 2016-09-30 02:30 | 46625.8213 | 1760.004
Devonshire Building | 2016-09-30 02:45 | 46626.0263 | 820.008
Devonshire Building | 2016-09-30 03:00 | 46626.2313 | 820.008
Devonshire Building | 2016-09-30 03:15 | 46626.4413 | 839.988
Devonshire Building | 2016-09-30 03:30 | 46626.6463 | 820.008
Devonshire Building | 2016-09-30 03:45 | 46626.8513 | 820.008
Devonshire Building | 2016-09-30 04:00 | 46627.0563 | 820.008
Devonshire Building | 2016-09-30 04:15 | 46627.2613 | 820.008
Devonshire Building | 2016-09-30 04:30 | 46627.4663 | 820.008
Devonshire Building | 2016-09-30 04:45 | 46627.6713 | 820.008
Devonshire Building | 2016-09-30 05:00 | 46627.8763 | 820.008
Devonshire Building | 2016-09-30 05:15 | 46628.0813 | 820.008
Devonshire Building | 2016-09-30 05:30 | 46628.2863 | 820.008
Devonshire Building | 2016-09-30 05:45 | 46628.4863 | 799.992
Devonshire Building | 2016-09-30 06:00 | 46628.6913 | 820.008
Devonshire Building | 2016-09-30 06:15 | 46628.8913 | 799.992
Devonshire Building | 2016-09-30 06:30 | 46629.0963 | 820.008
Devonshire Building | 2016-09-30 06:45 | 46629.2963 | 799.992
Devonshire Building | 2016-09-30 07:00 | 46629.5063 | 839.988
Devonshire Building | 2016-09-30 07:15 | 46629.7163 | 839.988
Devonshire Building | 2016-09-30 07:30 | 46629.9163 | 799.992
Devonshire Building | 2016-09-30 07:45 | 46630.1363 | 879.984
Devonshire Building | 2016-09-30 08:00 | 46630.3363 | 799.992
Devonshire Building | 2016-09-30 08:15 | 46630.5413 | 820.008
Devonshire Building | 2016-09-30 08:30 | 46630.7413 | 799.992
Devonshire Building | 2016-09-30 08:45 | 46630.9463 | 820.008
Devonshire Building | 2016-09-30 09:00 | 46631.4163 | 1879.992
Devonshire Building | 2016-09-30 09:15 | 46631.6363 | 879.984
Devonshire Building | 2016-09-30 09:30 | 46631.8763 | 960.012
Devonshire Building | 2016-09-30 09:45 | 46632.1413 | 1059.984
Devonshire Building | 2016-09-30 10:00 | 46632.4163 | 1100.016
Devonshire Building | 2016-09-30 10:15 | 46632.6913 | 1100.016
Devonshire Building | 2016-09-30 10:30 | 46633.1963 | 2019.996
Devonshire Building | 2016-09-30 10:45 | 46633.4563 | 1040.004
Devonshire Building | 2016-09-30 11:00 | 46633.7213 | 1059.984
Devonshire Building | 2016-09-30 11:15 | 46633.9863 | 1059.984
Devonshire Building | 2016-09-30 11:30 | 46634.2513 | 1059.984
Devonshire Building | 2016-09-30 11:45 | 46634.5013 | 1000.008
Devonshire Building | 2016-09-30 12:00 | 46634.7463 | 979.992
Devonshire Building | 2016-09-30 12:15 | 46635.2213 | 1900.008
Devonshire Building | 2016-09-30 12:30 | 46635.4463 | 900
Devonshire Building | 2016-09-30 12:45 | 46635.6713 | 900
Devonshire Building | 2016-09-30 13:00 | 46635.8963 | 900
Devonshire Building | 2016-09-30 13:15 | 46636.1213 | 900
Devonshire Building | 2016-09-30 13:30 | 46636.3513 | 920.016
Devonshire Building | 2016-09-30 13:45 | 46636.5713 | 879.984
Devonshire Building | 2016-09-30 14:00 | 46636.8013 | 920.016
Devonshire Building | 2016-09-30 14:15 | 46637.0313 | 920.016
Devonshire Building | 2016-09-30 14:30 | 46637.3013 | 1080
Devonshire Building | 2016-09-30 14:45 | 46637.7513 | 1800
Devonshire Building | 2016-09-30 15:00 | 46637.9813 | 920.016
Devonshire Building | 2016-09-30 15:15 | 46638.2313 | 1000.008
Devonshire Building | 2016-09-30 15:30 | 46638.5063 | 1100.016
Devonshire Building | 2016-09-30 15:45 | 46638.7863 | 1119.996
Devonshire Building | 2016-09-30 16:00 | 46639.1213 | 1339.992
Devonshire Building | 2016-09-30 16:15 | 46639.5163 | 1580.004
Devonshire Building | 2016-09-30 16:30 | 46639.8463 | 1320.012
Devonshire Building | 2016-09-30 16:45 | 46640.1413 | 1180.008
Devonshire Building | 2016-09-30 17:00 | 46640.4313 | 1159.992
Devonshire Building | 2016-09-30 17:15 | 46640.7013 | 1080
Devonshire Building | 2016-09-30 17:30 | 46640.9463 | 979.992
Devonshire Building | 2016-09-30 17:45 | 46641.1813 | 939.996
Devonshire Building | 2016-09-30 18:00 | 46641.4063 | 900
Devonshire Building | 2016-09-30 18:15 | 46641.8513 | 1779.984
Devonshire Building | 2016-09-30 18:30 | 46642.0563 | 820.008
Devonshire Building | 2016-09-30 18:45 | 46642.2563 | 799.992
Devonshire Building | 2016-09-30 19:00 | 46642.4613 | 820.008
Devonshire Building | 2016-09-30 19:15 | 46642.6663 | 820.008
Devonshire Building | 2016-09-30 19:30 | 46642.8713 | 820.008
Devonshire Building | 2016-09-30 19:45 | 46643.0713 | 799.992
Devonshire Building | 2016-09-30 20:00 | 46643.2763 | 820.008
Devonshire Building | 2016-09-30 20:15 | 46643.4763 | 799.992
Devonshire Building | 2016-09-30 20:30 | 46643.6813 | 820.008
Devonshire Building | 2016-09-30 20:45 | 46643.8863 | 820.008
Devonshire Building | 2016-09-30 21:00 | 46644.1013 | 860.004
Devonshire Building | 2016-09-30 21:15 | 46644.3013 | 799.992
Devonshire Building | 2016-09-30 21:30 | 46644.5063 | 820.008
Devonshire Building | 2016-09-30 21:45 | 46644.7113 | 820.008
Devonshire Building | 2016-09-30 22:00 | 46644.9113 | 799.992
Devonshire Building | 2016-09-30 22:15 | 46645.1163 | 820.008
Devonshire Building | 2016-09-30 22:30 | 46645.3213 | 820.008
Devonshire Building | 2016-09-30 22:45 | 46645.5263 | 820.008
Devonshire Building | 2016-09-30 23:00 | 46645.7263 | 799.992
Devonshire Building | 2016-09-30 23:15 | 46645.9313 | 820.008
Devonshire Building | 2016-09-30 23:30 | 46646.1363 | 820.008
Devonshire Building | 2016-09-30 23:45 | 46646.3413 | 820.008 | 799.992
Devonshire Building | 2016-10-01 | 46646.543 | 820.008
Devonshire Building | 2016-10-01 00:15 | 46646.748 | 820.008
Devonshire Building | 2016-10-01 00:30 | 46646.953 | 820.008
Devonshire Building | 2016-10-01 00:45 | 46647.163 | 839.988
Devonshire Building | 2016-10-01 01:00 | 46647.368 | 820.008
Devonshire Building | 2016-10-01 01:15 | 46647.573 | 820.008
Devonshire Building | 2016-10-01 01:30 | 46647.783 | 839.988
Devonshire Building | 2016-10-01 01:45 | 46647.993 | 839.988
Devonshire Building | 2016-10-01 02:00 | 46648.198 | 820.008
Devonshire Building | 2016-10-01 02:15 | 46648.408 | 839.988
Devonshire Building | 2016-10-01 02:30 | 46648.613 | 820.008
Devonshire Building | 2016-10-01 02:45 | 46648.823 | 839.988
Devonshire Building | 2016-10-01 03:00 | 46649.028 | 820.008
Devonshire Building | 2016-10-01 03:15 | 46649.238 | 839.988
Devonshire Building | 2016-10-01 03:30 | 46649.443 | 820.008
Devonshire Building | 2016-10-01 03:45 | 46649.648 | 820.008
Devonshire Building | 2016-10-01 04:00 | 46649.858 | 839.988
Devonshire Building | 2016-10-01 04:15 | 46650.063 | 820.008
Devonshire Building | 2016-10-01 04:30 | 46650.268 | 820.008
Devonshire Building | 2016-10-01 04:45 | 46650.478 | 839.988
Devonshire Building | 2016-10-01 05:00 | 46650.683 | 820.008
Devonshire Building | 2016-10-01 05:15 | 46650.888 | 820.008
Devonshire Building | 2016-10-01 05:30 | 46651.093 | 820.008
Devonshire Building | 2016-10-01 05:45 | 46651.298 | 820.008
Devonshire Building | 2016-10-01 06:00 | 46651.503 | 820.008
Devonshire Building | 2016-10-01 06:15 | 46651.708 | 820.008
Devonshire Building | 2016-10-01 06:30 | 46651.908 | 799.992
Devonshire Building | 2016-10-01 06:45 | 46652.113 | 820.008
Devonshire Building | 2016-10-01 07:00 | 46652.318 | 820.008
Devonshire Building | 2016-10-01 07:15 | 46652.518 | 799.992
Devonshire Building | 2016-10-01 07:30 | 46652.723 | 820.008
Devonshire Building | 2016-10-01 07:45 | 46652.938 | 860.004
Devonshire Building | 2016-10-01 08:00 | 46653.158 | 879.984
Devonshire Building | 2016-10-01 08:15 | 46653.373 | 860.004
Devonshire Building | 2016-10-01 08:30 | 46653.593 | 879.984
Devonshire Building | 2016-10-01 08:45 | 46653.808 | 860.004
Devonshire Building | 2016-10-01 09:00 | 46654.028 | 879.984
Devonshire Building | 2016-10-01 09:15 | 46654.243 | 860.004
Devonshire Building | 2016-10-01 09:30 | 46654.463 | 879.984
Devonshire Building | 2016-10-01 09:45 | 46654.678 | 860.004
Devonshire Building | 2016-10-01 10:00 | 46654.878 | 799.992
Devonshire Building | 2016-10-01 10:15 | 46655.078 | 799.992
Devonshire Building | 2016-10-01 10:30 | 46655.278 | 799.992
Devonshire Building | 2016-10-01 10:45 | 46655.478 | 799.992
Devonshire Building | 2016-10-01 11:00 | 46655.678 | 799.992
Devonshire Building | 2016-10-01 11:15 | 46655.878 | 799.992
Devonshire Building | 2016-10-01 11:30 | 46656.078 | 799.992
Devonshire Building | 2016-10-01 11:45 | 46656.283 | 820.008
Devonshire Building | 2016-10-01 12:00 | 46656.483 | 799.992
Devonshire Building | 2016-10-01 12:15 | 46656.683 | 799.992
Devonshire Building | 2016-10-01 12:30 | 46656.883 | 799.992
Devonshire Building | 2016-10-01 12:45 | 46657.088 | 820.008
Devonshire Building | 2016-10-01 13:00 | 46657.288 | 799.992
Devonshire Building | 2016-10-01 13:15 | 46657.493 | 820.008
Devonshire Building | 2016-10-01 13:30 | 46657.703 | 839.988
Devonshire Building | 2016-10-01 13:45 | 46657.903 | 799.992
Devonshire Building | 2016-10-01 14:00 | 46658.108 | 820.008
Devonshire Building | 2016-10-01 14:15 | 46658.308 | 799.992
Devonshire Building | 2016-10-01 14:30 | 46658.513 | 820.008
Devonshire Building | 2016-10-01 14:45 | 46658.713 | 799.992
Devonshire Building | 2016-10-01 15:00 | 46658.918 | 820.008
Devonshire Building | 2016-10-01 15:15 | 46659.348 | 1720.008
Devonshire Building | 2016-10-01 15:30 | 46659.553 | 820.008
Devonshire Building | 2016-10-01 15:45 | 46659.758 | 820.008
Devonshire Building | 2016-10-01 16:00 | 46659.963 | 820.008
Devonshire Building | 2016-10-01 16:15 | 46660.168 | 820.008
Devonshire Building | 2016-10-01 16:30 | 46660.373 | 820.008
Devonshire Building | 2016-10-01 16:45 | 46660.578 | 820.008
Devonshire Building | 2016-10-01 17:00 | 46660.783 | 820.008
Devonshire Building | 2016-10-01 17:15 | 46660.988 | 820.008
Devonshire Building | 2016-10-01 17:30 | 46661.188 | 799.992
Devonshire Building | 2016-10-01 17:45 | 46661.393 | 820.008
Devonshire Building | 2016-10-01 18:00 | 46661.593 | 799.992
Devonshire Building | 2016-10-01 18:15 | 46661.798 | 820.008
Devonshire Building | 2016-10-01 18:30 | 46662.003 | 820.008
Devonshire Building | 2016-10-01 18:45 | 46662.203 | 799.992
Devonshire Building | 2016-10-01 19:00 | 46662.408 | 820.008
Devonshire Building | 2016-10-01 19:15 | 46662.613 | 820.008
Devonshire Building | 2016-10-01 19:30 | 46662.813 | 799.992
Devonshire Building | 2016-10-01 19:45 | 46663.018 | 820.008
Devonshire Building | 2016-10-01 20:00 | 46663.223 | 820.008
Devonshire Building | 2016-10-01 20:15 | 46663.428 | 820.008
Devonshire Building | 2016-10-01 20:30 | 46663.633 | 820.008
Devonshire Building | 2016-10-01 20:45 | 46663.838 | 820.008
Devonshire Building | 2016-10-01 21:00 | 46664.063 | 900
Devonshire Building | 2016-10-01 21:15 | 46664.268 | 820.008
Devonshire Building | 2016-10-01 21:30 | 46664.473 | 820.008
Devonshire Building | 2016-10-01 21:45 | 46664.683 | 839.988
Devonshire Building | 2016-10-01 22:00 | 46664.888 | 820.008
Devonshire Building | 2016-10-01 22:15 | 46665.098 | 839.988
Devonshire Building | 2016-10-01 22:30 | 46665.303 | 820.008
Devonshire Building | 2016-10-01 22:45 | 46665.513 | 839.988
Devonshire Building | 2016-10-01 23:00 | 46665.723 | 839.988
Devonshire Building | 2016-10-01 23:15 | 46665.928 | 820.008
Devonshire Building | 2016-10-01 23:30 | 46666.138 | 839.988
Devonshire Building | 2016-10-01 23:45 | 46666.348 | 839.988 | 799.992
Devonshire Building | 2016-10-02 | 46666.5586 | 839.988
Devonshire Building | 2016-10-02 00:15 | 46666.7736 | 860.004
Devonshire Building | 2016-10-02 00:30 | 46666.9836 | 839.988
Devonshire Building | 2016-10-02 00:45 | 46667.1986 | 860.004
Devonshire Building | 2016-10-02 01:00 | 46667.4086 | 839.988
Devonshire Building | 2016-10-02 01:15 | 46667.6236 | 860.004
Devonshire Building | 2016-10-02 01:30 | 46667.8386 | 860.004
Devonshire Building | 2016-10-02 01:45 | 46668.0536 | 860.004
Devonshire Building | 2016-10-02 02:00 | 46668.2686 | 860.004
Devonshire Building | 2016-10-02 02:15 | 46668.4836 | 860.004
Devonshire Building | 2016-10-02 02:30 | 46668.6986 | 860.004
Devonshire Building | 2016-10-02 02:45 | 46668.9136 | 860.004
Devonshire Building | 2016-10-02 03:00 | 46669.1336 | 879.984
Devonshire Building | 2016-10-02 03:15 | 46669.3486 | 860.004
Devonshire Building | 2016-10-02 03:30 | 46669.5636 | 860.004
Devonshire Building | 2016-10-02 03:45 | 46669.7786 | 860.004
Devonshire Building | 2016-10-02 04:00 | 46669.9936 | 860.004
Devonshire Building | 2016-10-02 04:15 | 46670.2086 | 860.004
Devonshire Building | 2016-10-02 04:30 | 46670.4236 | 860.004
Devonshire Building | 2016-10-02 04:45 | 46670.6386 | 860.004
Devonshire Building | 2016-10-02 05:00 | 46670.8586 | 879.984
Devonshire Building | 2016-10-02 05:15 | 46671.0736 | 860.004
Devonshire Building | 2016-10-02 05:30 | 46671.2886 | 860.004
Devonshire Building | 2016-10-02 05:45 | 46671.5036 | 860.004
Devonshire Building | 2016-10-02 06:00 | 46671.7136 | 839.988
Devonshire Building | 2016-10-02 06:15 | 46671.9236 | 839.988
Devonshire Building | 2016-10-02 06:30 | 46672.1386 | 860.004
Devonshire Building | 2016-10-02 06:45 | 46672.3486 | 839.988
Devonshire Building | 2016-10-02 07:00 | 46672.5586 | 839.988
Devonshire Building | 2016-10-02 07:15 | 46672.7686 | 839.988
Devonshire Building | 2016-10-02 07:30 | 46672.9786 | 839.988
Devonshire Building | 2016-10-02 07:45 | 46673.2036 | 900
Devonshire Building | 2016-10-02 08:00 | 46673.4286 | 900
Devonshire Building | 2016-10-02 08:15 | 46673.6536 | 900
Devonshire Building | 2016-10-02 08:30 | 46673.8786 | 900
Devonshire Building | 2016-10-02 08:45 | 46674.0986 | 879.984
Devonshire Building | 2016-10-02 09:00 | 46674.3236 | 900
Devonshire Building | 2016-10-02 09:15 | 46674.5486 | 900
Devonshire Building | 2016-10-02 09:30 | 46674.7736 | 900
Devonshire Building | 2016-10-02 09:45 | 46674.9936 | 879.984
Devonshire Building | 2016-10-02 10:00 | 46675.1986 | 820.008
Devonshire Building | 2016-10-02 10:15 | 46675.4086 | 839.988
Devonshire Building | 2016-10-02 10:30 | 46675.6186 | 839.988
Devonshire Building | 2016-10-02 10:45 | 46675.8286 | 839.988
Devonshire Building | 2016-10-02 11:00 | 46676.0436 | 860.004
Devonshire Building | 2016-10-02 11:15 | 46676.2536 | 839.988
Devonshire Building | 2016-10-02 11:30 | 46676.4686 | 860.004
Devonshire Building | 2016-10-02 11:45 | 46676.6786 | 839.988
Devonshire Building | 2016-10-02 12:00 | 46676.8886 | 839.988
Devonshire Building | 2016-10-02 12:15 | 46677.1036 | 860.004
Devonshire Building | 2016-10-02 12:30 | 46677.3136 | 839.988
Devonshire Building | 2016-10-02 12:45 | 46677.5286 | 860.004
Devonshire Building | 2016-10-02 13:00 | 46677.7436 | 860.004
Devonshire Building | 2016-10-02 13:15 | 46678.0136 | 1080
Devonshire Building | 2016-10-02 13:30 | 46678.4286 | 1659.996
Devonshire Building | 2016-10-02 13:45 | 46678.6436 | 860.004
Devonshire Building | 2016-10-02 14:00 | 46678.8586 | 860.004
Devonshire Building | 2016-10-02 14:15 | 46679.0736 | 860.004
Devonshire Building | 2016-10-02 14:30 | 46679.2886 | 860.004
Devonshire Building | 2016-10-02 14:45 | 46679.5036 | 860.004
Devonshire Building | 2016-10-02 15:00 | 46679.7186 | 860.004
Devonshire Building | 2016-10-02 15:15 | 46679.9336 | 860.004
Devonshire Building | 2016-10-02 15:30 | 46680.1486 | 860.004
Devonshire Building | 2016-10-02 15:45 | 46680.3586 | 839.988
Devonshire Building | 2016-10-02 16:00 | 46680.5736 | 860.004
Devonshire Building | 2016-10-02 16:15 | 46680.7886 | 860.004
Devonshire Building | 2016-10-02 16:30 | 46681.0036 | 860.004
Devonshire Building | 2016-10-02 16:45 | 46681.2186 | 860.004
Devonshire Building | 2016-10-02 17:00 | 46681.4286 | 839.988
Devonshire Building | 2016-10-02 17:15 | 46681.6436 | 860.004
Devonshire Building | 2016-10-02 17:30 | 46681.8536 | 839.988
Devonshire Building | 2016-10-02 17:45 | 46682.0636 | 839.988
Devonshire Building | 2016-10-02 18:00 | 46682.2736 | 839.988
Devonshire Building | 2016-10-02 18:15 | 46682.4835 | 839.988
Devonshire Building | 2016-10-02 18:30 | 46682.6935 | 839.988
Devonshire Building | 2016-10-02 18:45 | 46682.9035 | 839.988
Devonshire Building | 2016-10-02 19:00 | 46683.1185 | 860.004
Devonshire Building | 2016-10-02 19:15 | 46683.3285 | 839.988
Devonshire Building | 2016-10-02 19:30 | 46683.5385 | 839.988
Devonshire Building | 2016-10-02 19:45 | 46683.7485 | 839.988
Devonshire Building | 2016-10-02 20:00 | 46683.9635 | 860.004
Devonshire Building | 2016-10-02 20:15 | 46684.1735 | 839.988
Devonshire Building | 2016-10-02 20:30 | 46684.3835 | 839.988
Devonshire Building | 2016-10-02 20:45 | 46684.5935 | 839.988
Devonshire Building | 2016-10-02 21:00 | 46684.8235 | 920.016
Devonshire Building | 2016-10-02 21:15 | 46685.0335 | 839.988
Devonshire Building | 2016-10-02 21:30 | 46685.2485 | 860.004
Devonshire Building | 2016-10-02 21:45 | 46685.4635 | 860.004
Devonshire Building | 2016-10-02 22:00 | 46685.6735 | 839.988
Devonshire Building | 2016-10-02 22:15 | 46685.8885 | 860.004
Devonshire Building | 2016-10-02 22:30 | 46686.0985 | 839.988
Devonshire Building | 2016-10-02 22:45 | 46686.3135 | 860.004
Devonshire Building | 2016-10-02 23:00 | 46686.5285 | 860.004
Devonshire Building | 2016-10-02 23:15 | 46686.7435 | 860.004
Devonshire Building | 2016-10-02 23:30 | 46686.9585 | 860.004
Devonshire Building | 2016-10-02 23:45 | 46687.1735 | 860.004 | 820.008
Devonshire Building | 2016-10-03 | 46687.3906 | 860.004
Devonshire Building | 2016-10-03 00:15 | 46687.6056 | 860.004
Devonshire Building | 2016-10-03 00:30 | 46687.8206 | 860.004
Devonshire Building | 2016-10-03 00:45 | 46688.0356 | 860.004
Devonshire Building | 2016-10-03 01:00 | 46688.2506 | 860.004
Devonshire Building | 2016-10-03 01:15 | 46688.4706 | 879.984
Devonshire Building | 2016-10-03 01:30 | 46688.6856 | 860.004
Devonshire Building | 2016-10-03 01:45 | 46688.9006 | 860.004
Devonshire Building | 2016-10-03 02:00 | 46689.1206 | 879.984
Devonshire Building | 2016-10-03 02:15 | 46689.3356 | 860.004
Devonshire Building | 2016-10-03 02:30 | 46689.5556 | 879.984
Devonshire Building | 2016-10-03 02:45 | 46689.7706 | 860.004
Devonshire Building | 2016-10-03 03:00 | 46689.9906 | 879.984
Devonshire Building | 2016-10-03 03:15 | 46690.2106 | 879.984
Devonshire Building | 2016-10-03 03:30 | 46690.4256 | 860.004
Devonshire Building | 2016-10-03 03:45 | 46690.6456 | 879.984
Devonshire Building | 2016-10-03 04:00 | 46690.8656 | 879.984
Devonshire Building | 2016-10-03 04:15 | 46691.0856 | 879.984
Devonshire Building | 2016-10-03 04:30 | 46691.3006 | 860.004
Devonshire Building | 2016-10-03 04:45 | 46691.5206 | 879.984
Devonshire Building | 2016-10-03 05:00 | 46691.7356 | 860.004
Devonshire Building | 2016-10-03 05:15 | 46691.9506 | 860.004
Devonshire Building | 2016-10-03 05:30 | 46692.1656 | 860.004
Devonshire Building | 2016-10-03 05:45 | 46692.3806 | 860.004
Devonshire Building | 2016-10-03 06:00 | 46692.5956 | 860.004
Devonshire Building | 2016-10-03 06:15 | 46692.8056 | 839.988
Devonshire Building | 2016-10-03 06:30 | 46693.0256 | 879.984
Devonshire Building | 2016-10-03 06:45 | 46693.2406 | 860.004
Devonshire Building | 2016-10-03 07:00 | 46693.4506 | 839.988
Devonshire Building | 2016-10-03 07:15 | 46693.9056 | 1820.016
Devonshire Building | 2016-10-03 07:30 | 46694.1306 | 900
Devonshire Building | 2016-10-03 07:45 | 46694.3706 | 960.012
Devonshire Building | 2016-10-03 08:00 | 46694.6056 | 939.996
Devonshire Building | 2016-10-03 08:15 | 46694.8406 | 939.996
Devonshire Building | 2016-10-03 08:30 | 46695.0756 | 939.996
Devonshire Building | 2016-10-03 08:45 | 46695.3056 | 920.016
Devonshire Building | 2016-10-03 09:00 | 46695.5456 | 960.012
Devonshire Building | 2016-10-03 09:15 | 46695.7856 | 960.012
Devonshire Building | 2016-10-03 09:30 | 46696.3456 | 2239.992
Devonshire Building | 2016-10-03 09:45 | 46696.6606 | 1260
Devonshire Building | 2016-10-03 10:00 | 46697.0056 | 1379.988
Devonshire Building | 2016-10-03 10:15 | 46697.3206 | 1260
Devonshire Building | 2016-10-03 10:30 | 46697.6256 | 1220.004
Devonshire Building | 2016-10-03 10:45 | 46697.9206 | 1180.008
Devonshire Building | 2016-10-03 11:00 | 46698.4756 | 2220.012
Devonshire Building | 2016-10-03 11:15 | 46698.7606 | 1140.012
Devonshire Building | 2016-10-03 11:30 | 46699.0556 | 1180.008
Devonshire Building | 2016-10-03 11:45 | 46699.3406 | 1140.012
Devonshire Building | 2016-10-03 12:00 | 46699.6056 | 1059.984
Devonshire Building | 2016-10-03 12:15 | 46699.8756 | 1080
Devonshire Building | 2016-10-03 12:30 | 46700.1456 | 1080
Devonshire Building | 2016-10-03 12:45 | 46700.4106 | 1059.984
Devonshire Building | 2016-10-03 13:00 | 46700.9256 | 2059.992
Devonshire Building | 2016-10-03 13:15 | 46701.1806 | 1019.988
Devonshire Building | 2016-10-03 13:30 | 46701.4406 | 1040.004
Devonshire Building | 2016-10-03 13:45 | 46701.7056 | 1059.984
Devonshire Building | 2016-10-03 14:00 | 46701.9606 | 1019.988
Devonshire Building | 2016-10-03 14:15 | 46702.2156 | 1019.988
Devonshire Building | 2016-10-03 14:30 | 46702.4656 | 1000.008
Devonshire Building | 2016-10-03 14:45 | 46702.7206 | 1019.988
Devonshire Building | 2016-10-03 15:00 | 46703.2156 | 1980
Devonshire Building | 2016-10-03 15:15 | 46703.4456 | 920.016
Devonshire Building | 2016-10-03 15:30 | 46703.6806 | 939.996
Devonshire Building | 2016-10-03 15:45 | 46703.9256 | 979.992
Devonshire Building | 2016-10-03 16:00 | 46704.2256 | 1199.988
Devonshire Building | 2016-10-03 16:15 | 46704.5306 | 1220.004
Devonshire Building | 2016-10-03 16:30 | 46704.8306 | 1199.988
Devonshire Building | 2016-10-03 16:45 | 46705.2056 | 1500.012
Devonshire Building | 2016-10-03 17:00 | 46705.5356 | 1320.012
Devonshire Building | 2016-10-03 17:15 | 46706.0656 | 2120.004
Devonshire Building | 2016-10-03 17:30 | 46706.3356 | 1080
Devonshire Building | 2016-10-03 17:45 | 46706.5906 | 1019.988
Devonshire Building | 2016-10-03 18:00 | 46706.8406 | 1000.008
Devonshire Building | 2016-10-03 18:15 | 46707.0806 | 960.012
Devonshire Building | 2016-10-03 18:30 | 46707.3206 | 960.012
Devonshire Building | 2016-10-03 18:45 | 46707.5506 | 920.016
Devonshire Building | 2016-10-03 19:00 | 46707.7806 | 920.016
Devonshire Building | 2016-10-03 19:15 | 46708.0106 | 920.016
Devonshire Building | 2016-10-03 19:30 | 46708.2406 | 920.016
Devonshire Building | 2016-10-03 19:45 | 46708.4656 | 900
Devonshire Building | 2016-10-03 20:00 | 46708.6906 | 900
Devonshire Building | 2016-10-03 20:15 | 46708.9156 | 900
Devonshire Building | 2016-10-03 20:30 | 46709.1406 | 900
Devonshire Building | 2016-10-03 20:45 | 46709.3656 | 900
Devonshire Building | 2016-10-03 21:00 | 46709.6006 | 939.996
Devonshire Building | 2016-10-03 21:15 | 46709.8206 | 879.984
Devonshire Building | 2016-10-03 21:30 | 46710.0406 | 879.984
Devonshire Building | 2016-10-03 21:45 | 46710.2606 | 879.984
Devonshire Building | 2016-10-03 22:00 | 46710.4806 | 879.984
Devonshire Building | 2016-10-03 22:15 | 46710.7006 | 879.984
Devonshire Building | 2016-10-03 22:30 | 46710.9206 | 879.984
Devonshire Building | 2016-10-03 22:45 | 46711.1406 | 879.984
Devonshire Building | 2016-10-03 23:00 | 46711.3606 | 879.984
Devonshire Building | 2016-10-03 23:15 | 46711.5856 | 900
Devonshire Building | 2016-10-03 23:30 | 46711.8056 | 879.984
Devonshire Building | 2016-10-03 23:45 | 46712.0306 | 900 | 839.988
Devonshire Building | 2016-10-04 | 46712.2539 | 900
Devonshire Building | 2016-10-04 00:15 | 46712.4789 | 900
Devonshire Building | 2016-10-04 00:30 | 46712.6989 | 879.984
Devonshire Building | 2016-10-04 00:45 | 46712.9289 | 920.016
Devonshire Building | 2016-10-04 01:00 | 46713.1539 | 900
Devonshire Building | 2016-10-04 01:15 | 46713.3789 | 900
Devonshire Building | 2016-10-04 01:30 | 46713.6089 | 920.016
Devonshire Building | 2016-10-04 01:45 | 46713.8339 | 900
Devonshire Building | 2016-10-04 02:00 | 46714.0639 | 920.016
Devonshire Building | 2016-10-04 02:15 | 46714.2939 | 920.016
Devonshire Building | 2016-10-04 02:30 | 46714.5189 | 900
Devonshire Building | 2016-10-04 02:45 | 46714.7489 | 920.016
Devonshire Building | 2016-10-04 03:00 | 46714.9839 | 939.996
Devonshire Building | 2016-10-04 03:15 | 46715.2139 | 920.016
Devonshire Building | 2016-10-04 03:30 | 46715.4439 | 920.016
Devonshire Building | 2016-10-04 03:45 | 46715.6739 | 920.016
Devonshire Building | 2016-10-04 04:00 | 46715.9089 | 939.996
Devonshire Building | 2016-10-04 04:15 | 46716.1389 | 920.016
Devonshire Building | 2016-10-04 04:30 | 46716.3689 | 920.016
Devonshire Building | 2016-10-04 04:45 | 46716.5939 | 900
Devonshire Building | 2016-10-04 05:00 | 46716.8239 | 920.016
Devonshire Building | 2016-10-04 05:15 | 46717.0489 | 900
Devonshire Building | 2016-10-04 05:30 | 46717.279 | 920.016
Devonshire Building | 2016-10-04 05:45 | 46717.504 | 900
Devonshire Building | 2016-10-04 06:00 | 46717.729 | 900
Devonshire Building | 2016-10-04 06:15 | 46717.9489 | 879.984
Devonshire Building | 2016-10-04 06:30 | 46718.1839 | 939.996
Devonshire Building | 2016-10-04 06:45 | 46718.4189 | 939.996
Devonshire Building | 2016-10-04 07:00 | 46718.649 | 920.016
Devonshire Building | 2016-10-04 07:15 | 46718.874 | 900
Devonshire Building | 2016-10-04 07:30 | 46719.1089 | 939.996
Devonshire Building | 2016-10-04 07:45 | 46719.349 | 960.012
Devonshire Building | 2016-10-04 08:00 | 46719.594 | 979.992
Devonshire Building | 2016-10-04 08:15 | 46720.1089 | 2059.992
Devonshire Building | 2016-10-04 08:30 | 46720.3539 | 979.992
Devonshire Building | 2016-10-04 08:45 | 46720.6039 | 1000.008
Devonshire Building | 2016-10-04 09:00 | 46720.8539 | 1000.008
Devonshire Building | 2016-10-04 09:15 | 46721.1089 | 1019.988
Devonshire Building | 2016-10-04 09:30 | 46721.3689 | 1040.004
Devonshire Building | 2016-10-04 09:45 | 46721.8389 | 1879.992
Devonshire Building | 2016-10-04 10:00 | 46722.1889 | 1400.004
Devonshire Building | 2016-10-04 10:15 | 46722.4989 | 1239.984
Devonshire Building | 2016-10-04 10:30 | 46722.7989 | 1199.988
Devonshire Building | 2016-10-04 10:45 | 46723.0839 | 1140.012
Devonshire Building | 2016-10-04 11:00 | 46723.3539 | 1080
Devonshire Building | 2016-10-04 11:15 | 46723.6189 | 1059.984
Devonshire Building | 2016-10-04 11:30 | 46723.9389 | 1280.016
Devonshire Building | 2016-10-04 11:45 | 46724.3989 | 1839.996
Devonshire Building | 2016-10-04 12:00 | 46724.6439 | 979.992
Devonshire Building | 2016-10-04 12:15 | 46724.9039 | 1040.004
Devonshire Building | 2016-10-04 12:30 | 46725.1539 | 1000.008
Devonshire Building | 2016-10-04 12:45 | 46725.4139 | 1040.004
Devonshire Building | 2016-10-04 13:00 | 46725.6789 | 1059.984
Devonshire Building | 2016-10-04 13:15 | 46725.9389 | 1040.004
Devonshire Building | 2016-10-04 13:30 | 46726.4939 | 2220.012
Devonshire Building | 2016-10-04 13:45 | 46726.7789 | 1140.012
Devonshire Building | 2016-10-04 14:00 | 46727.064 | 1140.012
Devonshire Building | 2016-10-04 14:15 | 46727.3439 | 1119.996
Devonshire Building | 2016-10-04 14:30 | 46727.619 | 1100.016
Devonshire Building | 2016-10-04 14:45 | 46727.894 | 1100.016
Devonshire Building | 2016-10-04 15:00 | 46728.169 | 1100.016
Devonshire Building | 2016-10-04 15:15 | 46728.629 | 1839.996
Devonshire Building | 2016-10-04 15:30 | 46728.974 | 1379.988
Devonshire Building | 2016-10-04 15:45 | 46729.239 | 1059.984
Devonshire Building | 2016-10-04 16:00 | 46729.5039 | 1059.984
Devonshire Building | 2016-10-04 16:15 | 46729.7689 | 1059.984
Devonshire Building | 2016-10-04 16:30 | 46730.0389 | 1080
Devonshire Building | 2016-10-04 16:45 | 46730.2989 | 1040.004
Devonshire Building | 2016-10-04 17:00 | 46730.5589 | 1040.004
Devonshire Building | 2016-10-04 17:15 | 46730.8189 | 1040.004
Devonshire Building | 2016-10-04 17:30 | 46731.069 | 1000.008
Devonshire Building | 2016-10-04 17:45 | 46731.319 | 1000.008
Devonshire Building | 2016-10-04 18:00 | 46731.804 | 1940.004
Devonshire Building | 2016-10-04 18:15 | 46732.039 | 939.996
Devonshire Building | 2016-10-04 18:30 | 46732.279 | 960.012
Devonshire Building | 2016-10-04 18:45 | 46732.514 | 939.996
Devonshire Building | 2016-10-04 19:00 | 46732.754 | 960.012
Devonshire Building | 2016-10-04 19:15 | 46732.989 | 939.996
Devonshire Building | 2016-10-04 19:30 | 46733.224 | 939.996
Devonshire Building | 2016-10-04 19:45 | 46733.464 | 960.012
Devonshire Building | 2016-10-04 20:00 | 46733.704 | 960.012
Devonshire Building | 2016-10-04 20:15 | 46733.944 | 960.012
Devonshire Building | 2016-10-04 20:30 | 46734.179 | 939.996
Devonshire Building | 2016-10-04 20:45 | 46734.424 | 979.992
Devonshire Building | 2016-10-04 21:00 | 46734.674 | 1000.008
Devonshire Building | 2016-10-04 21:15 | 46734.909 | 939.996
Devonshire Building | 2016-10-04 21:30 | 46735.149 | 960.012
Devonshire Building | 2016-10-04 21:45 | 46735.384 | 939.996
Devonshire Building | 2016-10-04 22:00 | 46735.619 | 939.996
Devonshire Building | 2016-10-04 22:15 | 46735.859 | 960.012
Devonshire Building | 2016-10-04 22:30 | 46736.099 | 960.012
Devonshire Building | 2016-10-04 22:45 | 46736.334 | 939.996
Devonshire Building | 2016-10-04 23:00 | 46736.574 | 960.012
Devonshire Building | 2016-10-04 23:15 | 46736.814 | 960.012
Devonshire Building | 2016-10-04 23:30 | 46737.054 | 960.012
Devonshire Building | 2016-10-04 23:45 | 46737.294 | 960.012 | 879.984
Devonshire Building | 2016-10-05 | 46737.5352 | 960.012
Devonshire Building | 2016-10-05 00:15 | 46737.7752 | 960.012
Devonshire Building | 2016-10-05 00:30 | 46738.0152 | 960.012
Devonshire Building | 2016-10-05 00:45 | 46738.2552 | 960.012
Devonshire Building | 2016-10-05 01:00 | 46738.4952 | 960.012
Devonshire Building | 2016-10-05 01:15 | 46738.7352 | 960.012
Devonshire Building | 2016-10-05 01:30 | 46738.9752 | 960.012
Devonshire Building | 2016-10-05 01:45 | 46739.2152 | 960.012
Devonshire Building | 2016-10-05 02:00 | 46739.4552 | 960.012
Devonshire Building | 2016-10-05 02:15 | 46739.6952 | 960.012
Devonshire Building | 2016-10-05 02:30 | 46739.9352 | 960.012
Devonshire Building | 2016-10-05 02:45 | 46740.1702 | 939.996
Devonshire Building | 2016-10-05 03:00 | 46740.4102 | 960.012
Devonshire Building | 2016-10-05 03:15 | 46740.6502 | 960.012
Devonshire Building | 2016-10-05 03:30 | 46740.8902 | 960.012
Devonshire Building | 2016-10-05 03:45 | 46741.1302 | 960.012
Devonshire Building | 2016-10-05 04:00 | 46741.3652 | 939.996
Devonshire Building | 2016-10-05 04:15 | 46741.6052 | 960.012
Devonshire Building | 2016-10-05 04:30 | 46741.8452 | 960.012
Devonshire Building | 2016-10-05 04:45 | 46742.0802 | 939.996
Devonshire Building | 2016-10-05 05:00 | 46742.3202 | 960.012
Devonshire Building | 2016-10-05 05:15 | 46742.5552 | 939.996
Devonshire Building | 2016-10-05 05:30 | 46742.7902 | 939.996
Devonshire Building | 2016-10-05 05:45 | 46743.0302 | 960.012
Devonshire Building | 2016-10-05 06:00 | 46743.2652 | 939.996
Devonshire Building | 2016-10-05 06:15 | 46743.5002 | 939.996
Devonshire Building | 2016-10-05 06:30 | 46743.7452 | 979.992
Devonshire Building | 2016-10-05 06:45 | 46743.9802 | 939.996
Devonshire Building | 2016-10-05 07:00 | 46744.2102 | 920.016
Devonshire Building | 2016-10-05 07:15 | 46744.4502 | 960.012
Devonshire Building | 2016-10-05 07:30 | 46744.6902 | 960.012
Devonshire Building | 2016-10-05 07:45 | 46744.9552 | 1059.984
Devonshire Building | 2016-10-05 08:00 | 46745.2102 | 1019.988
Devonshire Building | 2016-10-05 08:15 | 46745.7202 | 2040.012
Devonshire Building | 2016-10-05 08:30 | 46745.9752 | 1019.988
Devonshire Building | 2016-10-05 08:45 | 46746.2352 | 1040.004
Devonshire Building | 2016-10-05 09:00 | 46746.5002 | 1059.984
Devonshire Building | 2016-10-05 09:15 | 46746.7702 | 1080
Devonshire Building | 2016-10-05 09:30 | 46747.0602 | 1159.992
Devonshire Building | 2016-10-05 09:45 | 46747.3602 | 1199.988
Devonshire Building | 2016-10-05 10:00 | 46747.9252 | 2260.008
Devonshire Building | 2016-10-05 10:15 | 46748.2152 | 1159.992
Devonshire Building | 2016-10-05 10:30 | 46748.5052 | 1159.992
Devonshire Building | 2016-10-05 10:45 | 46748.8002 | 1180.008
Devonshire Building | 2016-10-05 11:00 | 46749.0902 | 1159.992
Devonshire Building | 2016-10-05 11:15 | 46749.6252 | 2139.984
Devonshire Building | 2016-10-05 11:30 | 46749.8952 | 1080
Devonshire Building | 2016-10-05 11:45 | 46750.2052 | 1239.984
Devonshire Building | 2016-10-05 12:00 | 46750.5852 | 1519.992
Devonshire Building | 2016-10-05 12:15 | 46750.9352 | 1400.004
Devonshire Building | 2016-10-05 12:30 | 46751.2452 | 1239.984
Devonshire Building | 2016-10-05 12:45 | 46751.5602 | 1260
Devonshire Building | 2016-10-05 13:00 | 46752.1302 | 2279.988
Devonshire Building | 2016-10-05 13:15 | 46752.4302 | 1199.988
Devonshire Building | 2016-10-05 13:30 | 46752.7152 | 1140.012
Devonshire Building | 2016-10-05 13:45 | 46752.9902 | 1100.016
Devonshire Building | 2016-10-05 14:00 | 46753.2602 | 1080
Devonshire Building | 2016-10-05 14:15 | 46753.5302 | 1080
Devonshire Building | 2016-10-05 14:30 | 46753.7902 | 1040.004
Devonshire Building | 2016-10-05 14:45 | 46754.3202 | 2120.004
Devonshire Building | 2016-10-05 15:00 | 46754.6002 | 1119.996
Devonshire Building | 2016-10-05 15:15 | 46754.8852 | 1140.012
Devonshire Building | 2016-10-05 15:30 | 46755.2002 | 1260
Devonshire Building | 2016-10-05 15:45 | 46755.5152 | 1260
Devonshire Building | 2016-10-05 16:00 | 46755.8152 | 1199.988
Devonshire Building | 2016-10-05 16:15 | 46756.1052 | 1159.992
Devonshire Building | 2016-10-05 16:30 | 46756.3852 | 1119.996
Devonshire Building | 2016-10-05 16:45 | 46756.6552 | 1080
Devonshire Building | 2016-10-05 17:00 | 46756.9202 | 1059.984
Devonshire Building | 2016-10-05 17:15 | 46757.4352 | 2059.992
Devonshire Building | 2016-10-05 17:30 | 46757.6902 | 1019.988
Devonshire Building | 2016-10-05 17:45 | 46757.9452 | 1019.988
Devonshire Building | 2016-10-05 18:00 | 46758.1952 | 1000.008
Devonshire Building | 2016-10-05 18:15 | 46758.4552 | 1040.004
Devonshire Building | 2016-10-05 18:30 | 46758.7102 | 1019.988
Devonshire Building | 2016-10-05 18:45 | 46758.9652 | 1019.988
Devonshire Building | 2016-10-05 19:00 | 46759.2202 | 1019.988
Devonshire Building | 2016-10-05 19:15 | 46759.4702 | 1000.008
Devonshire Building | 2016-10-05 19:30 | 46759.7152 | 979.992
Devonshire Building | 2016-10-05 19:45 | 46759.9652 | 1000.008
Devonshire Building | 2016-10-05 20:00 | 46760.2152 | 1000.008
Devonshire Building | 2016-10-05 20:15 | 46760.4602 | 979.992
Devonshire Building | 2016-10-05 20:30 | 46760.7002 | 960.012
Devonshire Building | 2016-10-05 20:45 | 46760.9452 | 979.992
Devonshire Building | 2016-10-05 21:00 | 46761.2002 | 1019.988
Devonshire Building | 2016-10-05 21:15 | 46761.4352 | 939.996
Devonshire Building | 2016-10-05 21:30 | 46761.6752 | 960.012
Devonshire Building | 2016-10-05 21:45 | 46761.9152 | 960.012
Devonshire Building | 2016-10-05 22:00 | 46762.1502 | 939.996
Devonshire Building | 2016-10-05 22:15 | 46762.3902 | 960.012
Devonshire Building | 2016-10-05 22:30 | 46762.6302 | 960.012
Devonshire Building | 2016-10-05 22:45 | 46762.8702 | 960.012
Devonshire Building | 2016-10-05 23:00 | 46763.1102 | 960.012
Devonshire Building | 2016-10-05 23:15 | 46763.3502 | 960.012
Devonshire Building | 2016-10-05 23:30 | 46763.5902 | 960.012
Devonshire Building | 2016-10-05 23:45 | 46763.8352 | 979.992 | 920.016
Devonshire Building | 2016-10-06 | 46764.0742 | 960.012
Devonshire Building | 2016-10-06 00:15 | 46764.3142 | 960.012
Devonshire Building | 2016-10-06 00:30 | 46764.5592 | 979.992
Devonshire Building | 2016-10-06 00:45 | 46764.7992 | 960.012
Devonshire Building | 2016-10-06 01:00 | 46765.0392 | 960.012
Devonshire Building | 2016-10-06 01:15 | 46765.2792 | 960.012
Devonshire Building | 2016-10-06 01:30 | 46765.5242 | 979.992
Devonshire Building | 2016-10-06 01:45 | 46765.7642 | 960.012
Devonshire Building | 2016-10-06 02:00 | 46766.0042 | 960.012
Devonshire Building | 2016-10-06 02:15 | 46766.2492 | 979.992
Devonshire Building | 2016-10-06 02:30 | 46766.4892 | 960.012
Devonshire Building | 2016-10-06 02:45 | 46766.7292 | 960.012
Devonshire Building | 2016-10-06 03:00 | 46766.9692 | 960.012
Devonshire Building | 2016-10-06 03:15 | 46767.2092 | 960.012
Devonshire Building | 2016-10-06 03:30 | 46767.4542 | 979.992
Devonshire Building | 2016-10-06 03:45 | 46767.6942 | 960.012
Devonshire Building | 2016-10-06 04:00 | 46767.9342 | 960.012
Devonshire Building | 2016-10-06 04:15 | 46768.1743 | 960.012
Devonshire Building | 2016-10-06 04:30 | 46768.4143 | 960.012
Devonshire Building | 2016-10-06 04:45 | 46768.6543 | 960.012
Devonshire Building | 2016-10-06 05:00 | 46768.8943 | 960.012
Devonshire Building | 2016-10-06 05:15 | 46769.1343 | 960.012
Devonshire Building | 2016-10-06 05:30 | 46769.3743 | 960.012
Devonshire Building | 2016-10-06 05:45 | 46769.6093 | 939.996
Devonshire Building | 2016-10-06 06:00 | 46769.8493 | 960.012
Devonshire Building | 2016-10-06 06:15 | 46770.0843 | 939.996
Devonshire Building | 2016-10-06 06:30 | 46770.3243 | 960.012
Devonshire Building | 2016-10-06 06:45 | 46770.5543 | 920.016
Devonshire Building | 2016-10-06 07:00 | 46770.7893 | 939.996
Devonshire Building | 2016-10-06 07:15 | 46771.0193 | 920.016
Devonshire Building | 2016-10-06 07:30 | 46771.2543 | 939.996
Devonshire Building | 2016-10-06 07:45 | 46771.7493 | 1980
Devonshire Building | 2016-10-06 08:00 | 46771.9993 | 1000.008
Devonshire Building | 2016-10-06 08:15 | 46772.2593 | 1040.004
Devonshire Building | 2016-10-06 08:30 | 46772.5143 | 1019.988
Devonshire Building | 2016-10-06 08:45 | 46772.7643 | 1000.008
Devonshire Building | 2016-10-06 09:00 | 46773.0243 | 1040.004
Devonshire Building | 2016-10-06 09:15 | 46773.3793 | 1419.984
Devonshire Building | 2016-10-06 09:30 | 46774.0293 | 2599.992
Devonshire Building | 2016-10-06 09:45 | 46774.4043 | 1500.012
Devonshire Building | 2016-10-06 10:00 | 46774.7743 | 1479.996
Devonshire Building | 2016-10-06 10:15 | 46775.1443 | 1479.996
Devonshire Building | 2016-10-06 10:30 | 46775.5443 | 1599.984
Devonshire Building | 2016-10-06 10:45 | 46776.1993 | 2620.008
Devonshire Building | 2016-10-06 11:00 | 46776.5893 | 1559.988
Devonshire Building | 2016-10-06 11:15 | 46776.9393 | 1400.004
Devonshire Building | 2016-10-06 11:30 | 46777.2593 | 1280.016
Devonshire Building | 2016-10-06 11:45 | 46777.5743 | 1260
Devonshire Building | 2016-10-06 12:00 | 46777.8793 | 1220.004
Devonshire Building | 2016-10-06 12:15 | 46778.4293 | 2199.996
Devonshire Building | 2016-10-06 12:30 | 46778.6943 | 1059.984
Devonshire Building | 2016-10-06 12:45 | 46778.9643 | 1080
Devonshire Building | 2016-10-06 13:00 | 46779.2393 | 1100.016
Devonshire Building | 2016-10-06 13:15 | 46779.5143 | 1100.016
Devonshire Building | 2016-10-06 13:30 | 46779.7843 | 1080
Devonshire Building | 2016-10-06 13:45 | 46780.1643 | 1519.992
Devonshire Building | 2016-10-06 14:00 | 46780.8743 | 2840.004
Devonshire Building | 2016-10-06 14:15 | 46781.3193 | 1779.984
Devonshire Building | 2016-10-06 14:30 | 46781.7093 | 1559.988
Devonshire Building | 2016-10-06 14:45 | 46782.0643 | 1419.984
Devonshire Building | 2016-10-06 15:00 | 46782.4093 | 1379.988
Devonshire Building | 2016-10-06 15:15 | 46782.7393 | 1320.012
Devonshire Building | 2016-10-06 15:30 | 46783.2943 | 2220.012
Devonshire Building | 2016-10-06 15:45 | 46783.6193 | 1299.996
Devonshire Building | 2016-10-06 16:00 | 46783.9093 | 1159.992
Devonshire Building | 2016-10-06 16:15 | 46784.1943 | 1140.012
Devonshire Building | 2016-10-06 16:30 | 46784.4843 | 1159.992
Devonshire Building | 2016-10-06 16:45 | 46784.7693 | 1140.012
Devonshire Building | 2016-10-06 17:00 | 46785.0493 | 1119.996
Devonshire Building | 2016-10-06 17:15 | 46785.3243 | 1100.016
Devonshire Building | 2016-10-06 17:30 | 46785.5893 | 1059.984
Devonshire Building | 2016-10-06 17:45 | 46785.8493 | 1040.004
Devonshire Building | 2016-10-06 18:00 | 46786.1043 | 1019.988
Devonshire Building | 2016-10-06 18:15 | 46786.3493 | 979.992
Devonshire Building | 2016-10-06 18:30 | 46786.5943 | 979.992
Devonshire Building | 2016-10-06 18:45 | 46786.8393 | 979.992
Devonshire Building | 2016-10-06 19:00 | 46787.0793 | 960.012
Devonshire Building | 2016-10-06 19:15 | 46787.3193 | 960.012
Devonshire Building | 2016-10-06 19:30 | 46787.5593 | 960.012
Devonshire Building | 2016-10-06 19:45 | 46787.7943 | 939.996
Devonshire Building | 2016-10-06 20:00 | 46788.0293 | 939.996
Devonshire Building | 2016-10-06 20:15 | 46788.2693 | 960.012
Devonshire Building | 2016-10-06 20:30 | 46788.5093 | 960.012
Devonshire Building | 2016-10-06 20:45 | 46788.7443 | 939.996
Devonshire Building | 2016-10-06 21:00 | 46789.0043 | 1040.004
Devonshire Building | 2016-10-06 21:15 | 46789.4593 | 1820.016
Devonshire Building | 2016-10-06 21:30 | 46789.6893 | 920.016
Devonshire Building | 2016-10-06 21:45 | 46789.9243 | 939.996
Devonshire Building | 2016-10-06 22:00 | 46790.1593 | 939.996
Devonshire Building | 2016-10-06 22:15 | 46790.3943 | 939.996
Devonshire Building | 2016-10-06 22:30 | 46790.6293 | 939.996
Devonshire Building | 2016-10-06 22:45 | 46790.8643 | 939.996
Devonshire Building | 2016-10-06 23:00 | 46791.0943 | 920.016
Devonshire Building | 2016-10-06 23:15 | 46791.3293 | 939.996
Devonshire Building | 2016-10-06 23:30 | 46791.5693 | 960.012
Devonshire Building | 2016-10-06 23:45 | 46791.8043 | 939.996 | 920.016
Devonshire Building | 2016-10-07 | 46792.0391 | 939.996
Devonshire Building | 2016-10-07 00:15 | 46792.2741 | 939.996
Devonshire Building | 2016-10-07 00:30 | 46792.5141 | 960.012
Devonshire Building | 2016-10-07 00:45 | 46792.7491 | 939.996
Devonshire Building | 2016-10-07 01:00 | 46792.9891 | 960.012
Devonshire Building | 2016-10-07 01:15 | 46793.2241 | 939.996
Devonshire Building | 2016-10-07 01:30 | 46793.4691 | 979.992
Devonshire Building | 2016-10-07 01:45 | 46793.7191 | 1000.008
Devonshire Building | 2016-10-07 02:00 | 46793.9791 | 1040.004
Devonshire Building | 2016-10-07 02:15 | 46794.2341 | 1019.988
Devonshire Building | 2016-10-07 02:30 | 46794.4891 | 1019.988
Devonshire Building | 2016-10-07 02:45 | 46794.7441 | 1019.988
Devonshire Building | 2016-10-07 03:00 | 46794.9991 | 1019.988
Devonshire Building | 2016-10-07 03:15 | 46795.2591 | 1040.004
Devonshire Building | 2016-10-07 03:30 | 46795.5091 | 1000.008
Devonshire Building | 2016-10-07 03:45 | 46795.7491 | 960.012
Devonshire Building | 2016-10-07 04:00 | 46795.9891 | 960.012
Devonshire Building | 2016-10-07 04:15 | 46796.2291 | 960.012
Devonshire Building | 2016-10-07 04:30 | 46796.4691 | 960.012
Devonshire Building | 2016-10-07 04:45 | 46796.7091 | 960.012
Devonshire Building | 2016-10-07 05:00 | 46796.9441 | 939.996
Devonshire Building | 2016-10-07 05:15 | 46797.1841 | 960.012
Devonshire Building | 2016-10-07 05:30 | 46797.4191 | 939.996
Devonshire Building | 2016-10-07 05:45 | 46797.6591 | 960.012
Devonshire Building | 2016-10-07 06:00 | 46797.8941 | 939.996
Devonshire Building | 2016-10-07 06:15 | 46798.1241 | 920.016
Devonshire Building | 2016-10-07 06:30 | 46798.3691 | 979.992
Devonshire Building | 2016-10-07 06:45 | 46798.6091 | 960.012
Devonshire Building | 2016-10-07 07:00 | 46798.8491 | 960.012
Devonshire Building | 2016-10-07 07:15 | 46799.0991 | 1000.008
Devonshire Building | 2016-10-07 07:30 | 46799.3341 | 939.996
Devonshire Building | 2016-10-07 07:45 | 46799.5691 | 939.996
Devonshire Building | 2016-10-07 08:00 | 46799.8091 | 960.012
Devonshire Building | 2016-10-07 08:15 | 46800.0441 | 939.996
Devonshire Building | 2016-10-07 08:30 | 46800.2791 | 939.996
Devonshire Building | 2016-10-07 08:45 | 46800.7641 | 1940.004
Devonshire Building | 2016-10-07 09:00 | 46801.0441 | 1119.996
Devonshire Building | 2016-10-07 09:15 | 46801.4291 | 1540.008
Devonshire Building | 2016-10-07 09:30 | 46801.7841 | 1419.984
Devonshire Building | 2016-10-07 09:45 | 46802.1141 | 1320.012
Devonshire Building | 2016-10-07 10:00 | 46802.4241 | 1239.984
Devonshire Building | 2016-10-07 10:15 | 46802.7341 | 1239.984
Devonshire Building | 2016-10-07 10:30 | 46803.2341 | 2000.016
Devonshire Building | 2016-10-07 10:45 | 46803.4941 | 1040.004
Devonshire Building | 2016-10-07 11:00 | 46803.7491 | 1019.988
Devonshire Building | 2016-10-07 11:15 | 46804.0091 | 1040.004
Devonshire Building | 2016-10-07 11:30 | 46804.2691 | 1040.004
Devonshire Building | 2016-10-07 11:45 | 46804.5391 | 1080
Devonshire Building | 2016-10-07 12:00 | 46805.0891 | 2199.996
Devonshire Building | 2016-10-07 12:15 | 46805.3691 | 1119.996
Devonshire Building | 2016-10-07 12:30 | 46805.6591 | 1159.992
Devonshire Building | 2016-10-07 12:45 | 46805.9441 | 1140.012
Devonshire Building | 2016-10-07 13:00 | 46806.2291 | 1140.012
Devonshire Building | 2016-10-07 13:15 | 46806.5241 | 1180.008
Devonshire Building | 2016-10-07 13:30 | 46806.8191 | 1180.008
Devonshire Building | 2016-10-07 13:45 | 46807.1291 | 1239.984
Devonshire Building | 2016-10-07 14:00 | 46807.4391 | 1239.984
Devonshire Building | 2016-10-07 14:15 | 46808.0091 | 2279.988
Devonshire Building | 2016-10-07 14:30 | 46808.3091 | 1199.988
Devonshire Building | 2016-10-07 14:45 | 46808.6191 | 1239.984
Devonshire Building | 2016-10-07 15:00 | 46808.9291 | 1239.984
Devonshire Building | 2016-10-07 15:15 | 46809.2591 | 1320.012
Devonshire Building | 2016-10-07 15:30 | 46809.5791 | 1280.016
Devonshire Building | 2016-10-07 15:45 | 46809.8891 | 1239.984
Devonshire Building | 2016-10-07 16:00 | 46810.1791 | 1159.992
Devonshire Building | 2016-10-07 16:15 | 46810.7891 | 2440.008
Devonshire Building | 2016-10-07 16:30 | 46811.0491 | 1040.004
Devonshire Building | 2016-10-07 16:45 | 46811.3141 | 1059.984
Devonshire Building | 2016-10-07 17:00 | 46811.5741 | 1040.004
Devonshire Building | 2016-10-07 17:15 | 46811.8341 | 1040.004
Devonshire Building | 2016-10-07 17:30 | 46812.0941 | 1040.004
Devonshire Building | 2016-10-07 17:45 | 46812.3491 | 1019.988
Devonshire Building | 2016-10-07 18:00 | 46812.5991 | 1000.008
Devonshire Building | 2016-10-07 18:15 | 46812.8491 | 1000.008
Devonshire Building | 2016-10-07 18:30 | 46813.0991 | 1000.008
Devonshire Building | 2016-10-07 18:45 | 46813.3441 | 979.992
Devonshire Building | 2016-10-07 19:00 | 46813.5891 | 979.992
Devonshire Building | 2016-10-07 19:15 | 46813.8291 | 960.012
Devonshire Building | 2016-10-07 19:30 | 46814.0741 | 979.992
Devonshire Building | 2016-10-07 19:45 | 46814.3291 | 1019.988
Devonshire Building | 2016-10-07 20:00 | 46814.5841 | 1019.988
Devonshire Building | 2016-10-07 20:15 | 46814.8391 | 1019.988
Devonshire Building | 2016-10-07 20:30 | 46815.0991 | 1040.004
Devonshire Building | 2016-10-07 20:45 | 46815.3541 | 1019.988
Devonshire Building | 2016-10-07 21:00 | 46815.6291 | 1100.016
Devonshire Building | 2016-10-07 21:15 | 46815.8841 | 1019.988
Devonshire Building | 2016-10-07 21:30 | 46816.1341 | 1000.008
Devonshire Building | 2016-10-07 21:45 | 46816.3741 | 960.012
Devonshire Building | 2016-10-07 22:00 | 46816.6091 | 939.996
Devonshire Building | 2016-10-07 22:15 | 46816.8491 | 960.012
Devonshire Building | 2016-10-07 22:30 | 46817.0891 | 960.012
Devonshire Building | 2016-10-07 22:45 | 46817.3291 | 960.012
Devonshire Building | 2016-10-07 23:00 | 46817.5691 | 960.012
Devonshire Building | 2016-10-07 23:15 | 46817.8141 | 979.992
Devonshire Building | 2016-10-07 23:30 | 46818.0541 | 960.012
Devonshire Building | 2016-10-07 23:45 | 46818.2941 | 960.012 | 920.016
Devonshire Building | 2016-10-08 | 46818.5391 | 979.992
Devonshire Building | 2016-10-08 00:15 | 46818.7791 | 960.012
Devonshire Building | 2016-10-08 00:30 | 46819.0241 | 979.992
Devonshire Building | 2016-10-08 00:45 | 46819.2641 | 960.012
Devonshire Building | 2016-10-08 01:00 | 46819.5091 | 979.992
Devonshire Building | 2016-10-08 01:15 | 46819.7541 | 979.992
Devonshire Building | 2016-10-08 01:30 | 46819.9941 | 960.012
Devonshire Building | 2016-10-08 01:45 | 46820.2391 | 979.992
Devonshire Building | 2016-10-08 02:00 | 46820.4791 | 960.012
Devonshire Building | 2016-10-08 02:15 | 46820.7241 | 979.992
Devonshire Building | 2016-10-08 02:30 | 46820.9641 | 960.012
Devonshire Building | 2016-10-08 02:45 | 46821.2091 | 979.992
Devonshire Building | 2016-10-08 03:00 | 46821.4491 | 960.012
Devonshire Building | 2016-10-08 03:15 | 46821.6941 | 979.992
Devonshire Building | 2016-10-08 03:30 | 46821.9341 | 960.012
Devonshire Building | 2016-10-08 03:45 | 46822.1791 | 979.992
Devonshire Building | 2016-10-08 04:00 | 46822.4191 | 960.012
Devonshire Building | 2016-10-08 04:15 | 46822.6641 | 979.992
Devonshire Building | 2016-10-08 04:30 | 46822.9041 | 960.012
Devonshire Building | 2016-10-08 04:45 | 46823.1491 | 979.992
Devonshire Building | 2016-10-08 05:00 | 46823.3891 | 960.012
Devonshire Building | 2016-10-08 05:15 | 46823.6341 | 979.992
Devonshire Building | 2016-10-08 05:30 | 46823.8741 | 960.012
Devonshire Building | 2016-10-08 05:45 | 46824.1191 | 979.992
Devonshire Building | 2016-10-08 06:00 | 46824.3591 | 960.012
Devonshire Building | 2016-10-08 06:15 | 46824.5991 | 960.012
Devonshire Building | 2016-10-08 06:30 | 46824.8391 | 960.012
Devonshire Building | 2016-10-08 06:45 | 46825.0841 | 979.992
Devonshire Building | 2016-10-08 07:00 | 46825.3241 | 960.012
Devonshire Building | 2016-10-08 07:15 | 46825.5591 | 939.996
Devonshire Building | 2016-10-08 07:30 | 46825.7991 | 960.012
Devonshire Building | 2016-10-08 07:45 | 46826.0391 | 960.012
Devonshire Building | 2016-10-08 08:00 | 46826.2741 | 939.996
Devonshire Building | 2016-10-08 08:15 | 46826.5091 | 939.996
Devonshire Building | 2016-10-08 08:30 | 46826.7441 | 939.996
Devonshire Building | 2016-10-08 08:45 | 46826.9841 | 960.012
Devonshire Building | 2016-10-08 09:00 | 46827.2191 | 939.996
Devonshire Building | 2016-10-08 09:15 | 46827.4541 | 939.996
Devonshire Building | 2016-10-08 09:30 | 46827.6891 | 939.996
Devonshire Building | 2016-10-08 09:45 | 46827.9241 | 939.996
Devonshire Building | 2016-10-08 10:00 | 46828.1591 | 939.996
Devonshire Building | 2016-10-08 10:15 | 46828.3941 | 939.996
Devonshire Building | 2016-10-08 10:30 | 46828.6341 | 960.012
Devonshire Building | 2016-10-08 10:45 | 46828.8691 | 939.996
Devonshire Building | 2016-10-08 11:00 | 46829.1041 | 939.996
Devonshire Building | 2016-10-08 11:15 | 46829.3441 | 960.012
Devonshire Building | 2016-10-08 11:30 | 46829.5791 | 939.996
Devonshire Building | 2016-10-08 11:45 | 46829.8141 | 939.996
Devonshire Building | 2016-10-08 12:00 | 46830.0541 | 960.012
Devonshire Building | 2016-10-08 12:15 | 46830.2891 | 939.996
Devonshire Building | 2016-10-08 12:30 | 46830.5291 | 960.012
Devonshire Building | 2016-10-08 12:45 | 46830.7641 | 939.996
Devonshire Building | 2016-10-08 13:00 | 46831.0041 | 960.012
Devonshire Building | 2016-10-08 13:15 | 46831.2391 | 939.996
Devonshire Building | 2016-10-08 13:30 | 46831.4791 | 960.012
Devonshire Building | 2016-10-08 13:45 | 46831.7191 | 960.012
Devonshire Building | 2016-10-08 14:00 | 46832.4591 | 2959.992
Devonshire Building | 2016-10-08 14:15 | 46832.6941 | 939.996
Devonshire Building | 2016-10-08 14:30 | 46832.9391 | 979.992
Devonshire Building | 2016-10-08 14:45 | 46833.1741 | 939.996
Devonshire Building | 2016-10-08 15:00 | 46833.4141 | 960.012
Devonshire Building | 2016-10-08 15:15 | 46833.6541 | 960.012
Devonshire Building | 2016-10-08 15:30 | 46833.8941 | 960.012
Devonshire Building | 2016-10-08 15:45 | 46834.1341 | 960.012
Devonshire Building | 2016-10-08 16:00 | 46834.3741 | 960.012
Devonshire Building | 2016-10-08 16:15 | 46834.6141 | 960.012
Devonshire Building | 2016-10-08 16:30 | 46834.8491 | 939.996
Devonshire Building | 2016-10-08 16:45 | 46835.0891 | 960.012
Devonshire Building | 2016-10-08 17:00 | 46835.3291 | 960.012
Devonshire Building | 2016-10-08 17:15 | 46835.5691 | 960.012
Devonshire Building | 2016-10-08 17:30 | 46835.8041 | 939.996
Devonshire Building | 2016-10-08 17:45 | 46836.0441 | 960.012
Devonshire Building | 2016-10-08 18:00 | 46836.2841 | 960.012
Devonshire Building | 2016-10-08 18:15 | 46836.5241 | 960.012
Devonshire Building | 2016-10-08 18:30 | 46836.7641 | 960.012
Devonshire Building | 2016-10-08 18:45 | 46837.0041 | 960.012
Devonshire Building | 2016-10-08 19:00 | 46837.2441 | 960.012
Devonshire Building | 2016-10-08 19:15 | 46837.4841 | 960.012
Devonshire Building | 2016-10-08 19:30 | 46837.7341 | 1000.008
Devonshire Building | 2016-10-08 19:45 | 46837.9941 | 1040.004
Devonshire Building | 2016-10-08 20:00 | 46838.2491 | 1019.988
Devonshire Building | 2016-10-08 20:15 | 46838.5091 | 1040.004
Devonshire Building | 2016-10-08 20:30 | 46838.7691 | 1040.004
Devonshire Building | 2016-10-08 20:45 | 46839.0291 | 1040.004
Devonshire Building | 2016-10-08 21:00 | 46839.2941 | 1059.984
Devonshire Building | 2016-10-08 21:15 | 46839.5491 | 1019.988
Devonshire Building | 2016-10-08 21:30 | 46839.8091 | 1040.004
Devonshire Building | 2016-10-08 21:45 | 46840.0491 | 960.012
Devonshire Building | 2016-10-08 22:00 | 46840.2941 | 979.992
Devonshire Building | 2016-10-08 22:15 | 46840.5341 | 960.012
Devonshire Building | 2016-10-08 22:30 | 46840.7791 | 979.992
Devonshire Building | 2016-10-08 22:45 | 46841.0241 | 979.992
Devonshire Building | 2016-10-08 23:00 | 46841.2641 | 960.012
Devonshire Building | 2016-10-08 23:15 | 46841.5091 | 979.992
Devonshire Building | 2016-10-08 23:30 | 46841.7541 | 979.992
Devonshire Building | 2016-10-08 23:45 | 46841.9991 | 979.992 | 939.996
Devonshire Building | 2016-10-09 | 46842.2383 | 960.012
Devonshire Building | 2016-10-09 00:15 | 46842.4833 | 979.992
Devonshire Building | 2016-10-09 00:30 | 46842.7283 | 979.992
Devonshire Building | 2016-10-09 00:45 | 46842.9733 | 979.992
Devonshire Building | 2016-10-09 01:00 | 46843.2183 | 979.992
Devonshire Building | 2016-10-09 01:15 | 46843.4633 | 979.992
Devonshire Building | 2016-10-09 01:30 | 46843.7083 | 979.992
Devonshire Building | 2016-10-09 01:45 | 46843.9483 | 960.012
Devonshire Building | 2016-10-09 02:00 | 46844.1933 | 979.992
Devonshire Building | 2016-10-09 02:15 | 46844.4383 | 979.992
Devonshire Building | 2016-10-09 02:30 | 46844.6833 | 979.992
Devonshire Building | 2016-10-09 02:45 | 46844.9283 | 979.992
Devonshire Building | 2016-10-09 03:00 | 46845.1733 | 979.992
Devonshire Building | 2016-10-09 03:15 | 46845.4183 | 979.992
Devonshire Building | 2016-10-09 03:30 | 46845.6633 | 979.992
Devonshire Building | 2016-10-09 03:45 | 46845.9083 | 979.992
Devonshire Building | 2016-10-09 04:00 | 46846.1533 | 979.992
Devonshire Building | 2016-10-09 04:15 | 46846.3983 | 979.992
Devonshire Building | 2016-10-09 04:30 | 46846.6432 | 979.992
Devonshire Building | 2016-10-09 04:45 | 46846.8882 | 979.992
Devonshire Building | 2016-10-09 05:00 | 46847.1332 | 979.992
Devonshire Building | 2016-10-09 05:15 | 46847.3782 | 979.992
Devonshire Building | 2016-10-09 05:30 | 46847.6232 | 979.992
Devonshire Building | 2016-10-09 05:45 | 46847.8682 | 979.992
Devonshire Building | 2016-10-09 06:00 | 46848.1082 | 960.012
Devonshire Building | 2016-10-09 06:15 | 46848.3532 | 979.992
Devonshire Building | 2016-10-09 06:30 | 46848.5982 | 979.992
Devonshire Building | 2016-10-09 06:45 | 46848.8432 | 979.992
Devonshire Building | 2016-10-09 07:00 | 46849.0882 | 979.992
Devonshire Building | 2016-10-09 07:15 | 46849.3282 | 960.012
Devonshire Building | 2016-10-09 07:30 | 46849.5682 | 960.012
Devonshire Building | 2016-10-09 07:45 | 46849.8132 | 979.992
Devonshire Building | 2016-10-09 08:00 | 46850.0532 | 960.012
Devonshire Building | 2016-10-09 08:15 | 46850.2932 | 960.012
Devonshire Building | 2016-10-09 08:30 | 46850.5332 | 960.012
Devonshire Building | 2016-10-09 08:45 | 46850.7682 | 939.996
Devonshire Building | 2016-10-09 09:00 | 46851.0082 | 960.012
Devonshire Building | 2016-10-09 09:15 | 46851.2432 | 939.996
Devonshire Building | 2016-10-09 09:30 | 46851.4833 | 960.012
Devonshire Building | 2016-10-09 09:45 | 46851.7182 | 939.996
Devonshire Building | 2016-10-09 10:00 | 46851.9583 | 960.012
Devonshire Building | 2016-10-09 10:15 | 46852.1933 | 939.996
Devonshire Building | 2016-10-09 10:30 | 46852.4333 | 960.012
Devonshire Building | 2016-10-09 10:45 | 46852.6683 | 939.996
Devonshire Building | 2016-10-09 11:00 | 46852.9083 | 960.012
Devonshire Building | 2016-10-09 11:15 | 46853.1433 | 939.996
Devonshire Building | 2016-10-09 11:30 | 46853.3833 | 960.012
Devonshire Building | 2016-10-09 11:45 | 46853.6233 | 960.012
Devonshire Building | 2016-10-09 12:00 | 46853.8633 | 960.012
Devonshire Building | 2016-10-09 12:15 | 46854.0983 | 939.996
Devonshire Building | 2016-10-09 12:30 | 46854.3383 | 960.012
Devonshire Building | 2016-10-09 12:45 | 46854.5783 | 960.012
Devonshire Building | 2016-10-09 13:00 | 46854.8233 | 979.992
Devonshire Building | 2016-10-09 13:15 | 46855.0633 | 960.012
Devonshire Building | 2016-10-09 13:30 | 46855.3033 | 960.012
Devonshire Building | 2016-10-09 13:45 | 46855.5483 | 979.992
Devonshire Building | 2016-10-09 14:00 | 46855.7883 | 960.012
Devonshire Building | 2016-10-09 14:15 | 46856.0283 | 960.012
Devonshire Building | 2016-10-09 14:30 | 46856.2733 | 979.992
Devonshire Building | 2016-10-09 14:45 | 46856.5133 | 960.012
Devonshire Building | 2016-10-09 15:00 | 46856.7583 | 979.992
Devonshire Building | 2016-10-09 15:15 | 46856.9983 | 960.012
Devonshire Building | 2016-10-09 15:30 | 46857.2433 | 979.992
Devonshire Building | 2016-10-09 15:45 | 46857.4833 | 960.012
Devonshire Building | 2016-10-09 16:00 | 46857.7233 | 960.012
Devonshire Building | 2016-10-09 16:15 | 46857.9633 | 960.012
Devonshire Building | 2016-10-09 16:30 | 46858.2033 | 960.012
Devonshire Building | 2016-10-09 16:45 | 46858.4433 | 960.012
Devonshire Building | 2016-10-09 17:00 | 46858.6833 | 960.012
Devonshire Building | 2016-10-09 17:15 | 46858.9233 | 960.012
Devonshire Building | 2016-10-09 17:30 | 46859.1633 | 960.012
Devonshire Building | 2016-10-09 17:45 | 46859.4033 | 960.012
Devonshire Building | 2016-10-09 18:00 | 46859.6433 | 960.012
Devonshire Building | 2016-10-09 18:15 | 46859.8833 | 960.012
Devonshire Building | 2016-10-09 18:30 | 46860.3633 | 1919.988
Devonshire Building | 2016-10-09 18:45 | 46860.8633 | 2000.016
Devonshire Building | 2016-10-09 19:00 | 46861.1033 | 960.012
Devonshire Building | 2016-10-09 19:15 | 46861.3433 | 960.012
Devonshire Building | 2016-10-09 19:30 | 46861.5933 | 1000.008
Devonshire Building | 2016-10-09 19:45 | 46861.8533 | 1040.004
Devonshire Building | 2016-10-09 20:00 | 46862.1133 | 1040.004
Devonshire Building | 2016-10-09 20:15 | 46862.3683 | 1019.988
Devonshire Building | 2016-10-09 20:30 | 46862.6283 | 1040.004
Devonshire Building | 2016-10-09 20:45 | 46862.8883 | 1040.004
Devonshire Building | 2016-10-09 21:00 | 46863.1583 | 1080
Devonshire Building | 2016-10-09 21:15 | 46863.4133 | 1019.988
Devonshire Building | 2016-10-09 21:30 | 46863.6733 | 1040.004
Devonshire Building | 2016-10-09 21:45 | 46863.9333 | 1040.004
Devonshire Building | 2016-10-09 22:00 | 46864.1733 | 960.012
Devonshire Building | 2016-10-09 22:15 | 46864.4183 | 979.992
Devonshire Building | 2016-10-09 22:30 | 46864.6633 | 979.992
Devonshire Building | 2016-10-09 22:45 | 46864.9083 | 979.992
Devonshire Building | 2016-10-09 23:00 | 46865.1533 | 979.992
Devonshire Building | 2016-10-09 23:15 | 46865.3983 | 979.992
Devonshire Building | 2016-10-09 23:30 | 46865.6433 | 979.992
Devonshire Building | 2016-10-09 23:45 | 46865.8933 | 1000.008 | 939.996
Devonshire Building | 2016-10-10 | 46866.1406 | 979.992
Devonshire Building | 2016-10-10 00:15 | 46866.3856 | 979.992
Devonshire Building | 2016-10-10 00:30 | 46866.6356 | 1000.008
Devonshire Building | 2016-10-10 00:45 | 46866.8806 | 979.992
Devonshire Building | 2016-10-10 01:00 | 46867.1256 | 979.992
Devonshire Building | 2016-10-10 01:15 | 46867.3756 | 1000.008
Devonshire Building | 2016-10-10 01:30 | 46867.6206 | 979.992
Devonshire Building | 2016-10-10 01:45 | 46867.8656 | 979.992
Devonshire Building | 2016-10-10 02:00 | 46868.1056 | 960.012
Devonshire Building | 2016-10-10 02:15 | 46868.3506 | 979.992
Devonshire Building | 2016-10-10 02:30 | 46868.5956 | 979.992
Devonshire Building | 2016-10-10 02:45 | 46868.8406 | 979.992
Devonshire Building | 2016-10-10 03:00 | 46869.0856 | 979.992
Devonshire Building | 2016-10-10 03:15 | 46869.3306 | 979.992
Devonshire Building | 2016-10-10 03:30 | 46869.5706 | 960.012
Devonshire Building | 2016-10-10 03:45 | 46869.8156 | 979.992
Devonshire Building | 2016-10-10 04:00 | 46870.0606 | 979.992
Devonshire Building | 2016-10-10 04:15 | 46870.3056 | 979.992
Devonshire Building | 2016-10-10 04:30 | 46870.5506 | 979.992
Devonshire Building | 2016-10-10 04:45 | 46870.7906 | 960.012
Devonshire Building | 2016-10-10 05:00 | 46871.0356 | 979.992
Devonshire Building | 2016-10-10 05:15 | 46871.2756 | 960.012
Devonshire Building | 2016-10-10 05:30 | 46871.5206 | 979.992
Devonshire Building | 2016-10-10 05:45 | 46871.7656 | 979.992
Devonshire Building | 2016-10-10 06:00 | 46872.0056 | 960.012
Devonshire Building | 2016-10-10 06:15 | 46872.2456 | 960.012
Devonshire Building | 2016-10-10 06:30 | 46872.4856 | 960.012
Devonshire Building | 2016-10-10 06:45 | 46872.7356 | 1000.008
Devonshire Building | 2016-10-10 07:00 | 46872.9706 | 939.996
Devonshire Building | 2016-10-10 07:15 | 46873.2106 | 960.012
Devonshire Building | 2016-10-10 07:30 | 46873.4506 | 960.012
Devonshire Building | 2016-10-10 07:45 | 46873.6906 | 960.012
Devonshire Building | 2016-10-10 08:00 | 46873.9356 | 979.992
Devonshire Building | 2016-10-10 08:15 | 46874.1806 | 979.992
Devonshire Building | 2016-10-10 08:30 | 46874.9206 | 2959.992
Devonshire Building | 2016-10-10 08:45 | 46875.1656 | 979.992
Devonshire Building | 2016-10-10 09:00 | 46875.4256 | 1040.004
Devonshire Building | 2016-10-10 09:15 | 46875.6656 | 960.012
Devonshire Building | 2016-10-10 09:30 | 46875.9156 | 1000.008
Devonshire Building | 2016-10-10 09:45 | 46876.6956 | 3120.012
Devonshire Building | 2016-10-10 10:00 | 46876.9656 | 1080
Devonshire Building | 2016-10-10 10:15 | 46877.2406 | 1100.016
Devonshire Building | 2016-10-10 10:30 | 46877.5256 | 1140.012
Devonshire Building | 2016-10-10 10:45 | 46877.8306 | 1220.004
Devonshire Building | 2016-10-10 11:00 | 46878.6656 | 3340.008
Devonshire Building | 2016-10-10 11:15 | 46879.0156 | 1400.004
Devonshire Building | 2016-10-10 11:30 | 46879.4506 | 1739.988
Devonshire Building | 2016-10-10 11:45 | 46879.8506 | 1599.984
Devonshire Building | 2016-10-10 12:00 | 46880.4906 | 2559.996
Devonshire Building | 2016-10-10 12:15 | 46881.1256 | 2540.016
Devonshire Building | 2016-10-10 12:30 | 46881.4906 | 1460.016
Devonshire Building | 2016-10-10 12:45 | 46881.8106 | 1280.016
Devonshire Building | 2016-10-10 13:00 | 46882.1156 | 1220.004
Devonshire Building | 2016-10-10 13:15 | 46882.4206 | 1220.004
Devonshire Building | 2016-10-10 13:30 | 46882.7106 | 1159.992
Devonshire Building | 2016-10-10 13:45 | 46883.5356 | 3300.012
Devonshire Building | 2016-10-10 14:00 | 46883.8156 | 1119.996
Devonshire Building | 2016-10-10 14:15 | 46884.1007 | 1140.012
Devonshire Building | 2016-10-10 14:30 | 46884.3857 | 1140.012
Devonshire Building | 2016-10-10 14:45 | 46884.6757 | 1159.992
Devonshire Building | 2016-10-10 15:00 | 46884.9557 | 1119.996
Devonshire Building | 2016-10-10 15:15 | 46885.2407 | 1140.012
Devonshire Building | 2016-10-10 15:30 | 46885.5307 | 1159.992
Devonshire Building | 2016-10-10 15:45 | 46885.8057 | 1100.016
Devonshire Building | 2016-10-10 16:00 | 46886.6357 | 3319.992
Devonshire Building | 2016-10-10 16:15 | 46886.9407 | 1220.004
Devonshire Building | 2016-10-10 16:30 | 46887.2607 | 1280.016
Devonshire Building | 2016-10-10 16:45 | 46887.5807 | 1280.016
Devonshire Building | 2016-10-10 17:00 | 46887.9007 | 1280.016
Devonshire Building | 2016-10-10 17:15 | 46888.2157 | 1260
Devonshire Building | 2016-10-10 17:30 | 46888.5157 | 1199.988
Devonshire Building | 2016-10-10 17:45 | 46888.8057 | 1159.992
Devonshire Building | 2016-10-10 18:00 | 46889.0807 | 1100.016
Devonshire Building | 2016-10-10 18:15 | 46889.3457 | 1059.984
Devonshire Building | 2016-10-10 18:30 | 46889.6107 | 1059.984
Devonshire Building | 2016-10-10 18:45 | 46889.8707 | 1040.004
Devonshire Building | 2016-10-10 19:00 | 46890.1257 | 1019.988
Devonshire Building | 2016-10-10 19:15 | 46890.3807 | 1019.988
Devonshire Building | 2016-10-10 19:30 | 46890.6307 | 1000.008
Devonshire Building | 2016-10-10 19:45 | 46890.8807 | 1000.008
Devonshire Building | 2016-10-10 20:00 | 46891.1307 | 1000.008
Devonshire Building | 2016-10-10 20:15 | 46891.3807 | 1000.008
Devonshire Building | 2016-10-10 20:30 | 46891.6307 | 1000.008
Devonshire Building | 2016-10-10 20:45 | 46891.8757 | 979.992
Devonshire Building | 2016-10-10 21:00 | 46892.3657 | 1959.984
Devonshire Building | 2016-10-10 21:15 | 46892.6057 | 960.012
Devonshire Building | 2016-10-10 21:30 | 46892.8507 | 979.992
Devonshire Building | 2016-10-10 21:45 | 46893.0907 | 960.012
Devonshire Building | 2016-10-10 22:00 | 46893.3307 | 960.012
Devonshire Building | 2016-10-10 22:15 | 46893.5707 | 960.012
Devonshire Building | 2016-10-10 22:30 | 46893.8107 | 960.012
Devonshire Building | 2016-10-10 22:45 | 46894.0557 | 979.992
Devonshire Building | 2016-10-10 23:00 | 46894.2957 | 960.012
Devonshire Building | 2016-10-10 23:15 | 46894.5407 | 979.992
Devonshire Building | 2016-10-10 23:30 | 46894.7857 | 979.992
Devonshire Building | 2016-10-10 23:45 | 46895.0307 | 979.992 | 939.996
Devonshire Building | 2016-10-11 | 46895.2734 | 979.992
Devonshire Building | 2016-10-11 00:15 | 46895.5184 | 979.992
Devonshire Building | 2016-10-11 00:30 | 46895.7634 | 979.992
Devonshire Building | 2016-10-11 00:45 | 46896.0134 | 1000.008
Devonshire Building | 2016-10-11 01:00 | 46896.2584 | 979.992
Devonshire Building | 2016-10-11 01:15 | 46896.5084 | 1000.008
Devonshire Building | 2016-10-11 01:30 | 46896.7584 | 1000.008
Devonshire Building | 2016-10-11 01:45 | 46897.0034 | 979.992
Devonshire Building | 2016-10-11 02:00 | 46897.2534 | 1000.008
Devonshire Building | 2016-10-11 02:15 | 46897.5034 | 1000.008
Devonshire Building | 2016-10-11 02:30 | 46897.7534 | 1000.008
Devonshire Building | 2016-10-11 02:45 | 46897.9984 | 979.992
Devonshire Building | 2016-10-11 03:00 | 46898.2484 | 1000.008
Devonshire Building | 2016-10-11 03:15 | 46898.4984 | 1000.008
Devonshire Building | 2016-10-11 03:30 | 46898.7484 | 1000.008
Devonshire Building | 2016-10-11 03:45 | 46898.9984 | 1000.008
Devonshire Building | 2016-10-11 04:00 | 46899.2534 | 1019.988
Devonshire Building | 2016-10-11 04:15 | 46899.5034 | 1000.008
Devonshire Building | 2016-10-11 04:30 | 46899.7535 | 1000.008
Devonshire Building | 2016-10-11 04:45 | 46900.0035 | 1000.008
Devonshire Building | 2016-10-11 05:00 | 46900.2485 | 979.992
Devonshire Building | 2016-10-11 05:15 | 46900.4985 | 1000.008
Devonshire Building | 2016-10-11 05:30 | 46900.7435 | 979.992
Devonshire Building | 2016-10-11 05:45 | 46900.9884 | 979.992
Devonshire Building | 2016-10-11 06:00 | 46901.2334 | 979.992
Devonshire Building | 2016-10-11 06:15 | 46901.4734 | 960.012
Devonshire Building | 2016-10-11 06:30 | 46901.7184 | 979.992
Devonshire Building | 2016-10-11 06:45 | 46901.9585 | 960.012
Devonshire Building | 2016-10-11 07:00 | 46902.1985 | 960.012
Devonshire Building | 2016-10-11 07:15 | 46902.4435 | 979.992
Devonshire Building | 2016-10-11 07:30 | 46902.6835 | 960.012
Devonshire Building | 2016-10-11 07:45 | 46902.9235 | 960.012
Devonshire Building | 2016-10-11 08:00 | 46903.1785 | 1019.988
Devonshire Building | 2016-10-11 08:15 | 46903.4235 | 979.992
Devonshire Building | 2016-10-11 08:30 | 46903.9535 | 2120.004
Devonshire Building | 2016-10-11 08:45 | 46904.2435 | 1159.992
Devonshire Building | 2016-10-11 09:00 | 46904.5485 | 1220.004
Devonshire Building | 2016-10-11 09:15 | 46904.8535 | 1220.004
Devonshire Building | 2016-10-11 09:30 | 46905.1535 | 1199.988
Devonshire Building | 2016-10-11 09:45 | 46905.4534 | 1199.988
Devonshire Building | 2016-10-11 10:00 | 46905.7534 | 1199.988
Devonshire Building | 2016-10-11 10:15 | 46906.3284 | 2300.004
Devonshire Building | 2016-10-11 10:30 | 46906.6834 | 1419.984
Devonshire Building | 2016-10-11 10:45 | 46907.0834 | 1599.984
Devonshire Building | 2016-10-11 11:00 | 46907.4534 | 1479.996
Devonshire Building | 2016-10-11 11:15 | 46907.8084 | 1419.984
Devonshire Building | 2016-10-11 11:30 | 46908.1584 | 1400.004
Devonshire Building | 2016-10-11 11:45 | 46908.5684 | 1640.016
Devonshire Building | 2016-10-11 12:00 | 46909.0534 | 1940.004
Devonshire Building | 2016-10-11 12:15 | 46909.3484 | 1180.008
Devonshire Building | 2016-10-11 12:30 | 46909.6334 | 1140.012
Devonshire Building | 2016-10-11 12:45 | 46909.9284 | 1180.008
Devonshire Building | 2016-10-11 13:00 | 46910.2134 | 1140.012
Devonshire Building | 2016-10-11 13:15 | 46910.7634 | 2199.996
Devonshire Building | 2016-10-11 13:30 | 46911.0634 | 1199.988
Devonshire Building | 2016-10-11 13:45 | 46911.3834 | 1280.016
Devonshire Building | 2016-10-11 14:00 | 46911.6984 | 1260
Devonshire Building | 2016-10-11 14:15 | 46912.0134 | 1260
Devonshire Building | 2016-10-11 14:30 | 46912.3234 | 1239.984
Devonshire Building | 2016-10-11 14:45 | 46912.6334 | 1239.984
Devonshire Building | 2016-10-11 15:00 | 46913.1634 | 2120.004
Devonshire Building | 2016-10-11 15:15 | 46913.5034 | 1360.008
Devonshire Building | 2016-10-11 15:30 | 46913.8134 | 1239.984
Devonshire Building | 2016-10-11 15:45 | 46914.1284 | 1260
Devonshire Building | 2016-10-11 16:00 | 46914.4284 | 1199.988
Devonshire Building | 2016-10-11 16:15 | 46914.7234 | 1180.008
Devonshire Building | 2016-10-11 16:30 | 46915.0084 | 1140.012
Devonshire Building | 2016-10-11 16:45 | 46915.2934 | 1140.012
Devonshire Building | 2016-10-11 17:00 | 46915.8134 | 2080.008
Devonshire Building | 2016-10-11 17:15 | 46916.0784 | 1059.984
Devonshire Building | 2016-10-11 17:30 | 46916.3334 | 1019.988
Devonshire Building | 2016-10-11 17:45 | 46916.5884 | 1019.988
Devonshire Building | 2016-10-11 18:00 | 46916.8484 | 1040.004
Devonshire Building | 2016-10-11 18:15 | 46917.1034 | 1019.988
Devonshire Building | 2016-10-11 18:30 | 46917.3584 | 1019.988
Devonshire Building | 2016-10-11 18:45 | 46917.6184 | 1040.004
Devonshire Building | 2016-10-11 19:00 | 46917.8734 | 1019.988
Devonshire Building | 2016-10-11 19:15 | 46918.1284 | 1019.988
Devonshire Building | 2016-10-11 19:30 | 46918.3884 | 1040.004
Devonshire Building | 2016-10-11 19:45 | 46918.6434 | 1019.988
Devonshire Building | 2016-10-11 20:00 | 46918.9034 | 1040.004
Devonshire Building | 2016-10-11 20:15 | 46919.1634 | 1040.004
Devonshire Building | 2016-10-11 20:30 | 46919.4184 | 1019.988
Devonshire Building | 2016-10-11 20:45 | 46919.6784 | 1040.004
Devonshire Building | 2016-10-11 21:00 | 46919.9384 | 1040.004
Devonshire Building | 2016-10-11 21:15 | 46920.1934 | 1019.988
Devonshire Building | 2016-10-11 21:30 | 46920.4484 | 1019.988
Devonshire Building | 2016-10-11 21:45 | 46920.6984 | 1000.008
Devonshire Building | 2016-10-11 22:00 | 46920.9534 | 1019.988
Devonshire Building | 2016-10-11 22:15 | 46921.2084 | 1019.988
Devonshire Building | 2016-10-11 22:30 | 46921.4584 | 1000.008
Devonshire Building | 2016-10-11 22:45 | 46921.7134 | 1019.988
Devonshire Building | 2016-10-11 23:00 | 46921.9684 | 1019.988
Devonshire Building | 2016-10-11 23:15 | 46922.2234 | 1019.988
Devonshire Building | 2016-10-11 23:30 | 46922.4784 | 1019.988
Devonshire Building | 2016-10-11 23:45 | 46922.7334 | 1019.988 | 960.012
Devonshire Building | 2016-10-12 | 46922.9883 | 1019.988
Devonshire Building | 2016-10-12 00:15 | 46923.2383 | 1000.008
Devonshire Building | 2016-10-12 00:30 | 46923.4983 | 1040.004
Devonshire Building | 2016-10-12 00:45 | 46923.7483 | 1000.008
Devonshire Building | 2016-10-12 01:00 | 46924.0033 | 1019.988
Devonshire Building | 2016-10-12 01:15 | 46924.2583 | 1019.988
Devonshire Building | 2016-10-12 01:30 | 46924.5133 | 1019.988
Devonshire Building | 2016-10-12 01:45 | 46924.7683 | 1019.988
Devonshire Building | 2016-10-12 02:00 | 46925.0183 | 1000.008
Devonshire Building | 2016-10-12 02:15 | 46925.2733 | 1019.988
Devonshire Building | 2016-10-12 02:30 | 46925.5283 | 1019.988
Devonshire Building | 2016-10-12 02:45 | 46925.7833 | 1019.988
Devonshire Building | 2016-10-12 03:00 | 46926.0333 | 1000.008
Devonshire Building | 2016-10-12 03:15 | 46926.2883 | 1019.988
Devonshire Building | 2016-10-12 03:30 | 46926.5433 | 1019.988
Devonshire Building | 2016-10-12 03:45 | 46926.7983 | 1019.988
Devonshire Building | 2016-10-12 04:00 | 46927.0483 | 1000.008
Devonshire Building | 2016-10-12 04:15 | 46927.3033 | 1019.988
Devonshire Building | 2016-10-12 04:30 | 46927.5583 | 1019.988
Devonshire Building | 2016-10-12 04:45 | 46927.8133 | 1019.988
Devonshire Building | 2016-10-12 05:00 | 46928.0633 | 1000.008
Devonshire Building | 2016-10-12 05:15 | 46928.3183 | 1019.988
Devonshire Building | 2016-10-12 05:30 | 46928.5732 | 1019.988
Devonshire Building | 2016-10-12 05:45 | 46928.8233 | 1000.008
Devonshire Building | 2016-10-12 06:00 | 46929.0733 | 1000.008
Devonshire Building | 2016-10-12 06:15 | 46929.3233 | 1000.008
Devonshire Building | 2016-10-12 06:30 | 46929.5733 | 1000.008
Devonshire Building | 2016-10-12 06:45 | 46929.8233 | 1000.008
Devonshire Building | 2016-10-12 07:00 | 46930.0683 | 979.992
Devonshire Building | 2016-10-12 07:15 | 46930.3133 | 979.992
Devonshire Building | 2016-10-12 07:30 | 46930.5683 | 1019.988
Devonshire Building | 2016-10-12 07:45 | 46930.8332 | 1059.984
Devonshire Building | 2016-10-12 08:00 | 46931.0832 | 1000.008
Devonshire Building | 2016-10-12 08:15 | 46931.5982 | 2059.992
Devonshire Building | 2016-10-12 08:30 | 46931.8532 | 1019.988
Devonshire Building | 2016-10-12 08:45 | 46932.1032 | 1000.008
Devonshire Building | 2016-10-12 09:00 | 46932.3532 | 1000.008
Devonshire Building | 2016-10-12 09:15 | 46932.6033 | 1000.008
Devonshire Building | 2016-10-12 09:30 | 46932.8533 | 1000.008
Devonshire Building | 2016-10-12 09:45 | 46933.1082 | 1019.988
Devonshire Building | 2016-10-12 10:00 | 46933.6083 | 2000.016
Devonshire Building | 2016-10-12 10:15 | 46933.8583 | 1000.008
Devonshire Building | 2016-10-12 10:30 | 46934.1133 | 1019.988
Devonshire Building | 2016-10-12 10:45 | 46934.3833 | 1080
Devonshire Building | 2016-10-12 11:00 | 46934.6883 | 1220.004
Devonshire Building | 2016-10-12 11:15 | 46935.0133 | 1299.996
Devonshire Building | 2016-10-12 11:30 | 46935.5832 | 2279.988
Devonshire Building | 2016-10-12 11:45 | 46935.8982 | 1260
Devonshire Building | 2016-10-12 12:00 | 46936.2082 | 1239.984
Devonshire Building | 2016-10-12 12:15 | 46936.5182 | 1239.984
Devonshire Building | 2016-10-12 12:30 | 46936.8232 | 1220.004
Devonshire Building | 2016-10-12 12:45 | 46937.1282 | 1220.004
Devonshire Building | 2016-10-12 13:00 | 46937.4282 | 1199.988
Devonshire Building | 2016-10-12 13:15 | 46937.9932 | 2260.008
Devonshire Building | 2016-10-12 13:30 | 46938.2882 | 1180.008
Devonshire Building | 2016-10-12 13:45 | 46938.5982 | 1239.984
Devonshire Building | 2016-10-12 14:00 | 46938.9082 | 1239.984
Devonshire Building | 2016-10-12 14:15 | 46939.2132 | 1220.004
Devonshire Building | 2016-10-12 14:30 | 46939.5182 | 1220.004
Devonshire Building | 2016-10-12 14:45 | 46939.8282 | 1239.984
Devonshire Building | 2016-10-12 15:00 | 46940.1282 | 1199.988
Devonshire Building | 2016-10-12 15:15 | 46940.6832 | 2220.012
Devonshire Building | 2016-10-12 15:30 | 46940.9832 | 1199.988
Devonshire Building | 2016-10-12 15:45 | 46941.2832 | 1199.988
Devonshire Building | 2016-10-12 16:00 | 46941.5732 | 1159.992
Devonshire Building | 2016-10-12 16:15 | 46941.9082 | 1339.992
Devonshire Building | 2016-10-12 16:30 | 46942.2432 | 1339.992
Devonshire Building | 2016-10-12 16:45 | 46942.5732 | 1320.012
Devonshire Building | 2016-10-12 17:00 | 46942.8982 | 1299.996
Devonshire Building | 2016-10-12 17:15 | 46943.2232 | 1299.996
Devonshire Building | 2016-10-12 17:30 | 46943.5282 | 1220.004
Devonshire Building | 2016-10-12 17:45 | 46943.8182 | 1159.992
Devonshire Building | 2016-10-12 18:00 | 46944.1032 | 1140.012
Devonshire Building | 2016-10-12 18:15 | 46944.3782 | 1100.016
Devonshire Building | 2016-10-12 18:30 | 46944.6482 | 1080
Devonshire Building | 2016-10-12 18:45 | 46944.9182 | 1080
Devonshire Building | 2016-10-12 19:00 | 46945.1882 | 1080
Devonshire Building | 2016-10-12 19:15 | 46945.4532 | 1059.984
Devonshire Building | 2016-10-12 19:30 | 46945.7182 | 1059.984
Devonshire Building | 2016-10-12 19:45 | 46945.9782 | 1040.004
Devonshire Building | 2016-10-12 20:00 | 46946.2532 | 1100.016
Devonshire Building | 2016-10-12 20:15 | 46946.7432 | 1959.984
Devonshire Building | 2016-10-12 20:30 | 46946.9982 | 1019.988
Devonshire Building | 2016-10-12 20:45 | 46947.2532 | 1019.988
Devonshire Building | 2016-10-12 21:00 | 46947.5082 | 1019.988
Devonshire Building | 2016-10-12 21:15 | 46947.7632 | 1019.988
Devonshire Building | 2016-10-12 21:30 | 46948.0182 | 1019.988
Devonshire Building | 2016-10-12 21:45 | 46948.2732 | 1019.988
Devonshire Building | 2016-10-12 22:00 | 46948.5282 | 1019.988
Devonshire Building | 2016-10-12 22:15 | 46948.7832 | 1019.988
Devonshire Building | 2016-10-12 22:30 | 46949.0382 | 1019.988
Devonshire Building | 2016-10-12 22:45 | 46949.2932 | 1019.988
Devonshire Building | 2016-10-12 23:00 | 46949.5532 | 1040.004
Devonshire Building | 2016-10-12 23:15 | 46949.8082 | 1019.988
Devonshire Building | 2016-10-12 23:30 | 46950.0632 | 1019.988
Devonshire Building | 2016-10-12 23:45 | 46950.3232 | 1040.004 | 979.992
Devonshire Building | 2016-10-13 | 46950.5781 | 1019.988
Devonshire Building | 2016-10-13 00:15 | 46950.8381 | 1040.004
Devonshire Building | 2016-10-13 00:30 | 46951.0981 | 1040.004
Devonshire Building | 2016-10-13 00:45 | 46951.3531 | 1019.988
Devonshire Building | 2016-10-13 01:00 | 46951.6131 | 1040.004
Devonshire Building | 2016-10-13 01:15 | 46951.8681 | 1019.988
Devonshire Building | 2016-10-13 01:30 | 46952.1281 | 1040.004
Devonshire Building | 2016-10-13 01:45 | 46952.3831 | 1019.988
Devonshire Building | 2016-10-13 02:00 | 46952.6431 | 1040.004
Devonshire Building | 2016-10-13 02:15 | 46952.9031 | 1040.004
Devonshire Building | 2016-10-13 02:30 | 46953.1581 | 1019.988
Devonshire Building | 2016-10-13 02:45 | 46953.4181 | 1040.004
Devonshire Building | 2016-10-13 03:00 | 46953.6781 | 1040.004
Devonshire Building | 2016-10-13 03:15 | 46953.9331 | 1019.988
Devonshire Building | 2016-10-13 03:30 | 46954.1931 | 1040.004
Devonshire Building | 2016-10-13 03:45 | 46954.4531 | 1040.004
Devonshire Building | 2016-10-13 04:00 | 46954.7081 | 1019.988
Devonshire Building | 2016-10-13 04:15 | 46954.9681 | 1040.004
Devonshire Building | 2016-10-13 04:30 | 46955.2281 | 1040.004
Devonshire Building | 2016-10-13 04:45 | 46955.4831 | 1019.988
Devonshire Building | 2016-10-13 05:00 | 46955.7431 | 1040.004
Devonshire Building | 2016-10-13 05:15 | 46956.0031 | 1040.004
Devonshire Building | 2016-10-13 05:30 | 46956.2581 | 1019.988
Devonshire Building | 2016-10-13 05:45 | 46956.5131 | 1019.988
Devonshire Building | 2016-10-13 06:00 | 46956.7681 | 1019.988
Devonshire Building | 2016-10-13 06:15 | 46957.0231 | 1019.988
Devonshire Building | 2016-10-13 06:30 | 46957.2731 | 1000.008
Devonshire Building | 2016-10-13 06:45 | 46957.5281 | 1019.988
Devonshire Building | 2016-10-13 07:00 | 46957.7831 | 1019.988
Devonshire Building | 2016-10-13 07:15 | 46958.0381 | 1019.988
Devonshire Building | 2016-10-13 07:30 | 46958.2931 | 1019.988
Devonshire Building | 2016-10-13 07:45 | 46958.5531 | 1040.004
Devonshire Building | 2016-10-13 08:00 | 46958.8281 | 1100.016
Devonshire Building | 2016-10-13 08:15 | 46959.1131 | 1140.012
Devonshire Building | 2016-10-13 08:30 | 46959.6781 | 2260.008
Devonshire Building | 2016-10-13 08:45 | 46959.9831 | 1220.004
Devonshire Building | 2016-10-13 09:00 | 46960.2981 | 1260
Devonshire Building | 2016-10-13 09:15 | 46960.6231 | 1299.996
Devonshire Building | 2016-10-13 09:30 | 46960.9381 | 1260
Devonshire Building | 2016-10-13 09:45 | 46961.2681 | 1320.012
Devonshire Building | 2016-10-13 10:00 | 46961.8731 | 2419.992
Devonshire Building | 2016-10-13 10:15 | 46962.1731 | 1199.988
Devonshire Building | 2016-10-13 10:30 | 46962.4781 | 1220.004
Devonshire Building | 2016-10-13 10:45 | 46962.7831 | 1220.004
Devonshire Building | 2016-10-13 11:00 | 46963.0881 | 1220.004
Devonshire Building | 2016-10-13 11:15 | 46963.3931 | 1220.004
Devonshire Building | 2016-10-13 11:30 | 46963.7031 | 1239.984
Devonshire Building | 2016-10-13 11:45 | 46964.2981 | 2379.996
Devonshire Building | 2016-10-13 12:00 | 46964.7931 | 1980
Devonshire Building | 2016-10-13 12:15 | 46965.1981 | 1620
Devonshire Building | 2016-10-13 12:30 | 46965.5731 | 1500.012
Devonshire Building | 2016-10-13 12:45 | 46965.9181 | 1379.988
Devonshire Building | 2016-10-13 13:00 | 46966.2431 | 1299.996
Devonshire Building | 2016-10-13 13:15 | 46966.5681 | 1299.996
Devonshire Building | 2016-10-13 13:30 | 46967.1481 | 2319.984
Devonshire Building | 2016-10-13 13:45 | 46967.4381 | 1159.992
Devonshire Building | 2016-10-13 14:00 | 46967.7281 | 1159.992
Devonshire Building | 2016-10-13 14:15 | 46968.0231 | 1180.008
Devonshire Building | 2016-10-13 14:30 | 46968.3181 | 1180.008
Devonshire Building | 2016-10-13 14:45 | 46968.6081 | 1159.992
Devonshire Building | 2016-10-13 15:00 | 46968.9181 | 1239.984
Devonshire Building | 2016-10-13 15:15 | 46969.2481 | 1320.012
Devonshire Building | 2016-10-13 15:30 | 46969.8431 | 2379.996
Devonshire Building | 2016-10-13 15:45 | 46970.1731 | 1320.012
Devonshire Building | 2016-10-13 16:00 | 46970.4881 | 1260
Devonshire Building | 2016-10-13 16:15 | 46970.8081 | 1280.016
Devonshire Building | 2016-10-13 16:30 | 46971.1231 | 1260
Devonshire Building | 2016-10-13 16:45 | 46971.4281 | 1220.004
Devonshire Building | 2016-10-13 17:00 | 46971.7231 | 1180.008
Devonshire Building | 2016-10-13 17:15 | 46972.0131 | 1159.992
Devonshire Building | 2016-10-13 17:30 | 46972.2931 | 1119.996
Devonshire Building | 2016-10-13 17:45 | 46972.5731 | 1119.996
Devonshire Building | 2016-10-13 18:00 | 46972.8431 | 1080
Devonshire Building | 2016-10-13 18:15 | 46973.1131 | 1080
Devonshire Building | 2016-10-13 18:30 | 46973.3781 | 1059.984
Devonshire Building | 2016-10-13 18:45 | 46973.6481 | 1080
Devonshire Building | 2016-10-13 19:00 | 46973.9131 | 1059.984
Devonshire Building | 2016-10-13 19:15 | 46974.1731 | 1040.004
Devonshire Building | 2016-10-13 19:30 | 46974.4381 | 1059.984
Devonshire Building | 2016-10-13 19:45 | 46974.7181 | 1119.996
Devonshire Building | 2016-10-13 20:00 | 46974.9981 | 1119.996
Devonshire Building | 2016-10-13 20:15 | 46975.2731 | 1100.016
Devonshire Building | 2016-10-13 20:30 | 46975.5531 | 1119.996
Devonshire Building | 2016-10-13 20:45 | 46975.8331 | 1119.996
Devonshire Building | 2016-10-13 21:00 | 46976.1331 | 1199.988
Devonshire Building | 2016-10-13 21:15 | 46976.4081 | 1100.016
Devonshire Building | 2016-10-13 21:30 | 46976.6881 | 1119.996
Devonshire Building | 2016-10-13 21:45 | 46976.9531 | 1059.984
Devonshire Building | 2016-10-13 22:00 | 46977.2131 | 1040.004
Devonshire Building | 2016-10-13 22:15 | 46977.4781 | 1059.984
Devonshire Building | 2016-10-13 22:30 | 46977.7381 | 1040.004
Devonshire Building | 2016-10-13 22:45 | 46977.9981 | 1040.004
Devonshire Building | 2016-10-13 23:00 | 46978.2581 | 1040.004
Devonshire Building | 2016-10-13 23:15 | 46978.5231 | 1059.984
Devonshire Building | 2016-10-13 23:30 | 46978.7831 | 1040.004
Devonshire Building | 2016-10-13 23:45 | 46979.0481 | 1059.984 | 1000.008
Devonshire Building | 2016-10-14 | 46979.3164 | 1059.984
Devonshire Building | 2016-10-14 00:15 | 46979.5764 | 1040.004
Devonshire Building | 2016-10-14 00:30 | 46979.8414 | 1059.984
Devonshire Building | 2016-10-14 00:45 | 46980.1064 | 1059.984
Devonshire Building | 2016-10-14 01:00 | 46980.3714 | 1059.984
Devonshire Building | 2016-10-14 01:15 | 46980.6364 | 1059.984
Devonshire Building | 2016-10-14 01:30 | 46980.9014 | 1059.984
Devonshire Building | 2016-10-14 01:45 | 46981.1664 | 1059.984
Devonshire Building | 2016-10-14 02:00 | 46981.4314 | 1059.984
Devonshire Building | 2016-10-14 02:15 | 46981.6964 | 1059.984
Devonshire Building | 2016-10-14 02:30 | 46981.9664 | 1080
Devonshire Building | 2016-10-14 02:45 | 46982.2314 | 1059.984
Devonshire Building | 2016-10-14 03:00 | 46982.4964 | 1059.984
Devonshire Building | 2016-10-14 03:15 | 46982.7614 | 1059.984
Devonshire Building | 2016-10-14 03:30 | 46983.0314 | 1080
Devonshire Building | 2016-10-14 03:45 | 46983.2964 | 1059.984
Devonshire Building | 2016-10-14 04:00 | 46983.5664 | 1080
Devonshire Building | 2016-10-14 04:15 | 46983.8314 | 1059.984
Devonshire Building | 2016-10-14 04:30 | 46984.0964 | 1059.984
Devonshire Building | 2016-10-14 04:45 | 46984.3664 | 1080
Devonshire Building | 2016-10-14 05:00 | 46984.6314 | 1059.984
Devonshire Building | 2016-10-14 05:15 | 46985.1463 | 2059.992
Devonshire Building | 2016-10-14 05:30 | 46985.4113 | 1059.984
Devonshire Building | 2016-10-14 05:45 | 46985.6763 | 1059.984
Devonshire Building | 2016-10-14 06:00 | 46985.9413 | 1059.984
Devonshire Building | 2016-10-14 06:15 | 46986.2013 | 1040.004
Devonshire Building | 2016-10-14 06:30 | 46986.4663 | 1059.984
Devonshire Building | 2016-10-14 06:45 | 46986.7313 | 1059.984
Devonshire Building | 2016-10-14 07:00 | 46986.9913 | 1040.004
Devonshire Building | 2016-10-14 07:15 | 46987.2563 | 1059.984
Devonshire Building | 2016-10-14 07:30 | 46987.5263 | 1080
Devonshire Building | 2016-10-14 07:45 | 46987.7913 | 1059.984
Devonshire Building | 2016-10-14 08:00 | 46988.0663 | 1100.016
Devonshire Building | 2016-10-14 08:15 | 46988.3263 | 1040.004
Devonshire Building | 2016-10-14 08:30 | 46988.5963 | 1080
Devonshire Building | 2016-10-14 08:45 | 46988.8863 | 1159.992
Devonshire Building | 2016-10-14 09:00 | 46989.4413 | 2220.012
Devonshire Building | 2016-10-14 09:15 | 46989.7163 | 1100.016
Devonshire Building | 2016-10-14 09:30 | 46990.0013 | 1140.012
Devonshire Building | 2016-10-14 09:45 | 46990.3063 | 1220.004
Devonshire Building | 2016-10-14 10:00 | 46990.5963 | 1159.992
Devonshire Building | 2016-10-14 10:15 | 46990.8963 | 1199.988
Devonshire Building | 2016-10-14 10:30 | 46991.2463 | 1400.004
Devonshire Building | 2016-10-14 10:45 | 46991.5463 | 1199.988
Devonshire Building | 2016-10-14 11:00 | 46992.1313 | 2340
Devonshire Building | 2016-10-14 11:15 | 46992.4613 | 1320.012
Devonshire Building | 2016-10-14 11:30 | 46992.8063 | 1379.988
Devonshire Building | 2016-10-14 11:45 | 46993.1463 | 1360.008
Devonshire Building | 2016-10-14 12:00 | 46993.4813 | 1339.992
Devonshire Building | 2016-10-14 12:15 | 46993.8163 | 1339.992
Devonshire Building | 2016-10-14 12:30 | 46994.1613 | 1379.988
Devonshire Building | 2016-10-14 12:45 | 46994.7513 | 2360.016
Devonshire Building | 2016-10-14 13:00 | 46995.0813 | 1320.012
Devonshire Building | 2016-10-14 13:15 | 46995.4113 | 1320.012
Devonshire Building | 2016-10-14 13:30 | 46995.7363 | 1299.996
Devonshire Building | 2016-10-14 13:45 | 46996.0613 | 1299.996
Devonshire Building | 2016-10-14 14:00 | 46996.3813 | 1280.016
Devonshire Building | 2016-10-14 14:15 | 46996.6963 | 1260
Devonshire Building | 2016-10-14 14:30 | 46997.0113 | 1260
Devonshire Building | 2016-10-14 14:45 | 46997.5963 | 2340
Devonshire Building | 2016-10-14 15:00 | 46997.9213 | 1299.996
Devonshire Building | 2016-10-14 15:15 | 46998.2713 | 1400.004
Devonshire Building | 2016-10-14 15:30 | 46998.6113 | 1360.008
Devonshire Building | 2016-10-14 15:45 | 46998.9713 | 1440
Devonshire Building | 2016-10-14 16:00 | 46999.3313 | 1440
Devonshire Building | 2016-10-14 16:15 | 46999.6863 | 1419.984
Devonshire Building | 2016-10-14 16:30 | 47000.0213 | 1339.992
Devonshire Building | 2016-10-14 16:45 | 47000.3613 | 1360.008
Devonshire Building | 2016-10-14 17:00 | 47000.6963 | 1339.992
Devonshire Building | 2016-10-14 17:15 | 47001.2713 | 2300.004
Devonshire Building | 2016-10-14 17:30 | 47001.5763 | 1220.004
Devonshire Building | 2016-10-14 17:45 | 47001.8813 | 1220.004
Devonshire Building | 2016-10-14 18:00 | 47002.1813 | 1199.988
Devonshire Building | 2016-10-14 18:15 | 47002.4713 | 1159.992
Devonshire Building | 2016-10-14 18:30 | 47002.7563 | 1140.012
Devonshire Building | 2016-10-14 18:45 | 47003.0363 | 1119.996
Devonshire Building | 2016-10-14 19:00 | 47003.3213 | 1140.012
Devonshire Building | 2016-10-14 19:15 | 47003.5963 | 1100.016
Devonshire Building | 2016-10-14 19:30 | 47003.8713 | 1100.016
Devonshire Building | 2016-10-14 19:45 | 47004.1463 | 1100.016
Devonshire Building | 2016-10-14 20:00 | 47004.4214 | 1100.016
Devonshire Building | 2016-10-14 20:15 | 47004.6964 | 1100.016
Devonshire Building | 2016-10-14 20:30 | 47004.9664 | 1080
Devonshire Building | 2016-10-14 20:45 | 47005.2414 | 1100.016
Devonshire Building | 2016-10-14 21:00 | 47005.5214 | 1119.996
Devonshire Building | 2016-10-14 21:15 | 47005.7914 | 1080
Devonshire Building | 2016-10-14 21:30 | 47006.0614 | 1080
Devonshire Building | 2016-10-14 21:45 | 47006.3314 | 1080
Devonshire Building | 2016-10-14 22:00 | 47006.6064 | 1100.016
Devonshire Building | 2016-10-14 22:15 | 47006.8764 | 1080
Devonshire Building | 2016-10-14 22:30 | 47007.1464 | 1080
Devonshire Building | 2016-10-14 22:45 | 47007.4214 | 1100.016
Devonshire Building | 2016-10-14 23:00 | 47007.6914 | 1080
Devonshire Building | 2016-10-14 23:15 | 47007.9664 | 1100.016
Devonshire Building | 2016-10-14 23:30 | 47008.2364 | 1080
Devonshire Building | 2016-10-14 23:45 | 47008.5114 | 1100.016 | 1040.004
Devonshire Building | 2016-10-15 | 47008.7852 | 1100.016
Devonshire Building | 2016-10-15 00:15 | 47009.0552 | 1080
Devonshire Building | 2016-10-15 00:30 | 47009.3302 | 1100.016
Devonshire Building | 2016-10-15 00:45 | 47009.6002 | 1080
Devonshire Building | 2016-10-15 01:00 | 47009.8752 | 1100.016
Devonshire Building | 2016-10-15 01:15 | 47010.1452 | 1080
Devonshire Building | 2016-10-15 01:30 | 47010.4202 | 1100.016
Devonshire Building | 2016-10-15 01:45 | 47010.6902 | 1080
Devonshire Building | 2016-10-15 02:00 | 47010.9652 | 1100.016
Devonshire Building | 2016-10-15 02:15 | 47011.2352 | 1080
Devonshire Building | 2016-10-15 02:30 | 47011.5102 | 1100.016
Devonshire Building | 2016-10-15 02:45 | 47011.7802 | 1080
Devonshire Building | 2016-10-15 03:00 | 47012.0552 | 1100.016
Devonshire Building | 2016-10-15 03:15 | 47012.3252 | 1080
Devonshire Building | 2016-10-15 03:30 | 47012.6002 | 1100.016
Devonshire Building | 2016-10-15 03:45 | 47012.8752 | 1100.016
Devonshire Building | 2016-10-15 04:00 | 47013.1452 | 1080
Devonshire Building | 2016-10-15 04:15 | 47013.4202 | 1100.016
Devonshire Building | 2016-10-15 04:30 | 47013.6902 | 1080
Devonshire Building | 2016-10-15 04:45 | 47013.9652 | 1100.016
Devonshire Building | 2016-10-15 05:00 | 47014.2352 | 1080
Devonshire Building | 2016-10-15 05:15 | 47014.5102 | 1100.016
Devonshire Building | 2016-10-15 05:30 | 47014.7802 | 1080
Devonshire Building | 2016-10-15 05:45 | 47015.0502 | 1080
Devonshire Building | 2016-10-15 06:00 | 47015.3252 | 1100.016
Devonshire Building | 2016-10-15 06:15 | 47015.5952 | 1080
Devonshire Building | 2016-10-15 06:30 | 47015.8652 | 1080
Devonshire Building | 2016-10-15 06:45 | 47016.1352 | 1080
Devonshire Building | 2016-10-15 07:00 | 47016.4102 | 1100.016
Devonshire Building | 2016-10-15 07:15 | 47016.6752 | 1059.984
Devonshire Building | 2016-10-15 07:30 | 47016.9452 | 1080
Devonshire Building | 2016-10-15 07:45 | 47017.2152 | 1080
Devonshire Building | 2016-10-15 08:00 | 47017.4952 | 1119.996
Devonshire Building | 2016-10-15 08:15 | 47017.7802 | 1140.012
Devonshire Building | 2016-10-15 08:30 | 47018.0602 | 1119.996
Devonshire Building | 2016-10-15 08:45 | 47018.3452 | 1140.012
Devonshire Building | 2016-10-15 09:00 | 47018.6302 | 1140.012
Devonshire Building | 2016-10-15 09:15 | 47018.9102 | 1119.996
Devonshire Building | 2016-10-15 09:30 | 47019.1902 | 1119.996
Devonshire Building | 2016-10-15 09:45 | 47019.4652 | 1100.016
Devonshire Building | 2016-10-15 10:00 | 47019.7302 | 1059.984
Devonshire Building | 2016-10-15 10:15 | 47019.9952 | 1059.984
Devonshire Building | 2016-10-15 10:30 | 47020.2602 | 1059.984
Devonshire Building | 2016-10-15 10:45 | 47020.5252 | 1059.984
Devonshire Building | 2016-10-15 11:00 | 47020.7952 | 1080
Devonshire Building | 2016-10-15 11:15 | 47021.0602 | 1059.984
Devonshire Building | 2016-10-15 11:30 | 47021.3302 | 1080
Devonshire Building | 2016-10-15 11:45 | 47021.5952 | 1059.984
Devonshire Building | 2016-10-15 12:00 | 47021.8652 | 1080
Devonshire Building | 2016-10-15 12:15 | 47022.1302 | 1059.984
Devonshire Building | 2016-10-15 12:30 | 47022.4002 | 1080
Devonshire Building | 2016-10-15 12:45 | 47022.6702 | 1080
Devonshire Building | 2016-10-15 13:00 | 47022.9402 | 1080
Devonshire Building | 2016-10-15 13:15 | 47023.2052 | 1059.984
Devonshire Building | 2016-10-15 13:30 | 47023.4752 | 1080
Devonshire Building | 2016-10-15 13:45 | 47023.7452 | 1080
Devonshire Building | 2016-10-15 14:00 | 47024.0102 | 1059.984
Devonshire Building | 2016-10-15 14:15 | 47024.2802 | 1080
Devonshire Building | 2016-10-15 14:30 | 47024.5552 | 1100.016
Devonshire Building | 2016-10-15 14:45 | 47024.8302 | 1100.016
Devonshire Building | 2016-10-15 15:00 | 47025.0952 | 1059.984
Devonshire Building | 2016-10-15 15:15 | 47025.3652 | 1080
Devonshire Building | 2016-10-15 15:30 | 47025.6352 | 1080
Devonshire Building | 2016-10-15 15:45 | 47025.9052 | 1080
Devonshire Building | 2016-10-15 16:00 | 47026.1702 | 1059.984
Devonshire Building | 2016-10-15 16:15 | 47026.4352 | 1059.984
Devonshire Building | 2016-10-15 16:30 | 47026.7052 | 1080
Devonshire Building | 2016-10-15 16:45 | 47026.9702 | 1059.984
Devonshire Building | 2016-10-15 17:00 | 47027.2352 | 1059.984
Devonshire Building | 2016-10-15 17:15 | 47027.5002 | 1059.984
Devonshire Building | 2016-10-15 17:30 | 47028.0102 | 2040.012
Devonshire Building | 2016-10-15 17:45 | 47028.2752 | 1059.984
Devonshire Building | 2016-10-15 18:00 | 47028.5452 | 1080
Devonshire Building | 2016-10-15 18:15 | 47028.8102 | 1059.984
Devonshire Building | 2016-10-15 18:30 | 47029.0802 | 1080
Devonshire Building | 2016-10-15 18:45 | 47029.3452 | 1059.984
Devonshire Building | 2016-10-15 19:00 | 47029.6152 | 1080
Devonshire Building | 2016-10-15 19:15 | 47029.8852 | 1080
Devonshire Building | 2016-10-15 19:30 | 47030.1552 | 1080
Devonshire Building | 2016-10-15 19:45 | 47030.4252 | 1080
Devonshire Building | 2016-10-15 20:00 | 47030.6952 | 1080
Devonshire Building | 2016-10-15 20:15 | 47030.9702 | 1100.016
Devonshire Building | 2016-10-15 20:30 | 47031.2402 | 1080
Devonshire Building | 2016-10-15 20:45 | 47031.5102 | 1080
Devonshire Building | 2016-10-15 21:00 | 47031.7952 | 1140.012
Devonshire Building | 2016-10-15 21:15 | 47032.0652 | 1080
Devonshire Building | 2016-10-15 21:30 | 47032.3302 | 1059.984
Devonshire Building | 2016-10-15 21:45 | 47032.6002 | 1080
Devonshire Building | 2016-10-15 22:00 | 47032.8652 | 1059.984
Devonshire Building | 2016-10-15 22:15 | 47033.1352 | 1080
Devonshire Building | 2016-10-15 22:30 | 47033.4002 | 1059.984
Devonshire Building | 2016-10-15 22:45 | 47033.6702 | 1080
Devonshire Building | 2016-10-15 23:00 | 47033.9402 | 1080
Devonshire Building | 2016-10-15 23:15 | 47034.2051 | 1059.984
Devonshire Building | 2016-10-15 23:30 | 47034.4751 | 1080
Devonshire Building | 2016-10-15 23:45 | 47034.7451 | 1080 | 1059.984
Devonshire Building | 2016-10-16 | 47035.0156 | 1080
Devonshire Building | 2016-10-16 00:15 | 47035.2856 | 1080
Devonshire Building | 2016-10-16 00:30 | 47035.5556 | 1080
Devonshire Building | 2016-10-16 00:45 | 47035.8256 | 1080
Devonshire Building | 2016-10-16 01:00 | 47036.0956 | 1080
Devonshire Building | 2016-10-16 01:15 | 47036.3706 | 1100.016
Devonshire Building | 2016-10-16 01:30 | 47036.6406 | 1080
Devonshire Building | 2016-10-16 01:45 | 47036.9156 | 1100.016
Devonshire Building | 2016-10-16 02:00 | 47037.1906 | 1100.016
Devonshire Building | 2016-10-16 02:15 | 47037.4606 | 1080
Devonshire Building | 2016-10-16 02:30 | 47037.7306 | 1080
Devonshire Building | 2016-10-16 02:45 | 47038.0006 | 1080
Devonshire Building | 2016-10-16 03:00 | 47038.2706 | 1080
Devonshire Building | 2016-10-16 03:15 | 47038.5456 | 1100.016
Devonshire Building | 2016-10-16 03:30 | 47038.8207 | 1100.016
Devonshire Building | 2016-10-16 03:45 | 47039.0906 | 1080
Devonshire Building | 2016-10-16 04:00 | 47039.3657 | 1100.016
Devonshire Building | 2016-10-16 04:15 | 47039.6407 | 1100.016
Devonshire Building | 2016-10-16 04:30 | 47039.9157 | 1100.016
Devonshire Building | 2016-10-16 04:45 | 47040.1957 | 1119.996
Devonshire Building | 2016-10-16 05:00 | 47040.4707 | 1100.016
Devonshire Building | 2016-10-16 05:15 | 47040.7407 | 1080
Devonshire Building | 2016-10-16 05:30 | 47041.0157 | 1100.016
Devonshire Building | 2016-10-16 05:45 | 47041.2857 | 1080
Devonshire Building | 2016-10-16 06:00 | 47041.5607 | 1100.016
Devonshire Building | 2016-10-16 06:15 | 47041.8307 | 1080
Devonshire Building | 2016-10-16 06:30 | 47042.1007 | 1080
Devonshire Building | 2016-10-16 06:45 | 47042.3707 | 1080
Devonshire Building | 2016-10-16 07:00 | 47042.6407 | 1080
Devonshire Building | 2016-10-16 07:15 | 47042.9057 | 1059.984
Devonshire Building | 2016-10-16 07:30 | 47043.1757 | 1080
Devonshire Building | 2016-10-16 07:45 | 47043.4557 | 1119.996
Devonshire Building | 2016-10-16 08:00 | 47043.7407 | 1140.012
Devonshire Building | 2016-10-16 08:15 | 47044.0207 | 1119.996
Devonshire Building | 2016-10-16 08:30 | 47044.3057 | 1140.012
Devonshire Building | 2016-10-16 08:45 | 47044.5857 | 1119.996
Devonshire Building | 2016-10-16 09:00 | 47044.8657 | 1119.996
Devonshire Building | 2016-10-16 09:15 | 47045.1457 | 1119.996
Devonshire Building | 2016-10-16 09:30 | 47045.4307 | 1140.012
Devonshire Building | 2016-10-16 09:45 | 47045.7107 | 1119.996
Devonshire Building | 2016-10-16 10:00 | 47045.9707 | 1040.004
Devonshire Building | 2016-10-16 10:15 | 47046.2357 | 1059.984
Devonshire Building | 2016-10-16 10:30 | 47046.5007 | 1059.984
Devonshire Building | 2016-10-16 10:45 | 47046.7607 | 1040.004
Devonshire Building | 2016-10-16 11:00 | 47047.0257 | 1059.984
Devonshire Building | 2016-10-16 11:15 | 47047.2907 | 1059.984
Devonshire Building | 2016-10-16 11:30 | 47047.5557 | 1059.984
Devonshire Building | 2016-10-16 11:45 | 47047.8157 | 1040.004
Devonshire Building | 2016-10-16 12:00 | 47048.0807 | 1059.984
Devonshire Building | 2016-10-16 12:15 | 47048.3456 | 1059.984
Devonshire Building | 2016-10-16 12:30 | 47048.6106 | 1059.984
Devonshire Building | 2016-10-16 12:45 | 47048.8756 | 1059.984
Devonshire Building | 2016-10-16 13:00 | 47049.1406 | 1059.984
Devonshire Building | 2016-10-16 13:15 | 47049.4106 | 1080
Devonshire Building | 2016-10-16 13:30 | 47049.6756 | 1059.984
Devonshire Building | 2016-10-16 13:45 | 47049.9406 | 1059.984
Devonshire Building | 2016-10-16 14:00 | 47050.2106 | 1080
Devonshire Building | 2016-10-16 14:15 | 47050.4756 | 1059.984
Devonshire Building | 2016-10-16 14:30 | 47050.7406 | 1059.984
Devonshire Building | 2016-10-16 14:45 | 47051.0106 | 1080
Devonshire Building | 2016-10-16 15:00 | 47051.2756 | 1059.984
Devonshire Building | 2016-10-16 15:15 | 47051.5456 | 1080
Devonshire Building | 2016-10-16 15:30 | 47051.8106 | 1059.984
Devonshire Building | 2016-10-16 15:45 | 47052.0806 | 1080
Devonshire Building | 2016-10-16 16:00 | 47052.3456 | 1059.984
Devonshire Building | 2016-10-16 16:15 | 47052.6106 | 1059.984
Devonshire Building | 2016-10-16 16:30 | 47052.8806 | 1080
Devonshire Building | 2016-10-16 16:45 | 47053.1456 | 1059.984
Devonshire Building | 2016-10-16 17:00 | 47053.4106 | 1059.984
Devonshire Building | 2016-10-16 17:15 | 47053.6806 | 1080
Devonshire Building | 2016-10-16 17:30 | 47053.9456 | 1059.984
Devonshire Building | 2016-10-16 17:45 | 47054.2106 | 1059.984
Devonshire Building | 2016-10-16 18:00 | 47054.4756 | 1059.984
Devonshire Building | 2016-10-16 18:15 | 47054.7406 | 1059.984
Devonshire Building | 2016-10-16 18:30 | 47055.0056 | 1059.984
Devonshire Building | 2016-10-16 18:45 | 47055.2706 | 1059.984
Devonshire Building | 2016-10-16 19:00 | 47055.5356 | 1059.984
Devonshire Building | 2016-10-16 19:15 | 47055.8006 | 1059.984
Devonshire Building | 2016-10-16 19:30 | 47056.0656 | 1059.984
Devonshire Building | 2016-10-16 19:45 | 47056.3356 | 1080
Devonshire Building | 2016-10-16 20:00 | 47056.6006 | 1059.984
Devonshire Building | 2016-10-16 20:15 | 47056.8656 | 1059.984
Devonshire Building | 2016-10-16 20:30 | 47057.1305 | 1059.984
Devonshire Building | 2016-10-16 20:45 | 47057.3955 | 1059.984
Devonshire Building | 2016-10-16 21:00 | 47057.6855 | 1159.992
Devonshire Building | 2016-10-16 21:15 | 47057.9555 | 1080
Devonshire Building | 2016-10-16 21:30 | 47058.2205 | 1059.984
Devonshire Building | 2016-10-16 21:45 | 47058.4905 | 1080
Devonshire Building | 2016-10-16 22:00 | 47058.7605 | 1080
Devonshire Building | 2016-10-16 22:15 | 47059.0305 | 1080
Devonshire Building | 2016-10-16 22:30 | 47059.3005 | 1080
Devonshire Building | 2016-10-16 22:45 | 47059.5705 | 1080
Devonshire Building | 2016-10-16 23:00 | 47059.8405 | 1080
Devonshire Building | 2016-10-16 23:15 | 47060.1105 | 1080
Devonshire Building | 2016-10-16 23:30 | 47060.3855 | 1100.016
Devonshire Building | 2016-10-16 23:45 | 47060.6555 | 1080 | 1040.004
Devonshire Building | 2016-10-17 | 47060.9297 | 1100.016
Devonshire Building | 2016-10-17 00:15 | 47061.1997 | 1080
Devonshire Building | 2016-10-17 00:30 | 47061.4747 | 1100.016
Devonshire Building | 2016-10-17 00:45 | 47061.7497 | 1100.016
Devonshire Building | 2016-10-17 01:00 | 47062.0247 | 1100.016
Devonshire Building | 2016-10-17 01:15 | 47062.2997 | 1100.016
Devonshire Building | 2016-10-17 01:30 | 47062.5747 | 1100.016
Devonshire Building | 2016-10-17 01:45 | 47062.8447 | 1080
Devonshire Building | 2016-10-17 02:00 | 47063.3547 | 2040.012
Devonshire Building | 2016-10-17 02:15 | 47063.6297 | 1100.016
Devonshire Building | 2016-10-17 02:30 | 47063.9047 | 1100.016
Devonshire Building | 2016-10-17 02:45 | 47064.1797 | 1100.016
Devonshire Building | 2016-10-17 03:00 | 47064.4597 | 1119.996
Devonshire Building | 2016-10-17 03:15 | 47064.7347 | 1100.016
Devonshire Building | 2016-10-17 03:30 | 47065.0147 | 1119.996
Devonshire Building | 2016-10-17 03:45 | 47065.2897 | 1100.016
Devonshire Building | 2016-10-17 04:00 | 47065.5697 | 1119.996
Devonshire Building | 2016-10-17 04:15 | 47065.8447 | 1100.016
Devonshire Building | 2016-10-17 04:30 | 47066.1247 | 1119.996
Devonshire Building | 2016-10-17 04:45 | 47066.3997 | 1100.016
Devonshire Building | 2016-10-17 05:00 | 47066.6747 | 1100.016
Devonshire Building | 2016-10-17 05:15 | 47066.9547 | 1119.996
Devonshire Building | 2016-10-17 05:30 | 47067.2297 | 1100.016
Devonshire Building | 2016-10-17 05:45 | 47067.5047 | 1100.016
Devonshire Building | 2016-10-17 06:00 | 47067.7798 | 1100.016
Devonshire Building | 2016-10-17 06:15 | 47068.0498 | 1080
Devonshire Building | 2016-10-17 06:30 | 47068.3248 | 1100.016
Devonshire Building | 2016-10-17 06:45 | 47068.6048 | 1119.996
Devonshire Building | 2016-10-17 07:00 | 47068.8798 | 1100.016
Devonshire Building | 2016-10-17 07:15 | 47069.1548 | 1100.016
Devonshire Building | 2016-10-17 07:30 | 47069.4298 | 1100.016
Devonshire Building | 2016-10-17 07:45 | 47069.7298 | 1199.988
Devonshire Building | 2016-10-17 08:00 | 47070.0198 | 1159.992
Devonshire Building | 2016-10-17 08:15 | 47070.3098 | 1159.992
Devonshire Building | 2016-10-17 08:30 | 47070.8448 | 2139.984
Devonshire Building | 2016-10-17 08:45 | 47071.1398 | 1180.008
Devonshire Building | 2016-10-17 09:00 | 47071.4398 | 1199.988
Devonshire Building | 2016-10-17 09:15 | 47071.7698 | 1320.012
Devonshire Building | 2016-10-17 09:30 | 47072.3948 | 2499.984
Devonshire Building | 2016-10-17 09:45 | 47072.7898 | 1580.004
Devonshire Building | 2016-10-17 10:00 | 47073.1748 | 1540.008
Devonshire Building | 2016-10-17 10:15 | 47073.5848 | 1640.016
Devonshire Building | 2016-10-17 10:30 | 47074.0048 | 1680.012
Devonshire Building | 2016-10-17 10:45 | 47074.4048 | 1599.984
Devonshire Building | 2016-10-17 11:00 | 47075.0148 | 2440.008
Devonshire Building | 2016-10-17 11:15 | 47075.3548 | 1360.008
Devonshire Building | 2016-10-17 11:30 | 47075.6898 | 1339.992
Devonshire Building | 2016-10-17 11:45 | 47076.0148 | 1299.996
Devonshire Building | 2016-10-17 12:00 | 47076.3348 | 1280.016
Devonshire Building | 2016-10-17 12:15 | 47076.6598 | 1299.996
Devonshire Building | 2016-10-17 12:30 | 47077.2448 | 2340
Devonshire Building | 2016-10-17 12:45 | 47077.5548 | 1239.984
Devonshire Building | 2016-10-17 13:00 | 47077.8648 | 1239.984
Devonshire Building | 2016-10-17 13:15 | 47078.1748 | 1239.984
Devonshire Building | 2016-10-17 13:30 | 47078.4798 | 1220.004
Devonshire Building | 2016-10-17 13:45 | 47078.8048 | 1299.996
Devonshire Building | 2016-10-17 14:00 | 47079.1198 | 1260
Devonshire Building | 2016-10-17 14:15 | 47079.4398 | 1280.016
Devonshire Building | 2016-10-17 14:30 | 47079.7448 | 1220.004
Devonshire Building | 2016-10-17 14:45 | 47080.3048 | 2239.992
Devonshire Building | 2016-10-17 15:00 | 47080.6048 | 1199.988
Devonshire Building | 2016-10-17 15:15 | 47080.9047 | 1199.988
Devonshire Building | 2016-10-17 15:30 | 47081.2047 | 1199.988
Devonshire Building | 2016-10-17 15:45 | 47081.5047 | 1199.988
Devonshire Building | 2016-10-17 16:00 | 47081.7997 | 1180.008
Devonshire Building | 2016-10-17 16:15 | 47082.0997 | 1199.988
Devonshire Building | 2016-10-17 16:30 | 47082.3997 | 1199.988
Devonshire Building | 2016-10-17 16:45 | 47082.6947 | 1180.008
Devonshire Building | 2016-10-17 17:00 | 47083.2397 | 2180.016
Devonshire Building | 2016-10-17 17:15 | 47083.5247 | 1140.012
Devonshire Building | 2016-10-17 17:30 | 47083.8147 | 1159.992
Devonshire Building | 2016-10-17 17:45 | 47084.1047 | 1159.992
Devonshire Building | 2016-10-17 18:00 | 47084.3897 | 1140.012
Devonshire Building | 2016-10-17 18:15 | 47084.6697 | 1119.996
Devonshire Building | 2016-10-17 18:30 | 47084.9547 | 1140.012
Devonshire Building | 2016-10-17 18:45 | 47085.2398 | 1140.012
Devonshire Building | 2016-10-17 19:00 | 47085.5248 | 1140.012
Devonshire Building | 2016-10-17 19:15 | 47085.8048 | 1119.996
Devonshire Building | 2016-10-17 19:30 | 47086.0898 | 1140.012
Devonshire Building | 2016-10-17 19:45 | 47086.3748 | 1140.012
Devonshire Building | 2016-10-17 20:00 | 47086.6548 | 1119.996
Devonshire Building | 2016-10-17 20:15 | 47086.9398 | 1140.012
Devonshire Building | 2016-10-17 20:30 | 47087.2248 | 1140.012
Devonshire Building | 2016-10-17 20:45 | 47087.5098 | 1140.012
Devonshire Building | 2016-10-17 21:00 | 47087.8048 | 1180.008
Devonshire Building | 2016-10-17 21:15 | 47088.0798 | 1100.016
Devonshire Building | 2016-10-17 21:30 | 47088.3548 | 1100.016
Devonshire Building | 2016-10-17 21:45 | 47088.6348 | 1119.996
Devonshire Building | 2016-10-17 22:00 | 47088.9148 | 1119.996
Devonshire Building | 2016-10-17 22:15 | 47089.1898 | 1100.016
Devonshire Building | 2016-10-17 22:30 | 47089.4698 | 1119.996
Devonshire Building | 2016-10-17 22:45 | 47089.7498 | 1119.996
Devonshire Building | 2016-10-17 23:00 | 47090.0298 | 1119.996
Devonshire Building | 2016-10-17 23:15 | 47090.3098 | 1119.996
Devonshire Building | 2016-10-17 23:30 | 47090.5898 | 1119.996
Devonshire Building | 2016-10-17 23:45 | 47090.8698 | 1119.996 | 1080
Devonshire Building | 2016-10-18 | 47091.1484 | 1119.996
Devonshire Building | 2016-10-18 00:15 | 47091.4334 | 1140.012
Devonshire Building | 2016-10-18 00:30 | 47091.7134 | 1119.996
Devonshire Building | 2016-10-18 00:45 | 47091.9984 | 1140.012
Devonshire Building | 2016-10-18 01:00 | 47092.2784 | 1119.996
Devonshire Building | 2016-10-18 01:15 | 47092.5584 | 1119.996
Devonshire Building | 2016-10-18 01:30 | 47092.8434 | 1140.012
Devonshire Building | 2016-10-18 01:45 | 47093.1234 | 1119.996
Devonshire Building | 2016-10-18 02:00 | 47093.4034 | 1119.996
Devonshire Building | 2016-10-18 02:15 | 47093.6884 | 1140.012
Devonshire Building | 2016-10-18 02:30 | 47093.9684 | 1119.996
Devonshire Building | 2016-10-18 02:45 | 47094.2484 | 1119.996
Devonshire Building | 2016-10-18 03:00 | 47094.5284 | 1119.996
Devonshire Building | 2016-10-18 03:15 | 47094.8134 | 1140.012
Devonshire Building | 2016-10-18 03:30 | 47095.0934 | 1119.996
Devonshire Building | 2016-10-18 03:45 | 47095.3734 | 1119.996
Devonshire Building | 2016-10-18 04:00 | 47095.6534 | 1119.996
Devonshire Building | 2016-10-18 04:15 | 47095.9384 | 1140.012
Devonshire Building | 2016-10-18 04:30 | 47096.2184 | 1119.996
Devonshire Building | 2016-10-18 04:45 | 47096.4984 | 1119.996
Devonshire Building | 2016-10-18 05:00 | 47096.7784 | 1119.996
Devonshire Building | 2016-10-18 05:15 | 47097.0634 | 1140.012
Devonshire Building | 2016-10-18 05:30 | 47097.3434 | 1119.996
Devonshire Building | 2016-10-18 05:45 | 47097.6234 | 1119.996
Devonshire Building | 2016-10-18 06:00 | 47097.9034 | 1119.996
Devonshire Building | 2016-10-18 06:15 | 47098.1834 | 1119.996
Devonshire Building | 2016-10-18 06:30 | 47098.4584 | 1100.016
Devonshire Building | 2016-10-18 06:45 | 47098.7384 | 1119.996
Devonshire Building | 2016-10-18 07:00 | 47099.0184 | 1119.996
Devonshire Building | 2016-10-18 07:15 | 47099.2934 | 1100.016
Devonshire Building | 2016-10-18 07:30 | 47099.5785 | 1140.012
Devonshire Building | 2016-10-18 07:45 | 47099.8884 | 1239.984
Devonshire Building | 2016-10-18 08:00 | 47100.1934 | 1220.004
Devonshire Building | 2016-10-18 08:15 | 47100.7434 | 2199.996
Devonshire Building | 2016-10-18 08:30 | 47101.0484 | 1220.004
Devonshire Building | 2016-10-18 08:45 | 47101.3734 | 1299.996
Devonshire Building | 2016-10-18 09:00 | 47101.7385 | 1460.016
Devonshire Building | 2016-10-18 09:15 | 47102.1384 | 1599.984
Devonshire Building | 2016-10-18 09:30 | 47102.5684 | 1720.008
Devonshire Building | 2016-10-18 09:45 | 47103.2435 | 2700
Devonshire Building | 2016-10-18 10:00 | 47103.6535 | 1640.016
Devonshire Building | 2016-10-18 10:15 | 47104.0485 | 1580.004
Devonshire Building | 2016-10-18 10:30 | 47104.4335 | 1540.008
Devonshire Building | 2016-10-18 10:45 | 47104.8085 | 1500.012
Devonshire Building | 2016-10-18 11:00 | 47105.1635 | 1419.984
Devonshire Building | 2016-10-18 11:15 | 47105.5135 | 1400.004
Devonshire Building | 2016-10-18 11:30 | 47106.1385 | 2499.984
Devonshire Building | 2016-10-18 11:45 | 47106.4885 | 1400.004
Devonshire Building | 2016-10-18 12:00 | 47106.8285 | 1360.008
Devonshire Building | 2016-10-18 12:15 | 47107.1735 | 1379.988
Devonshire Building | 2016-10-18 12:30 | 47107.5135 | 1360.008
Devonshire Building | 2016-10-18 12:45 | 47107.8485 | 1339.992
Devonshire Building | 2016-10-18 13:00 | 47108.4635 | 2459.988
Devonshire Building | 2016-10-18 13:15 | 47108.8235 | 1440
Devonshire Building | 2016-10-18 13:30 | 47109.1784 | 1419.984
Devonshire Building | 2016-10-18 13:45 | 47109.5384 | 1440
Devonshire Building | 2016-10-18 14:00 | 47109.9034 | 1460.016
Devonshire Building | 2016-10-18 14:15 | 47110.4384 | 2139.984
Devonshire Building | 2016-10-18 14:30 | 47110.8634 | 1699.992
Devonshire Building | 2016-10-18 14:45 | 47111.2184 | 1419.984
Devonshire Building | 2016-10-18 15:00 | 47111.5584 | 1360.008
Devonshire Building | 2016-10-18 15:15 | 47111.8984 | 1360.008
Devonshire Building | 2016-10-18 15:30 | 47112.2234 | 1299.996
Devonshire Building | 2016-10-18 15:45 | 47112.5384 | 1260
Devonshire Building | 2016-10-18 16:00 | 47112.8484 | 1239.984
Devonshire Building | 2016-10-18 16:15 | 47113.3984 | 2199.996
Devonshire Building | 2016-10-18 16:30 | 47113.6834 | 1140.012
Devonshire Building | 2016-10-18 16:45 | 47113.9734 | 1159.992
Devonshire Building | 2016-10-18 17:00 | 47114.2534 | 1119.996
Devonshire Building | 2016-10-18 17:15 | 47114.5384 | 1140.012
Devonshire Building | 2016-10-18 17:30 | 47114.8184 | 1119.996
Devonshire Building | 2016-10-18 17:45 | 47115.0984 | 1119.996
Devonshire Building | 2016-10-18 18:00 | 47115.3784 | 1119.996
Devonshire Building | 2016-10-18 18:15 | 47115.6634 | 1140.012
Devonshire Building | 2016-10-18 18:30 | 47115.9434 | 1119.996
Devonshire Building | 2016-10-18 18:45 | 47116.2234 | 1119.996
Devonshire Building | 2016-10-18 19:00 | 47116.5084 | 1140.012
Devonshire Building | 2016-10-18 19:15 | 47116.7884 | 1119.996
Devonshire Building | 2016-10-18 19:30 | 47117.0734 | 1140.012
Devonshire Building | 2016-10-18 19:45 | 47117.3584 | 1140.012
Devonshire Building | 2016-10-18 20:00 | 47117.6435 | 1140.012
Devonshire Building | 2016-10-18 20:15 | 47117.9285 | 1140.012
Devonshire Building | 2016-10-18 20:30 | 47118.2085 | 1119.996
Devonshire Building | 2016-10-18 20:45 | 47118.4935 | 1140.012
Devonshire Building | 2016-10-18 21:00 | 47118.7985 | 1220.004
Devonshire Building | 2016-10-18 21:15 | 47119.0835 | 1140.012
Devonshire Building | 2016-10-18 21:30 | 47119.3635 | 1119.996
Devonshire Building | 2016-10-18 21:45 | 47119.6485 | 1140.012
Devonshire Building | 2016-10-18 22:00 | 47119.9285 | 1119.996
Devonshire Building | 2016-10-18 22:15 | 47120.2135 | 1140.012
Devonshire Building | 2016-10-18 22:30 | 47120.4985 | 1140.012
Devonshire Building | 2016-10-18 22:45 | 47120.7835 | 1140.012
Devonshire Building | 2016-10-18 23:00 | 47121.0685 | 1140.012
Devonshire Building | 2016-10-18 23:15 | 47121.3535 | 1140.012
Devonshire Building | 2016-10-18 23:30 | 47121.6385 | 1140.012
Devonshire Building | 2016-10-18 23:45 | 47121.9235 | 1140.012 | 1100.016
Devonshire Building | 2016-10-19 | 47122.2109 | 1140.012
Devonshire Building | 2016-10-19 00:15 | 47122.4959 | 1140.012
Devonshire Building | 2016-10-19 00:30 | 47122.7859 | 1159.992
Devonshire Building | 2016-10-19 00:45 | 47123.0709 | 1140.012
Devonshire Building | 2016-10-19 01:00 | 47123.3559 | 1140.012
Devonshire Building | 2016-10-19 01:15 | 47123.641 | 1140.012
Devonshire Building | 2016-10-19 01:30 | 47123.9309 | 1159.992
Devonshire Building | 2016-10-19 01:45 | 47124.216 | 1140.012
Devonshire Building | 2016-10-19 02:00 | 47124.501 | 1140.012
Devonshire Building | 2016-10-19 02:15 | 47124.791 | 1159.992
Devonshire Building | 2016-10-19 02:30 | 47125.076 | 1140.012
Devonshire Building | 2016-10-19 02:45 | 47125.361 | 1140.012
Devonshire Building | 2016-10-19 03:00 | 47125.651 | 1159.992
Devonshire Building | 2016-10-19 03:15 | 47125.936 | 1140.012
Devonshire Building | 2016-10-19 03:30 | 47126.221 | 1140.012
Devonshire Building | 2016-10-19 03:45 | 47126.506 | 1140.012
Devonshire Building | 2016-10-19 04:00 | 47126.796 | 1159.992
Devonshire Building | 2016-10-19 04:15 | 47127.081 | 1140.012
Devonshire Building | 2016-10-19 04:30 | 47127.366 | 1140.012
Devonshire Building | 2016-10-19 04:45 | 47127.651 | 1140.012
Devonshire Building | 2016-10-19 05:00 | 47127.931 | 1119.996
Devonshire Building | 2016-10-19 05:15 | 47128.216 | 1140.012
Devonshire Building | 2016-10-19 05:30 | 47128.506 | 1159.992
Devonshire Building | 2016-10-19 05:45 | 47129.026 | 2080.008
Devonshire Building | 2016-10-19 06:00 | 47129.306 | 1119.996
Devonshire Building | 2016-10-19 06:15 | 47129.586 | 1119.996
Devonshire Building | 2016-10-19 06:30 | 47129.866 | 1119.996
Devonshire Building | 2016-10-19 06:45 | 47130.141 | 1100.016
Devonshire Building | 2016-10-19 07:00 | 47130.421 | 1119.996
Devonshire Building | 2016-10-19 07:15 | 47130.711 | 1159.992
Devonshire Building | 2016-10-19 07:30 | 47131.006 | 1180.008
Devonshire Building | 2016-10-19 07:45 | 47131.301 | 1180.008
Devonshire Building | 2016-10-19 08:00 | 47131.591 | 1159.992
Devonshire Building | 2016-10-19 08:15 | 47131.886 | 1180.008
Devonshire Building | 2016-10-19 08:30 | 47132.181 | 1180.008
Devonshire Building | 2016-10-19 08:45 | 47132.486 | 1220.004
Devonshire Building | 2016-10-19 09:00 | 47133.066 | 2319.984
Devonshire Building | 2016-10-19 09:15 | 47133.401 | 1339.992
Devonshire Building | 2016-10-19 09:30 | 47133.746 | 1379.988
Devonshire Building | 2016-10-19 09:45 | 47134.101 | 1419.984
Devonshire Building | 2016-10-19 10:00 | 47134.451 | 1400.004
Devonshire Building | 2016-10-19 10:15 | 47135.046 | 2379.996
Devonshire Building | 2016-10-19 10:30 | 47135.376 | 1320.012
Devonshire Building | 2016-10-19 10:45 | 47135.701 | 1299.996
Devonshire Building | 2016-10-19 11:00 | 47136.021 | 1280.016
Devonshire Building | 2016-10-19 11:15 | 47136.341 | 1280.016
Devonshire Building | 2016-10-19 11:30 | 47136.661 | 1280.016
Devonshire Building | 2016-10-19 11:45 | 47137.236 | 2300.004
Devonshire Building | 2016-10-19 12:00 | 47137.541 | 1220.004
Devonshire Building | 2016-10-19 12:15 | 47137.856 | 1260
Devonshire Building | 2016-10-19 12:30 | 47138.216 | 1440
Devonshire Building | 2016-10-19 12:45 | 47138.591 | 1500.012
Devonshire Building | 2016-10-19 13:00 | 47138.951 | 1440
Devonshire Building | 2016-10-19 13:15 | 47139.301 | 1400.004
Devonshire Building | 2016-10-19 13:30 | 47139.651 | 1400.004
Devonshire Building | 2016-10-19 13:45 | 47140.216 | 2260.008
Devonshire Building | 2016-10-19 14:00 | 47140.521 | 1220.004
Devonshire Building | 2016-10-19 14:15 | 47140.831 | 1239.984
Devonshire Building | 2016-10-19 14:30 | 47141.146 | 1260
Devonshire Building | 2016-10-19 14:45 | 47141.451 | 1220.004
Devonshire Building | 2016-10-19 15:00 | 47141.761 | 1239.984
Devonshire Building | 2016-10-19 15:15 | 47142.071 | 1239.984
Devonshire Building | 2016-10-19 15:30 | 47142.666 | 2379.996
Devonshire Building | 2016-10-19 15:45 | 47143.011 | 1379.988
Devonshire Building | 2016-10-19 16:00 | 47143.366 | 1419.984
Devonshire Building | 2016-10-19 16:15 | 47143.711 | 1379.988
Devonshire Building | 2016-10-19 16:30 | 47144.051 | 1360.008
Devonshire Building | 2016-10-19 16:45 | 47144.381 | 1320.012
Devonshire Building | 2016-10-19 17:00 | 47144.711 | 1320.012
Devonshire Building | 2016-10-19 17:15 | 47145.031 | 1280.016
Devonshire Building | 2016-10-19 17:30 | 47145.351 | 1280.016
Devonshire Building | 2016-10-19 17:45 | 47145.661 | 1239.984
Devonshire Building | 2016-10-19 18:00 | 47145.961 | 1199.988
Devonshire Building | 2016-10-19 18:15 | 47146.261 | 1199.988
Devonshire Building | 2016-10-19 18:30 | 47146.556 | 1180.008
Devonshire Building | 2016-10-19 18:45 | 47147.076 | 2080.008
Devonshire Building | 2016-10-19 19:00 | 47147.356 | 1119.996
Devonshire Building | 2016-10-19 19:15 | 47147.636 | 1119.996
Devonshire Building | 2016-10-19 19:30 | 47147.921 | 1140.012
Devonshire Building | 2016-10-19 19:45 | 47148.216 | 1180.008
Devonshire Building | 2016-10-19 20:00 | 47148.516 | 1199.988
Devonshire Building | 2016-10-19 20:15 | 47148.811 | 1180.008
Devonshire Building | 2016-10-19 20:30 | 47149.111 | 1199.988
Devonshire Building | 2016-10-19 20:45 | 47149.406 | 1180.008
Devonshire Building | 2016-10-19 21:00 | 47149.716 | 1239.984
Devonshire Building | 2016-10-19 21:15 | 47150.011 | 1180.008
Devonshire Building | 2016-10-19 21:30 | 47150.311 | 1199.988
Devonshire Building | 2016-10-19 21:45 | 47150.596 | 1140.012
Devonshire Building | 2016-10-19 22:00 | 47150.881 | 1140.012
Devonshire Building | 2016-10-19 22:15 | 47151.161 | 1119.996
Devonshire Building | 2016-10-19 22:30 | 47151.446 | 1140.012
Devonshire Building | 2016-10-19 22:45 | 47151.726 | 1119.996
Devonshire Building | 2016-10-19 23:00 | 47152.011 | 1140.012
Devonshire Building | 2016-10-19 23:15 | 47152.296 | 1140.012
Devonshire Building | 2016-10-19 23:30 | 47152.581 | 1140.012
Devonshire Building | 2016-10-19 23:45 | 47152.861 | 1119.996 | 1100.016
Devonshire Building | 2016-10-20 | 47153.1484 | 1159.992
Devonshire Building | 2016-10-20 00:15 | 47153.4334 | 1140.012
Devonshire Building | 2016-10-20 00:30 | 47153.7184 | 1140.012
Devonshire Building | 2016-10-20 00:45 | 47154.0084 | 1159.992
Devonshire Building | 2016-10-20 01:00 | 47154.2934 | 1140.012
Devonshire Building | 2016-10-20 01:15 | 47154.5834 | 1159.992
Devonshire Building | 2016-10-20 01:30 | 47154.8734 | 1159.992
Devonshire Building | 2016-10-20 01:45 | 47155.1634 | 1159.992
Devonshire Building | 2016-10-20 02:00 | 47155.4484 | 1140.012
Devonshire Building | 2016-10-20 02:15 | 47155.7384 | 1159.992
Devonshire Building | 2016-10-20 02:30 | 47156.0234 | 1140.012
Devonshire Building | 2016-10-20 02:45 | 47156.3134 | 1159.992
Devonshire Building | 2016-10-20 03:00 | 47156.6034 | 1159.992
Devonshire Building | 2016-10-20 03:15 | 47156.8884 | 1140.012
Devonshire Building | 2016-10-20 03:30 | 47157.1734 | 1140.012
Devonshire Building | 2016-10-20 03:45 | 47157.4634 | 1159.992
Devonshire Building | 2016-10-20 04:00 | 47157.7484 | 1140.012
Devonshire Building | 2016-10-20 04:15 | 47158.0335 | 1140.012
Devonshire Building | 2016-10-20 04:30 | 47158.3185 | 1140.012
Devonshire Building | 2016-10-20 04:45 | 47158.6035 | 1140.012
Devonshire Building | 2016-10-20 05:00 | 47158.8885 | 1140.012
Devonshire Building | 2016-10-20 05:15 | 47159.1735 | 1140.012
Devonshire Building | 2016-10-20 05:30 | 47159.4585 | 1140.012
Devonshire Building | 2016-10-20 05:45 | 47159.7435 | 1140.012
Devonshire Building | 2016-10-20 06:00 | 47160.0235 | 1119.996
Devonshire Building | 2016-10-20 06:15 | 47160.3035 | 1119.996
Devonshire Building | 2016-10-20 06:30 | 47160.5785 | 1100.016
Devonshire Building | 2016-10-20 06:45 | 47160.8585 | 1119.996
Devonshire Building | 2016-10-20 07:00 | 47161.1335 | 1100.016
Devonshire Building | 2016-10-20 07:15 | 47161.4085 | 1100.016
Devonshire Building | 2016-10-20 07:30 | 47161.6985 | 1159.992
Devonshire Building | 2016-10-20 07:45 | 47162.2085 | 2040.012
Devonshire Building | 2016-10-20 08:00 | 47162.4885 | 1119.996
Devonshire Building | 2016-10-20 08:15 | 47162.7685 | 1119.996
Devonshire Building | 2016-10-20 08:30 | 47163.0535 | 1140.012
Devonshire Building | 2016-10-20 08:45 | 47163.3385 | 1140.012
Devonshire Building | 2016-10-20 09:00 | 47163.6285 | 1159.992
Devonshire Building | 2016-10-20 09:15 | 47163.9235 | 1180.008
Devonshire Building | 2016-10-20 09:30 | 47164.5185 | 2379.996
Devonshire Building | 2016-10-20 09:45 | 47164.9085 | 1559.988
Devonshire Building | 2016-10-20 10:00 | 47165.2985 | 1559.988
Devonshire Building | 2016-10-20 10:15 | 47165.6785 | 1519.992
Devonshire Building | 2016-10-20 10:30 | 47166.0485 | 1479.996
Devonshire Building | 2016-10-20 10:45 | 47166.6585 | 2440.008
Devonshire Building | 2016-10-20 11:00 | 47166.9985 | 1360.008
Devonshire Building | 2016-10-20 11:15 | 47167.3385 | 1360.008
Devonshire Building | 2016-10-20 11:30 | 47167.6685 | 1320.012
Devonshire Building | 2016-10-20 11:45 | 47167.9985 | 1320.012
Devonshire Building | 2016-10-20 12:00 | 47168.3435 | 1379.988
Devonshire Building | 2016-10-20 12:15 | 47168.9835 | 2559.996
Devonshire Building | 2016-10-20 12:30 | 47169.3285 | 1379.988
Devonshire Building | 2016-10-20 12:45 | 47169.6785 | 1400.004
Devonshire Building | 2016-10-20 13:00 | 47170.0235 | 1379.988
Devonshire Building | 2016-10-20 13:15 | 47170.3585 | 1339.992
Devonshire Building | 2016-10-20 13:30 | 47170.6935 | 1339.992
Devonshire Building | 2016-10-20 13:45 | 47171.0285 | 1339.992
Devonshire Building | 2016-10-20 14:00 | 47171.3635 | 1339.992
Devonshire Building | 2016-10-20 14:15 | 47171.9635 | 2400.012
Devonshire Building | 2016-10-20 14:30 | 47172.2885 | 1299.996
Devonshire Building | 2016-10-20 14:45 | 47172.6035 | 1260
Devonshire Building | 2016-10-20 15:00 | 47172.9285 | 1299.996
Devonshire Building | 2016-10-20 15:15 | 47173.2535 | 1299.996
Devonshire Building | 2016-10-20 15:30 | 47173.5735 | 1280.016
Devonshire Building | 2016-10-20 15:45 | 47174.1635 | 2360.016
Devonshire Building | 2016-10-20 16:00 | 47174.4685 | 1220.004
Devonshire Building | 2016-10-20 16:15 | 47174.7685 | 1199.988
Devonshire Building | 2016-10-20 16:30 | 47175.0735 | 1220.004
Devonshire Building | 2016-10-20 16:45 | 47175.3785 | 1220.004
Devonshire Building | 2016-10-20 17:00 | 47175.6835 | 1220.004
Devonshire Building | 2016-10-20 17:15 | 47175.9835 | 1199.988
Devonshire Building | 2016-10-20 17:30 | 47176.2885 | 1220.004
Devonshire Building | 2016-10-20 17:45 | 47176.5885 | 1199.988
Devonshire Building | 2016-10-20 18:00 | 47176.8985 | 1239.984
Devonshire Building | 2016-10-20 18:15 | 47177.2385 | 1360.008
Devonshire Building | 2016-10-20 18:30 | 47177.5835 | 1379.988
Devonshire Building | 2016-10-20 18:45 | 47177.9235 | 1360.008
Devonshire Building | 2016-10-20 19:00 | 47178.2585 | 1339.992
Devonshire Building | 2016-10-20 19:15 | 47178.5885 | 1320.012
Devonshire Building | 2016-10-20 19:30 | 47178.9085 | 1280.016
Devonshire Building | 2016-10-20 19:45 | 47179.2185 | 1239.984
Devonshire Building | 2016-10-20 20:00 | 47179.5235 | 1220.004
Devonshire Building | 2016-10-20 20:15 | 47179.8285 | 1220.004
Devonshire Building | 2016-10-20 20:30 | 47180.1285 | 1199.988
Devonshire Building | 2016-10-20 20:45 | 47180.4285 | 1199.988
Devonshire Building | 2016-10-20 21:00 | 47180.7435 | 1260
Devonshire Building | 2016-10-20 21:15 | 47181.0335 | 1159.992
Devonshire Building | 2016-10-20 21:30 | 47181.3235 | 1159.992
Devonshire Building | 2016-10-20 21:45 | 47181.6085 | 1140.012
Devonshire Building | 2016-10-20 22:00 | 47181.8985 | 1159.992
Devonshire Building | 2016-10-20 22:15 | 47182.1885 | 1159.992
Devonshire Building | 2016-10-20 22:30 | 47182.4785 | 1159.992
Devonshire Building | 2016-10-20 22:45 | 47182.7685 | 1159.992
Devonshire Building | 2016-10-20 23:00 | 47183.0585 | 1159.992
Devonshire Building | 2016-10-20 23:15 | 47183.3485 | 1159.992
Devonshire Building | 2016-10-20 23:30 | 47183.6435 | 1180.008
Devonshire Building | 2016-10-20 23:45 | 47183.9335 | 1159.992 | 1100.016
Devonshire Building | 2016-10-21 | 47184.2266 | 1159.992
Devonshire Building | 2016-10-21 00:15 | 47184.5166 | 1159.992
Devonshire Building | 2016-10-21 00:30 | 47184.8116 | 1180.008
Devonshire Building | 2016-10-21 00:45 | 47185.1016 | 1159.992
Devonshire Building | 2016-10-21 01:00 | 47185.3916 | 1159.992
Devonshire Building | 2016-10-21 01:15 | 47185.6866 | 1180.008
Devonshire Building | 2016-10-21 01:30 | 47185.9766 | 1159.992
Devonshire Building | 2016-10-21 01:45 | 47186.2666 | 1159.992
Devonshire Building | 2016-10-21 02:00 | 47186.5616 | 1180.008
Devonshire Building | 2016-10-21 02:15 | 47186.8516 | 1159.992
Devonshire Building | 2016-10-21 02:30 | 47187.1466 | 1180.008
Devonshire Building | 2016-10-21 02:45 | 47187.4366 | 1159.992
Devonshire Building | 2016-10-21 03:00 | 47187.9666 | 2120.004
Devonshire Building | 2016-10-21 03:15 | 47188.2616 | 1180.008
Devonshire Building | 2016-10-21 03:30 | 47188.5516 | 1159.992
Devonshire Building | 2016-10-21 03:45 | 47188.8466 | 1180.008
Devonshire Building | 2016-10-21 04:00 | 47189.1366 | 1159.992
Devonshire Building | 2016-10-21 04:15 | 47189.4316 | 1180.008
Devonshire Building | 2016-10-21 04:30 | 47189.7216 | 1159.992
Devonshire Building | 2016-10-21 04:45 | 47190.0166 | 1180.008
Devonshire Building | 2016-10-21 05:00 | 47190.3066 | 1159.992
Devonshire Building | 2016-10-21 05:15 | 47190.5966 | 1159.992
Devonshire Building | 2016-10-21 05:30 | 47190.8866 | 1159.992
Devonshire Building | 2016-10-21 05:45 | 47191.1765 | 1159.992
Devonshire Building | 2016-10-21 06:00 | 47191.4665 | 1159.992
Devonshire Building | 2016-10-21 06:15 | 47191.7516 | 1140.012
Devonshire Building | 2016-10-21 06:30 | 47192.0415 | 1159.992
Devonshire Building | 2016-10-21 06:45 | 47192.3315 | 1159.992
Devonshire Building | 2016-10-21 07:00 | 47192.6165 | 1140.012
Devonshire Building | 2016-10-21 07:15 | 47192.9065 | 1159.992
Devonshire Building | 2016-10-21 07:30 | 47193.1965 | 1159.992
Devonshire Building | 2016-10-21 07:45 | 47193.4915 | 1180.008
Devonshire Building | 2016-10-21 08:00 | 47193.7915 | 1199.988
Devonshire Building | 2016-10-21 08:15 | 47194.0865 | 1180.008
Devonshire Building | 2016-10-21 08:30 | 47194.3965 | 1239.984
Devonshire Building | 2016-10-21 08:45 | 47194.7465 | 1400.004
Devonshire Building | 2016-10-21 09:00 | 47195.5365 | 3160.008
Devonshire Building | 2016-10-21 09:15 | 47196.0665 | 2120.004
Devonshire Building | 2016-10-21 09:30 | 47196.5265 | 1839.996
Devonshire Building | 2016-10-21 09:45 | 47196.9665 | 1760.004
Devonshire Building | 2016-10-21 10:00 | 47197.3565 | 1559.988
Devonshire Building | 2016-10-21 10:15 | 47197.7165 | 1440
Devonshire Building | 2016-10-21 10:30 | 47198.2965 | 2319.984
Devonshire Building | 2016-10-21 10:45 | 47198.6115 | 1260
Devonshire Building | 2016-10-21 11:00 | 47198.9065 | 1180.008
Devonshire Building | 2016-10-21 11:15 | 47199.2115 | 1220.004
Devonshire Building | 2016-10-21 11:30 | 47199.5215 | 1239.984
Devonshire Building | 2016-10-21 11:45 | 47199.8365 | 1260
Devonshire Building | 2016-10-21 12:00 | 47200.4265 | 2360.016
Devonshire Building | 2016-10-21 12:15 | 47200.7515 | 1299.996
Devonshire Building | 2016-10-21 12:30 | 47201.0815 | 1320.012
Devonshire Building | 2016-10-21 12:45 | 47201.4165 | 1339.992
Devonshire Building | 2016-10-21 13:00 | 47201.7465 | 1320.012
Devonshire Building | 2016-10-21 13:15 | 47202.0815 | 1339.992
Devonshire Building | 2016-10-21 13:30 | 47202.4365 | 1419.984
Devonshire Building | 2016-10-21 13:45 | 47202.7915 | 1419.984
Devonshire Building | 2016-10-21 14:00 | 47203.1465 | 1419.984
Devonshire Building | 2016-10-21 14:15 | 47203.7615 | 2459.988
Devonshire Building | 2016-10-21 14:30 | 47204.1065 | 1379.988
Devonshire Building | 2016-10-21 14:45 | 47204.4515 | 1379.988
Devonshire Building | 2016-10-21 15:00 | 47204.7865 | 1339.992
Devonshire Building | 2016-10-21 15:15 | 47205.1215 | 1339.992
Devonshire Building | 2016-10-21 15:30 | 47205.4615 | 1360.008
Devonshire Building | 2016-10-21 15:45 | 47205.8115 | 1400.004
Devonshire Building | 2016-10-21 16:00 | 47206.1615 | 1400.004
Devonshire Building | 2016-10-21 16:15 | 47206.5015 | 1360.008
Devonshire Building | 2016-10-21 16:30 | 47207.0965 | 2379.996
Devonshire Building | 2016-10-21 16:45 | 47207.4315 | 1339.992
Devonshire Building | 2016-10-21 17:00 | 47207.7665 | 1339.992
Devonshire Building | 2016-10-21 17:15 | 47208.0965 | 1320.012
Devonshire Building | 2016-10-21 17:30 | 47208.4165 | 1280.016
Devonshire Building | 2016-10-21 17:45 | 47208.7365 | 1280.016
Devonshire Building | 2016-10-21 18:00 | 47209.0465 | 1239.984
Devonshire Building | 2016-10-21 18:15 | 47209.3565 | 1239.984
Devonshire Building | 2016-10-21 18:30 | 47209.6615 | 1220.004
Devonshire Building | 2016-10-21 18:45 | 47209.9615 | 1199.988
Devonshire Building | 2016-10-21 19:00 | 47210.2615 | 1199.988
Devonshire Building | 2016-10-21 19:15 | 47210.5615 | 1199.988
Devonshire Building | 2016-10-21 19:30 | 47210.8615 | 1199.988
Devonshire Building | 2016-10-21 19:45 | 47211.1565 | 1180.008
Devonshire Building | 2016-10-21 20:00 | 47211.4565 | 1199.988
Devonshire Building | 2016-10-21 20:15 | 47211.7515 | 1180.008
Devonshire Building | 2016-10-21 20:30 | 47212.0515 | 1199.988
Devonshire Building | 2016-10-21 20:45 | 47212.3465 | 1180.008
Devonshire Building | 2016-10-21 21:00 | 47212.6515 | 1220.004
Devonshire Building | 2016-10-21 21:15 | 47212.9465 | 1180.008
Devonshire Building | 2016-10-21 21:30 | 47213.2365 | 1159.992
Devonshire Building | 2016-10-21 21:45 | 47213.5315 | 1180.008
Devonshire Building | 2016-10-21 22:00 | 47213.8215 | 1159.992
Devonshire Building | 2016-10-21 22:15 | 47214.1165 | 1180.008
Devonshire Building | 2016-10-21 22:30 | 47214.4065 | 1159.992
Devonshire Building | 2016-10-21 22:45 | 47214.7015 | 1180.008
Devonshire Building | 2016-10-21 23:00 | 47214.9965 | 1180.008
Devonshire Building | 2016-10-21 23:15 | 47215.2865 | 1159.992
Devonshire Building | 2016-10-21 23:30 | 47215.5815 | 1180.008
Devonshire Building | 2016-10-21 23:45 | 47215.8765 | 1180.008 | 1140.012
Devonshire Building | 2016-10-22 | 47216.1641 | 1159.992
Devonshire Building | 2016-10-22 00:15 | 47216.4591 | 1180.008
Devonshire Building | 2016-10-22 00:30 | 47216.7541 | 1180.008
Devonshire Building | 2016-10-22 00:45 | 47217.0491 | 1180.008
Devonshire Building | 2016-10-22 01:00 | 47217.3441 | 1180.008
Devonshire Building | 2016-10-22 01:15 | 47217.6391 | 1180.008
Devonshire Building | 2016-10-22 01:30 | 47217.9341 | 1180.008
Devonshire Building | 2016-10-22 01:45 | 47218.2291 | 1180.008
Devonshire Building | 2016-10-22 02:00 | 47218.5241 | 1180.008
Devonshire Building | 2016-10-22 02:15 | 47218.8191 | 1180.008
Devonshire Building | 2016-10-22 02:30 | 47219.1141 | 1180.008
Devonshire Building | 2016-10-22 02:45 | 47219.4091 | 1180.008
Devonshire Building | 2016-10-22 03:00 | 47219.7041 | 1180.008
Devonshire Building | 2016-10-22 03:15 | 47219.9991 | 1180.008
Devonshire Building | 2016-10-22 03:30 | 47220.2891 | 1159.992
Devonshire Building | 2016-10-22 03:45 | 47220.5841 | 1180.008
Devonshire Building | 2016-10-22 04:00 | 47220.8741 | 1159.992
Devonshire Building | 2016-10-22 04:15 | 47221.1641 | 1159.992
Devonshire Building | 2016-10-22 04:30 | 47221.4591 | 1180.008
Devonshire Building | 2016-10-22 04:45 | 47221.7491 | 1159.992
Devonshire Building | 2016-10-22 05:00 | 47222.0391 | 1159.992
Devonshire Building | 2016-10-22 05:15 | 47222.3291 | 1159.992
Devonshire Building | 2016-10-22 05:30 | 47222.6191 | 1159.992
Devonshire Building | 2016-10-22 05:45 | 47222.9091 | 1159.992
Devonshire Building | 2016-10-22 06:00 | 47223.1991 | 1159.992
Devonshire Building | 2016-10-22 06:15 | 47223.4891 | 1159.992
Devonshire Building | 2016-10-22 06:30 | 47223.7791 | 1159.992
Devonshire Building | 2016-10-22 06:45 | 47224.0641 | 1140.012
Devonshire Building | 2016-10-22 07:00 | 47224.3491 | 1140.012
Devonshire Building | 2016-10-22 07:15 | 47224.6341 | 1140.012
Devonshire Building | 2016-10-22 07:30 | 47224.9191 | 1140.012
Devonshire Building | 2016-10-22 07:45 | 47225.2141 | 1180.008
Devonshire Building | 2016-10-22 08:00 | 47225.5141 | 1199.988
Devonshire Building | 2016-10-22 08:15 | 47225.8141 | 1199.988
Devonshire Building | 2016-10-22 08:30 | 47226.1141 | 1199.988
Devonshire Building | 2016-10-22 08:45 | 47226.4141 | 1199.988
Devonshire Building | 2016-10-22 09:00 | 47226.7141 | 1199.988
Devonshire Building | 2016-10-22 09:15 | 47227.0091 | 1180.008
Devonshire Building | 2016-10-22 09:30 | 47227.3091 | 1199.988
Devonshire Building | 2016-10-22 09:45 | 47227.6091 | 1199.988
Devonshire Building | 2016-10-22 10:00 | 47227.8891 | 1119.996
Devonshire Building | 2016-10-22 10:15 | 47228.1691 | 1119.996
Devonshire Building | 2016-10-22 10:30 | 47228.4491 | 1119.996
Devonshire Building | 2016-10-22 10:45 | 47228.7341 | 1140.012
Devonshire Building | 2016-10-22 11:00 | 47229.0141 | 1119.996
Devonshire Building | 2016-10-22 11:15 | 47229.2991 | 1140.012
Devonshire Building | 2016-10-22 11:30 | 47229.8291 | 2120.004
Devonshire Building | 2016-10-22 11:45 | 47230.1091 | 1119.996
Devonshire Building | 2016-10-22 12:00 | 47230.3941 | 1140.012
Devonshire Building | 2016-10-22 12:15 | 47230.6741 | 1119.996
Devonshire Building | 2016-10-22 12:30 | 47230.9541 | 1119.996
Devonshire Building | 2016-10-22 12:45 | 47231.2391 | 1140.012
Devonshire Building | 2016-10-22 13:00 | 47231.5191 | 1119.996
Devonshire Building | 2016-10-22 13:15 | 47231.8041 | 1140.012
Devonshire Building | 2016-10-22 13:30 | 47232.0841 | 1119.996
Devonshire Building | 2016-10-22 13:45 | 47232.3691 | 1140.012
Devonshire Building | 2016-10-22 14:00 | 47232.6491 | 1119.996
Devonshire Building | 2016-10-22 14:15 | 47232.9341 | 1140.012
Devonshire Building | 2016-10-22 14:30 | 47233.2141 | 1119.996
Devonshire Building | 2016-10-22 14:45 | 47233.4991 | 1140.012
Devonshire Building | 2016-10-22 15:00 | 47233.7841 | 1140.012
Devonshire Building | 2016-10-22 15:15 | 47234.0691 | 1140.012
Devonshire Building | 2016-10-22 15:30 | 47234.3491 | 1119.996
Devonshire Building | 2016-10-22 15:45 | 47234.6341 | 1140.012
Devonshire Building | 2016-10-22 16:00 | 47234.9141 | 1119.996
Devonshire Building | 2016-10-22 16:15 | 47235.1941 | 1119.996
Devonshire Building | 2016-10-22 16:30 | 47235.4791 | 1140.012
Devonshire Building | 2016-10-22 16:45 | 47235.7591 | 1119.996
Devonshire Building | 2016-10-22 17:00 | 47236.0441 | 1140.012
Devonshire Building | 2016-10-22 17:15 | 47236.3241 | 1119.996
Devonshire Building | 2016-10-22 17:30 | 47236.6091 | 1140.012
Devonshire Building | 2016-10-22 17:45 | 47236.8891 | 1119.996
Devonshire Building | 2016-10-22 18:00 | 47237.1741 | 1140.012
Devonshire Building | 2016-10-22 18:15 | 47237.4541 | 1119.996
Devonshire Building | 2016-10-22 18:30 | 47237.7391 | 1140.012
Devonshire Building | 2016-10-22 18:45 | 47238.0291 | 1159.992
Devonshire Building | 2016-10-22 19:00 | 47238.3141 | 1140.012
Devonshire Building | 2016-10-22 19:15 | 47238.5991 | 1140.012
Devonshire Building | 2016-10-22 19:30 | 47238.8841 | 1140.012
Devonshire Building | 2016-10-22 19:45 | 47239.1741 | 1159.992
Devonshire Building | 2016-10-22 20:00 | 47239.4591 | 1140.012
Devonshire Building | 2016-10-22 20:15 | 47239.7441 | 1140.012
Devonshire Building | 2016-10-22 20:30 | 47240.0341 | 1159.992
Devonshire Building | 2016-10-22 20:45 | 47240.3191 | 1140.012
Devonshire Building | 2016-10-22 21:00 | 47240.6291 | 1239.984
Devonshire Building | 2016-10-22 21:15 | 47240.9191 | 1159.992
Devonshire Building | 2016-10-22 21:30 | 47241.2091 | 1159.992
Devonshire Building | 2016-10-22 21:45 | 47241.4941 | 1140.012
Devonshire Building | 2016-10-22 22:00 | 47241.7841 | 1159.992
Devonshire Building | 2016-10-22 22:15 | 47242.0741 | 1159.992
Devonshire Building | 2016-10-22 22:30 | 47242.3641 | 1159.992
Devonshire Building | 2016-10-22 22:45 | 47242.6541 | 1159.992
Devonshire Building | 2016-10-22 23:00 | 47242.9441 | 1159.992
Devonshire Building | 2016-10-22 23:15 | 47243.2341 | 1159.992
Devonshire Building | 2016-10-22 23:30 | 47243.5241 | 1159.992
Devonshire Building | 2016-10-22 23:45 | 47243.8141 | 1159.992 | 1119.996
Devonshire Building | 2016-10-23 | 47244.1055 | 1159.992
Devonshire Building | 2016-10-23 00:15 | 47244.4005 | 1180.008
Devonshire Building | 2016-10-23 00:30 | 47244.6905 | 1159.992
Devonshire Building | 2016-10-23 00:45 | 47244.9855 | 1180.008
Devonshire Building | 2016-10-23 01:00 | 47245.2755 | 1159.992
Devonshire Building | 2016-10-23 01:15 | 47245.5705 | 1180.008
Devonshire Building | 2016-10-23 01:30 | 47245.8655 | 1180.008
Devonshire Building | 2016-10-23 01:45 | 47246.1605 | 1180.008
Devonshire Building | 2016-10-23 02:00 | 47246.4505 | 1159.992
Devonshire Building | 2016-10-23 02:15 | 47246.7455 | 1180.008
Devonshire Building | 2016-10-23 02:30 | 47247.0405 | 1180.008
Devonshire Building | 2016-10-23 02:45 | 47247.3305 | 1159.992
Devonshire Building | 2016-10-23 03:00 | 47247.6255 | 1180.008
Devonshire Building | 2016-10-23 03:15 | 47247.9205 | 1180.008
Devonshire Building | 2016-10-23 03:30 | 47248.2105 | 1159.992
Devonshire Building | 2016-10-23 03:45 | 47248.5055 | 1180.008
Devonshire Building | 2016-10-23 04:00 | 47248.7955 | 1159.992
Devonshire Building | 2016-10-23 04:15 | 47249.0905 | 1180.008
Devonshire Building | 2016-10-23 04:30 | 47249.3805 | 1159.992
Devonshire Building | 2016-10-23 04:45 | 47249.6755 | 1180.008
Devonshire Building | 2016-10-23 05:00 | 47249.9655 | 1159.992
Devonshire Building | 2016-10-23 05:15 | 47250.2605 | 1180.008
Devonshire Building | 2016-10-23 05:30 | 47250.5555 | 1180.008
Devonshire Building | 2016-10-23 05:45 | 47250.8505 | 1180.008
Devonshire Building | 2016-10-23 06:00 | 47251.1405 | 1159.992
Devonshire Building | 2016-10-23 06:15 | 47251.4355 | 1180.008
Devonshire Building | 2016-10-23 06:30 | 47251.7305 | 1180.008
Devonshire Building | 2016-10-23 06:45 | 47252.0255 | 1180.008
Devonshire Building | 2016-10-23 07:00 | 47252.3155 | 1159.992
Devonshire Building | 2016-10-23 07:15 | 47252.6105 | 1180.008
Devonshire Building | 2016-10-23 07:30 | 47252.9005 | 1159.992
Devonshire Building | 2016-10-23 07:45 | 47253.2055 | 1220.004
Devonshire Building | 2016-10-23 08:00 | 47253.5105 | 1220.004
Devonshire Building | 2016-10-23 08:15 | 47253.8155 | 1220.004
Devonshire Building | 2016-10-23 08:30 | 47254.1255 | 1239.984
Devonshire Building | 2016-10-23 08:45 | 47254.4305 | 1220.004
Devonshire Building | 2016-10-23 09:00 | 47254.7355 | 1220.004
Devonshire Building | 2016-10-23 09:15 | 47255.0405 | 1220.004
Devonshire Building | 2016-10-23 09:30 | 47255.3455 | 1220.004
Devonshire Building | 2016-10-23 09:45 | 47255.6455 | 1199.988
Devonshire Building | 2016-10-23 10:00 | 47255.9305 | 1140.012
Devonshire Building | 2016-10-23 10:15 | 47256.2205 | 1159.992
Devonshire Building | 2016-10-23 10:30 | 47256.5055 | 1140.012
Devonshire Building | 2016-10-23 10:45 | 47256.7905 | 1140.012
Devonshire Building | 2016-10-23 11:00 | 47257.0755 | 1140.012
Devonshire Building | 2016-10-23 11:15 | 47257.3605 | 1140.012
Devonshire Building | 2016-10-23 11:30 | 47257.6455 | 1140.012
Devonshire Building | 2016-10-23 11:45 | 47257.9305 | 1140.012
Devonshire Building | 2016-10-23 12:00 | 47258.2155 | 1140.012
Devonshire Building | 2016-10-23 12:15 | 47258.5005 | 1140.012
Devonshire Building | 2016-10-23 12:30 | 47259.0355 | 2139.984
Devonshire Building | 2016-10-23 12:45 | 47259.3205 | 1140.012
Devonshire Building | 2016-10-23 13:00 | 47259.6105 | 1159.992
Devonshire Building | 2016-10-23 13:15 | 47259.8955 | 1140.012
Devonshire Building | 2016-10-23 13:30 | 47260.1805 | 1140.012
Devonshire Building | 2016-10-23 13:45 | 47260.4705 | 1159.992
Devonshire Building | 2016-10-23 14:00 | 47260.7555 | 1140.012
Devonshire Building | 2016-10-23 14:15 | 47261.0455 | 1159.992
Devonshire Building | 2016-10-23 14:30 | 47261.3355 | 1159.992
Devonshire Building | 2016-10-23 14:45 | 47261.6205 | 1140.012
Devonshire Building | 2016-10-23 15:00 | 47261.9105 | 1159.992
Devonshire Building | 2016-10-23 15:15 | 47262.2005 | 1159.992
Devonshire Building | 2016-10-23 15:30 | 47262.4855 | 1140.012
Devonshire Building | 2016-10-23 15:45 | 47262.7755 | 1159.992
Devonshire Building | 2016-10-23 16:00 | 47263.0605 | 1140.012
Devonshire Building | 2016-10-23 16:15 | 47263.3505 | 1159.992
Devonshire Building | 2016-10-23 16:30 | 47263.6405 | 1159.992
Devonshire Building | 2016-10-23 16:45 | 47263.9255 | 1140.012
Devonshire Building | 2016-10-23 17:00 | 47264.2105 | 1140.012
Devonshire Building | 2016-10-23 17:15 | 47264.5005 | 1159.992
Devonshire Building | 2016-10-23 17:30 | 47264.7855 | 1140.012
Devonshire Building | 2016-10-23 17:45 | 47265.0705 | 1140.012
Devonshire Building | 2016-10-23 18:00 | 47265.3605 | 1159.992
Devonshire Building | 2016-10-23 18:15 | 47265.6455 | 1140.012
Devonshire Building | 2016-10-23 18:30 | 47265.9305 | 1140.012
Devonshire Building | 2016-10-23 18:45 | 47266.2155 | 1140.012
Devonshire Building | 2016-10-23 19:00 | 47266.5055 | 1159.992
Devonshire Building | 2016-10-23 19:15 | 47266.7905 | 1140.012
Devonshire Building | 2016-10-23 19:30 | 47267.0805 | 1159.992
Devonshire Building | 2016-10-23 19:45 | 47267.3655 | 1140.012
Devonshire Building | 2016-10-23 20:00 | 47267.6555 | 1159.992
Devonshire Building | 2016-10-23 20:15 | 47267.9405 | 1140.012
Devonshire Building | 2016-10-23 20:30 | 47268.2305 | 1159.992
Devonshire Building | 2016-10-23 20:45 | 47268.5205 | 1159.992
Devonshire Building | 2016-10-23 21:00 | 47268.8155 | 1180.008
Devonshire Building | 2016-10-23 21:15 | 47269.1005 | 1140.012
Devonshire Building | 2016-10-23 21:30 | 47269.3905 | 1159.992
Devonshire Building | 2016-10-23 21:45 | 47269.6805 | 1159.992
Devonshire Building | 2016-10-23 22:00 | 47269.9655 | 1140.012
Devonshire Building | 2016-10-23 22:15 | 47270.2555 | 1159.992
Devonshire Building | 2016-10-23 22:30 | 47270.5455 | 1159.992
Devonshire Building | 2016-10-23 22:45 | 47270.8355 | 1159.992
Devonshire Building | 2016-10-23 23:00 | 47271.1255 | 1159.992
Devonshire Building | 2016-10-23 23:15 | 47271.4205 | 1180.008
Devonshire Building | 2016-10-23 23:30 | 47271.7105 | 1159.992
Devonshire Building | 2016-10-23 23:45 | 47272.0005 | 1159.992 | 1140.012
Devonshire Building | 2016-10-24 | 47272.293 | 1180.008
Devonshire Building | 2016-10-24 00:15 | 47272.588 | 1180.008
Devonshire Building | 2016-10-24 00:30 | 47272.878 | 1159.992
Devonshire Building | 2016-10-24 00:45 | 47273.173 | 1180.008
Devonshire Building | 2016-10-24 01:00 | 47273.473 | 1199.988
Devonshire Building | 2016-10-24 01:15 | 47273.768 | 1180.008
Devonshire Building | 2016-10-24 01:30 | 47274.063 | 1180.008
Devonshire Building | 2016-10-24 01:45 | 47274.358 | 1180.008
Devonshire Building | 2016-10-24 02:00 | 47274.653 | 1180.008
Devonshire Building | 2016-10-24 02:15 | 47274.948 | 1180.008
Devonshire Building | 2016-10-24 02:30 | 47275.248 | 1199.988
Devonshire Building | 2016-10-24 02:45 | 47275.543 | 1180.008
Devonshire Building | 2016-10-24 03:00 | 47275.838 | 1180.008
Devonshire Building | 2016-10-24 03:15 | 47276.133 | 1180.008
Devonshire Building | 2016-10-24 03:30 | 47276.428 | 1180.008
Devonshire Building | 2016-10-24 03:45 | 47276.723 | 1180.008
Devonshire Building | 2016-10-24 04:00 | 47277.018 | 1180.008
Devonshire Building | 2016-10-24 04:15 | 47277.313 | 1180.008
Devonshire Building | 2016-10-24 04:30 | 47277.608 | 1180.008
Devonshire Building | 2016-10-24 04:45 | 47277.903 | 1180.008
Devonshire Building | 2016-10-24 05:00 | 47278.198 | 1180.008
Devonshire Building | 2016-10-24 05:15 | 47278.493 | 1180.008
Devonshire Building | 2016-10-24 05:30 | 47278.788 | 1180.008
Devonshire Building | 2016-10-24 05:45 | 47279.078 | 1159.992
Devonshire Building | 2016-10-24 06:00 | 47279.373 | 1180.008
Devonshire Building | 2016-10-24 06:15 | 47279.668 | 1180.008
Devonshire Building | 2016-10-24 06:30 | 47279.958 | 1159.992
Devonshire Building | 2016-10-24 06:45 | 47280.253 | 1180.008
Devonshire Building | 2016-10-24 07:00 | 47280.543 | 1159.992
Devonshire Building | 2016-10-24 07:15 | 47280.833 | 1159.992
Devonshire Building | 2016-10-24 07:30 | 47281.388 | 2220.012
Devonshire Building | 2016-10-24 07:45 | 47281.688 | 1199.988
Devonshire Building | 2016-10-24 08:00 | 47281.993 | 1220.004
Devonshire Building | 2016-10-24 08:15 | 47282.303 | 1239.984
Devonshire Building | 2016-10-24 08:30 | 47282.608 | 1220.004
Devonshire Building | 2016-10-24 08:45 | 47282.918 | 1239.984
Devonshire Building | 2016-10-24 09:00 | 47283.233 | 1260
Devonshire Building | 2016-10-24 09:15 | 47283.643 | 1640.016
Devonshire Building | 2016-10-24 09:30 | 47284.123 | 1919.988
Devonshire Building | 2016-10-24 09:45 | 47284.428 | 1220.004
Devonshire Building | 2016-10-24 10:00 | 47284.748 | 1280.016
Devonshire Building | 2016-10-24 10:15 | 47285.068 | 1280.016
Devonshire Building | 2016-10-24 10:30 | 47285.368 | 1199.988
Devonshire Building | 2016-10-24 10:45 | 47285.668 | 1199.988
Devonshire Building | 2016-10-24 11:00 | 47286.283 | 2459.988
Devonshire Building | 2016-10-24 11:15 | 47286.603 | 1280.016
Devonshire Building | 2016-10-24 11:30 | 47286.928 | 1299.996
Devonshire Building | 2016-10-24 11:45 | 47287.258 | 1320.012
Devonshire Building | 2016-10-24 12:00 | 47287.593 | 1339.992
Devonshire Building | 2016-10-24 12:15 | 47287.943 | 1400.004
Devonshire Building | 2016-10-24 12:30 | 47288.283 | 1360.008
Devonshire Building | 2016-10-24 12:45 | 47288.893 | 2440.008
Devonshire Building | 2016-10-24 13:00 | 47289.258 | 1460.016
Devonshire Building | 2016-10-24 13:15 | 47289.623 | 1460.016
Devonshire Building | 2016-10-24 13:30 | 47289.978 | 1419.984
Devonshire Building | 2016-10-24 13:45 | 47290.323 | 1379.988
Devonshire Building | 2016-10-24 14:00 | 47290.668 | 1379.988
Devonshire Building | 2016-10-24 14:15 | 47291.008 | 1360.008
Devonshire Building | 2016-10-24 14:30 | 47291.388 | 1519.992
Devonshire Building | 2016-10-24 14:45 | 47292.013 | 2499.984
Devonshire Building | 2016-10-24 15:00 | 47292.333 | 1280.016
Devonshire Building | 2016-10-24 15:15 | 47292.658 | 1299.996
Devonshire Building | 2016-10-24 15:30 | 47293.013 | 1419.984
Devonshire Building | 2016-10-24 15:45 | 47293.378 | 1460.016
Devonshire Building | 2016-10-24 16:00 | 47293.758 | 1519.992
Devonshire Building | 2016-10-24 16:15 | 47294.398 | 2559.996
Devonshire Building | 2016-10-24 16:30 | 47294.763 | 1460.016
Devonshire Building | 2016-10-24 16:45 | 47295.123 | 1440
Devonshire Building | 2016-10-24 17:00 | 47295.458 | 1339.992
Devonshire Building | 2016-10-24 17:15 | 47295.788 | 1320.012
Devonshire Building | 2016-10-24 17:30 | 47296.108 | 1280.016
Devonshire Building | 2016-10-24 17:45 | 47296.423 | 1260
Devonshire Building | 2016-10-24 18:00 | 47296.728 | 1220.004
Devonshire Building | 2016-10-24 18:15 | 47297.038 | 1239.984
Devonshire Building | 2016-10-24 18:30 | 47297.338 | 1199.988
Devonshire Building | 2016-10-24 18:45 | 47297.643 | 1220.004
Devonshire Building | 2016-10-24 19:00 | 47297.943 | 1199.988
Devonshire Building | 2016-10-24 19:15 | 47298.243 | 1199.988
Devonshire Building | 2016-10-24 19:30 | 47298.543 | 1199.988
Devonshire Building | 2016-10-24 19:45 | 47298.838 | 1180.008
Devonshire Building | 2016-10-24 20:00 | 47299.138 | 1199.988
Devonshire Building | 2016-10-24 20:15 | 47299.433 | 1180.008
Devonshire Building | 2016-10-24 20:30 | 47299.733 | 1199.988
Devonshire Building | 2016-10-24 20:45 | 47300.028 | 1180.008
Devonshire Building | 2016-10-24 21:00 | 47300.348 | 1280.016
Devonshire Building | 2016-10-24 21:15 | 47300.638 | 1159.992
Devonshire Building | 2016-10-24 21:30 | 47300.933 | 1180.008
Devonshire Building | 2016-10-24 21:45 | 47301.228 | 1180.008
Devonshire Building | 2016-10-24 22:00 | 47301.523 | 1180.008
Devonshire Building | 2016-10-24 22:15 | 47301.813 | 1159.992
Devonshire Building | 2016-10-24 22:30 | 47302.108 | 1180.008
Devonshire Building | 2016-10-24 22:45 | 47302.403 | 1180.008
Devonshire Building | 2016-10-24 23:00 | 47302.703 | 1199.988
Devonshire Building | 2016-10-24 23:15 | 47302.998 | 1180.008
Devonshire Building | 2016-10-24 23:30 | 47303.293 | 1180.008
Devonshire Building | 2016-10-24 23:45 | 47303.593 | 1199.988 | 1159.992
Devonshire Building | 2016-10-25 | 47303.8906 | 1180.008
Devonshire Building | 2016-10-25 00:15 | 47304.1906 | 1199.988
Devonshire Building | 2016-10-25 00:30 | 47304.4906 | 1199.988
Devonshire Building | 2016-10-25 00:45 | 47304.7906 | 1199.988
Devonshire Building | 2016-10-25 01:00 | 47305.0906 | 1199.988
Devonshire Building | 2016-10-25 01:15 | 47305.3906 | 1199.988
Devonshire Building | 2016-10-25 01:30 | 47305.6856 | 1180.008
Devonshire Building | 2016-10-25 01:45 | 47305.9906 | 1220.004
Devonshire Building | 2016-10-25 02:00 | 47306.2906 | 1199.988
Devonshire Building | 2016-10-25 02:15 | 47306.5906 | 1199.988
Devonshire Building | 2016-10-25 02:30 | 47306.8856 | 1180.008
Devonshire Building | 2016-10-25 02:45 | 47307.1856 | 1199.988
Devonshire Building | 2016-10-25 03:00 | 47307.4856 | 1199.988
Devonshire Building | 2016-10-25 03:15 | 47307.7856 | 1199.988
Devonshire Building | 2016-10-25 03:30 | 47308.0856 | 1199.988
Devonshire Building | 2016-10-25 03:45 | 47308.3856 | 1199.988
Devonshire Building | 2016-10-25 04:00 | 47308.6906 | 1220.004
Devonshire Building | 2016-10-25 04:15 | 47308.9906 | 1199.988
Devonshire Building | 2016-10-25 04:30 | 47309.2906 | 1199.988
Devonshire Building | 2016-10-25 04:45 | 47309.5906 | 1199.988
Devonshire Building | 2016-10-25 05:00 | 47309.8856 | 1180.008
Devonshire Building | 2016-10-25 05:15 | 47310.4406 | 2220.012
Devonshire Building | 2016-10-25 05:30 | 47310.7406 | 1199.988
Devonshire Building | 2016-10-25 05:45 | 47311.0406 | 1199.988
Devonshire Building | 2016-10-25 06:00 | 47311.3356 | 1180.008
Devonshire Building | 2016-10-25 06:15 | 47311.6306 | 1180.008
Devonshire Building | 2016-10-25 06:30 | 47311.9356 | 1220.004
Devonshire Building | 2016-10-25 06:45 | 47312.2356 | 1199.988
Devonshire Building | 2016-10-25 07:00 | 47312.5306 | 1180.008
Devonshire Building | 2016-10-25 07:15 | 47312.8306 | 1199.988
Devonshire Building | 2016-10-25 07:30 | 47313.1306 | 1199.988
Devonshire Building | 2016-10-25 07:45 | 47313.4406 | 1239.984
Devonshire Building | 2016-10-25 08:00 | 47313.7556 | 1260
Devonshire Building | 2016-10-25 08:15 | 47314.0706 | 1260
Devonshire Building | 2016-10-25 08:30 | 47314.3856 | 1260
Devonshire Building | 2016-10-25 08:45 | 47314.7106 | 1299.996
Devonshire Building | 2016-10-25 09:00 | 47315.3206 | 2440.008
Devonshire Building | 2016-10-25 09:15 | 47315.6906 | 1479.996
Devonshire Building | 2016-10-25 09:30 | 47316.1406 | 1800
Devonshire Building | 2016-10-25 09:45 | 47316.5906 | 1800
Devonshire Building | 2016-10-25 10:00 | 47317.1456 | 2220.012
Devonshire Building | 2016-10-25 10:15 | 47317.6506 | 2019.996
Devonshire Building | 2016-10-25 10:30 | 47318.0106 | 1440
Devonshire Building | 2016-10-25 10:45 | 47318.3506 | 1360.008
Devonshire Building | 2016-10-25 11:00 | 47318.6806 | 1320.012
Devonshire Building | 2016-10-25 11:15 | 47319.0106 | 1320.012
Devonshire Building | 2016-10-25 11:30 | 47319.3456 | 1339.992
Devonshire Building | 2016-10-25 11:45 | 47320.0356 | 2760.012
Devonshire Building | 2016-10-25 12:00 | 47320.4806 | 1779.984
Devonshire Building | 2016-10-25 12:15 | 47320.9156 | 1739.988
Devonshire Building | 2016-10-25 12:30 | 47321.3406 | 1699.992
Devonshire Building | 2016-10-25 12:45 | 47321.7556 | 1659.996
Devonshire Building | 2016-10-25 13:00 | 47322.1606 | 1620
Devonshire Building | 2016-10-25 13:15 | 47322.7456 | 2340
Devonshire Building | 2016-10-25 13:30 | 47323.0956 | 1400.004
Devonshire Building | 2016-10-25 13:45 | 47323.4556 | 1440
Devonshire Building | 2016-10-25 14:00 | 47323.8056 | 1400.004
Devonshire Building | 2016-10-25 14:15 | 47324.1556 | 1400.004
Devonshire Building | 2016-10-25 14:30 | 47324.5006 | 1379.988
Devonshire Building | 2016-10-25 14:45 | 47324.8506 | 1400.004
Devonshire Building | 2016-10-25 15:00 | 47325.4806 | 2520
Devonshire Building | 2016-10-25 15:15 | 47325.8656 | 1540.008
Devonshire Building | 2016-10-25 15:30 | 47326.2556 | 1559.988
Devonshire Building | 2016-10-25 15:45 | 47326.6306 | 1500.012
Devonshire Building | 2016-10-25 16:00 | 47327.0006 | 1479.996
Devonshire Building | 2016-10-25 16:15 | 47327.3556 | 1419.984
Devonshire Building | 2016-10-25 16:30 | 47327.7156 | 1440
Devonshire Building | 2016-10-25 16:45 | 47328.3206 | 2419.992
Devonshire Building | 2016-10-25 17:00 | 47328.6406 | 1280.016
Devonshire Building | 2016-10-25 17:15 | 47328.9606 | 1280.016
Devonshire Building | 2016-10-25 17:30 | 47329.2806 | 1280.016
Devonshire Building | 2016-10-25 17:45 | 47329.5956 | 1260
Devonshire Building | 2016-10-25 18:00 | 47329.9156 | 1280.016
Devonshire Building | 2016-10-25 18:15 | 47330.2306 | 1260
Devonshire Building | 2016-10-25 18:30 | 47330.5506 | 1280.016
Devonshire Building | 2016-10-25 18:45 | 47330.8606 | 1239.984
Devonshire Building | 2016-10-25 19:00 | 47331.1756 | 1260
Devonshire Building | 2016-10-25 19:15 | 47331.4856 | 1239.984
Devonshire Building | 2016-10-25 19:30 | 47331.7956 | 1239.984
Devonshire Building | 2016-10-25 19:45 | 47332.1006 | 1220.004
Devonshire Building | 2016-10-25 20:00 | 47332.4106 | 1239.984
Devonshire Building | 2016-10-25 20:15 | 47332.7156 | 1220.004
Devonshire Building | 2016-10-25 20:30 | 47333.0256 | 1239.984
Devonshire Building | 2016-10-25 20:45 | 47333.3356 | 1239.984
Devonshire Building | 2016-10-25 21:00 | 47333.6506 | 1260
Devonshire Building | 2016-10-25 21:15 | 47333.9556 | 1220.004
Devonshire Building | 2016-10-25 21:30 | 47334.2656 | 1239.984
Devonshire Building | 2016-10-25 21:45 | 47334.5706 | 1220.004
Devonshire Building | 2016-10-25 22:00 | 47334.8756 | 1220.004
Devonshire Building | 2016-10-25 22:15 | 47335.1856 | 1239.984
Devonshire Building | 2016-10-25 22:30 | 47335.4906 | 1220.004
Devonshire Building | 2016-10-25 22:45 | 47335.8006 | 1239.984
Devonshire Building | 2016-10-25 23:00 | 47336.1106 | 1239.984
Devonshire Building | 2016-10-25 23:15 | 47336.4156 | 1220.004
Devonshire Building | 2016-10-25 23:30 | 47336.7306 | 1260
Devonshire Building | 2016-10-25 23:45 | 47337.0356 | 1220.004 | 1180.008
Devonshire Building | 2016-10-26 | 47337.3438 | 1239.984
Devonshire Building | 2016-10-26 00:15 | 47337.6588 | 1260
Devonshire Building | 2016-10-26 00:30 | 47337.9687 | 1239.984
Devonshire Building | 2016-10-26 00:45 | 47338.2787 | 1239.984
Devonshire Building | 2016-10-26 01:00 | 47338.5887 | 1239.984
Devonshire Building | 2016-10-26 01:15 | 47338.9037 | 1260
Devonshire Building | 2016-10-26 01:30 | 47339.2137 | 1239.984
Devonshire Building | 2016-10-26 01:45 | 47339.5287 | 1260
Devonshire Building | 2016-10-26 02:00 | 47339.8387 | 1239.984
Devonshire Building | 2016-10-26 02:15 | 47340.1537 | 1260
Devonshire Building | 2016-10-26 02:30 | 47340.4637 | 1239.984
Devonshire Building | 2016-10-26 02:45 | 47340.7737 | 1239.984
Devonshire Building | 2016-10-26 03:00 | 47341.0887 | 1260
Devonshire Building | 2016-10-26 03:15 | 47341.3987 | 1239.984
Devonshire Building | 2016-10-26 03:30 | 47341.7087 | 1239.984
Devonshire Building | 2016-10-26 03:45 | 47342.0187 | 1239.984
Devonshire Building | 2016-10-26 04:00 | 47342.3287 | 1239.984
Devonshire Building | 2016-10-26 04:15 | 47342.6387 | 1239.984
Devonshire Building | 2016-10-26 04:30 | 47342.9487 | 1239.984
Devonshire Building | 2016-10-26 04:45 | 47343.2587 | 1239.984
Devonshire Building | 2016-10-26 05:00 | 47343.5687 | 1239.984
Devonshire Building | 2016-10-26 05:15 | 47343.8787 | 1239.984
Devonshire Building | 2016-10-26 05:30 | 47344.1887 | 1239.984
Devonshire Building | 2016-10-26 05:45 | 47344.4987 | 1239.984
Devonshire Building | 2016-10-26 06:00 | 47344.8087 | 1239.984
Devonshire Building | 2016-10-26 06:15 | 47345.1137 | 1220.004
Devonshire Building | 2016-10-26 06:30 | 47345.4237 | 1239.984
Devonshire Building | 2016-10-26 06:45 | 47345.7287 | 1220.004
Devonshire Building | 2016-10-26 07:00 | 47346.2837 | 2220.012
Devonshire Building | 2016-10-26 07:15 | 47346.5837 | 1199.988
Devonshire Building | 2016-10-26 07:30 | 47346.8987 | 1260
Devonshire Building | 2016-10-26 07:45 | 47347.2087 | 1239.984
Devonshire Building | 2016-10-26 08:00 | 47347.5237 | 1260
Devonshire Building | 2016-10-26 08:15 | 47347.8487 | 1299.996
Devonshire Building | 2016-10-26 08:30 | 47348.1687 | 1280.016
Devonshire Building | 2016-10-26 08:45 | 47348.4887 | 1280.016
Devonshire Building | 2016-10-26 09:00 | 47348.8137 | 1299.996
Devonshire Building | 2016-10-26 09:15 | 47349.1487 | 1339.992
Devonshire Building | 2016-10-26 09:30 | 47349.7687 | 2480.004
Devonshire Building | 2016-10-26 09:45 | 47350.1437 | 1500.012
Devonshire Building | 2016-10-26 10:00 | 47350.5337 | 1559.988
Devonshire Building | 2016-10-26 10:15 | 47350.9037 | 1479.996
Devonshire Building | 2016-10-26 10:30 | 47351.2637 | 1440
Devonshire Building | 2016-10-26 10:45 | 47351.6137 | 1400.004
Devonshire Building | 2016-10-26 11:00 | 47352.2337 | 2480.004
Devonshire Building | 2016-10-26 11:15 | 47352.5587 | 1299.996
Devonshire Building | 2016-10-26 11:30 | 47352.8887 | 1320.012
Devonshire Building | 2016-10-26 11:45 | 47353.2137 | 1299.996
Devonshire Building | 2016-10-26 12:00 | 47353.5437 | 1320.012
Devonshire Building | 2016-10-26 12:15 | 47353.8837 | 1360.008
Devonshire Building | 2016-10-26 12:30 | 47354.2337 | 1400.004
Devonshire Building | 2016-10-26 12:45 | 47354.7087 | 1900.008
Devonshire Building | 2016-10-26 13:00 | 47355.1837 | 1900.008
Devonshire Building | 2016-10-26 13:15 | 47355.5437 | 1440
Devonshire Building | 2016-10-26 13:30 | 47355.9037 | 1440
Devonshire Building | 2016-10-26 13:45 | 47356.2687 | 1460.016
Devonshire Building | 2016-10-26 14:00 | 47356.6287 | 1440
Devonshire Building | 2016-10-26 14:15 | 47356.9837 | 1419.984
Devonshire Building | 2016-10-26 14:30 | 47357.3287 | 1379.988
Devonshire Building | 2016-10-26 14:45 | 47357.9587 | 2520
Devonshire Building | 2016-10-26 15:00 | 47358.3137 | 1419.984
Devonshire Building | 2016-10-26 15:15 | 47358.6587 | 1379.988
Devonshire Building | 2016-10-26 15:30 | 47359.0037 | 1379.988
Devonshire Building | 2016-10-26 15:45 | 47359.3437 | 1360.008
Devonshire Building | 2016-10-26 16:00 | 47359.6937 | 1400.004
Devonshire Building | 2016-10-26 16:15 | 47360.0537 | 1440
Devonshire Building | 2016-10-26 16:30 | 47360.4337 | 1519.992
Devonshire Building | 2016-10-26 16:45 | 47360.8137 | 1519.992
Devonshire Building | 2016-10-26 17:00 | 47361.1937 | 1519.992
Devonshire Building | 2016-10-26 17:15 | 47361.8187 | 2499.984
Devonshire Building | 2016-10-26 17:30 | 47362.1837 | 1460.016
Devonshire Building | 2016-10-26 17:45 | 47362.5387 | 1419.984
Devonshire Building | 2016-10-26 18:00 | 47362.8787 | 1360.008
Devonshire Building | 2016-10-26 18:15 | 47363.2137 | 1339.992
Devonshire Building | 2016-10-26 18:30 | 47363.5387 | 1299.996
Devonshire Building | 2016-10-26 18:45 | 47363.8637 | 1299.996
Devonshire Building | 2016-10-26 19:00 | 47364.1837 | 1280.016
Devonshire Building | 2016-10-26 19:15 | 47364.5037 | 1280.016
Devonshire Building | 2016-10-26 19:30 | 47364.8237 | 1280.016
Devonshire Building | 2016-10-26 19:45 | 47365.1387 | 1260
Devonshire Building | 2016-10-26 20:00 | 47365.4537 | 1260
Devonshire Building | 2016-10-26 20:15 | 47365.7687 | 1260
Devonshire Building | 2016-10-26 20:30 | 47366.0887 | 1280.016
Devonshire Building | 2016-10-26 20:45 | 47366.3987 | 1239.984
Devonshire Building | 2016-10-26 21:00 | 47366.7187 | 1280.016
Devonshire Building | 2016-10-26 21:15 | 47367.0287 | 1239.984
Devonshire Building | 2016-10-26 21:30 | 47367.3437 | 1260
Devonshire Building | 2016-10-26 21:45 | 47367.6537 | 1239.984
Devonshire Building | 2016-10-26 22:00 | 47367.9637 | 1239.984
Devonshire Building | 2016-10-26 22:15 | 47368.2787 | 1260
Devonshire Building | 2016-10-26 22:30 | 47368.5887 | 1239.984
Devonshire Building | 2016-10-26 22:45 | 47368.9037 | 1260
Devonshire Building | 2016-10-26 23:00 | 47369.2137 | 1239.984
Devonshire Building | 2016-10-26 23:15 | 47369.5287 | 1260
Devonshire Building | 2016-10-26 23:30 | 47369.8437 | 1260
Devonshire Building | 2016-10-26 23:45 | 47370.1537 | 1239.984 | 1199.988
Devonshire Building | 2016-10-27 | 47370.4688 | 1260
Devonshire Building | 2016-10-27 00:15 | 47370.7838 | 1260
Devonshire Building | 2016-10-27 00:30 | 47371.0987 | 1260
Devonshire Building | 2016-10-27 00:45 | 47371.4137 | 1260
Devonshire Building | 2016-10-27 01:00 | 47371.7288 | 1260
Devonshire Building | 2016-10-27 01:15 | 47372.0437 | 1260
Devonshire Building | 2016-10-27 01:30 | 47372.3587 | 1260
Devonshire Building | 2016-10-27 01:45 | 47372.6738 | 1260
Devonshire Building | 2016-10-27 02:00 | 47372.9887 | 1260
Devonshire Building | 2016-10-27 02:15 | 47373.3037 | 1260
Devonshire Building | 2016-10-27 02:30 | 47373.6188 | 1260
Devonshire Building | 2016-10-27 02:45 | 47373.9337 | 1260
Devonshire Building | 2016-10-27 03:00 | 47374.2437 | 1239.984
Devonshire Building | 2016-10-27 03:15 | 47374.5587 | 1260
Devonshire Building | 2016-10-27 03:30 | 47374.8737 | 1260
Devonshire Building | 2016-10-27 03:45 | 47375.1837 | 1239.984
Devonshire Building | 2016-10-27 04:00 | 47375.4987 | 1260
Devonshire Building | 2016-10-27 04:15 | 47375.8087 | 1239.984
Devonshire Building | 2016-10-27 04:30 | 47376.1187 | 1239.984
Devonshire Building | 2016-10-27 04:45 | 47376.4337 | 1260
Devonshire Building | 2016-10-27 05:00 | 47376.7437 | 1239.984
Devonshire Building | 2016-10-27 05:15 | 47377.0537 | 1239.984
Devonshire Building | 2016-10-27 05:30 | 47377.3637 | 1239.984
Devonshire Building | 2016-10-27 05:45 | 47377.6737 | 1239.984
Devonshire Building | 2016-10-27 06:00 | 47377.9837 | 1239.984
Devonshire Building | 2016-10-27 06:15 | 47378.2937 | 1239.984
Devonshire Building | 2016-10-27 06:30 | 47378.6087 | 1260
Devonshire Building | 2016-10-27 06:45 | 47378.9187 | 1239.984
Devonshire Building | 2016-10-27 07:00 | 47379.2287 | 1239.984
Devonshire Building | 2016-10-27 07:15 | 47379.5337 | 1220.004
Devonshire Building | 2016-10-27 07:30 | 47379.8487 | 1260
Devonshire Building | 2016-10-27 07:45 | 47380.1587 | 1239.984
Devonshire Building | 2016-10-27 08:00 | 47380.4687 | 1239.984
Devonshire Building | 2016-10-27 08:15 | 47380.9837 | 2059.992
Devonshire Building | 2016-10-27 08:30 | 47381.3337 | 1400.004
Devonshire Building | 2016-10-27 08:45 | 47381.6387 | 1220.004
Devonshire Building | 2016-10-27 09:00 | 47381.9687 | 1320.012
Devonshire Building | 2016-10-27 09:15 | 47382.2787 | 1239.984
Devonshire Building | 2016-10-27 09:30 | 47382.5887 | 1239.984
Devonshire Building | 2016-10-27 09:45 | 47382.8987 | 1239.984
Devonshire Building | 2016-10-27 10:00 | 47383.4637 | 2260.008
Devonshire Building | 2016-10-27 10:15 | 47383.7787 | 1260
Devonshire Building | 2016-10-27 10:30 | 47384.1537 | 1500.012
Devonshire Building | 2016-10-27 10:45 | 47384.5937 | 1760.004
Devonshire Building | 2016-10-27 11:00 | 47385.0337 | 1760.004
Devonshire Building | 2016-10-27 11:15 | 47385.4687 | 1739.988
Devonshire Building | 2016-10-27 11:30 | 47386.1787 | 2840.004
Devonshire Building | 2016-10-27 11:45 | 47386.5987 | 1680.012
Devonshire Building | 2016-10-27 12:00 | 47386.9937 | 1580.004
Devonshire Building | 2016-10-27 12:15 | 47387.3787 | 1540.008
Devonshire Building | 2016-10-27 12:30 | 47387.7587 | 1519.992
Devonshire Building | 2016-10-27 12:45 | 47388.1287 | 1479.996
Devonshire Building | 2016-10-27 13:00 | 47388.4887 | 1440
Devonshire Building | 2016-10-27 13:15 | 47388.8487 | 1440
Devonshire Building | 2016-10-27 13:30 | 47389.4787 | 2520
Devonshire Building | 2016-10-27 13:45 | 47389.8287 | 1400.004
Devonshire Building | 2016-10-27 14:00 | 47390.1737 | 1379.988
Devonshire Building | 2016-10-27 14:15 | 47390.5237 | 1400.004
Devonshire Building | 2016-10-27 14:30 | 47390.8787 | 1419.984
Devonshire Building | 2016-10-27 14:45 | 47391.2287 | 1400.004
Devonshire Building | 2016-10-27 15:00 | 47391.5887 | 1440
Devonshire Building | 2016-10-27 15:15 | 47391.9337 | 1379.988
Devonshire Building | 2016-10-27 15:30 | 47392.5437 | 2440.008
Devonshire Building | 2016-10-27 15:45 | 47392.9087 | 1460.016
Devonshire Building | 2016-10-27 16:00 | 47393.2737 | 1460.016
Devonshire Building | 2016-10-27 16:15 | 47393.6387 | 1460.016
Devonshire Building | 2016-10-27 16:30 | 47394.0037 | 1460.016
Devonshire Building | 2016-10-27 16:45 | 47394.3637 | 1440
Devonshire Building | 2016-10-27 17:00 | 47394.7237 | 1440
Devonshire Building | 2016-10-27 17:15 | 47395.0737 | 1400.004
Devonshire Building | 2016-10-27 17:30 | 47395.4287 | 1419.984
Devonshire Building | 2016-10-27 17:45 | 47395.7787 | 1400.004
Devonshire Building | 2016-10-27 18:00 | 47396.1287 | 1400.004
Devonshire Building | 2016-10-27 18:15 | 47396.5737 | 1779.984
Devonshire Building | 2016-10-27 18:30 | 47397.0287 | 1820.016
Devonshire Building | 2016-10-27 18:45 | 47397.3487 | 1280.016
Devonshire Building | 2016-10-27 19:00 | 47397.6687 | 1280.016
Devonshire Building | 2016-10-27 19:15 | 47397.9937 | 1299.996
Devonshire Building | 2016-10-27 19:30 | 47398.3137 | 1280.016
Devonshire Building | 2016-10-27 19:45 | 47398.6337 | 1280.016
Devonshire Building | 2016-10-27 20:00 | 47398.9537 | 1280.016
Devonshire Building | 2016-10-27 20:15 | 47399.2737 | 1280.016
Devonshire Building | 2016-10-27 20:30 | 47399.5937 | 1280.016
Devonshire Building | 2016-10-27 20:45 | 47399.9137 | 1280.016
Devonshire Building | 2016-10-27 21:00 | 47400.2387 | 1299.996
Devonshire Building | 2016-10-27 21:15 | 47400.5537 | 1260
Devonshire Building | 2016-10-27 21:30 | 47400.8637 | 1239.984
Devonshire Building | 2016-10-27 21:45 | 47401.1787 | 1260
Devonshire Building | 2016-10-27 22:00 | 47401.4887 | 1239.984
Devonshire Building | 2016-10-27 22:15 | 47401.8037 | 1260
Devonshire Building | 2016-10-27 22:30 | 47402.1137 | 1239.984
Devonshire Building | 2016-10-27 22:45 | 47402.4287 | 1260
Devonshire Building | 2016-10-27 23:00 | 47402.7437 | 1260
Devonshire Building | 2016-10-27 23:15 | 47403.0587 | 1260
Devonshire Building | 2016-10-27 23:30 | 47403.3737 | 1260
Devonshire Building | 2016-10-27 23:45 | 47403.6887 | 1260 | 1220.004
Devonshire Building | 2016-10-28 | 47404.0078 | 1280.016
Devonshire Building | 2016-10-28 00:15 | 47404.3228 | 1260
Devonshire Building | 2016-10-28 00:30 | 47404.6378 | 1260
Devonshire Building | 2016-10-28 00:45 | 47404.9528 | 1260
Devonshire Building | 2016-10-28 01:00 | 47405.2678 | 1260
Devonshire Building | 2016-10-28 01:15 | 47405.5878 | 1280.016
Devonshire Building | 2016-10-28 01:30 | 47405.9028 | 1260
Devonshire Building | 2016-10-28 01:45 | 47406.2178 | 1260
Devonshire Building | 2016-10-28 02:00 | 47406.5328 | 1260
Devonshire Building | 2016-10-28 02:15 | 47406.8478 | 1260
Devonshire Building | 2016-10-28 02:30 | 47407.1628 | 1260
Devonshire Building | 2016-10-28 02:45 | 47407.4778 | 1260
Devonshire Building | 2016-10-28 03:00 | 47407.7928 | 1260
Devonshire Building | 2016-10-28 03:15 | 47408.1078 | 1260
Devonshire Building | 2016-10-28 03:30 | 47408.4228 | 1260
Devonshire Building | 2016-10-28 03:45 | 47408.7378 | 1260
Devonshire Building | 2016-10-28 04:00 | 47409.0528 | 1260
Devonshire Building | 2016-10-28 04:15 | 47409.3678 | 1260
Devonshire Building | 2016-10-28 04:30 | 47409.6828 | 1260
Devonshire Building | 2016-10-28 04:45 | 47409.9978 | 1260
Devonshire Building | 2016-10-28 05:00 | 47410.3128 | 1260
Devonshire Building | 2016-10-28 05:15 | 47410.6278 | 1260
Devonshire Building | 2016-10-28 05:30 | 47410.9428 | 1260
Devonshire Building | 2016-10-28 05:45 | 47411.2528 | 1239.984
Devonshire Building | 2016-10-28 06:00 | 47411.5678 | 1260
Devonshire Building | 2016-10-28 06:15 | 47411.8778 | 1239.984
Devonshire Building | 2016-10-28 06:30 | 47412.1928 | 1260
Devonshire Building | 2016-10-28 06:45 | 47412.5078 | 1260
Devonshire Building | 2016-10-28 07:00 | 47412.8178 | 1239.984
Devonshire Building | 2016-10-28 07:15 | 47413.1278 | 1239.984
Devonshire Building | 2016-10-28 07:30 | 47413.6178 | 1959.984
Devonshire Building | 2016-10-28 07:45 | 47414.0228 | 1620
Devonshire Building | 2016-10-28 08:00 | 47414.3328 | 1239.984
Devonshire Building | 2016-10-28 08:15 | 47414.6378 | 1220.004
Devonshire Building | 2016-10-28 08:30 | 47414.9528 | 1260
Devonshire Building | 2016-10-28 08:45 | 47415.2728 | 1280.016
Devonshire Building | 2016-10-28 09:00 | 47415.5978 | 1299.996
Devonshire Building | 2016-10-28 09:15 | 47415.9778 | 1519.992
Devonshire Building | 2016-10-28 09:30 | 47416.7178 | 2959.992
Devonshire Building | 2016-10-28 09:45 | 47417.1528 | 1739.988
Devonshire Building | 2016-10-28 10:00 | 47417.5478 | 1580.004
Devonshire Building | 2016-10-28 10:15 | 47417.9178 | 1479.996
Devonshire Building | 2016-10-28 10:30 | 47418.2728 | 1419.984
Devonshire Building | 2016-10-28 10:45 | 47418.6128 | 1360.008
Devonshire Building | 2016-10-28 11:00 | 47419.0128 | 1599.984
Devonshire Building | 2016-10-28 11:15 | 47419.5178 | 2019.996
Devonshire Building | 2016-10-28 11:30 | 47419.8278 | 1239.984
Devonshire Building | 2016-10-28 11:45 | 47420.1478 | 1280.016
Devonshire Building | 2016-10-28 12:00 | 47420.4678 | 1280.016
Devonshire Building | 2016-10-28 12:15 | 47420.7928 | 1299.996
Devonshire Building | 2016-10-28 12:30 | 47421.1378 | 1379.988
Devonshire Building | 2016-10-28 12:45 | 47421.4978 | 1440
Devonshire Building | 2016-10-28 13:00 | 47422.1478 | 2599.992
Devonshire Building | 2016-10-28 13:15 | 47422.5378 | 1559.988
Devonshire Building | 2016-10-28 13:30 | 47422.9228 | 1540.008
Devonshire Building | 2016-10-28 13:45 | 47423.3028 | 1519.992
Devonshire Building | 2016-10-28 14:00 | 47423.6928 | 1559.988
Devonshire Building | 2016-10-28 14:15 | 47424.0778 | 1540.008
Devonshire Building | 2016-10-28 14:30 | 47424.4478 | 1479.996
Devonshire Building | 2016-10-28 14:45 | 47424.8228 | 1500.012
Devonshire Building | 2016-10-28 15:00 | 47425.1928 | 1479.996
Devonshire Building | 2016-10-28 15:15 | 47425.8228 | 2520
Devonshire Building | 2016-10-28 15:30 | 47426.1928 | 1479.996
Devonshire Building | 2016-10-28 15:45 | 47426.5678 | 1500.012
Devonshire Building | 2016-10-28 16:00 | 47426.9378 | 1479.996
Devonshire Building | 2016-10-28 16:15 | 47427.2928 | 1419.984
Devonshire Building | 2016-10-28 16:30 | 47427.6428 | 1400.004
Devonshire Building | 2016-10-28 16:45 | 47427.9928 | 1400.004
Devonshire Building | 2016-10-28 17:00 | 47428.3328 | 1360.008
Devonshire Building | 2016-10-28 17:15 | 47428.6678 | 1339.992
Devonshire Building | 2016-10-28 17:30 | 47428.9978 | 1320.012
Devonshire Building | 2016-10-28 17:45 | 47429.3228 | 1299.996
Devonshire Building | 2016-10-28 18:00 | 47429.6528 | 1320.012
Devonshire Building | 2016-10-28 18:15 | 47429.9778 | 1299.996
Devonshire Building | 2016-10-28 18:30 | 47430.5578 | 2319.984
Devonshire Building | 2016-10-28 18:45 | 47430.8728 | 1260
Devonshire Building | 2016-10-28 19:00 | 47431.1928 | 1280.016
Devonshire Building | 2016-10-28 19:15 | 47431.5078 | 1260
Devonshire Building | 2016-10-28 19:30 | 47431.8228 | 1260
Devonshire Building | 2016-10-28 19:45 | 47432.1428 | 1280.016
Devonshire Building | 2016-10-28 20:00 | 47432.4628 | 1280.016
Devonshire Building | 2016-10-28 20:15 | 47432.7828 | 1280.016
Devonshire Building | 2016-10-28 20:30 | 47433.1028 | 1280.016
Devonshire Building | 2016-10-28 20:45 | 47433.4228 | 1280.016
Devonshire Building | 2016-10-28 21:00 | 47433.7478 | 1299.996
Devonshire Building | 2016-10-28 21:15 | 47434.0628 | 1260
Devonshire Building | 2016-10-28 21:30 | 47434.3778 | 1260
Devonshire Building | 2016-10-28 21:45 | 47434.6928 | 1260
Devonshire Building | 2016-10-28 22:00 | 47435.0078 | 1260
Devonshire Building | 2016-10-28 22:15 | 47435.3228 | 1260
Devonshire Building | 2016-10-28 22:30 | 47435.6378 | 1260
Devonshire Building | 2016-10-28 22:45 | 47435.9478 | 1239.984
Devonshire Building | 2016-10-28 23:00 | 47436.2628 | 1260
Devonshire Building | 2016-10-28 23:15 | 47436.5778 | 1260
Devonshire Building | 2016-10-28 23:30 | 47436.8928 | 1260
Devonshire Building | 2016-10-28 23:45 | 47437.2028 | 1239.984 | 1220.004
Devonshire Building | 2016-10-29 | 47437.5195 | 1260
Devonshire Building | 2016-10-29 00:15 | 47437.8345 | 1260
Devonshire Building | 2016-10-29 00:30 | 47438.1445 | 1239.984
Devonshire Building | 2016-10-29 00:45 | 47438.4595 | 1260
Devonshire Building | 2016-10-29 01:00 | 47438.7745 | 1260
Devonshire Building | 2016-10-29 01:15 | 47439.0895 | 1260
Devonshire Building | 2016-10-29 01:30 | 47439.3995 | 1239.984
Devonshire Building | 2016-10-29 01:45 | 47439.7145 | 1260
Devonshire Building | 2016-10-29 02:00 | 47440.0245 | 1239.984
Devonshire Building | 2016-10-29 02:15 | 47440.3395 | 1260
Devonshire Building | 2016-10-29 02:30 | 47440.6495 | 1239.984
Devonshire Building | 2016-10-29 02:45 | 47440.9645 | 1260
Devonshire Building | 2016-10-29 03:00 | 47441.2745 | 1239.984
Devonshire Building | 2016-10-29 03:15 | 47441.5895 | 1260
Devonshire Building | 2016-10-29 03:30 | 47441.8995 | 1239.984
Devonshire Building | 2016-10-29 03:45 | 47442.2145 | 1260
Devonshire Building | 2016-10-29 04:00 | 47442.7695 | 2220.012
Devonshire Building | 2016-10-29 04:15 | 47443.0795 | 1239.984
Devonshire Building | 2016-10-29 04:30 | 47443.3895 | 1239.984
Devonshire Building | 2016-10-29 04:45 | 47443.7045 | 1260
Devonshire Building | 2016-10-29 05:00 | 47444.0145 | 1239.984
Devonshire Building | 2016-10-29 05:15 | 47444.3295 | 1260
Devonshire Building | 2016-10-29 05:30 | 47444.6395 | 1239.984
Devonshire Building | 2016-10-29 05:45 | 47444.9495 | 1239.984
Devonshire Building | 2016-10-29 06:00 | 47445.2595 | 1239.984
Devonshire Building | 2016-10-29 06:15 | 47445.5695 | 1239.984
Devonshire Building | 2016-10-29 06:30 | 47445.8795 | 1239.984
Devonshire Building | 2016-10-29 06:45 | 47446.1895 | 1239.984
Devonshire Building | 2016-10-29 07:00 | 47446.4945 | 1220.004
Devonshire Building | 2016-10-29 07:15 | 47446.8045 | 1239.984
Devonshire Building | 2016-10-29 07:30 | 47447.1095 | 1220.004
Devonshire Building | 2016-10-29 07:45 | 47447.4145 | 1220.004
Devonshire Building | 2016-10-29 08:00 | 47447.7195 | 1220.004
Devonshire Building | 2016-10-29 08:15 | 47448.0245 | 1220.004
Devonshire Building | 2016-10-29 08:30 | 47448.3295 | 1220.004
Devonshire Building | 2016-10-29 08:45 | 47448.6345 | 1220.004
Devonshire Building | 2016-10-29 09:00 | 47448.9495 | 1260
Devonshire Building | 2016-10-29 09:15 | 47449.2495 | 1199.988
Devonshire Building | 2016-10-29 09:30 | 47449.5545 | 1220.004
Devonshire Building | 2016-10-29 09:45 | 47449.8595 | 1220.004
Devonshire Building | 2016-10-29 10:00 | 47450.1645 | 1220.004
Devonshire Building | 2016-10-29 10:15 | 47450.4695 | 1220.004
Devonshire Building | 2016-10-29 10:30 | 47450.7745 | 1220.004
Devonshire Building | 2016-10-29 10:45 | 47451.0745 | 1199.988
Devonshire Building | 2016-10-29 11:00 | 47451.3795 | 1220.004
Devonshire Building | 2016-10-29 11:15 | 47451.6845 | 1220.004
Devonshire Building | 2016-10-29 11:30 | 47451.9895 | 1220.004
Devonshire Building | 2016-10-29 11:45 | 47452.2945 | 1220.004
Devonshire Building | 2016-10-29 12:00 | 47452.5995 | 1220.004
Devonshire Building | 2016-10-29 12:15 | 47452.9045 | 1220.004
Devonshire Building | 2016-10-29 12:30 | 47453.2195 | 1260
Devonshire Building | 2016-10-29 12:45 | 47453.5245 | 1220.004
Devonshire Building | 2016-10-29 13:00 | 47453.8295 | 1220.004
Devonshire Building | 2016-10-29 13:15 | 47454.1345 | 1220.004
Devonshire Building | 2016-10-29 13:30 | 47454.4545 | 1280.016
Devonshire Building | 2016-10-29 13:45 | 47455.0195 | 2260.008
Devonshire Building | 2016-10-29 14:00 | 47455.3445 | 1299.996
Devonshire Building | 2016-10-29 14:15 | 47455.6695 | 1299.996
Devonshire Building | 2016-10-29 14:30 | 47455.9945 | 1299.996
Devonshire Building | 2016-10-29 14:45 | 47456.3145 | 1280.016
Devonshire Building | 2016-10-29 15:00 | 47456.6395 | 1299.996
Devonshire Building | 2016-10-29 15:15 | 47456.9595 | 1280.016
Devonshire Building | 2016-10-29 15:30 | 47457.2845 | 1299.996
Devonshire Building | 2016-10-29 15:45 | 47457.6045 | 1280.016
Devonshire Building | 2016-10-29 16:00 | 47457.9195 | 1260
Devonshire Building | 2016-10-29 16:15 | 47458.2245 | 1220.004
Devonshire Building | 2016-10-29 16:30 | 47458.5295 | 1220.004
Devonshire Building | 2016-10-29 16:45 | 47458.8295 | 1199.988
Devonshire Building | 2016-10-29 17:00 | 47459.1345 | 1220.004
Devonshire Building | 2016-10-29 17:15 | 47459.4395 | 1220.004
Devonshire Building | 2016-10-29 17:30 | 47459.7445 | 1220.004
Devonshire Building | 2016-10-29 17:45 | 47460.0445 | 1199.988
Devonshire Building | 2016-10-29 18:00 | 47460.3545 | 1239.984
Devonshire Building | 2016-10-29 18:15 | 47460.6545 | 1199.988
Devonshire Building | 2016-10-29 18:30 | 47460.9595 | 1220.004
Devonshire Building | 2016-10-29 18:45 | 47461.2695 | 1239.984
Devonshire Building | 2016-10-29 19:00 | 47461.5695 | 1199.988
Devonshire Building | 2016-10-29 19:15 | 47461.8745 | 1220.004
Devonshire Building | 2016-10-29 19:30 | 47462.1795 | 1220.004
Devonshire Building | 2016-10-29 19:45 | 47462.4845 | 1220.004
Devonshire Building | 2016-10-29 20:00 | 47462.7895 | 1220.004
Devonshire Building | 2016-10-29 20:15 | 47463.0995 | 1239.984
Devonshire Building | 2016-10-29 20:30 | 47463.4045 | 1220.004
Devonshire Building | 2016-10-29 20:45 | 47463.7095 | 1220.004
Devonshire Building | 2016-10-29 21:00 | 47464.0395 | 1320.012
Devonshire Building | 2016-10-29 21:15 | 47464.3445 | 1220.004
Devonshire Building | 2016-10-29 21:30 | 47464.6495 | 1220.004
Devonshire Building | 2016-10-29 21:45 | 47464.9595 | 1239.984
Devonshire Building | 2016-10-29 22:00 | 47465.2645 | 1220.004
Devonshire Building | 2016-10-29 22:15 | 47465.5695 | 1220.004
Devonshire Building | 2016-10-29 22:30 | 47466.1195 | 2199.996
Devonshire Building | 2016-10-29 22:45 | 47466.4245 | 1220.004
Devonshire Building | 2016-10-29 23:00 | 47466.7345 | 1239.984
Devonshire Building | 2016-10-29 23:15 | 47467.0395 | 1220.004
Devonshire Building | 2016-10-29 23:30 | 47467.3495 | 1239.984
Devonshire Building | 2016-10-29 23:45 | 47467.6545 | 1220.004 | 1199.988
Devonshire Building | 2016-10-30 | 47467.9648 | 1239.984
Devonshire Building | 2016-10-30 00:15 | 47468.2748 | 1239.984
Devonshire Building | 2016-10-30 00:30 | 47468.5848 | 1239.984
Devonshire Building | 2016-10-30 00:45 | 47468.8898 | 1220.004
Devonshire Building | 2016-10-30 01:00 | 47469.1998 | 1239.984
Devonshire Building | 2016-10-30 01:15 | 47469.5048 | 1220.004
Devonshire Building | 2016-10-30 01:30 | 47469.8148 | 1239.984
Devonshire Building | 2016-10-30 01:45 | 47470.1198 | 1220.004
Devonshire Building | 2016-10-30 02:00 | 47470.4298 | 1239.984
Devonshire Building | 2016-10-30 02:15 | 47470.7348 | 1220.004
Devonshire Building | 2016-10-30 02:30 | 47471.0448 | 1239.984
Devonshire Building | 2016-10-30 02:45 | 47471.3498 | 1220.004
Devonshire Building | 2016-10-30 03:00 | 47471.6598 | 1239.984
Devonshire Building | 2016-10-30 03:15 | 47471.9648 | 1220.004
Devonshire Building | 2016-10-30 03:30 | 47472.2748 | 1239.984
Devonshire Building | 2016-10-30 03:45 | 47472.5798 | 1220.004
Devonshire Building | 2016-10-30 04:00 | 47472.8898 | 1239.984
Devonshire Building | 2016-10-30 04:15 | 47473.1998 | 1239.984
Devonshire Building | 2016-10-30 04:30 | 47473.5048 | 1220.004
Devonshire Building | 2016-10-30 04:45 | 47473.8148 | 1239.984
Devonshire Building | 2016-10-30 05:00 | 47474.1248 | 1239.984
Devonshire Building | 2016-10-30 05:15 | 47474.4348 | 1239.984
Devonshire Building | 2016-10-30 05:30 | 47474.7448 | 1239.984
Devonshire Building | 2016-10-30 05:45 | 47475.0498 | 1220.004
Devonshire Building | 2016-10-30 06:00 | 47475.3598 | 1239.984
Devonshire Building | 2016-10-30 06:15 | 47475.6698 | 1239.984
Devonshire Building | 2016-10-30 06:30 | 47475.9798 | 1239.984
Devonshire Building | 2016-10-30 06:45 | 47476.2848 | 1220.004
Devonshire Building | 2016-10-30 07:00 | 47476.5998 | 1260
Devonshire Building | 2016-10-30 07:15 | 47476.9048 | 1220.004
Devonshire Building | 2016-10-30 07:30 | 47477.2148 | 1239.984
Devonshire Building | 2016-10-30 07:45 | 47477.5198 | 1220.004
Devonshire Building | 2016-10-30 08:00 | 47477.8248 | 1220.004
Devonshire Building | 2016-10-30 08:15 | 47478.1298 | 1220.004
Devonshire Building | 2016-10-30 08:30 | 47478.4348 | 1220.004
Devonshire Building | 2016-10-30 08:45 | 47478.7398 | 1220.004
Devonshire Building | 2016-10-30 09:00 | 47479.0448 | 1220.004
Devonshire Building | 2016-10-30 09:15 | 47479.3448 | 1199.988
Devonshire Building | 2016-10-30 09:30 | 47479.6498 | 1220.004
Devonshire Building | 2016-10-30 09:45 | 47479.9498 | 1199.988
Devonshire Building | 2016-10-30 10:00 | 47480.2498 | 1199.988
Devonshire Building | 2016-10-30 10:15 | 47480.5548 | 1220.004
Devonshire Building | 2016-10-30 10:30 | 47480.8548 | 1199.988
Devonshire Building | 2016-10-30 10:45 | 47481.1548 | 1199.988
Devonshire Building | 2016-10-30 11:00 | 47481.4598 | 1220.004
Devonshire Building | 2016-10-30 11:15 | 47481.7598 | 1199.988
Devonshire Building | 2016-10-30 11:30 | 47482.1948 | 1739.988
Devonshire Building | 2016-10-30 11:45 | 47482.5998 | 1620
Devonshire Building | 2016-10-30 12:00 | 47482.8998 | 1199.988
Devonshire Building | 2016-10-30 12:15 | 47483.2048 | 1220.004
Devonshire Building | 2016-10-30 12:30 | 47483.5048 | 1199.988
Devonshire Building | 2016-10-30 12:45 | 47483.8048 | 1199.988
Devonshire Building | 2016-10-30 13:00 | 47484.1098 | 1220.004
Devonshire Building | 2016-10-30 13:15 | 47484.4148 | 1220.004
Devonshire Building | 2016-10-30 13:30 | 47484.7248 | 1239.984
Devonshire Building | 2016-10-30 13:45 | 47485.0448 | 1280.016
Devonshire Building | 2016-10-30 14:00 | 47485.3648 | 1280.016
Devonshire Building | 2016-10-30 14:15 | 47485.6898 | 1299.996
Devonshire Building | 2016-10-30 14:30 | 47486.0098 | 1280.016
Devonshire Building | 2016-10-30 14:45 | 47486.3298 | 1280.016
Devonshire Building | 2016-10-30 15:00 | 47486.6648 | 1339.992
Devonshire Building | 2016-10-30 15:15 | 47486.9848 | 1280.016
Devonshire Building | 2016-10-30 15:30 | 47487.3048 | 1280.016
Devonshire Building | 2016-10-30 15:45 | 47487.6248 | 1280.016
Devonshire Building | 2016-10-30 16:00 | 47487.9298 | 1220.004
Devonshire Building | 2016-10-30 16:15 | 47488.2348 | 1220.004
Devonshire Building | 2016-10-30 16:30 | 47488.5398 | 1220.004
Devonshire Building | 2016-10-30 16:45 | 47488.8448 | 1220.004
Devonshire Building | 2016-10-30 17:00 | 47489.1498 | 1220.004
Devonshire Building | 2016-10-30 17:15 | 47489.4498 | 1199.988
Devonshire Building | 2016-10-30 17:30 | 47489.7548 | 1220.004
Devonshire Building | 2016-10-30 17:45 | 47490.0598 | 1220.004
Devonshire Building | 2016-10-30 18:00 | 47490.3648 | 1220.004
Devonshire Building | 2016-10-30 18:15 | 47490.6648 | 1199.988
Devonshire Building | 2016-10-30 18:30 | 47490.9648 | 1199.988
Devonshire Building | 2016-10-30 18:45 | 47491.2648 | 1199.988
Devonshire Building | 2016-10-30 19:00 | 47491.5698 | 1220.004
Devonshire Building | 2016-10-30 19:15 | 47491.8698 | 1199.988
Devonshire Building | 2016-10-30 19:30 | 47492.1748 | 1220.004
Devonshire Building | 2016-10-30 19:45 | 47492.4748 | 1199.988
Devonshire Building | 2016-10-30 20:00 | 47492.7798 | 1220.004
Devonshire Building | 2016-10-30 20:15 | 47493.0798 | 1199.988
Devonshire Building | 2016-10-30 20:30 | 47493.3848 | 1220.004
Devonshire Building | 2016-10-30 20:45 | 47493.6898 | 1220.004
Devonshire Building | 2016-10-30 21:00 | 47493.9948 | 1220.004
Devonshire Building | 2016-10-30 21:15 | 47494.2948 | 1199.988
Devonshire Building | 2016-10-30 21:30 | 47494.5998 | 1220.004
Devonshire Building | 2016-10-30 21:45 | 47494.9048 | 1220.004
Devonshire Building | 2016-10-30 22:00 | 47495.4648 | 2239.992
Devonshire Building | 2016-10-30 22:15 | 47495.7648 | 1199.988
Devonshire Building | 2016-10-30 22:30 | 47496.0698 | 1220.004
Devonshire Building | 2016-10-30 22:45 | 47496.3748 | 1220.004
Devonshire Building | 2016-10-30 23:00 | 47496.6848 | 1239.984
Devonshire Building | 2016-10-30 23:15 | 47496.9898 | 1220.004
Devonshire Building | 2016-10-30 23:30 | 47497.2948 | 1220.004
Devonshire Building | 2016-10-30 23:45 | 47497.5998 | 1220.004 | 1199.988
Devonshire Building | 2016-10-31 | 47497.9062 | 1220.004
Devonshire Building | 2016-10-31 00:15 | 47498.2162 | 1239.984
Devonshire Building | 2016-10-31 00:30 | 47498.5212 | 1220.004
Devonshire Building | 2016-10-31 00:45 | 47498.8312 | 1239.984
Devonshire Building | 2016-10-31 01:00 | 47499.1362 | 1220.004
Devonshire Building | 2016-10-31 01:15 | 47499.4462 | 1239.984
Devonshire Building | 2016-10-31 01:30 | 47499.7512 | 1220.004
Devonshire Building | 2016-10-31 01:45 | 47500.0612 | 1239.984
Devonshire Building | 2016-10-31 02:00 | 47500.3712 | 1239.984
Devonshire Building | 2016-10-31 02:15 | 47500.6762 | 1220.004
Devonshire Building | 2016-10-31 02:30 | 47500.9862 | 1239.984
Devonshire Building | 2016-10-31 02:45 | 47501.2912 | 1220.004
Devonshire Building | 2016-10-31 03:00 | 47501.6012 | 1239.984
Devonshire Building | 2016-10-31 03:15 | 47501.9062 | 1220.004
Devonshire Building | 2016-10-31 03:30 | 47502.2162 | 1239.984
Devonshire Building | 2016-10-31 03:45 | 47502.5212 | 1220.004
Devonshire Building | 2016-10-31 04:00 | 47502.8312 | 1239.984
Devonshire Building | 2016-10-31 04:15 | 47503.1362 | 1220.004
Devonshire Building | 2016-10-31 04:30 | 47503.4412 | 1220.004
Devonshire Building | 2016-10-31 04:45 | 47503.7512 | 1239.984
Devonshire Building | 2016-10-31 05:00 | 47504.0562 | 1220.004
Devonshire Building | 2016-10-31 05:15 | 47504.3662 | 1239.984
Devonshire Building | 2016-10-31 05:30 | 47504.6712 | 1220.004
Devonshire Building | 2016-10-31 05:45 | 47504.9762 | 1220.004
Devonshire Building | 2016-10-31 06:00 | 47505.2862 | 1239.984
Devonshire Building | 2016-10-31 06:15 | 47505.5912 | 1220.004
Devonshire Building | 2016-10-31 06:30 | 47505.8962 | 1220.004
Devonshire Building | 2016-10-31 06:45 | 47506.2012 | 1220.004
Devonshire Building | 2016-10-31 07:00 | 47506.5062 | 1220.004
Devonshire Building | 2016-10-31 07:15 | 47506.8062 | 1199.988
Devonshire Building | 2016-10-31 07:30 | 47507.1112 | 1220.004
Devonshire Building | 2016-10-31 07:45 | 47507.4362 | 1299.996
Devonshire Building | 2016-10-31 08:00 | 47507.7362 | 1199.988
Devonshire Building | 2016-10-31 08:15 | 47508.2212 | 1940.004
Devonshire Building | 2016-10-31 08:30 | 47508.5962 | 1500.012
Devonshire Building | 2016-10-31 08:45 | 47508.9162 | 1280.016
Devonshire Building | 2016-10-31 09:00 | 47509.2462 | 1320.012
Devonshire Building | 2016-10-31 09:15 | 47509.5512 | 1220.004
Devonshire Building | 2016-10-31 09:30 | 47509.8562 | 1220.004
Devonshire Building | 2016-10-31 09:45 | 47510.1612 | 1220.004
Devonshire Building | 2016-10-31 10:00 | 47510.4712 | 1239.984
Devonshire Building | 2016-10-31 10:15 | 47511.0412 | 2279.988
Devonshire Building | 2016-10-31 10:30 | 47511.3662 | 1299.996
Devonshire Building | 2016-10-31 10:45 | 47511.7112 | 1379.988
Devonshire Building | 2016-10-31 11:00 | 47512.1312 | 1680.012
Devonshire Building | 2016-10-31 11:15 | 47512.5762 | 1779.984
Devonshire Building | 2016-10-31 11:30 | 47513.2662 | 2760.012
Devonshire Building | 2016-10-31 11:45 | 47513.7162 | 1800
Devonshire Building | 2016-10-31 12:00 | 47514.1762 | 1839.996
Devonshire Building | 2016-10-31 12:15 | 47514.6162 | 1760.004
Devonshire Building | 2016-10-31 12:30 | 47515.0362 | 1680.012
Devonshire Building | 2016-10-31 12:45 | 47515.7012 | 2660.004
Devonshire Building | 2016-10-31 13:00 | 47516.0762 | 1500.012
Devonshire Building | 2016-10-31 13:15 | 47516.4462 | 1479.996
Devonshire Building | 2016-10-31 13:30 | 47516.8112 | 1460.016
Devonshire Building | 2016-10-31 13:45 | 47517.1662 | 1419.984
Devonshire Building | 2016-10-31 14:00 | 47517.5162 | 1400.004
Devonshire Building | 2016-10-31 14:15 | 47518.1312 | 2459.988
Devonshire Building | 2016-10-31 14:30 | 47518.4562 | 1299.996
Devonshire Building | 2016-10-31 14:45 | 47518.7812 | 1299.996
Devonshire Building | 2016-10-31 15:00 | 47519.1012 | 1280.016
Devonshire Building | 2016-10-31 15:15 | 47519.4262 | 1299.996
Devonshire Building | 2016-10-31 15:30 | 47519.8912 | 1860.012
Devonshire Building | 2016-10-31 15:45 | 47520.3862 | 1980
Devonshire Building | 2016-10-31 16:00 | 47520.7512 | 1460.016
Devonshire Building | 2016-10-31 16:15 | 47521.1262 | 1500.012
Devonshire Building | 2016-10-31 16:30 | 47521.4912 | 1460.016
Devonshire Building | 2016-10-31 16:45 | 47521.8662 | 1500.012
Devonshire Building | 2016-10-31 17:00 | 47522.2262 | 1440
Devonshire Building | 2016-10-31 17:15 | 47522.8562 | 2520
Devonshire Building | 2016-10-31 17:30 | 47523.1962 | 1360.008
Devonshire Building | 2016-10-31 17:45 | 47523.5412 | 1379.988
Devonshire Building | 2016-10-31 18:00 | 47523.8912 | 1400.004
Devonshire Building | 2016-10-31 18:15 | 47524.2312 | 1360.008
Devonshire Building | 2016-10-31 18:30 | 47524.5662 | 1339.992
Devonshire Building | 2016-10-31 18:45 | 47524.9012 | 1339.992
Devonshire Building | 2016-10-31 19:00 | 47525.2412 | 1360.008
Devonshire Building | 2016-10-31 19:15 | 47525.5712 | 1320.012
Devonshire Building | 2016-10-31 19:30 | 47525.9012 | 1320.012
Devonshire Building | 2016-10-31 19:45 | 47526.2262 | 1299.996
Devonshire Building | 2016-10-31 20:00 | 47526.5512 | 1299.996
Devonshire Building | 2016-10-31 20:15 | 47526.8712 | 1280.016
Devonshire Building | 2016-10-31 20:30 | 47527.1913 | 1280.016
Devonshire Building | 2016-10-31 20:45 | 47527.5063 | 1260
Devonshire Building | 2016-10-31 21:00 | 47527.8213 | 1260
Devonshire Building | 2016-10-31 21:15 | 47528.1363 | 1260
Devonshire Building | 2016-10-31 21:30 | 47528.4462 | 1239.984
Devonshire Building | 2016-10-31 21:45 | 47528.7612 | 1260
Devonshire Building | 2016-10-31 22:00 | 47529.0912 | 1320.012
Devonshire Building | 2016-10-31 22:15 | 47529.3963 | 1220.004
Devonshire Building | 2016-10-31 22:30 | 47529.6962 | 1199.988
Devonshire Building | 2016-10-31 22:45 | 47530.0012 | 1220.004
Devonshire Building | 2016-10-31 23:00 | 47530.3063 | 1220.004
Devonshire Building | 2016-10-31 23:15 | 47530.6113 | 1220.004
Devonshire Building | 2016-10-31 23:30 | 47530.9163 | 1220.004
Devonshire Building | 2016-10-31 23:45 | 47531.2213 | 1220.004 | 1199.988
Devonshire Building | 2016-11-01 | 47531.5312 | 1239.984
Devonshire Building | 2016-11-01 00:15 | 47532.3463 | 3260.016
Devonshire Building | 2016-11-01 00:30 | 47532.6863 | 1360.008
Devonshire Building | 2016-11-01 00:45 | 47533.0413 | 1419.984
Devonshire Building | 2016-11-01 01:00 | 47533.4113 | 1479.996
Devonshire Building | 2016-11-01 01:15 | 47533.7812 | 1479.996
Devonshire Building | 2016-11-01 01:30 | 47534.1463 | 1460.016
Devonshire Building | 2016-11-01 01:45 | 47534.5163 | 1479.996
Devonshire Building | 2016-11-01 02:00 | 47534.8863 | 1479.996
Devonshire Building | 2016-11-01 02:15 | 47535.2563 | 1479.996
Devonshire Building | 2016-11-01 02:30 | 47535.6263 | 1479.996
Devonshire Building | 2016-11-01 02:45 | 47535.9962 | 1479.996
Devonshire Building | 2016-11-01 03:00 | 47536.3662 | 1479.996
Devonshire Building | 2016-11-01 03:15 | 47536.7362 | 1479.996
Devonshire Building | 2016-11-01 03:30 | 47537.1062 | 1479.996
Devonshire Building | 2016-11-01 03:45 | 47537.4762 | 1479.996
Devonshire Building | 2016-11-01 04:00 | 47537.8512 | 1500.012
Devonshire Building | 2016-11-01 04:15 | 47538.2163 | 1460.016
Devonshire Building | 2016-11-01 04:30 | 47538.5863 | 1479.996
Devonshire Building | 2016-11-01 04:45 | 47538.9563 | 1479.996
Devonshire Building | 2016-11-01 05:00 | 47539.3262 | 1479.996
Devonshire Building | 2016-11-01 05:15 | 47539.6962 | 1479.996
Devonshire Building | 2016-11-01 05:30 | 47540.0662 | 1479.996
Devonshire Building | 2016-11-01 05:45 | 47540.4313 | 1460.016
Devonshire Building | 2016-11-01 06:00 | 47540.8012 | 1479.996
Devonshire Building | 2016-11-01 06:15 | 47541.1663 | 1460.016
Devonshire Building | 2016-11-01 06:30 | 47541.5363 | 1479.996
Devonshire Building | 2016-11-01 06:45 | 47541.9013 | 1460.016
Devonshire Building | 2016-11-01 07:00 | 47542.2663 | 1460.016
Devonshire Building | 2016-11-01 07:15 | 47542.6313 | 1460.016
Devonshire Building | 2016-11-01 07:30 | 47542.9963 | 1460.016
Devonshire Building | 2016-11-01 07:45 | 47543.3713 | 1500.012
Devonshire Building | 2016-11-01 08:00 | 47543.9213 | 2199.996
Devonshire Building | 2016-11-01 08:15 | 47544.6413 | 2880
Devonshire Building | 2016-11-01 08:30 | 47545.0113 | 1479.996
Devonshire Building | 2016-11-01 08:45 | 47545.3863 | 1500.012
Devonshire Building | 2016-11-01 09:00 | 47545.7613 | 1500.012
Devonshire Building | 2016-11-01 09:15 | 47546.1263 | 1460.016
Devonshire Building | 2016-11-01 09:30 | 47546.4863 | 1440
Devonshire Building | 2016-11-01 09:45 | 47546.8413 | 1419.984
Devonshire Building | 2016-11-01 10:00 | 47547.2013 | 1440
Devonshire Building | 2016-11-01 10:15 | 47548.1463 | 3780
Devonshire Building | 2016-11-01 10:30 | 47548.4863 | 1360.008
Devonshire Building | 2016-11-01 10:45 | 47548.8513 | 1460.016
Devonshire Building | 2016-11-01 11:00 | 47549.2613 | 1640.016
Devonshire Building | 2016-11-01 11:15 | 47550.1763 | 3660.012
Devonshire Building | 2016-11-01 11:30 | 47550.5813 | 1620
Devonshire Building | 2016-11-01 11:45 | 47550.9613 | 1519.992
Devonshire Building | 2016-11-01 12:00 | 47551.3213 | 1440
Devonshire Building | 2016-11-01 12:15 | 47551.6763 | 1419.984
Devonshire Building | 2016-11-01 12:30 | 47552.0213 | 1379.988
Devonshire Building | 2016-11-01 12:45 | 47552.8813 | 3440.016
Devonshire Building | 2016-11-01 13:00 | 47553.2013 | 1280.016
Devonshire Building | 2016-11-01 13:15 | 47553.5263 | 1299.996
Devonshire Building | 2016-11-01 13:30 | 47553.8463 | 1280.016
Devonshire Building | 2016-11-01 13:45 | 47554.1663 | 1280.016
Devonshire Building | 2016-11-01 14:00 | 47554.4913 | 1299.996
Devonshire Building | 2016-11-01 14:15 | 47555.3313 | 3359.988
Devonshire Building | 2016-11-01 14:30 | 47555.6563 | 1299.996
Devonshire Building | 2016-11-01 14:45 | 47555.9763 | 1280.016
Devonshire Building | 2016-11-01 15:00 | 47556.3463 | 1479.996
Devonshire Building | 2016-11-01 15:15 | 47556.7563 | 1640.016
Devonshire Building | 2016-11-01 15:30 | 47557.1763 | 1680.012
Devonshire Building | 2016-11-01 15:45 | 47557.5813 | 1620
Devonshire Building | 2016-11-01 16:00 | 47557.9863 | 1620
Devonshire Building | 2016-11-01 16:15 | 47558.3663 | 1519.992
Devonshire Building | 2016-11-01 16:30 | 47559.2363 | 3480.012
Devonshire Building | 2016-11-01 16:45 | 47559.5913 | 1419.984
Devonshire Building | 2016-11-01 17:00 | 47559.9413 | 1400.004
Devonshire Building | 2016-11-01 17:15 | 47560.3013 | 1440
Devonshire Building | 2016-11-01 17:30 | 47560.6413 | 1360.008
Devonshire Building | 2016-11-01 17:45 | 47560.9763 | 1339.992
Devonshire Building | 2016-11-01 18:00 | 47561.3063 | 1320.012
Devonshire Building | 2016-11-01 18:15 | 47561.6363 | 1320.012
Devonshire Building | 2016-11-01 18:30 | 47561.9663 | 1320.012
Devonshire Building | 2016-11-01 18:45 | 47562.2963 | 1320.012
Devonshire Building | 2016-11-01 19:00 | 47562.6213 | 1299.996
Devonshire Building | 2016-11-01 19:15 | 47562.9513 | 1320.012
Devonshire Building | 2016-11-01 19:30 | 47563.2763 | 1299.996
Devonshire Building | 2016-11-01 19:45 | 47564.0963 | 3279.996
Devonshire Building | 2016-11-01 20:00 | 47564.4213 | 1299.996
Devonshire Building | 2016-11-01 20:15 | 47564.7413 | 1280.016
Devonshire Building | 2016-11-01 20:30 | 47565.0713 | 1320.012
Devonshire Building | 2016-11-01 20:45 | 47565.3963 | 1299.996
Devonshire Building | 2016-11-01 21:00 | 47565.7213 | 1299.996
Devonshire Building | 2016-11-01 21:15 | 47566.0413 | 1280.016
Devonshire Building | 2016-11-01 21:30 | 47566.3563 | 1260
Devonshire Building | 2016-11-01 21:45 | 47566.6713 | 1260
Devonshire Building | 2016-11-01 22:00 | 47566.9863 | 1260
Devonshire Building | 2016-11-01 22:15 | 47567.2913 | 1220.004
Devonshire Building | 2016-11-01 22:30 | 47567.6013 | 1239.984
Devonshire Building | 2016-11-01 22:45 | 47567.9063 | 1220.004
Devonshire Building | 2016-11-01 23:00 | 47568.2163 | 1239.984
Devonshire Building | 2016-11-01 23:15 | 47568.5213 | 1220.004
Devonshire Building | 2016-11-01 23:30 | 47568.8313 | 1239.984
Devonshire Building | 2016-11-01 23:45 | 47569.1363 | 1220.004 | 1220.004
Devonshire Building | 2016-11-02 | 47569.4453 | 1239.984
Devonshire Building | 2016-11-02 00:15 | 47569.7503 | 1220.004
Devonshire Building | 2016-11-02 00:30 | 47570.0603 | 1239.984
Devonshire Building | 2016-11-02 00:45 | 47570.3653 | 1220.004
Devonshire Building | 2016-11-02 01:00 | 47570.6753 | 1239.984
Devonshire Building | 2016-11-02 01:15 | 47570.9803 | 1220.004
Devonshire Building | 2016-11-02 01:30 | 47571.2903 | 1239.984
Devonshire Building | 2016-11-02 01:45 | 47571.6003 | 1239.984
Devonshire Building | 2016-11-02 02:00 | 47571.9053 | 1220.004
Devonshire Building | 2016-11-02 02:15 | 47572.2103 | 1220.004
Devonshire Building | 2016-11-02 02:30 | 47572.5203 | 1239.984
Devonshire Building | 2016-11-02 02:45 | 47572.8253 | 1220.004
Devonshire Building | 2016-11-02 03:00 | 47573.1353 | 1239.984
Devonshire Building | 2016-11-02 03:15 | 47573.4403 | 1220.004
Devonshire Building | 2016-11-02 03:30 | 47573.7503 | 1239.984
Devonshire Building | 2016-11-02 03:45 | 47574.0553 | 1220.004
Devonshire Building | 2016-11-02 04:00 | 47574.3603 | 1220.004
Devonshire Building | 2016-11-02 04:15 | 47574.6703 | 1239.984
Devonshire Building | 2016-11-02 04:30 | 47574.9753 | 1220.004
Devonshire Building | 2016-11-02 04:45 | 47575.2803 | 1220.004
Devonshire Building | 2016-11-02 05:00 | 47575.5903 | 1239.984
Devonshire Building | 2016-11-02 05:15 | 47575.8953 | 1220.004
Devonshire Building | 2016-11-02 05:30 | 47576.2003 | 1220.004
Devonshire Building | 2016-11-02 05:45 | 47576.5053 | 1220.004
Devonshire Building | 2016-11-02 06:00 | 47576.8103 | 1220.004
Devonshire Building | 2016-11-02 06:15 | 47577.1153 | 1220.004
Devonshire Building | 2016-11-02 06:30 | 47577.4203 | 1220.004
Devonshire Building | 2016-11-02 06:45 | 47577.7203 | 1199.988
Devonshire Building | 2016-11-02 07:00 | 47578.0203 | 1199.988
Devonshire Building | 2016-11-02 07:15 | 47578.3203 | 1199.988
Devonshire Building | 2016-11-02 07:30 | 47578.6203 | 1199.988
Devonshire Building | 2016-11-02 07:45 | 47579.2603 | 2559.996
Devonshire Building | 2016-11-02 08:00 | 47579.7503 | 1959.984
Devonshire Building | 2016-11-02 08:15 | 47580.0603 | 1239.984
Devonshire Building | 2016-11-02 08:30 | 47580.3753 | 1260
Devonshire Building | 2016-11-02 08:45 | 47580.7003 | 1299.996
Devonshire Building | 2016-11-02 09:00 | 47581.0153 | 1260
Devonshire Building | 2016-11-02 09:15 | 47581.3303 | 1260
Devonshire Building | 2016-11-02 09:30 | 47581.6453 | 1260
Devonshire Building | 2016-11-02 09:45 | 47581.9703 | 1299.996
Devonshire Building | 2016-11-02 10:00 | 47582.3053 | 1339.992
Devonshire Building | 2016-11-02 10:15 | 47583.1653 | 3440.016
Devonshire Building | 2016-11-02 10:30 | 47583.4903 | 1299.996
Devonshire Building | 2016-11-02 10:45 | 47583.8203 | 1320.012
Devonshire Building | 2016-11-02 11:00 | 47584.1703 | 1400.004
Devonshire Building | 2016-11-02 11:15 | 47584.5853 | 1659.996
Devonshire Building | 2016-11-02 11:30 | 47585.4053 | 3279.996
Devonshire Building | 2016-11-02 11:45 | 47585.7653 | 1440
Devonshire Building | 2016-11-02 12:00 | 47586.1253 | 1440
Devonshire Building | 2016-11-02 12:15 | 47586.4803 | 1419.984
Devonshire Building | 2016-11-02 12:30 | 47586.8403 | 1440
Devonshire Building | 2016-11-02 12:45 | 47587.2053 | 1460.016
Devonshire Building | 2016-11-02 13:00 | 47587.9903 | 3139.992
Devonshire Building | 2016-11-02 13:15 | 47588.4203 | 1720.008
Devonshire Building | 2016-11-02 13:30 | 47588.7603 | 1360.008
Devonshire Building | 2016-11-02 13:45 | 47589.1003 | 1360.008
Devonshire Building | 2016-11-02 14:00 | 47589.4503 | 1400.004
Devonshire Building | 2016-11-02 14:15 | 47589.7903 | 1360.008
Devonshire Building | 2016-11-02 14:30 | 47590.1303 | 1360.008
Devonshire Building | 2016-11-02 14:45 | 47590.5103 | 1519.992
Devonshire Building | 2016-11-02 15:00 | 47591.4103 | 3600
Devonshire Building | 2016-11-02 15:15 | 47591.8453 | 1739.988
Devonshire Building | 2016-11-02 15:30 | 47592.2553 | 1640.016
Devonshire Building | 2016-11-02 15:45 | 47592.6303 | 1500.012
Devonshire Building | 2016-11-02 16:00 | 47592.9953 | 1460.016
Devonshire Building | 2016-11-02 16:15 | 47593.3453 | 1400.004
Devonshire Building | 2016-11-02 16:30 | 47593.6903 | 1379.988
Devonshire Building | 2016-11-02 16:45 | 47594.5253 | 3340.008
Devonshire Building | 2016-11-02 17:00 | 47594.8653 | 1360.008
Devonshire Building | 2016-11-02 17:15 | 47595.2103 | 1379.988
Devonshire Building | 2016-11-02 17:30 | 47595.5653 | 1419.984
Devonshire Building | 2016-11-02 17:45 | 47595.9103 | 1379.988
Devonshire Building | 2016-11-02 18:00 | 47596.2553 | 1379.988
Devonshire Building | 2016-11-02 18:15 | 47596.5903 | 1339.992
Devonshire Building | 2016-11-02 18:30 | 47596.9303 | 1360.008
Devonshire Building | 2016-11-02 18:45 | 47597.2603 | 1320.012
Devonshire Building | 2016-11-02 19:00 | 47597.5903 | 1320.012
Devonshire Building | 2016-11-02 19:15 | 47597.9153 | 1299.996
Devonshire Building | 2016-11-02 19:30 | 47598.2403 | 1299.996
Devonshire Building | 2016-11-02 19:45 | 47599.0603 | 3279.996
Devonshire Building | 2016-11-02 20:00 | 47599.3803 | 1280.016
Devonshire Building | 2016-11-02 20:15 | 47599.7053 | 1299.996
Devonshire Building | 2016-11-02 20:30 | 47600.0303 | 1299.996
Devonshire Building | 2016-11-02 20:45 | 47600.3603 | 1320.012
Devonshire Building | 2016-11-02 21:00 | 47600.6803 | 1280.016
Devonshire Building | 2016-11-02 21:15 | 47601.0053 | 1299.996
Devonshire Building | 2016-11-02 21:30 | 47601.3303 | 1299.996
Devonshire Building | 2016-11-02 21:45 | 47601.6553 | 1299.996
Devonshire Building | 2016-11-02 22:00 | 47601.9703 | 1260
Devonshire Building | 2016-11-02 22:15 | 47602.2803 | 1239.984
Devonshire Building | 2016-11-02 22:30 | 47602.5903 | 1239.984
Devonshire Building | 2016-11-02 22:45 | 47602.9003 | 1239.984
Devonshire Building | 2016-11-02 23:00 | 47603.2153 | 1260
Devonshire Building | 2016-11-02 23:15 | 47603.5253 | 1239.984
Devonshire Building | 2016-11-02 23:30 | 47603.8353 | 1239.984
Devonshire Building | 2016-11-02 23:45 | 47604.1503 | 1260 | 1199.988
Devonshire Building | 2016-11-03 | 47604.4609 | 1239.984
Devonshire Building | 2016-11-03 00:15 | 47604.7759 | 1260
Devonshire Building | 2016-11-03 00:30 | 47605.0859 | 1239.984
Devonshire Building | 2016-11-03 00:45 | 47605.4009 | 1260
Devonshire Building | 2016-11-03 01:00 | 47605.7109 | 1239.984
Devonshire Building | 2016-11-03 01:15 | 47606.0259 | 1260
Devonshire Building | 2016-11-03 01:30 | 47606.3359 | 1239.984
Devonshire Building | 2016-11-03 01:45 | 47606.6509 | 1260
Devonshire Building | 2016-11-03 02:00 | 47606.9659 | 1260
Devonshire Building | 2016-11-03 02:15 | 47607.2759 | 1239.984
Devonshire Building | 2016-11-03 02:30 | 47607.5909 | 1260
Devonshire Building | 2016-11-03 02:45 | 47607.9009 | 1239.984
Devonshire Building | 2016-11-03 03:00 | 47608.2109 | 1239.984
Devonshire Building | 2016-11-03 03:15 | 47608.5259 | 1260
Devonshire Building | 2016-11-03 03:30 | 47608.8359 | 1239.984
Devonshire Building | 2016-11-03 03:45 | 47609.1459 | 1239.984
Devonshire Building | 2016-11-03 04:00 | 47609.4609 | 1260
Devonshire Building | 2016-11-03 04:15 | 47609.7709 | 1239.984
Devonshire Building | 2016-11-03 04:30 | 47610.0859 | 1260
Devonshire Building | 2016-11-03 04:45 | 47610.3959 | 1239.984
Devonshire Building | 2016-11-03 05:00 | 47610.7059 | 1239.984
Devonshire Building | 2016-11-03 05:15 | 47611.0209 | 1260
Devonshire Building | 2016-11-03 05:30 | 47611.3309 | 1239.984
Devonshire Building | 2016-11-03 05:45 | 47611.6409 | 1239.984
Devonshire Building | 2016-11-03 06:00 | 47611.9509 | 1239.984
Devonshire Building | 2016-11-03 06:15 | 47612.2609 | 1239.984
Devonshire Building | 2016-11-03 06:30 | 47612.5709 | 1239.984
Devonshire Building | 2016-11-03 06:45 | 47612.8859 | 1260
Devonshire Building | 2016-11-03 07:00 | 47613.1909 | 1220.004
Devonshire Building | 2016-11-03 07:15 | 47613.4959 | 1220.004
Devonshire Building | 2016-11-03 07:30 | 47614.3059 | 3240
Devonshire Building | 2016-11-03 07:45 | 47614.6109 | 1220.004
Devonshire Building | 2016-11-03 08:00 | 47614.9159 | 1220.004
Devonshire Building | 2016-11-03 08:15 | 47615.2209 | 1220.004
Devonshire Building | 2016-11-03 08:30 | 47615.5209 | 1199.988
Devonshire Building | 2016-11-03 08:45 | 47615.8309 | 1239.984
Devonshire Building | 2016-11-03 09:00 | 47616.1409 | 1239.984
Devonshire Building | 2016-11-03 09:15 | 47616.4459 | 1220.004
Devonshire Building | 2016-11-03 09:30 | 47616.7559 | 1239.984
Devonshire Building | 2016-11-03 09:45 | 47617.3859 | 2520
Devonshire Building | 2016-11-03 10:00 | 47617.8959 | 2040.012
Devonshire Building | 2016-11-03 10:15 | 47618.2259 | 1320.012
Devonshire Building | 2016-11-03 10:30 | 47618.5659 | 1360.008
Devonshire Building | 2016-11-03 10:45 | 47618.9359 | 1479.996
Devonshire Building | 2016-11-03 11:00 | 47619.5659 | 2520
Devonshire Building | 2016-11-03 11:15 | 47620.2609 | 2779.992
Devonshire Building | 2016-11-03 11:30 | 47620.6659 | 1620
Devonshire Building | 2016-11-03 11:45 | 47621.0709 | 1620
Devonshire Building | 2016-11-03 12:00 | 47621.4659 | 1580.004
Devonshire Building | 2016-11-03 12:15 | 47621.9259 | 1839.996
Devonshire Building | 2016-11-03 12:30 | 47622.7559 | 3319.992
Devonshire Building | 2016-11-03 12:45 | 47623.1509 | 1580.004
Devonshire Building | 2016-11-03 13:00 | 47623.5409 | 1559.988
Devonshire Building | 2016-11-03 13:15 | 47623.9459 | 1620
Devonshire Building | 2016-11-03 13:30 | 47624.3459 | 1599.984
Devonshire Building | 2016-11-03 13:45 | 47625.2559 | 3639.996
Devonshire Building | 2016-11-03 14:00 | 47625.6359 | 1519.992
Devonshire Building | 2016-11-03 14:15 | 47626.0209 | 1540.008
Devonshire Building | 2016-11-03 14:30 | 47626.4009 | 1519.992
Devonshire Building | 2016-11-03 14:45 | 47626.7759 | 1500.012
Devonshire Building | 2016-11-03 15:00 | 47627.1509 | 1500.012
Devonshire Building | 2016-11-03 15:15 | 47627.5159 | 1460.016
Devonshire Building | 2016-11-03 15:30 | 47628.3809 | 3459.996
Devonshire Building | 2016-11-03 15:45 | 47628.7259 | 1379.988
Devonshire Building | 2016-11-03 16:00 | 47629.0659 | 1360.008
Devonshire Building | 2016-11-03 16:15 | 47629.4159 | 1400.004
Devonshire Building | 2016-11-03 16:30 | 47629.8009 | 1540.008
Devonshire Building | 2016-11-03 16:45 | 47630.1809 | 1519.992
Devonshire Building | 2016-11-03 17:00 | 47630.5659 | 1540.008
Devonshire Building | 2016-11-03 17:15 | 47631.4909 | 3700.008
Devonshire Building | 2016-11-03 17:30 | 47631.8909 | 1599.984
Devonshire Building | 2016-11-03 17:45 | 47632.2909 | 1599.984
Devonshire Building | 2016-11-03 18:00 | 47632.6709 | 1519.992
Devonshire Building | 2016-11-03 18:15 | 47633.0309 | 1440
Devonshire Building | 2016-11-03 18:30 | 47633.3809 | 1400.004
Devonshire Building | 2016-11-03 18:45 | 47633.7209 | 1360.008
Devonshire Building | 2016-11-03 19:00 | 47634.0559 | 1339.992
Devonshire Building | 2016-11-03 19:15 | 47634.3859 | 1320.012
Devonshire Building | 2016-11-03 19:30 | 47634.7159 | 1320.012
Devonshire Building | 2016-11-03 19:45 | 47635.0409 | 1299.996
Devonshire Building | 2016-11-03 20:00 | 47635.3659 | 1299.996
Devonshire Building | 2016-11-03 20:15 | 47635.6859 | 1280.016
Devonshire Building | 2016-11-03 20:30 | 47636.0059 | 1280.016
Devonshire Building | 2016-11-03 20:45 | 47636.3259 | 1280.016
Devonshire Building | 2016-11-03 21:00 | 47636.6459 | 1280.016
Devonshire Building | 2016-11-03 21:15 | 47636.9659 | 1280.016
Devonshire Building | 2016-11-03 21:30 | 47637.2859 | 1280.016
Devonshire Building | 2016-11-03 21:45 | 47637.6059 | 1280.016
Devonshire Building | 2016-11-03 22:00 | 47637.9459 | 1360.008
Devonshire Building | 2016-11-03 22:15 | 47638.2559 | 1239.984
Devonshire Building | 2016-11-03 22:30 | 47638.5709 | 1260
Devonshire Building | 2016-11-03 22:45 | 47638.8859 | 1260
Devonshire Building | 2016-11-03 23:00 | 47639.2009 | 1260
Devonshire Building | 2016-11-03 23:15 | 47639.5209 | 1280.016
Devonshire Building | 2016-11-03 23:30 | 47639.8359 | 1260
Devonshire Building | 2016-11-03 23:45 | 47640.1559 | 1280.016 | 1199.988
Devonshire Building | 2016-11-04 | 47640.4688 | 1260
Devonshire Building | 2016-11-04 00:15 | 47640.8638 | 1580.004
Devonshire Building | 2016-11-04 00:30 | 47641.6237 | 3039.984
Devonshire Building | 2016-11-04 00:45 | 47641.9438 | 1280.016
Devonshire Building | 2016-11-04 01:00 | 47642.2638 | 1280.016
Devonshire Building | 2016-11-04 01:15 | 47642.5838 | 1280.016
Devonshire Building | 2016-11-04 01:30 | 47642.9038 | 1280.016
Devonshire Building | 2016-11-04 01:45 | 47643.2288 | 1299.996
Devonshire Building | 2016-11-04 02:00 | 47643.5488 | 1280.016
Devonshire Building | 2016-11-04 02:15 | 47643.8688 | 1280.016
Devonshire Building | 2016-11-04 02:30 | 47644.1888 | 1280.016
Devonshire Building | 2016-11-04 02:45 | 47644.5088 | 1280.016
Devonshire Building | 2016-11-04 03:00 | 47644.8338 | 1299.996
Devonshire Building | 2016-11-04 03:15 | 47645.1538 | 1280.016
Devonshire Building | 2016-11-04 03:30 | 47645.4738 | 1280.016
Devonshire Building | 2016-11-04 03:45 | 47645.7938 | 1280.016
Devonshire Building | 2016-11-04 04:00 | 47646.1138 | 1280.016
Devonshire Building | 2016-11-04 04:15 | 47646.4338 | 1280.016
Devonshire Building | 2016-11-04 04:30 | 47646.7588 | 1299.996
Devonshire Building | 2016-11-04 04:45 | 47647.0788 | 1280.016
Devonshire Building | 2016-11-04 05:00 | 47647.3988 | 1280.016
Devonshire Building | 2016-11-04 05:15 | 47647.7188 | 1280.016
Devonshire Building | 2016-11-04 05:30 | 47648.0438 | 1299.996
Devonshire Building | 2016-11-04 05:45 | 47648.3638 | 1280.016
Devonshire Building | 2016-11-04 06:00 | 47648.6838 | 1280.016
Devonshire Building | 2016-11-04 06:15 | 47649.0038 | 1280.016
Devonshire Building | 2016-11-04 06:30 | 47649.3288 | 1299.996
Devonshire Building | 2016-11-04 06:45 | 47649.6438 | 1260
Devonshire Building | 2016-11-04 07:00 | 47649.9638 | 1280.016
Devonshire Building | 2016-11-04 07:15 | 47650.2788 | 1260
Devonshire Building | 2016-11-04 07:30 | 47650.5938 | 1260
Devonshire Building | 2016-11-04 07:45 | 47650.9088 | 1260
Devonshire Building | 2016-11-04 08:00 | 47651.2238 | 1260
Devonshire Building | 2016-11-04 08:15 | 47651.9938 | 3080.016
Devonshire Building | 2016-11-04 08:30 | 47652.3588 | 1460.016
Devonshire Building | 2016-11-04 08:45 | 47652.6738 | 1260
Devonshire Building | 2016-11-04 09:00 | 47652.9888 | 1260
Devonshire Building | 2016-11-04 09:15 | 47653.3088 | 1280.016
Devonshire Building | 2016-11-04 09:30 | 47653.6238 | 1260
Devonshire Building | 2016-11-04 09:45 | 47653.9438 | 1280.016
Devonshire Building | 2016-11-04 10:00 | 47654.2688 | 1299.996
Devonshire Building | 2016-11-04 10:15 | 47654.5988 | 1320.012
Devonshire Building | 2016-11-04 10:30 | 47654.9438 | 1379.988
Devonshire Building | 2016-11-04 10:45 | 47655.8488 | 3620.016
Devonshire Building | 2016-11-04 11:00 | 47656.2488 | 1599.984
Devonshire Building | 2016-11-04 11:15 | 47656.6688 | 1680.012
Devonshire Building | 2016-11-04 11:30 | 47657.0888 | 1680.012
Devonshire Building | 2016-11-04 11:45 | 47657.5038 | 1659.996
Devonshire Building | 2016-11-04 12:00 | 47658.2288 | 2900.016
Devonshire Building | 2016-11-04 12:15 | 47658.8388 | 2440.008
Devonshire Building | 2016-11-04 12:30 | 47659.2438 | 1620
Devonshire Building | 2016-11-04 12:45 | 47659.6289 | 1540.008
Devonshire Building | 2016-11-04 13:00 | 47660.0088 | 1519.992
Devonshire Building | 2016-11-04 13:15 | 47660.3839 | 1500.012
Devonshire Building | 2016-11-04 13:30 | 47660.9638 | 2319.984
Devonshire Building | 2016-11-04 13:45 | 47661.6688 | 2819.988
Devonshire Building | 2016-11-04 14:00 | 47662.0588 | 1559.988
Devonshire Building | 2016-11-04 14:15 | 47662.4538 | 1580.004
Devonshire Building | 2016-11-04 14:30 | 47662.8488 | 1580.004
Devonshire Building | 2016-11-04 14:45 | 47663.2338 | 1540.008
Devonshire Building | 2016-11-04 15:00 | 47663.6188 | 1540.008
Devonshire Building | 2016-11-04 15:15 | 47663.9988 | 1519.992
Devonshire Building | 2016-11-04 15:30 | 47664.3738 | 1500.012
Devonshire Building | 2016-11-04 15:45 | 47665.2738 | 3600
Devonshire Building | 2016-11-04 16:00 | 47665.6588 | 1540.008
Devonshire Building | 2016-11-04 16:15 | 47666.0738 | 1659.996
Devonshire Building | 2016-11-04 16:30 | 47666.4888 | 1659.996
Devonshire Building | 2016-11-04 16:45 | 47666.8989 | 1640.016
Devonshire Building | 2016-11-04 17:00 | 47667.2939 | 1580.004
Devonshire Building | 2016-11-04 17:15 | 47667.6789 | 1540.008
Devonshire Building | 2016-11-04 17:30 | 47668.5539 | 3499.992
Devonshire Building | 2016-11-04 17:45 | 47668.9039 | 1400.004
Devonshire Building | 2016-11-04 18:00 | 47669.2539 | 1400.004
Devonshire Building | 2016-11-04 18:15 | 47669.6089 | 1419.984
Devonshire Building | 2016-11-04 18:30 | 47669.9589 | 1400.004
Devonshire Building | 2016-11-04 18:45 | 47670.3089 | 1400.004
Devonshire Building | 2016-11-04 19:00 | 47670.6539 | 1379.988
Devonshire Building | 2016-11-04 19:15 | 47670.9988 | 1379.988
Devonshire Building | 2016-11-04 19:30 | 47671.3438 | 1379.988
Devonshire Building | 2016-11-04 19:45 | 47671.6788 | 1339.992
Devonshire Building | 2016-11-04 20:00 | 47672.0188 | 1360.008
Devonshire Building | 2016-11-04 20:15 | 47672.3488 | 1320.012
Devonshire Building | 2016-11-04 20:30 | 47672.6838 | 1339.992
Devonshire Building | 2016-11-04 20:45 | 47673.0138 | 1320.012
Devonshire Building | 2016-11-04 21:00 | 47673.3488 | 1339.992
Devonshire Building | 2016-11-04 21:15 | 47673.6788 | 1320.012
Devonshire Building | 2016-11-04 21:30 | 47674.0089 | 1320.012
Devonshire Building | 2016-11-04 21:45 | 47674.3389 | 1320.012
Devonshire Building | 2016-11-04 22:00 | 47674.6889 | 1400.004
Devonshire Building | 2016-11-04 22:15 | 47675.0189 | 1320.012
Devonshire Building | 2016-11-04 22:30 | 47675.3439 | 1299.996
Devonshire Building | 2016-11-04 22:45 | 47675.6739 | 1320.012
Devonshire Building | 2016-11-04 23:00 | 47675.9989 | 1299.996
Devonshire Building | 2016-11-04 23:15 | 47676.3289 | 1320.012
Devonshire Building | 2016-11-04 23:30 | 47676.6589 | 1320.012
Devonshire Building | 2016-11-04 23:45 | 47676.9889 | 1320.012 | 1260
Devonshire Building | 2016-11-05 | 47677.3203 | 1320.012
Devonshire Building | 2016-11-05 00:15 | 47677.6553 | 1339.992
Devonshire Building | 2016-11-05 00:30 | 47677.9853 | 1320.012
Devonshire Building | 2016-11-05 00:45 | 47678.3203 | 1339.992
Devonshire Building | 2016-11-05 01:00 | 47678.6503 | 1320.012
Devonshire Building | 2016-11-05 01:15 | 47678.9803 | 1320.012
Devonshire Building | 2016-11-05 01:30 | 47679.3153 | 1339.992
Devonshire Building | 2016-11-05 01:45 | 47679.6453 | 1320.012
Devonshire Building | 2016-11-05 02:00 | 47680.2303 | 2340
Devonshire Building | 2016-11-05 02:15 | 47680.5653 | 1339.992
Devonshire Building | 2016-11-05 02:30 | 47680.8953 | 1320.012
Devonshire Building | 2016-11-05 02:45 | 47681.2303 | 1339.992
Devonshire Building | 2016-11-05 03:00 | 47681.5653 | 1339.992
Devonshire Building | 2016-11-05 03:15 | 47681.9003 | 1339.992
Devonshire Building | 2016-11-05 03:30 | 47682.2303 | 1320.012
Devonshire Building | 2016-11-05 03:45 | 47682.5653 | 1339.992
Devonshire Building | 2016-11-05 04:00 | 47682.9003 | 1339.992
Devonshire Building | 2016-11-05 04:15 | 47683.2303 | 1320.012
Devonshire Building | 2016-11-05 04:30 | 47683.5653 | 1339.992
Devonshire Building | 2016-11-05 04:45 | 47683.9003 | 1339.992
Devonshire Building | 2016-11-05 05:00 | 47684.2303 | 1320.012
Devonshire Building | 2016-11-05 05:15 | 47684.5653 | 1339.992
Devonshire Building | 2016-11-05 05:30 | 47684.9003 | 1339.992
Devonshire Building | 2016-11-05 05:45 | 47685.2353 | 1339.992
Devonshire Building | 2016-11-05 06:00 | 47685.5653 | 1320.012
Devonshire Building | 2016-11-05 06:15 | 47685.9003 | 1339.992
Devonshire Building | 2016-11-05 06:30 | 47686.2353 | 1339.992
Devonshire Building | 2016-11-05 06:45 | 47686.5703 | 1339.992
Devonshire Building | 2016-11-05 07:00 | 47686.9003 | 1320.012
Devonshire Building | 2016-11-05 07:15 | 47687.2353 | 1339.992
Devonshire Building | 2016-11-05 07:30 | 47687.5703 | 1339.992
Devonshire Building | 2016-11-05 07:45 | 47687.9003 | 1320.012
Devonshire Building | 2016-11-05 08:00 | 47688.2303 | 1320.012
Devonshire Building | 2016-11-05 08:15 | 47688.5653 | 1339.992
Devonshire Building | 2016-11-05 08:30 | 47688.8953 | 1320.012
Devonshire Building | 2016-11-05 08:45 | 47689.2203 | 1299.996
Devonshire Building | 2016-11-05 09:00 | 47689.5503 | 1320.012
Devonshire Building | 2016-11-05 09:15 | 47689.8803 | 1320.012
Devonshire Building | 2016-11-05 09:30 | 47690.2103 | 1320.012
Devonshire Building | 2016-11-05 09:45 | 47690.5353 | 1299.996
Devonshire Building | 2016-11-05 10:00 | 47691.1203 | 2340
Devonshire Building | 2016-11-05 10:15 | 47691.4403 | 1280.016
Devonshire Building | 2016-11-05 10:30 | 47691.7603 | 1280.016
Devonshire Building | 2016-11-05 10:45 | 47692.0753 | 1260
Devonshire Building | 2016-11-05 11:00 | 47692.3903 | 1260
Devonshire Building | 2016-11-05 11:15 | 47692.7003 | 1239.984
Devonshire Building | 2016-11-05 11:30 | 47693.0103 | 1239.984
Devonshire Building | 2016-11-05 11:45 | 47693.3203 | 1239.984
Devonshire Building | 2016-11-05 12:00 | 47693.6353 | 1260
Devonshire Building | 2016-11-05 12:15 | 47693.9553 | 1280.016
Devonshire Building | 2016-11-05 12:30 | 47694.2753 | 1280.016
Devonshire Building | 2016-11-05 12:45 | 47694.5903 | 1260
Devonshire Building | 2016-11-05 13:00 | 47694.9053 | 1260
Devonshire Building | 2016-11-05 13:15 | 47695.2153 | 1239.984
Devonshire Building | 2016-11-05 13:30 | 47695.5403 | 1299.996
Devonshire Building | 2016-11-05 13:45 | 47695.8703 | 1320.012
Devonshire Building | 2016-11-05 14:00 | 47696.2003 | 1320.012
Devonshire Building | 2016-11-05 14:15 | 47696.5353 | 1339.992
Devonshire Building | 2016-11-05 14:30 | 47696.8653 | 1320.012
Devonshire Building | 2016-11-05 14:45 | 47697.4653 | 2400.012
Devonshire Building | 2016-11-05 15:00 | 47697.8053 | 1360.008
Devonshire Building | 2016-11-05 15:15 | 47698.1403 | 1339.992
Devonshire Building | 2016-11-05 15:30 | 47698.4803 | 1360.008
Devonshire Building | 2016-11-05 15:45 | 47698.8203 | 1360.008
Devonshire Building | 2016-11-05 16:00 | 47699.1553 | 1339.992
Devonshire Building | 2016-11-05 16:15 | 47699.4903 | 1339.992
Devonshire Building | 2016-11-05 16:30 | 47699.8303 | 1360.008
Devonshire Building | 2016-11-05 16:45 | 47700.1653 | 1339.992
Devonshire Building | 2016-11-05 17:00 | 47700.5003 | 1339.992
Devonshire Building | 2016-11-05 17:15 | 47700.8303 | 1320.012
Devonshire Building | 2016-11-05 17:30 | 47701.1503 | 1280.016
Devonshire Building | 2016-11-05 17:45 | 47701.4703 | 1280.016
Devonshire Building | 2016-11-05 18:00 | 47701.7903 | 1280.016
Devonshire Building | 2016-11-05 18:15 | 47702.1103 | 1280.016
Devonshire Building | 2016-11-05 18:30 | 47702.4353 | 1299.996
Devonshire Building | 2016-11-05 18:45 | 47702.7553 | 1280.016
Devonshire Building | 2016-11-05 19:00 | 47703.0753 | 1280.016
Devonshire Building | 2016-11-05 19:15 | 47703.4003 | 1299.996
Devonshire Building | 2016-11-05 19:30 | 47703.7204 | 1280.016
Devonshire Building | 2016-11-05 19:45 | 47704.0454 | 1299.996
Devonshire Building | 2016-11-05 20:00 | 47704.3703 | 1299.996
Devonshire Building | 2016-11-05 20:15 | 47704.6953 | 1299.996
Devonshire Building | 2016-11-05 20:30 | 47705.0254 | 1320.012
Devonshire Building | 2016-11-05 20:45 | 47705.3504 | 1299.996
Devonshire Building | 2016-11-05 21:00 | 47705.6753 | 1299.996
Devonshire Building | 2016-11-05 21:15 | 47706.0054 | 1320.012
Devonshire Building | 2016-11-05 21:30 | 47706.3304 | 1299.996
Devonshire Building | 2016-11-05 21:45 | 47706.6604 | 1320.012
Devonshire Building | 2016-11-05 22:00 | 47707.0104 | 1400.004
Devonshire Building | 2016-11-05 22:15 | 47707.3454 | 1339.992
Devonshire Building | 2016-11-05 22:30 | 47707.6754 | 1320.012
Devonshire Building | 2016-11-05 22:45 | 47708.0104 | 1339.992
Devonshire Building | 2016-11-05 23:00 | 47708.3454 | 1339.992
Devonshire Building | 2016-11-05 23:15 | 47708.6754 | 1320.012
Devonshire Building | 2016-11-05 23:30 | 47709.0104 | 1339.992
Devonshire Building | 2016-11-05 23:45 | 47709.3454 | 1339.992 | 1239.984
Devonshire Building | 2016-11-06 | 47709.6797 | 1339.992
Devonshire Building | 2016-11-06 00:15 | 47710.0147 | 1339.992
Devonshire Building | 2016-11-06 00:30 | 47710.3547 | 1360.008
Devonshire Building | 2016-11-06 00:45 | 47710.6897 | 1339.992
Devonshire Building | 2016-11-06 01:00 | 47711.0297 | 1360.008
Devonshire Building | 2016-11-06 01:15 | 47711.3647 | 1339.992
Devonshire Building | 2016-11-06 01:30 | 47711.9497 | 2340
Devonshire Building | 2016-11-06 01:45 | 47712.2847 | 1339.992
Devonshire Building | 2016-11-06 02:00 | 47712.6247 | 1360.008
Devonshire Building | 2016-11-06 02:15 | 47712.9647 | 1360.008
Devonshire Building | 2016-11-06 02:30 | 47713.3047 | 1360.008
Devonshire Building | 2016-11-06 02:45 | 47713.6447 | 1360.008
Devonshire Building | 2016-11-06 03:00 | 47713.9797 | 1339.992
Devonshire Building | 2016-11-06 03:15 | 47714.3197 | 1360.008
Devonshire Building | 2016-11-06 03:30 | 47714.6597 | 1360.008
Devonshire Building | 2016-11-06 03:45 | 47714.9997 | 1360.008
Devonshire Building | 2016-11-06 04:00 | 47715.3397 | 1360.008
Devonshire Building | 2016-11-06 04:15 | 47715.6797 | 1360.008
Devonshire Building | 2016-11-06 04:30 | 47716.0197 | 1360.008
Devonshire Building | 2016-11-06 04:45 | 47716.3597 | 1360.008
Devonshire Building | 2016-11-06 05:00 | 47716.6997 | 1360.008
Devonshire Building | 2016-11-06 05:15 | 47717.0397 | 1360.008
Devonshire Building | 2016-11-06 05:30 | 47717.3797 | 1360.008
Devonshire Building | 2016-11-06 05:45 | 47717.7197 | 1360.008
Devonshire Building | 2016-11-06 06:00 | 47718.0597 | 1360.008
Devonshire Building | 2016-11-06 06:15 | 47718.3997 | 1360.008
Devonshire Building | 2016-11-06 06:30 | 47718.7397 | 1360.008
Devonshire Building | 2016-11-06 06:45 | 47719.0797 | 1360.008
Devonshire Building | 2016-11-06 07:00 | 47719.4197 | 1360.008
Devonshire Building | 2016-11-06 07:15 | 47719.7547 | 1339.992
Devonshire Building | 2016-11-06 07:30 | 47720.0947 | 1360.008
Devonshire Building | 2016-11-06 07:45 | 47720.4347 | 1360.008
Devonshire Building | 2016-11-06 08:00 | 47720.7747 | 1360.008
Devonshire Building | 2016-11-06 08:15 | 47721.1097 | 1339.992
Devonshire Building | 2016-11-06 08:30 | 47721.4497 | 1360.008
Devonshire Building | 2016-11-06 08:45 | 47721.7847 | 1339.992
Devonshire Building | 2016-11-06 09:00 | 47722.1247 | 1360.008
Devonshire Building | 2016-11-06 09:15 | 47722.4597 | 1339.992
Devonshire Building | 2016-11-06 09:30 | 47722.7897 | 1320.012
Devonshire Building | 2016-11-06 09:45 | 47723.1247 | 1339.992
Devonshire Building | 2016-11-06 10:00 | 47723.4597 | 1339.992
Devonshire Building | 2016-11-06 10:15 | 47723.7947 | 1339.992
Devonshire Building | 2016-11-06 10:30 | 47724.1247 | 1320.012
Devonshire Building | 2016-11-06 10:45 | 47724.4597 | 1339.992
Devonshire Building | 2016-11-06 11:00 | 47724.7947 | 1339.992
Devonshire Building | 2016-11-06 11:15 | 47725.1297 | 1339.992
Devonshire Building | 2016-11-06 11:30 | 47725.4647 | 1339.992
Devonshire Building | 2016-11-06 11:45 | 47725.8047 | 1360.008
Devonshire Building | 2016-11-06 12:00 | 47726.1397 | 1339.992
Devonshire Building | 2016-11-06 12:15 | 47726.4747 | 1339.992
Devonshire Building | 2016-11-06 12:30 | 47726.8147 | 1360.008
Devonshire Building | 2016-11-06 12:45 | 47727.1497 | 1339.992
Devonshire Building | 2016-11-06 13:00 | 47727.4897 | 1360.008
Devonshire Building | 2016-11-06 13:15 | 47727.8297 | 1360.008
Devonshire Building | 2016-11-06 13:30 | 47728.1747 | 1379.988
Devonshire Building | 2016-11-06 13:45 | 47728.5297 | 1419.984
Devonshire Building | 2016-11-06 14:00 | 47728.8897 | 1440
Devonshire Building | 2016-11-06 14:15 | 47729.2447 | 1419.984
Devonshire Building | 2016-11-06 14:30 | 47729.5997 | 1419.984
Devonshire Building | 2016-11-06 14:45 | 47729.9547 | 1419.984
Devonshire Building | 2016-11-06 15:00 | 47730.3147 | 1440
Devonshire Building | 2016-11-06 15:15 | 47730.6697 | 1419.984
Devonshire Building | 2016-11-06 15:30 | 47731.0297 | 1440
Devonshire Building | 2016-11-06 15:45 | 47731.3847 | 1419.984
Devonshire Building | 2016-11-06 16:00 | 47731.7247 | 1360.008
Devonshire Building | 2016-11-06 16:15 | 47732.0647 | 1360.008
Devonshire Building | 2016-11-06 16:30 | 47732.3997 | 1339.992
Devonshire Building | 2016-11-06 16:45 | 47732.9947 | 2379.996
Devonshire Building | 2016-11-06 17:00 | 47733.3347 | 1360.008
Devonshire Building | 2016-11-06 17:15 | 47733.6697 | 1339.992
Devonshire Building | 2016-11-06 17:30 | 47734.0097 | 1360.008
Devonshire Building | 2016-11-06 17:45 | 47734.3447 | 1339.992
Devonshire Building | 2016-11-06 18:00 | 47734.6847 | 1360.008
Devonshire Building | 2016-11-06 18:15 | 47735.0197 | 1339.992
Devonshire Building | 2016-11-06 18:30 | 47735.3597 | 1360.008
Devonshire Building | 2016-11-06 18:45 | 47735.6947 | 1339.992
Devonshire Building | 2016-11-06 19:00 | 47736.0297 | 1339.992
Devonshire Building | 2016-11-06 19:15 | 47736.3697 | 1360.008
Devonshire Building | 2016-11-06 19:30 | 47736.7047 | 1339.992
Devonshire Building | 2016-11-06 19:45 | 47737.0397 | 1339.992
Devonshire Building | 2016-11-06 20:00 | 47737.3747 | 1339.992
Devonshire Building | 2016-11-06 20:15 | 47737.7097 | 1339.992
Devonshire Building | 2016-11-06 20:30 | 47738.0447 | 1339.992
Devonshire Building | 2016-11-06 20:45 | 47738.3797 | 1339.992
Devonshire Building | 2016-11-06 21:00 | 47738.7197 | 1360.008
Devonshire Building | 2016-11-06 21:15 | 47739.0547 | 1339.992
Devonshire Building | 2016-11-06 21:30 | 47739.3947 | 1360.008
Devonshire Building | 2016-11-06 21:45 | 47739.7297 | 1339.992
Devonshire Building | 2016-11-06 22:00 | 47740.0947 | 1460.016
Devonshire Building | 2016-11-06 22:15 | 47740.4347 | 1360.008
Devonshire Building | 2016-11-06 22:30 | 47740.7747 | 1360.008
Devonshire Building | 2016-11-06 22:45 | 47741.1147 | 1360.008
Devonshire Building | 2016-11-06 23:00 | 47741.4547 | 1360.008
Devonshire Building | 2016-11-06 23:15 | 47741.7947 | 1360.008
Devonshire Building | 2016-11-06 23:30 | 47742.1397 | 1379.988
Devonshire Building | 2016-11-06 23:45 | 47742.4797 | 1360.008 | 1320.012
Devonshire Building | 2016-11-07 | 47742.8242 | 1379.988
Devonshire Building | 2016-11-07 00:15 | 47743.1692 | 1379.988
Devonshire Building | 2016-11-07 00:30 | 47743.5142 | 1379.988
Devonshire Building | 2016-11-07 00:45 | 47743.8592 | 1379.988
Devonshire Building | 2016-11-07 01:00 | 47744.2042 | 1379.988
Devonshire Building | 2016-11-07 01:15 | 47744.5492 | 1379.988
Devonshire Building | 2016-11-07 01:30 | 47744.8942 | 1379.988
Devonshire Building | 2016-11-07 01:45 | 47745.2392 | 1379.988
Devonshire Building | 2016-11-07 02:00 | 47745.5842 | 1379.988
Devonshire Building | 2016-11-07 02:15 | 47745.9292 | 1379.988
Devonshire Building | 2016-11-07 02:30 | 47746.2792 | 1400.004
Devonshire Building | 2016-11-07 02:45 | 47746.6242 | 1379.988
Devonshire Building | 2016-11-07 03:00 | 47746.9742 | 1400.004
Devonshire Building | 2016-11-07 03:15 | 47747.3192 | 1379.988
Devonshire Building | 2016-11-07 03:30 | 47747.6642 | 1379.988
Devonshire Building | 2016-11-07 03:45 | 47748.0142 | 1400.004
Devonshire Building | 2016-11-07 04:00 | 47748.3592 | 1379.988
Devonshire Building | 2016-11-07 04:15 | 47748.7092 | 1400.004
Devonshire Building | 2016-11-07 04:30 | 47749.0542 | 1379.988
Devonshire Building | 2016-11-07 04:45 | 47749.3992 | 1379.988
Devonshire Building | 2016-11-07 05:00 | 47749.7492 | 1400.004
Devonshire Building | 2016-11-07 05:15 | 47750.0942 | 1379.988
Devonshire Building | 2016-11-07 05:30 | 47750.4442 | 1400.004
Devonshire Building | 2016-11-07 05:45 | 47750.7892 | 1379.988
Devonshire Building | 2016-11-07 06:00 | 47751.1392 | 1400.004
Devonshire Building | 2016-11-07 06:15 | 47751.4842 | 1379.988
Devonshire Building | 2016-11-07 06:30 | 47751.8342 | 1400.004
Devonshire Building | 2016-11-07 06:45 | 47752.4092 | 2300.004
Devonshire Building | 2016-11-07 07:00 | 47752.7492 | 1360.008
Devonshire Building | 2016-11-07 07:15 | 47753.0892 | 1360.008
Devonshire Building | 2016-11-07 07:30 | 47753.4392 | 1400.004
Devonshire Building | 2016-11-07 07:45 | 47753.7742 | 1339.992
Devonshire Building | 2016-11-07 08:00 | 47754.1142 | 1360.008
Devonshire Building | 2016-11-07 08:15 | 47754.4492 | 1339.992
Devonshire Building | 2016-11-07 08:30 | 47754.8042 | 1419.984
Devonshire Building | 2016-11-07 08:45 | 47755.1442 | 1360.008
Devonshire Building | 2016-11-07 09:00 | 47755.5042 | 1440
Devonshire Building | 2016-11-07 09:15 | 47755.8692 | 1460.016
Devonshire Building | 2016-11-07 09:30 | 47756.2292 | 1440
Devonshire Building | 2016-11-07 09:45 | 47756.8492 | 2480.004
Devonshire Building | 2016-11-07 10:00 | 47757.2542 | 1620
Devonshire Building | 2016-11-07 10:15 | 47757.7242 | 1879.992
Devonshire Building | 2016-11-07 10:30 | 47758.1942 | 1879.992
Devonshire Building | 2016-11-07 10:45 | 47758.6842 | 1959.984
Devonshire Building | 2016-11-07 11:00 | 47759.4442 | 3039.984
Devonshire Building | 2016-11-07 11:15 | 47759.9242 | 1919.988
Devonshire Building | 2016-11-07 11:30 | 47760.3592 | 1739.988
Devonshire Building | 2016-11-07 11:45 | 47760.7792 | 1680.012
Devonshire Building | 2016-11-07 12:00 | 47761.2042 | 1699.992
Devonshire Building | 2016-11-07 12:15 | 47761.6292 | 1699.992
Devonshire Building | 2016-11-07 12:30 | 47762.3142 | 2739.996
Devonshire Building | 2016-11-07 12:45 | 47762.7192 | 1620
Devonshire Building | 2016-11-07 13:00 | 47763.1292 | 1640.016
Devonshire Building | 2016-11-07 13:15 | 47763.5342 | 1620
Devonshire Building | 2016-11-07 13:30 | 47763.9492 | 1659.996
Devonshire Building | 2016-11-07 13:45 | 47764.3592 | 1640.016
Devonshire Building | 2016-11-07 14:00 | 47764.7642 | 1620
Devonshire Building | 2016-11-07 14:15 | 47765.4642 | 2800.008
Devonshire Building | 2016-11-07 14:30 | 47765.8992 | 1739.988
Devonshire Building | 2016-11-07 14:45 | 47766.3342 | 1739.988
Devonshire Building | 2016-11-07 15:00 | 47766.7592 | 1699.992
Devonshire Building | 2016-11-07 15:15 | 47767.1792 | 1680.012
Devonshire Building | 2016-11-07 15:30 | 47767.5842 | 1620
Devonshire Building | 2016-11-07 15:45 | 47768.0192 | 1739.988
Devonshire Building | 2016-11-07 16:00 | 47768.6542 | 2540.016
Devonshire Building | 2016-11-07 16:15 | 47769.0542 | 1599.984
Devonshire Building | 2016-11-07 16:30 | 47769.4642 | 1640.016
Devonshire Building | 2016-11-07 16:45 | 47769.8692 | 1620
Devonshire Building | 2016-11-07 17:00 | 47770.2692 | 1599.984
Devonshire Building | 2016-11-07 17:15 | 47770.6692 | 1599.984
Devonshire Building | 2016-11-07 17:30 | 47771.0642 | 1580.004
Devonshire Building | 2016-11-07 17:45 | 47771.4592 | 1580.004
Devonshire Building | 2016-11-07 18:00 | 47772.1142 | 2620.008
Devonshire Building | 2016-11-07 18:15 | 47772.4992 | 1540.008
Devonshire Building | 2016-11-07 18:30 | 47772.8742 | 1500.012
Devonshire Building | 2016-11-07 18:45 | 47773.2592 | 1540.008
Devonshire Building | 2016-11-07 19:00 | 47773.6392 | 1519.992
Devonshire Building | 2016-11-07 19:15 | 47774.0242 | 1540.008
Devonshire Building | 2016-11-07 19:30 | 47774.4042 | 1519.992
Devonshire Building | 2016-11-07 19:45 | 47774.7842 | 1519.992
Devonshire Building | 2016-11-07 20:00 | 47775.1692 | 1540.008
Devonshire Building | 2016-11-07 20:15 | 47775.5542 | 1540.008
Devonshire Building | 2016-11-07 20:30 | 47775.9342 | 1519.992
Devonshire Building | 2016-11-07 20:45 | 47776.3092 | 1500.012
Devonshire Building | 2016-11-07 21:00 | 47776.6892 | 1519.992
Devonshire Building | 2016-11-07 21:15 | 47777.0642 | 1500.012
Devonshire Building | 2016-11-07 21:30 | 47777.4342 | 1479.996
Devonshire Building | 2016-11-07 21:45 | 47777.8092 | 1500.012
Devonshire Building | 2016-11-07 22:00 | 47778.1942 | 1540.008
Devonshire Building | 2016-11-07 22:15 | 47778.5542 | 1440
Devonshire Building | 2016-11-07 22:30 | 47778.9142 | 1440
Devonshire Building | 2016-11-07 22:45 | 47779.2742 | 1440
Devonshire Building | 2016-11-07 23:00 | 47779.6392 | 1460.016
Devonshire Building | 2016-11-07 23:15 | 47779.9992 | 1440
Devonshire Building | 2016-11-07 23:30 | 47780.3642 | 1460.016
Devonshire Building | 2016-11-07 23:45 | 47780.7292 | 1460.016 | 1339.992
Devonshire Building | 2016-11-08 | 47781.3438 | 2459.988
Devonshire Building | 2016-11-08 00:15 | 47781.7088 | 1460.016
Devonshire Building | 2016-11-08 00:30 | 47782.0738 | 1460.016
Devonshire Building | 2016-11-08 00:45 | 47782.4438 | 1479.996
Devonshire Building | 2016-11-08 01:00 | 47782.8088 | 1460.016
Devonshire Building | 2016-11-08 01:15 | 47783.1788 | 1479.996
Devonshire Building | 2016-11-08 01:30 | 47783.5438 | 1460.016
Devonshire Building | 2016-11-08 01:45 | 47783.9138 | 1479.996
Devonshire Building | 2016-11-08 02:00 | 47784.2788 | 1460.016
Devonshire Building | 2016-11-08 02:15 | 47784.6438 | 1460.016
Devonshire Building | 2016-11-08 02:30 | 47785.0088 | 1460.016
Devonshire Building | 2016-11-08 02:45 | 47785.3738 | 1460.016
Devonshire Building | 2016-11-08 03:00 | 47785.7388 | 1460.016
Devonshire Building | 2016-11-08 03:15 | 47786.1038 | 1460.016
Devonshire Building | 2016-11-08 03:30 | 47786.4688 | 1460.016
Devonshire Building | 2016-11-08 03:45 | 47786.8388 | 1479.996
Devonshire Building | 2016-11-08 04:00 | 47787.2038 | 1460.016
Devonshire Building | 2016-11-08 04:15 | 47787.5638 | 1440
Devonshire Building | 2016-11-08 04:30 | 47787.9288 | 1460.016
Devonshire Building | 2016-11-08 04:45 | 47788.2938 | 1460.016
Devonshire Building | 2016-11-08 05:00 | 47788.6588 | 1460.016
Devonshire Building | 2016-11-08 05:15 | 47789.0238 | 1460.016
Devonshire Building | 2016-11-08 05:30 | 47789.3838 | 1440
Devonshire Building | 2016-11-08 05:45 | 47789.7488 | 1460.016
Devonshire Building | 2016-11-08 06:00 | 47790.1138 | 1460.016
Devonshire Building | 2016-11-08 06:15 | 47790.4788 | 1460.016
Devonshire Building | 2016-11-08 06:30 | 47790.8438 | 1460.016
Devonshire Building | 2016-11-08 06:45 | 47791.2038 | 1440
Devonshire Building | 2016-11-08 07:00 | 47791.5638 | 1440
Devonshire Building | 2016-11-08 07:15 | 47791.9238 | 1440
Devonshire Building | 2016-11-08 07:30 | 47792.2838 | 1440
Devonshire Building | 2016-11-08 07:45 | 47792.9038 | 2480.004
Devonshire Building | 2016-11-08 08:00 | 47793.2788 | 1500.012
Devonshire Building | 2016-11-08 08:15 | 47793.6538 | 1500.012
Devonshire Building | 2016-11-08 08:30 | 47794.0338 | 1519.992
Devonshire Building | 2016-11-08 08:45 | 47794.4088 | 1500.012
Devonshire Building | 2016-11-08 09:00 | 47794.7838 | 1500.012
Devonshire Building | 2016-11-08 09:15 | 47795.1588 | 1500.012
Devonshire Building | 2016-11-08 09:30 | 47795.5338 | 1500.012
Devonshire Building | 2016-11-08 09:45 | 47795.9138 | 1519.992
Devonshire Building | 2016-11-08 10:00 | 47796.2988 | 1540.008
Devonshire Building | 2016-11-08 10:15 | 47796.9838 | 2739.996
Devonshire Building | 2016-11-08 10:30 | 47797.4188 | 1739.988
Devonshire Building | 2016-11-08 10:45 | 47797.9588 | 2160
Devonshire Building | 2016-11-08 11:00 | 47798.4788 | 2080.008
Devonshire Building | 2016-11-08 11:15 | 47798.9688 | 1959.984
Devonshire Building | 2016-11-08 11:30 | 47799.5838 | 2459.988
Devonshire Building | 2016-11-08 11:45 | 47800.1138 | 2120.004
Devonshire Building | 2016-11-08 12:00 | 47800.5238 | 1640.016
Devonshire Building | 2016-11-08 12:15 | 47800.9338 | 1640.016
Devonshire Building | 2016-11-08 12:30 | 47801.3488 | 1659.996
Devonshire Building | 2016-11-08 12:45 | 47801.7638 | 1659.996
Devonshire Building | 2016-11-08 13:00 | 47802.2238 | 1839.996
Devonshire Building | 2016-11-08 13:15 | 47802.8788 | 2620.008
Devonshire Building | 2016-11-08 13:30 | 47803.2888 | 1640.016
Devonshire Building | 2016-11-08 13:45 | 47803.6989 | 1640.016
Devonshire Building | 2016-11-08 14:00 | 47804.1138 | 1659.996
Devonshire Building | 2016-11-08 14:15 | 47804.5239 | 1640.016
Devonshire Building | 2016-11-08 14:30 | 47804.9289 | 1620
Devonshire Building | 2016-11-08 14:45 | 47805.3288 | 1599.984
Devonshire Building | 2016-11-08 15:00 | 47805.7338 | 1620
Devonshire Building | 2016-11-08 15:15 | 47806.1439 | 1640.016
Devonshire Building | 2016-11-08 15:30 | 47806.7839 | 2559.996
Devonshire Building | 2016-11-08 15:45 | 47807.1638 | 1519.992
Devonshire Building | 2016-11-08 16:00 | 47807.5489 | 1540.008
Devonshire Building | 2016-11-08 16:15 | 47807.9339 | 1540.008
Devonshire Building | 2016-11-08 16:30 | 47808.3189 | 1540.008
Devonshire Building | 2016-11-08 16:45 | 47808.7139 | 1580.004
Devonshire Building | 2016-11-08 17:00 | 47809.1039 | 1559.988
Devonshire Building | 2016-11-08 17:15 | 47809.4839 | 1519.992
Devonshire Building | 2016-11-08 17:30 | 47810.1389 | 2620.008
Devonshire Building | 2016-11-08 17:45 | 47810.5189 | 1519.992
Devonshire Building | 2016-11-08 18:00 | 47810.8988 | 1519.992
Devonshire Building | 2016-11-08 18:15 | 47811.2788 | 1519.992
Devonshire Building | 2016-11-08 18:30 | 47811.6539 | 1500.012
Devonshire Building | 2016-11-08 18:45 | 47812.0338 | 1519.992
Devonshire Building | 2016-11-08 19:00 | 47812.4089 | 1500.012
Devonshire Building | 2016-11-08 19:15 | 47812.7839 | 1500.012
Devonshire Building | 2016-11-08 19:30 | 47813.1589 | 1500.012
Devonshire Building | 2016-11-08 19:45 | 47813.5339 | 1500.012
Devonshire Building | 2016-11-08 20:00 | 47813.9139 | 1519.992
Devonshire Building | 2016-11-08 20:15 | 47814.2889 | 1500.012
Devonshire Building | 2016-11-08 20:30 | 47814.6639 | 1500.012
Devonshire Building | 2016-11-08 20:45 | 47815.0389 | 1500.012
Devonshire Building | 2016-11-08 21:00 | 47815.4189 | 1519.992
Devonshire Building | 2016-11-08 21:15 | 47815.7939 | 1500.012
Devonshire Building | 2016-11-08 21:30 | 47816.1689 | 1500.012
Devonshire Building | 2016-11-08 21:45 | 47816.5489 | 1519.992
Devonshire Building | 2016-11-08 22:00 | 47816.9439 | 1580.004
Devonshire Building | 2016-11-08 22:15 | 47817.3139 | 1479.996
Devonshire Building | 2016-11-08 22:30 | 47817.6889 | 1500.012
Devonshire Building | 2016-11-08 22:45 | 47818.0589 | 1479.996
Devonshire Building | 2016-11-08 23:00 | 47818.4339 | 1500.012
Devonshire Building | 2016-11-08 23:15 | 47818.8089 | 1500.012
Devonshire Building | 2016-11-08 23:30 | 47819.1839 | 1500.012
Devonshire Building | 2016-11-08 23:45 | 47819.5589 | 1500.012 | 1440
Devonshire Building | 2016-11-09 | 47819.9336 | 1500.012
Devonshire Building | 2016-11-09 00:15 | 47820.3086 | 1500.012
Devonshire Building | 2016-11-09 00:30 | 47820.6886 | 1519.992
Devonshire Building | 2016-11-09 00:45 | 47821.0686 | 1519.992
Devonshire Building | 2016-11-09 01:00 | 47821.4436 | 1500.012
Devonshire Building | 2016-11-09 01:15 | 47821.8236 | 1519.992
Devonshire Building | 2016-11-09 01:30 | 47822.2036 | 1519.992
Devonshire Building | 2016-11-09 01:45 | 47822.5986 | 1580.004
Devonshire Building | 2016-11-09 02:00 | 47822.9886 | 1559.988
Devonshire Building | 2016-11-09 02:15 | 47823.3786 | 1559.988
Devonshire Building | 2016-11-09 02:30 | 47823.7686 | 1559.988
Devonshire Building | 2016-11-09 02:45 | 47824.1636 | 1580.004
Devonshire Building | 2016-11-09 03:00 | 47824.5536 | 1559.988
Devonshire Building | 2016-11-09 03:15 | 47824.9436 | 1559.988
Devonshire Building | 2016-11-09 03:30 | 47825.3336 | 1559.988
Devonshire Building | 2016-11-09 03:45 | 47825.7236 | 1559.988
Devonshire Building | 2016-11-09 04:00 | 47826.0986 | 1500.012
Devonshire Building | 2016-11-09 04:15 | 47826.4686 | 1479.996
Devonshire Building | 2016-11-09 04:30 | 47826.8436 | 1500.012
Devonshire Building | 2016-11-09 04:45 | 47827.2136 | 1479.996
Devonshire Building | 2016-11-09 05:00 | 47827.5836 | 1479.996
Devonshire Building | 2016-11-09 05:15 | 47827.9536 | 1479.996
Devonshire Building | 2016-11-09 05:30 | 47828.3286 | 1500.012
Devonshire Building | 2016-11-09 05:45 | 47828.6986 | 1479.996
Devonshire Building | 2016-11-09 06:00 | 47829.0686 | 1479.996
Devonshire Building | 2016-11-09 06:15 | 47829.4386 | 1479.996
Devonshire Building | 2016-11-09 06:30 | 47829.8086 | 1479.996
Devonshire Building | 2016-11-09 06:45 | 47830.1736 | 1460.016
Devonshire Building | 2016-11-09 07:00 | 47830.5386 | 1460.016
Devonshire Building | 2016-11-09 07:15 | 47830.9036 | 1460.016
Devonshire Building | 2016-11-09 07:30 | 47831.2986 | 1580.004
Devonshire Building | 2016-11-09 07:45 | 47831.9036 | 2419.992
Devonshire Building | 2016-11-09 08:00 | 47832.2686 | 1460.016
Devonshire Building | 2016-11-09 08:15 | 47832.6286 | 1440
Devonshire Building | 2016-11-09 08:30 | 47832.9936 | 1460.016
Devonshire Building | 2016-11-09 08:45 | 47833.3536 | 1440
Devonshire Building | 2016-11-09 09:00 | 47833.7186 | 1460.016
Devonshire Building | 2016-11-09 09:15 | 47834.0936 | 1500.012
Devonshire Building | 2016-11-09 09:30 | 47834.4586 | 1460.016
Devonshire Building | 2016-11-09 09:45 | 47834.8286 | 1479.996
Devonshire Building | 2016-11-09 10:00 | 47835.2036 | 1500.012
Devonshire Building | 2016-11-09 10:15 | 47835.8386 | 2540.016
Devonshire Building | 2016-11-09 10:30 | 47836.2086 | 1479.996
Devonshire Building | 2016-11-09 10:45 | 47836.5986 | 1559.988
Devonshire Building | 2016-11-09 11:00 | 47837.0086 | 1640.016
Devonshire Building | 2016-11-09 11:15 | 47837.4336 | 1699.992
Devonshire Building | 2016-11-09 11:30 | 47838.0436 | 2440.008
Devonshire Building | 2016-11-09 11:45 | 47838.6686 | 2499.984
Devonshire Building | 2016-11-09 12:00 | 47839.1536 | 1940.004
Devonshire Building | 2016-11-09 12:15 | 47839.6086 | 1820.016
Devonshire Building | 2016-11-09 12:30 | 47840.0536 | 1779.984
Devonshire Building | 2016-11-09 12:45 | 47840.4886 | 1739.988
Devonshire Building | 2016-11-09 13:00 | 47840.9186 | 1720.008
Devonshire Building | 2016-11-09 13:15 | 47841.6136 | 2779.992
Devonshire Building | 2016-11-09 13:30 | 47842.0186 | 1620
Devonshire Building | 2016-11-09 13:45 | 47842.4236 | 1620
Devonshire Building | 2016-11-09 14:00 | 47842.8336 | 1640.016
Devonshire Building | 2016-11-09 14:15 | 47843.2536 | 1680.012
Devonshire Building | 2016-11-09 14:30 | 47843.6686 | 1659.996
Devonshire Building | 2016-11-09 14:45 | 47844.3636 | 2779.992
Devonshire Building | 2016-11-09 15:00 | 47844.7736 | 1640.016
Devonshire Building | 2016-11-09 15:15 | 47845.1936 | 1680.012
Devonshire Building | 2016-11-09 15:30 | 47845.6086 | 1659.996
Devonshire Building | 2016-11-09 15:45 | 47846.0236 | 1659.996
Devonshire Building | 2016-11-09 16:00 | 47846.4436 | 1680.012
Devonshire Building | 2016-11-09 16:15 | 47846.8586 | 1659.996
Devonshire Building | 2016-11-09 16:30 | 47847.2686 | 1640.016
Devonshire Building | 2016-11-09 16:45 | 47847.9586 | 2760.012
Devonshire Building | 2016-11-09 17:00 | 47848.3736 | 1659.996
Devonshire Building | 2016-11-09 17:15 | 47848.7936 | 1680.012
Devonshire Building | 2016-11-09 17:30 | 47849.2186 | 1699.992
Devonshire Building | 2016-11-09 17:45 | 47849.6436 | 1699.992
Devonshire Building | 2016-11-09 18:00 | 47850.0636 | 1680.012
Devonshire Building | 2016-11-09 18:15 | 47850.4736 | 1640.016
Devonshire Building | 2016-11-09 18:30 | 47850.8836 | 1640.016
Devonshire Building | 2016-11-09 18:45 | 47851.2986 | 1659.996
Devonshire Building | 2016-11-09 19:00 | 47851.7136 | 1659.996
Devonshire Building | 2016-11-09 19:15 | 47852.1236 | 1640.016
Devonshire Building | 2016-11-09 19:30 | 47852.5286 | 1620
Devonshire Building | 2016-11-09 19:45 | 47852.9336 | 1620
Devonshire Building | 2016-11-09 20:00 | 47853.3336 | 1599.984
Devonshire Building | 2016-11-09 20:15 | 47853.7336 | 1599.984
Devonshire Building | 2016-11-09 20:30 | 47854.1286 | 1580.004
Devonshire Building | 2016-11-09 20:45 | 47854.5286 | 1599.984
Devonshire Building | 2016-11-09 21:00 | 47855.1786 | 2599.992
Devonshire Building | 2016-11-09 21:15 | 47855.5686 | 1559.988
Devonshire Building | 2016-11-09 21:30 | 47855.9586 | 1559.988
Devonshire Building | 2016-11-09 21:45 | 47856.3486 | 1559.988
Devonshire Building | 2016-11-09 22:00 | 47856.7336 | 1540.008
Devonshire Building | 2016-11-09 22:15 | 47857.1086 | 1500.012
Devonshire Building | 2016-11-09 22:30 | 47857.4836 | 1500.012
Devonshire Building | 2016-11-09 22:45 | 47857.8586 | 1500.012
Devonshire Building | 2016-11-09 23:00 | 47858.2336 | 1500.012
Devonshire Building | 2016-11-09 23:15 | 47858.6136 | 1519.992
Devonshire Building | 2016-11-09 23:30 | 47858.9886 | 1500.012
Devonshire Building | 2016-11-09 23:45 | 47859.3686 | 1519.992 | 1440
Devonshire Building | 2016-11-10 | 47859.75 | 1519.992
Devonshire Building | 2016-11-10 00:15 | 47860.13 | 1519.992
Devonshire Building | 2016-11-10 00:30 | 47860.51 | 1519.992
Devonshire Building | 2016-11-10 00:45 | 47860.895 | 1540.008
Devonshire Building | 2016-11-10 01:00 | 47861.275 | 1519.992
Devonshire Building | 2016-11-10 01:15 | 47861.655 | 1519.992
Devonshire Building | 2016-11-10 01:30 | 47862.035 | 1519.992
Devonshire Building | 2016-11-10 01:45 | 47862.42 | 1540.008
Devonshire Building | 2016-11-10 02:00 | 47862.805 | 1540.008
Devonshire Building | 2016-11-10 02:15 | 47863.185 | 1519.992
Devonshire Building | 2016-11-10 02:30 | 47863.57 | 1540.008
Devonshire Building | 2016-11-10 02:45 | 47863.955 | 1540.008
Devonshire Building | 2016-11-10 03:00 | 47864.335 | 1519.992
Devonshire Building | 2016-11-10 03:15 | 47864.72 | 1540.008
Devonshire Building | 2016-11-10 03:30 | 47865.105 | 1540.008
Devonshire Building | 2016-11-10 03:45 | 47865.49 | 1540.008
Devonshire Building | 2016-11-10 04:00 | 47865.875 | 1540.008
Devonshire Building | 2016-11-10 04:15 | 47866.255 | 1519.992
Devonshire Building | 2016-11-10 04:30 | 47866.64 | 1540.008
Devonshire Building | 2016-11-10 04:45 | 47867.025 | 1540.008
Devonshire Building | 2016-11-10 05:00 | 47867.405 | 1519.992
Devonshire Building | 2016-11-10 05:15 | 47867.79 | 1540.008
Devonshire Building | 2016-11-10 05:30 | 47868.17 | 1519.992
Devonshire Building | 2016-11-10 05:45 | 47868.55 | 1519.992
Devonshire Building | 2016-11-10 06:00 | 47868.935 | 1540.008
Devonshire Building | 2016-11-10 06:15 | 47869.315 | 1519.992
Devonshire Building | 2016-11-10 06:30 | 47869.695 | 1519.992
Devonshire Building | 2016-11-10 06:45 | 47870.075 | 1519.992
Devonshire Building | 2016-11-10 07:00 | 47870.45 | 1500.012
Devonshire Building | 2016-11-10 07:15 | 47870.825 | 1500.012
Devonshire Building | 2016-11-10 07:30 | 47871.2 | 1500.012
Devonshire Building | 2016-11-10 07:45 | 47871.575 | 1500.012
Devonshire Building | 2016-11-10 08:00 | 47872.215 | 2559.996
Devonshire Building | 2016-11-10 08:15 | 47872.585 | 1479.996
Devonshire Building | 2016-11-10 08:30 | 47872.955 | 1479.996
Devonshire Building | 2016-11-10 08:45 | 47873.325 | 1479.996
Devonshire Building | 2016-11-10 09:00 | 47873.705 | 1519.992
Devonshire Building | 2016-11-10 09:15 | 47874.085 | 1519.992
Devonshire Building | 2016-11-10 09:30 | 47874.465 | 1519.992
Devonshire Building | 2016-11-10 09:45 | 47874.84 | 1500.012
Devonshire Building | 2016-11-10 10:00 | 47875.22 | 1519.992
Devonshire Building | 2016-11-10 10:15 | 47875.605 | 1540.008
Devonshire Building | 2016-11-10 10:30 | 47876.27 | 2660.004
Devonshire Building | 2016-11-10 10:45 | 47876.69 | 1680.012
Devonshire Building | 2016-11-10 11:00 | 47877.135 | 1779.984
Devonshire Building | 2016-11-10 11:15 | 47877.585 | 1800
Devonshire Building | 2016-11-10 11:30 | 47878.03 | 1779.984
Devonshire Building | 2016-11-10 11:45 | 47878.6 | 2279.988
Devonshire Building | 2016-11-10 12:00 | 47879.185 | 2340
Devonshire Building | 2016-11-10 12:15 | 47879.625 | 1760.004
Devonshire Building | 2016-11-10 12:30 | 47880.065 | 1760.004
Devonshire Building | 2016-11-10 12:45 | 47880.505 | 1760.004
Devonshire Building | 2016-11-10 13:00 | 47880.945 | 1760.004
Devonshire Building | 2016-11-10 13:15 | 47881.69 | 2980.008
Devonshire Building | 2016-11-10 13:30 | 47882.155 | 1860.012
Devonshire Building | 2016-11-10 13:45 | 47882.625 | 1879.992
Devonshire Building | 2016-11-10 14:00 | 47883.09 | 1860.012
Devonshire Building | 2016-11-10 14:15 | 47883.555 | 1860.012
Devonshire Building | 2016-11-10 14:30 | 47884.02 | 1860.012
Devonshire Building | 2016-11-10 14:45 | 47884.49 | 1879.992
Devonshire Building | 2016-11-10 15:00 | 47885.245 | 3020.004
Devonshire Building | 2016-11-10 15:15 | 47885.875 | 2520
Devonshire Building | 2016-11-10 15:30 | 47886.45 | 2300.004
Devonshire Building | 2016-11-10 15:45 | 47887 | 2199.996
Devonshire Building | 2016-11-10 16:00 | 47887.52 | 2080.008
Devonshire Building | 2016-11-10 16:15 | 47888.02 | 2000.016
Devonshire Building | 2016-11-10 16:30 | 47888.5 | 1919.988
Devonshire Building | 2016-11-10 16:45 | 47888.955 | 1820.016
Devonshire Building | 2016-11-10 17:00 | 47889.665 | 2840.004
Devonshire Building | 2016-11-10 17:15 | 47890.075 | 1640.016
Devonshire Building | 2016-11-10 17:30 | 47890.505 | 1720.008
Devonshire Building | 2016-11-10 17:45 | 47890.905 | 1599.984
Devonshire Building | 2016-11-10 18:00 | 47891.3 | 1580.004
Devonshire Building | 2016-11-10 18:15 | 47891.7 | 1599.984
Devonshire Building | 2016-11-10 18:30 | 47892.095 | 1580.004
Devonshire Building | 2016-11-10 18:45 | 47892.495 | 1599.984
Devonshire Building | 2016-11-10 19:00 | 47892.925 | 1720.008
Devonshire Building | 2016-11-10 19:15 | 47893.355 | 1720.008
Devonshire Building | 2016-11-10 19:30 | 47893.785 | 1720.008
Devonshire Building | 2016-11-10 19:45 | 47894.21 | 1699.992
Devonshire Building | 2016-11-10 20:00 | 47894.63 | 1680.012
Devonshire Building | 2016-11-10 20:15 | 47895.05 | 1680.012
Devonshire Building | 2016-11-10 20:30 | 47895.46 | 1640.016
Devonshire Building | 2016-11-10 20:45 | 47895.865 | 1620
Devonshire Building | 2016-11-10 21:00 | 47896.27 | 1620
Devonshire Building | 2016-11-10 21:15 | 47896.67 | 1599.984
Devonshire Building | 2016-11-10 21:30 | 47897.07 | 1599.984
Devonshire Building | 2016-11-10 21:45 | 47897.465 | 1580.004
Devonshire Building | 2016-11-10 22:00 | 47897.885 | 1680.012
Devonshire Building | 2016-11-10 22:15 | 47898.27 | 1540.008
Devonshire Building | 2016-11-10 22:30 | 47898.66 | 1559.988
Devonshire Building | 2016-11-10 22:45 | 47899.045 | 1540.008
Devonshire Building | 2016-11-10 23:00 | 47899.435 | 1559.988
Devonshire Building | 2016-11-10 23:15 | 47899.825 | 1559.988
Devonshire Building | 2016-11-10 23:30 | 47900.21 | 1540.008
Devonshire Building | 2016-11-10 23:45 | 47900.6 | 1559.988 | 1479.996
Devonshire Building | 2016-11-11 | 47900.9883 | 1559.988
Devonshire Building | 2016-11-11 00:15 | 47901.3783 | 1559.988
Devonshire Building | 2016-11-11 00:30 | 47901.7733 | 1580.004
Devonshire Building | 2016-11-11 00:45 | 47902.1633 | 1559.988
Devonshire Building | 2016-11-11 01:00 | 47902.5533 | 1559.988
Devonshire Building | 2016-11-11 01:15 | 47902.9483 | 1580.004
Devonshire Building | 2016-11-11 01:30 | 47903.3383 | 1559.988
Devonshire Building | 2016-11-11 01:45 | 47903.7333 | 1580.004
Devonshire Building | 2016-11-11 02:00 | 47904.3783 | 2580.012
Devonshire Building | 2016-11-11 02:15 | 47904.7683 | 1559.988
Devonshire Building | 2016-11-11 02:30 | 47905.1583 | 1559.988
Devonshire Building | 2016-11-11 02:45 | 47905.5483 | 1559.988
Devonshire Building | 2016-11-11 03:00 | 47905.9383 | 1559.988
Devonshire Building | 2016-11-11 03:15 | 47906.3283 | 1559.988
Devonshire Building | 2016-11-11 03:30 | 47906.7133 | 1540.008
Devonshire Building | 2016-11-11 03:45 | 47907.1033 | 1559.988
Devonshire Building | 2016-11-11 04:00 | 47907.4933 | 1559.988
Devonshire Building | 2016-11-11 04:15 | 47907.8833 | 1559.988
Devonshire Building | 2016-11-11 04:30 | 47908.2732 | 1559.988
Devonshire Building | 2016-11-11 04:45 | 47908.6583 | 1540.008
Devonshire Building | 2016-11-11 05:00 | 47909.0482 | 1559.988
Devonshire Building | 2016-11-11 05:15 | 47909.4382 | 1559.988
Devonshire Building | 2016-11-11 05:30 | 47909.8232 | 1540.008
Devonshire Building | 2016-11-11 05:45 | 47910.2082 | 1540.008
Devonshire Building | 2016-11-11 06:00 | 47910.5933 | 1540.008
Devonshire Building | 2016-11-11 06:15 | 47910.9783 | 1540.008
Devonshire Building | 2016-11-11 06:30 | 47911.3633 | 1540.008
Devonshire Building | 2016-11-11 06:45 | 47911.7433 | 1519.992
Devonshire Building | 2016-11-11 07:00 | 47912.1233 | 1519.992
Devonshire Building | 2016-11-11 07:15 | 47912.5083 | 1540.008
Devonshire Building | 2016-11-11 07:30 | 47912.8883 | 1519.992
Devonshire Building | 2016-11-11 07:45 | 47913.2682 | 1519.992
Devonshire Building | 2016-11-11 08:00 | 47913.6533 | 1540.008
Devonshire Building | 2016-11-11 08:15 | 47914.0332 | 1519.992
Devonshire Building | 2016-11-11 08:30 | 47914.4132 | 1519.992
Devonshire Building | 2016-11-11 08:45 | 47914.7982 | 1540.008
Devonshire Building | 2016-11-11 09:00 | 47915.1782 | 1519.992
Devonshire Building | 2016-11-11 09:15 | 47915.5582 | 1519.992
Devonshire Building | 2016-11-11 09:30 | 47915.9432 | 1540.008
Devonshire Building | 2016-11-11 09:45 | 47916.3332 | 1559.988
Devonshire Building | 2016-11-11 10:00 | 47917.0382 | 2819.988
Devonshire Building | 2016-11-11 10:15 | 47917.4932 | 1820.016
Devonshire Building | 2016-11-11 10:30 | 47917.9782 | 1940.004
Devonshire Building | 2016-11-11 10:45 | 47918.5282 | 2199.996
Devonshire Building | 2016-11-11 11:00 | 47919.0432 | 2059.992
Devonshire Building | 2016-11-11 11:15 | 47919.8082 | 3060
Devonshire Building | 2016-11-11 11:30 | 47920.2682 | 1839.996
Devonshire Building | 2016-11-11 11:45 | 47920.7332 | 1860.012
Devonshire Building | 2016-11-11 12:00 | 47921.1832 | 1800
Devonshire Building | 2016-11-11 12:15 | 47921.6232 | 1760.004
Devonshire Building | 2016-11-11 12:30 | 47922.0582 | 1739.988
Devonshire Building | 2016-11-11 12:45 | 47922.7432 | 2739.996
Devonshire Building | 2016-11-11 13:00 | 47923.1782 | 1739.988
Devonshire Building | 2016-11-11 13:15 | 47923.6282 | 1800
Devonshire Building | 2016-11-11 13:30 | 47924.0932 | 1860.012
Devonshire Building | 2016-11-11 13:45 | 47924.5532 | 1839.996
Devonshire Building | 2016-11-11 14:00 | 47925.0232 | 1879.992
Devonshire Building | 2016-11-11 14:15 | 47925.5332 | 2040.012
Devonshire Building | 2016-11-11 14:30 | 47926.0582 | 2099.988
Devonshire Building | 2016-11-11 14:45 | 47926.6932 | 2540.016
Devonshire Building | 2016-11-11 15:00 | 47927.2932 | 2400.012
Devonshire Building | 2016-11-11 15:15 | 47927.7482 | 1820.016
Devonshire Building | 2016-11-11 15:30 | 47928.1932 | 1779.984
Devonshire Building | 2016-11-11 15:45 | 47928.6382 | 1779.984
Devonshire Building | 2016-11-11 16:00 | 47929.0882 | 1800
Devonshire Building | 2016-11-11 16:15 | 47929.5232 | 1739.988
Devonshire Building | 2016-11-11 16:30 | 47929.9982 | 1900.008
Devonshire Building | 2016-11-11 16:45 | 47930.4782 | 1919.988
Devonshire Building | 2016-11-11 17:00 | 47930.9582 | 1919.988
Devonshire Building | 2016-11-11 17:15 | 47931.7232 | 3060
Devonshire Building | 2016-11-11 17:30 | 47932.2232 | 2000.016
Devonshire Building | 2016-11-11 17:45 | 47932.6982 | 1900.008
Devonshire Building | 2016-11-11 18:00 | 47933.1732 | 1900.008
Devonshire Building | 2016-11-11 18:15 | 47933.6232 | 1800
Devonshire Building | 2016-11-11 18:30 | 47934.0632 | 1760.004
Devonshire Building | 2016-11-11 18:45 | 47934.4882 | 1699.992
Devonshire Building | 2016-11-11 19:00 | 47934.9032 | 1659.996
Devonshire Building | 2016-11-11 19:15 | 47935.3132 | 1640.016
Devonshire Building | 2016-11-11 19:30 | 47935.7132 | 1599.984
Devonshire Building | 2016-11-11 19:45 | 47936.1132 | 1599.984
Devonshire Building | 2016-11-11 20:00 | 47936.5132 | 1599.984
Devonshire Building | 2016-11-11 20:15 | 47936.9082 | 1580.004
Devonshire Building | 2016-11-11 20:30 | 47937.3082 | 1599.984
Devonshire Building | 2016-11-11 20:45 | 47937.7032 | 1580.004
Devonshire Building | 2016-11-11 21:00 | 47938.0982 | 1580.004
Devonshire Building | 2016-11-11 21:15 | 47938.4932 | 1580.004
Devonshire Building | 2016-11-11 21:30 | 47938.8882 | 1580.004
Devonshire Building | 2016-11-11 21:45 | 47939.2782 | 1559.988
Devonshire Building | 2016-11-11 22:00 | 47939.6932 | 1659.996
Devonshire Building | 2016-11-11 22:15 | 47940.0832 | 1559.988
Devonshire Building | 2016-11-11 22:30 | 47940.4682 | 1540.008
Devonshire Building | 2016-11-11 22:45 | 47940.8582 | 1559.988
Devonshire Building | 2016-11-11 23:00 | 47941.2532 | 1580.004
Devonshire Building | 2016-11-11 23:15 | 47941.6432 | 1559.988
Devonshire Building | 2016-11-11 23:30 | 47942.0332 | 1559.988
Devonshire Building | 2016-11-11 23:45 | 47942.4232 | 1559.988 | 1519.992
Devonshire Building | 2016-11-12 | 47942.8164 | 1559.988
Devonshire Building | 2016-11-12 00:15 | 47943.2064 | 1559.988
Devonshire Building | 2016-11-12 00:30 | 47943.6014 | 1580.004
Devonshire Building | 2016-11-12 00:45 | 47943.9964 | 1580.004
Devonshire Building | 2016-11-12 01:00 | 47944.3914 | 1580.004
Devonshire Building | 2016-11-12 01:15 | 47944.7864 | 1580.004
Devonshire Building | 2016-11-12 01:30 | 47945.1814 | 1580.004
Devonshire Building | 2016-11-12 01:45 | 47945.5764 | 1580.004
Devonshire Building | 2016-11-12 02:00 | 47945.9714 | 1580.004
Devonshire Building | 2016-11-12 02:15 | 47946.3664 | 1580.004
Devonshire Building | 2016-11-12 02:30 | 47946.7614 | 1580.004
Devonshire Building | 2016-11-12 02:45 | 47947.1564 | 1580.004
Devonshire Building | 2016-11-12 03:00 | 47947.5514 | 1580.004
Devonshire Building | 2016-11-12 03:15 | 47947.9414 | 1559.988
Devonshire Building | 2016-11-12 03:30 | 47948.3364 | 1580.004
Devonshire Building | 2016-11-12 03:45 | 47948.7314 | 1580.004
Devonshire Building | 2016-11-12 04:00 | 47949.1264 | 1580.004
Devonshire Building | 2016-11-12 04:15 | 47949.5214 | 1580.004
Devonshire Building | 2016-11-12 04:30 | 47949.9164 | 1580.004
Devonshire Building | 2016-11-12 04:45 | 47950.3164 | 1599.984
Devonshire Building | 2016-11-12 05:00 | 47950.7114 | 1580.004
Devonshire Building | 2016-11-12 05:15 | 47951.1064 | 1580.004
Devonshire Building | 2016-11-12 05:30 | 47951.5014 | 1580.004
Devonshire Building | 2016-11-12 05:45 | 47951.8964 | 1580.004
Devonshire Building | 2016-11-12 06:00 | 47952.2914 | 1580.004
Devonshire Building | 2016-11-12 06:15 | 47952.6814 | 1559.988
Devonshire Building | 2016-11-12 06:30 | 47953.0764 | 1580.004
Devonshire Building | 2016-11-12 06:45 | 47953.4664 | 1559.988
Devonshire Building | 2016-11-12 07:00 | 47953.8614 | 1580.004
Devonshire Building | 2016-11-12 07:15 | 47954.2514 | 1559.988
Devonshire Building | 2016-11-12 07:30 | 47954.6414 | 1559.988
Devonshire Building | 2016-11-12 07:45 | 47955.0314 | 1559.988
Devonshire Building | 2016-11-12 08:00 | 47955.4214 | 1559.988
Devonshire Building | 2016-11-12 08:15 | 47955.8064 | 1540.008
Devonshire Building | 2016-11-12 08:30 | 47956.1964 | 1559.988
Devonshire Building | 2016-11-12 08:45 | 47956.5814 | 1540.008
Devonshire Building | 2016-11-12 09:00 | 47956.9664 | 1540.008
Devonshire Building | 2016-11-12 09:15 | 47957.3514 | 1540.008
Devonshire Building | 2016-11-12 09:30 | 47957.7364 | 1540.008
Devonshire Building | 2016-11-12 09:45 | 47958.1214 | 1540.008
Devonshire Building | 2016-11-12 10:00 | 47958.5014 | 1519.992
Devonshire Building | 2016-11-12 10:15 | 47958.8814 | 1519.992
Devonshire Building | 2016-11-12 10:30 | 47959.2664 | 1540.008
Devonshire Building | 2016-11-12 10:45 | 47959.9014 | 2540.016
Devonshire Building | 2016-11-12 11:00 | 47960.2814 | 1519.992
Devonshire Building | 2016-11-12 11:15 | 47960.6614 | 1519.992
Devonshire Building | 2016-11-12 11:30 | 47961.0464 | 1540.008
Devonshire Building | 2016-11-12 11:45 | 47961.4264 | 1519.992
Devonshire Building | 2016-11-12 12:00 | 47961.8064 | 1519.992
Devonshire Building | 2016-11-12 12:15 | 47962.1914 | 1540.008
Devonshire Building | 2016-11-12 12:30 | 47962.5714 | 1519.992
Devonshire Building | 2016-11-12 12:45 | 47962.9564 | 1540.008
Devonshire Building | 2016-11-12 13:00 | 47963.3414 | 1540.008
Devonshire Building | 2016-11-12 13:15 | 47963.7264 | 1540.008
Devonshire Building | 2016-11-12 13:30 | 47964.1164 | 1559.988
Devonshire Building | 2016-11-12 13:45 | 47964.5214 | 1620
Devonshire Building | 2016-11-12 14:00 | 47964.9264 | 1620
Devonshire Building | 2016-11-12 14:15 | 47965.3264 | 1599.984
Devonshire Building | 2016-11-12 14:30 | 47965.7314 | 1620
Devonshire Building | 2016-11-12 14:45 | 47966.1364 | 1620
Devonshire Building | 2016-11-12 15:00 | 47966.5364 | 1599.984
Devonshire Building | 2016-11-12 15:15 | 47966.9414 | 1620
Devonshire Building | 2016-11-12 15:30 | 47967.3464 | 1620
Devonshire Building | 2016-11-12 15:45 | 47967.7464 | 1599.984
Devonshire Building | 2016-11-12 16:00 | 47968.1514 | 1620
Devonshire Building | 2016-11-12 16:15 | 47968.5414 | 1559.988
Devonshire Building | 2016-11-12 16:30 | 47968.9264 | 1540.008
Devonshire Building | 2016-11-12 16:45 | 47969.3114 | 1540.008
Devonshire Building | 2016-11-12 17:00 | 47969.6964 | 1540.008
Devonshire Building | 2016-11-12 17:15 | 47970.0814 | 1540.008
Devonshire Building | 2016-11-12 17:30 | 47970.4664 | 1540.008
Devonshire Building | 2016-11-12 17:45 | 47970.8514 | 1540.008
Devonshire Building | 2016-11-12 18:00 | 47971.2364 | 1540.008
Devonshire Building | 2016-11-12 18:15 | 47971.6214 | 1540.008
Devonshire Building | 2016-11-12 18:30 | 47972.0064 | 1540.008
Devonshire Building | 2016-11-12 18:45 | 47972.3864 | 1519.992
Devonshire Building | 2016-11-12 19:00 | 47972.7714 | 1540.008
Devonshire Building | 2016-11-12 19:15 | 47973.1564 | 1540.008
Devonshire Building | 2016-11-12 19:30 | 47973.5414 | 1540.008
Devonshire Building | 2016-11-12 19:45 | 47973.9264 | 1540.008
Devonshire Building | 2016-11-12 20:00 | 47974.3114 | 1540.008
Devonshire Building | 2016-11-12 20:15 | 47974.6964 | 1540.008
Devonshire Building | 2016-11-12 20:30 | 47975.0814 | 1540.008
Devonshire Building | 2016-11-12 20:45 | 47975.4714 | 1559.988
Devonshire Building | 2016-11-12 21:00 | 47975.8564 | 1540.008
Devonshire Building | 2016-11-12 21:15 | 47976.2464 | 1559.988
Devonshire Building | 2016-11-12 21:30 | 47976.6314 | 1540.008
Devonshire Building | 2016-11-12 21:45 | 47977.0214 | 1559.988
Devonshire Building | 2016-11-12 22:00 | 47977.4314 | 1640.016
Devonshire Building | 2016-11-12 22:15 | 47977.8164 | 1540.008
Devonshire Building | 2016-11-12 22:30 | 47978.2064 | 1559.988
Devonshire Building | 2016-11-12 22:45 | 47978.5964 | 1559.988
Devonshire Building | 2016-11-12 23:00 | 47978.9864 | 1559.988
Devonshire Building | 2016-11-12 23:15 | 47979.3714 | 1540.008
Devonshire Building | 2016-11-12 23:30 | 47979.7614 | 1559.988
Devonshire Building | 2016-11-12 23:45 | 47980.1514 | 1559.988 | 1519.992
Devonshire Building | 2016-11-13 | 47980.5391 | 1559.988
Devonshire Building | 2016-11-13 00:15 | 47980.9291 | 1559.988
Devonshire Building | 2016-11-13 00:30 | 47981.3191 | 1559.988
Devonshire Building | 2016-11-13 00:45 | 47981.7141 | 1580.004
Devonshire Building | 2016-11-13 01:00 | 47982.1041 | 1559.988
Devonshire Building | 2016-11-13 01:15 | 47982.494 | 1559.988
Devonshire Building | 2016-11-13 01:30 | 47982.889 | 1580.004
Devonshire Building | 2016-11-13 01:45 | 47983.279 | 1559.988
Devonshire Building | 2016-11-13 02:00 | 47983.669 | 1559.988
Devonshire Building | 2016-11-13 02:15 | 47984.059 | 1559.988
Devonshire Building | 2016-11-13 02:30 | 47984.454 | 1580.004
Devonshire Building | 2016-11-13 02:45 | 47984.844 | 1559.988
Devonshire Building | 2016-11-13 03:00 | 47985.234 | 1559.988
Devonshire Building | 2016-11-13 03:15 | 47985.624 | 1559.988
Devonshire Building | 2016-11-13 03:30 | 47986.014 | 1559.988
Devonshire Building | 2016-11-13 03:45 | 47986.404 | 1559.988
Devonshire Building | 2016-11-13 04:00 | 47987.049 | 2580.012
Devonshire Building | 2016-11-13 04:15 | 47987.439 | 1559.988
Devonshire Building | 2016-11-13 04:30 | 47987.834 | 1580.004
Devonshire Building | 2016-11-13 04:45 | 47988.224 | 1559.988
Devonshire Building | 2016-11-13 05:00 | 47988.614 | 1559.988
Devonshire Building | 2016-11-13 05:15 | 47989.004 | 1559.988
Devonshire Building | 2016-11-13 05:30 | 47989.399 | 1580.004
Devonshire Building | 2016-11-13 05:45 | 47989.789 | 1559.988
Devonshire Building | 2016-11-13 06:00 | 47990.179 | 1559.988
Devonshire Building | 2016-11-13 06:15 | 47990.574 | 1580.004
Devonshire Building | 2016-11-13 06:30 | 47990.964 | 1559.988
Devonshire Building | 2016-11-13 06:45 | 47991.354 | 1559.988
Devonshire Building | 2016-11-13 07:00 | 47991.744 | 1559.988
Devonshire Building | 2016-11-13 07:15 | 47992.134 | 1559.988
Devonshire Building | 2016-11-13 07:30 | 47992.524 | 1559.988
Devonshire Building | 2016-11-13 07:45 | 47992.914 | 1559.988
Devonshire Building | 2016-11-13 08:00 | 47993.304 | 1559.988
Devonshire Building | 2016-11-13 08:15 | 47993.694 | 1559.988
Devonshire Building | 2016-11-13 08:30 | 47994.079 | 1540.008
Devonshire Building | 2016-11-13 08:45 | 47994.464 | 1540.008
Devonshire Building | 2016-11-13 09:00 | 47994.849 | 1540.008
Devonshire Building | 2016-11-13 09:15 | 47995.234 | 1540.008
Devonshire Building | 2016-11-13 09:30 | 47995.614 | 1519.992
Devonshire Building | 2016-11-13 09:45 | 47995.999 | 1540.008
Devonshire Building | 2016-11-13 10:00 | 47996.379 | 1519.992
Devonshire Building | 2016-11-13 10:15 | 47996.764 | 1540.008
Devonshire Building | 2016-11-13 10:30 | 47997.144 | 1519.992
Devonshire Building | 2016-11-13 10:45 | 47997.529 | 1540.008
Devonshire Building | 2016-11-13 11:00 | 47997.919 | 1559.988
Devonshire Building | 2016-11-13 11:15 | 47998.299 | 1519.992
Devonshire Building | 2016-11-13 11:30 | 47998.684 | 1540.008
Devonshire Building | 2016-11-13 11:45 | 47999.069 | 1540.008
Devonshire Building | 2016-11-13 12:00 | 47999.449 | 1519.992
Devonshire Building | 2016-11-13 12:15 | 47999.834 | 1540.008
Devonshire Building | 2016-11-13 12:30 | 48000.219 | 1540.008
Devonshire Building | 2016-11-13 12:45 | 48000.604 | 1540.008
Devonshire Building | 2016-11-13 13:00 | 48000.989 | 1540.008
Devonshire Building | 2016-11-13 13:15 | 48001.374 | 1540.008
Devonshire Building | 2016-11-13 13:30 | 48001.769 | 1580.004
Devonshire Building | 2016-11-13 13:45 | 48002.169 | 1599.984
Devonshire Building | 2016-11-13 14:00 | 48002.574 | 1620
Devonshire Building | 2016-11-13 14:15 | 48002.979 | 1620
Devonshire Building | 2016-11-13 14:30 | 48003.379 | 1599.984
Devonshire Building | 2016-11-13 14:45 | 48003.784 | 1620
Devonshire Building | 2016-11-13 15:00 | 48004.184 | 1599.984
Devonshire Building | 2016-11-13 15:15 | 48004.589 | 1620
Devonshire Building | 2016-11-13 15:30 | 48004.989 | 1599.984
Devonshire Building | 2016-11-13 15:45 | 48005.399 | 1640.016
Devonshire Building | 2016-11-13 16:00 | 48005.789 | 1559.988
Devonshire Building | 2016-11-13 16:15 | 48006.174 | 1540.008
Devonshire Building | 2016-11-13 16:30 | 48006.559 | 1540.008
Devonshire Building | 2016-11-13 16:45 | 48006.949 | 1559.988
Devonshire Building | 2016-11-13 17:00 | 48007.334 | 1540.008
Devonshire Building | 2016-11-13 17:15 | 48007.719 | 1540.008
Devonshire Building | 2016-11-13 17:30 | 48008.104 | 1540.008
Devonshire Building | 2016-11-13 17:45 | 48008.489 | 1540.008
Devonshire Building | 2016-11-13 18:00 | 48008.869 | 1519.992
Devonshire Building | 2016-11-13 18:15 | 48009.254 | 1540.008
Devonshire Building | 2016-11-13 18:30 | 48009.639 | 1540.008
Devonshire Building | 2016-11-13 18:45 | 48010.024 | 1540.008
Devonshire Building | 2016-11-13 19:00 | 48010.409 | 1540.008
Devonshire Building | 2016-11-13 19:15 | 48010.794 | 1540.008
Devonshire Building | 2016-11-13 19:30 | 48011.174 | 1519.992
Devonshire Building | 2016-11-13 19:45 | 48011.564 | 1559.988
Devonshire Building | 2016-11-13 20:00 | 48011.949 | 1540.008
Devonshire Building | 2016-11-13 20:15 | 48012.334 | 1540.008
Devonshire Building | 2016-11-13 20:30 | 48012.724 | 1559.988
Devonshire Building | 2016-11-13 20:45 | 48013.109 | 1540.008
Devonshire Building | 2016-11-13 21:00 | 48013.494 | 1540.008
Devonshire Building | 2016-11-13 21:15 | 48013.884 | 1559.988
Devonshire Building | 2016-11-13 21:30 | 48014.269 | 1540.008
Devonshire Building | 2016-11-13 21:45 | 48014.654 | 1540.008
Devonshire Building | 2016-11-13 22:00 | 48015.064 | 1640.016
Devonshire Building | 2016-11-13 22:15 | 48015.449 | 1540.008
Devonshire Building | 2016-11-13 22:30 | 48015.834 | 1540.008
Devonshire Building | 2016-11-13 22:45 | 48016.224 | 1559.988
Devonshire Building | 2016-11-13 23:00 | 48016.609 | 1540.008
Devonshire Building | 2016-11-13 23:15 | 48016.994 | 1540.008
Devonshire Building | 2016-11-13 23:30 | 48017.379 | 1540.008
Devonshire Building | 2016-11-13 23:45 | 48017.769 | 1559.988 | 1519.992
Devonshire Building | 2016-11-14 | 48018.1562 | 1540.008
Devonshire Building | 2016-11-14 00:15 | 48018.5462 | 1559.988
Devonshire Building | 2016-11-14 00:30 | 48018.9362 | 1559.988
Devonshire Building | 2016-11-14 00:45 | 48019.3212 | 1540.008
Devonshire Building | 2016-11-14 01:00 | 48019.7112 | 1559.988
Devonshire Building | 2016-11-14 01:15 | 48020.1012 | 1559.988
Devonshire Building | 2016-11-14 01:30 | 48020.4962 | 1580.004
Devonshire Building | 2016-11-14 01:45 | 48020.8862 | 1559.988
Devonshire Building | 2016-11-14 02:00 | 48021.2762 | 1559.988
Devonshire Building | 2016-11-14 02:15 | 48021.6662 | 1559.988
Devonshire Building | 2016-11-14 02:30 | 48022.0612 | 1580.004
Devonshire Building | 2016-11-14 02:45 | 48022.4512 | 1559.988
Devonshire Building | 2016-11-14 03:00 | 48022.8412 | 1559.988
Devonshire Building | 2016-11-14 03:15 | 48023.2362 | 1580.004
Devonshire Building | 2016-11-14 03:30 | 48023.6262 | 1559.988
Devonshire Building | 2016-11-14 03:45 | 48024.0162 | 1559.988
Devonshire Building | 2016-11-14 04:00 | 48024.4062 | 1559.988
Devonshire Building | 2016-11-14 04:15 | 48024.7912 | 1540.008
Devonshire Building | 2016-11-14 04:30 | 48025.1812 | 1559.988
Devonshire Building | 2016-11-14 04:45 | 48025.5712 | 1559.988
Devonshire Building | 2016-11-14 05:00 | 48025.9612 | 1559.988
Devonshire Building | 2016-11-14 05:15 | 48026.3462 | 1540.008
Devonshire Building | 2016-11-14 05:30 | 48026.7362 | 1559.988
Devonshire Building | 2016-11-14 05:45 | 48027.1262 | 1559.988
Devonshire Building | 2016-11-14 06:00 | 48027.7562 | 2520
Devonshire Building | 2016-11-14 06:15 | 48028.1412 | 1540.008
Devonshire Building | 2016-11-14 06:30 | 48028.5262 | 1540.008
Devonshire Building | 2016-11-14 06:45 | 48028.9112 | 1540.008
Devonshire Building | 2016-11-14 07:00 | 48029.2912 | 1519.992
Devonshire Building | 2016-11-14 07:15 | 48029.6762 | 1540.008
Devonshire Building | 2016-11-14 07:30 | 48030.0562 | 1519.992
Devonshire Building | 2016-11-14 07:45 | 48030.4412 | 1540.008
Devonshire Building | 2016-11-14 08:00 | 48030.8262 | 1540.008
Devonshire Building | 2016-11-14 08:15 | 48031.2062 | 1519.992
Devonshire Building | 2016-11-14 08:30 | 48031.5862 | 1519.992
Devonshire Building | 2016-11-14 08:45 | 48031.9712 | 1540.008
Devonshire Building | 2016-11-14 09:00 | 48032.3512 | 1519.992
Devonshire Building | 2016-11-14 09:15 | 48032.7312 | 1519.992
Devonshire Building | 2016-11-14 09:30 | 48033.1062 | 1500.012
Devonshire Building | 2016-11-14 09:45 | 48033.4862 | 1519.992
Devonshire Building | 2016-11-14 10:00 | 48034.1162 | 2520
Devonshire Building | 2016-11-14 10:15 | 48034.4962 | 1519.992
Devonshire Building | 2016-11-14 10:30 | 48034.8712 | 1500.012
Devonshire Building | 2016-11-14 10:45 | 48035.2662 | 1580.004
Devonshire Building | 2016-11-14 11:00 | 48036.0262 | 3039.984
Devonshire Building | 2016-11-14 11:15 | 48036.5512 | 2099.988
Devonshire Building | 2016-11-14 11:30 | 48037.0512 | 2000.016
Devonshire Building | 2016-11-14 11:45 | 48037.5362 | 1940.004
Devonshire Building | 2016-11-14 12:00 | 48038.0162 | 1919.988
Devonshire Building | 2016-11-14 12:15 | 48038.4812 | 1860.012
Devonshire Building | 2016-11-14 12:30 | 48039.1912 | 2840.004
Devonshire Building | 2016-11-14 12:45 | 48039.6162 | 1699.992
Devonshire Building | 2016-11-14 13:00 | 48040.0512 | 1739.988
Devonshire Building | 2016-11-14 13:15 | 48040.4862 | 1739.988
Devonshire Building | 2016-11-14 13:30 | 48040.9462 | 1839.996
Devonshire Building | 2016-11-14 13:45 | 48041.7112 | 3060
Devonshire Building | 2016-11-14 14:00 | 48042.2112 | 2000.016
Devonshire Building | 2016-11-14 14:15 | 48042.6962 | 1940.004
Devonshire Building | 2016-11-14 14:30 | 48043.1612 | 1860.012
Devonshire Building | 2016-11-14 14:45 | 48043.6112 | 1800
Devonshire Building | 2016-11-14 15:00 | 48044.0562 | 1779.984
Devonshire Building | 2016-11-14 15:15 | 48044.7912 | 2940.012
Devonshire Building | 2016-11-14 15:30 | 48045.2462 | 1820.016
Devonshire Building | 2016-11-14 15:45 | 48045.7062 | 1839.996
Devonshire Building | 2016-11-14 16:00 | 48046.1612 | 1820.016
Devonshire Building | 2016-11-14 16:15 | 48046.6112 | 1800
Devonshire Building | 2016-11-14 16:30 | 48047.0612 | 1800
Devonshire Building | 2016-11-14 16:45 | 48047.7862 | 2900.016
Devonshire Building | 2016-11-14 17:00 | 48048.2212 | 1739.988
Devonshire Building | 2016-11-14 17:15 | 48048.6612 | 1760.004
Devonshire Building | 2016-11-14 17:30 | 48049.0912 | 1720.008
Devonshire Building | 2016-11-14 17:45 | 48049.5262 | 1739.988
Devonshire Building | 2016-11-14 18:00 | 48049.9662 | 1760.004
Devonshire Building | 2016-11-14 18:15 | 48050.3912 | 1699.992
Devonshire Building | 2016-11-14 18:30 | 48050.8112 | 1680.012
Devonshire Building | 2016-11-14 18:45 | 48051.2362 | 1699.992
Devonshire Building | 2016-11-14 19:00 | 48051.6512 | 1659.996
Devonshire Building | 2016-11-14 19:15 | 48052.0712 | 1680.012
Devonshire Building | 2016-11-14 19:30 | 48052.4812 | 1640.016
Devonshire Building | 2016-11-14 19:45 | 48052.8862 | 1620
Devonshire Building | 2016-11-14 20:00 | 48053.2862 | 1599.984
Devonshire Building | 2016-11-14 20:15 | 48053.6762 | 1559.988
Devonshire Building | 2016-11-14 20:30 | 48054.0712 | 1580.004
Devonshire Building | 2016-11-14 20:45 | 48054.4612 | 1559.988
Devonshire Building | 2016-11-14 21:00 | 48054.8512 | 1559.988
Devonshire Building | 2016-11-14 21:15 | 48055.2412 | 1559.988
Devonshire Building | 2016-11-14 21:30 | 48055.6312 | 1559.988
Devonshire Building | 2016-11-14 21:45 | 48056.0212 | 1559.988
Devonshire Building | 2016-11-14 22:00 | 48056.4262 | 1620
Devonshire Building | 2016-11-14 22:15 | 48056.8062 | 1519.992
Devonshire Building | 2016-11-14 22:30 | 48057.1912 | 1540.008
Devonshire Building | 2016-11-14 22:45 | 48057.5712 | 1519.992
Devonshire Building | 2016-11-14 23:00 | 48057.9562 | 1540.008
Devonshire Building | 2016-11-14 23:15 | 48058.3412 | 1540.008
Devonshire Building | 2016-11-14 23:30 | 48058.7212 | 1519.992
Devonshire Building | 2016-11-14 23:45 | 48059.1062 | 1540.008 | 1500.012
Devonshire Building | 2016-11-15 | 48059.4883 | 1540.008
Devonshire Building | 2016-11-15 00:15 | 48059.8783 | 1559.988
Devonshire Building | 2016-11-15 00:30 | 48060.2633 | 1540.008
Devonshire Building | 2016-11-15 00:45 | 48060.6483 | 1540.008
Devonshire Building | 2016-11-15 01:00 | 48061.0383 | 1559.988
Devonshire Building | 2016-11-15 01:15 | 48061.4233 | 1540.008
Devonshire Building | 2016-11-15 01:30 | 48061.8133 | 1559.988
Devonshire Building | 2016-11-15 01:45 | 48062.1983 | 1540.008
Devonshire Building | 2016-11-15 02:00 | 48062.5883 | 1559.988
Devonshire Building | 2016-11-15 02:15 | 48062.9733 | 1540.008
Devonshire Building | 2016-11-15 02:30 | 48063.3583 | 1540.008
Devonshire Building | 2016-11-15 02:45 | 48063.7483 | 1559.988
Devonshire Building | 2016-11-15 03:00 | 48064.1333 | 1540.008
Devonshire Building | 2016-11-15 03:15 | 48064.5183 | 1540.008
Devonshire Building | 2016-11-15 03:30 | 48064.9083 | 1559.988
Devonshire Building | 2016-11-15 03:45 | 48065.2933 | 1540.008
Devonshire Building | 2016-11-15 04:00 | 48065.6783 | 1540.008
Devonshire Building | 2016-11-15 04:15 | 48066.0633 | 1540.008
Devonshire Building | 2016-11-15 04:30 | 48066.4483 | 1540.008
Devonshire Building | 2016-11-15 04:45 | 48066.8333 | 1540.008
Devonshire Building | 2016-11-15 05:00 | 48067.4683 | 2540.016
Devonshire Building | 2016-11-15 05:15 | 48067.8533 | 1540.008
Devonshire Building | 2016-11-15 05:30 | 48068.2383 | 1540.008
Devonshire Building | 2016-11-15 05:45 | 48068.6233 | 1540.008
Devonshire Building | 2016-11-15 06:00 | 48069.0083 | 1540.008
Devonshire Building | 2016-11-15 06:15 | 48069.3933 | 1540.008
Devonshire Building | 2016-11-15 06:30 | 48069.7783 | 1540.008
Devonshire Building | 2016-11-15 06:45 | 48070.1583 | 1519.992
Devonshire Building | 2016-11-15 07:00 | 48070.5383 | 1519.992
Devonshire Building | 2016-11-15 07:15 | 48070.9233 | 1540.008
Devonshire Building | 2016-11-15 07:30 | 48071.3033 | 1519.992
Devonshire Building | 2016-11-15 07:45 | 48071.6733 | 1479.996
Devonshire Building | 2016-11-15 08:00 | 48072.0583 | 1540.008
Devonshire Building | 2016-11-15 08:15 | 48072.4433 | 1540.008
Devonshire Building | 2016-11-15 08:30 | 48072.8333 | 1559.988
Devonshire Building | 2016-11-15 08:45 | 48073.2233 | 1559.988
Devonshire Building | 2016-11-15 09:00 | 48073.6233 | 1599.984
Devonshire Building | 2016-11-15 09:15 | 48074.0133 | 1559.988
Devonshire Building | 2016-11-15 09:30 | 48074.4033 | 1559.988
Devonshire Building | 2016-11-15 09:45 | 48075.0633 | 2639.988
Devonshire Building | 2016-11-15 10:00 | 48075.4533 | 1559.988
Devonshire Building | 2016-11-15 10:15 | 48075.8283 | 1500.012
Devonshire Building | 2016-11-15 10:30 | 48076.2083 | 1519.992
Devonshire Building | 2016-11-15 10:45 | 48076.6033 | 1580.004
Devonshire Building | 2016-11-15 11:00 | 48077.2833 | 2720.016
Devonshire Building | 2016-11-15 11:15 | 48077.7333 | 1800
Devonshire Building | 2016-11-15 11:30 | 48078.1883 | 1820.016
Devonshire Building | 2016-11-15 11:45 | 48078.6333 | 1779.984
Devonshire Building | 2016-11-15 12:00 | 48079.0883 | 1820.016
Devonshire Building | 2016-11-15 12:15 | 48079.5283 | 1760.004
Devonshire Building | 2016-11-15 12:30 | 48080.2633 | 2940.012
Devonshire Building | 2016-11-15 12:45 | 48080.7183 | 1820.016
Devonshire Building | 2016-11-15 13:00 | 48081.1733 | 1820.016
Devonshire Building | 2016-11-15 13:15 | 48081.6133 | 1760.004
Devonshire Building | 2016-11-15 13:30 | 48082.0383 | 1699.992
Devonshire Building | 2016-11-15 13:45 | 48082.6033 | 2260.008
Devonshire Building | 2016-11-15 14:00 | 48083.1633 | 2239.992
Devonshire Building | 2016-11-15 14:15 | 48083.5733 | 1640.016
Devonshire Building | 2016-11-15 14:30 | 48083.9933 | 1680.012
Devonshire Building | 2016-11-15 14:45 | 48084.4133 | 1680.012
Devonshire Building | 2016-11-15 15:00 | 48084.8433 | 1720.008
Devonshire Building | 2016-11-15 15:15 | 48085.2733 | 1720.008
Devonshire Building | 2016-11-15 15:30 | 48085.9983 | 2900.016
Devonshire Building | 2016-11-15 15:45 | 48086.5033 | 2019.996
Devonshire Building | 2016-11-15 16:00 | 48086.9783 | 1900.008
Devonshire Building | 2016-11-15 16:15 | 48087.4233 | 1779.984
Devonshire Building | 2016-11-15 16:30 | 48087.8533 | 1720.008
Devonshire Building | 2016-11-15 16:45 | 48088.2733 | 1680.012
Devonshire Building | 2016-11-15 17:00 | 48088.6783 | 1620
Devonshire Building | 2016-11-15 17:15 | 48089.3633 | 2739.996
Devonshire Building | 2016-11-15 17:30 | 48089.7483 | 1540.008
Devonshire Building | 2016-11-15 17:45 | 48090.1283 | 1519.992
Devonshire Building | 2016-11-15 18:00 | 48090.5083 | 1519.992
Devonshire Building | 2016-11-15 18:15 | 48090.8883 | 1519.992
Devonshire Building | 2016-11-15 18:30 | 48091.2633 | 1500.012
Devonshire Building | 2016-11-15 18:45 | 48091.6433 | 1519.992
Devonshire Building | 2016-11-15 19:00 | 48092.0183 | 1500.012
Devonshire Building | 2016-11-15 19:15 | 48092.3983 | 1519.992
Devonshire Building | 2016-11-15 19:30 | 48092.7733 | 1500.012
Devonshire Building | 2016-11-15 19:45 | 48093.1533 | 1519.992
Devonshire Building | 2016-11-15 20:00 | 48093.5333 | 1519.992
Devonshire Building | 2016-11-15 20:15 | 48093.9083 | 1500.012
Devonshire Building | 2016-11-15 20:30 | 48094.2883 | 1519.992
Devonshire Building | 2016-11-15 20:45 | 48094.6683 | 1519.992
Devonshire Building | 2016-11-15 21:00 | 48095.0433 | 1500.012
Devonshire Building | 2016-11-15 21:15 | 48095.4233 | 1519.992
Devonshire Building | 2016-11-15 21:30 | 48095.7983 | 1500.012
Devonshire Building | 2016-11-15 21:45 | 48096.1783 | 1519.992
Devonshire Building | 2016-11-15 22:00 | 48096.5783 | 1599.984
Devonshire Building | 2016-11-15 22:15 | 48096.9583 | 1519.992
Devonshire Building | 2016-11-15 22:30 | 48097.3333 | 1500.012
Devonshire Building | 2016-11-15 22:45 | 48097.7083 | 1500.012
Devonshire Building | 2016-11-15 23:00 | 48098.0883 | 1519.992
Devonshire Building | 2016-11-15 23:15 | 48098.4633 | 1500.012
Devonshire Building | 2016-11-15 23:30 | 48098.8383 | 1500.012
Devonshire Building | 2016-11-15 23:45 | 48099.2183 | 1519.992 | 1479.996
Devonshire Building | 2016-11-16 | 48099.5938 | 1500.012
Devonshire Building | 2016-11-16 00:15 | 48099.9737 | 1519.992
Devonshire Building | 2016-11-16 00:30 | 48100.3488 | 1500.012
Devonshire Building | 2016-11-16 00:45 | 48100.7287 | 1519.992
Devonshire Building | 2016-11-16 01:00 | 48101.1087 | 1519.992
Devonshire Building | 2016-11-16 01:15 | 48101.4837 | 1500.012
Devonshire Building | 2016-11-16 01:30 | 48101.8588 | 1500.012
Devonshire Building | 2016-11-16 01:45 | 48102.2388 | 1519.992
Devonshire Building | 2016-11-16 02:00 | 48102.6138 | 1500.012
Devonshire Building | 2016-11-16 02:15 | 48102.9888 | 1500.012
Devonshire Building | 2016-11-16 02:30 | 48103.3688 | 1519.992
Devonshire Building | 2016-11-16 02:45 | 48103.7438 | 1500.012
Devonshire Building | 2016-11-16 03:00 | 48104.1188 | 1500.012
Devonshire Building | 2016-11-16 03:15 | 48104.4938 | 1500.012
Devonshire Building | 2016-11-16 03:30 | 48104.8738 | 1519.992
Devonshire Building | 2016-11-16 03:45 | 48105.2488 | 1500.012
Devonshire Building | 2016-11-16 04:00 | 48105.6238 | 1500.012
Devonshire Building | 2016-11-16 04:15 | 48106.0038 | 1519.992
Devonshire Building | 2016-11-16 04:30 | 48106.3788 | 1500.012
Devonshire Building | 2016-11-16 04:45 | 48106.7588 | 1519.992
Devonshire Building | 2016-11-16 05:00 | 48107.1338 | 1500.012
Devonshire Building | 2016-11-16 05:15 | 48107.5088 | 1500.012
Devonshire Building | 2016-11-16 05:30 | 48107.8838 | 1500.012
Devonshire Building | 2016-11-16 05:45 | 48108.2638 | 1519.992
Devonshire Building | 2016-11-16 06:00 | 48108.6388 | 1500.012
Devonshire Building | 2016-11-16 06:15 | 48109.0138 | 1500.012
Devonshire Building | 2016-11-16 06:30 | 48109.3888 | 1500.012
Devonshire Building | 2016-11-16 06:45 | 48109.7638 | 1500.012
Devonshire Building | 2016-11-16 07:00 | 48110.1338 | 1479.996
Devonshire Building | 2016-11-16 07:15 | 48110.5038 | 1479.996
Devonshire Building | 2016-11-16 07:30 | 48110.8788 | 1500.012
Devonshire Building | 2016-11-16 07:45 | 48111.2988 | 1680.012
Devonshire Building | 2016-11-16 08:00 | 48111.9238 | 2499.984
Devonshire Building | 2016-11-16 08:15 | 48112.3038 | 1519.992
Devonshire Building | 2016-11-16 08:30 | 48112.6838 | 1519.992
Devonshire Building | 2016-11-16 08:45 | 48113.0638 | 1519.992
Devonshire Building | 2016-11-16 09:00 | 48113.4388 | 1500.012
Devonshire Building | 2016-11-16 09:15 | 48113.8188 | 1519.992
Devonshire Building | 2016-11-16 09:30 | 48114.2038 | 1540.008
Devonshire Building | 2016-11-16 09:45 | 48114.5888 | 1540.008
Devonshire Building | 2016-11-16 10:00 | 48114.9688 | 1519.992
Devonshire Building | 2016-11-16 10:15 | 48115.6288 | 2639.988
Devonshire Building | 2016-11-16 10:30 | 48116.0088 | 1519.992
Devonshire Building | 2016-11-16 10:45 | 48116.4138 | 1620
Devonshire Building | 2016-11-16 11:00 | 48116.8688 | 1820.016
Devonshire Building | 2016-11-16 11:15 | 48117.3888 | 2080.008
Devonshire Building | 2016-11-16 11:30 | 48117.9288 | 2160
Devonshire Building | 2016-11-16 11:45 | 48118.5838 | 2620.008
Devonshire Building | 2016-11-16 12:00 | 48119.1388 | 2220.012
Devonshire Building | 2016-11-16 12:15 | 48119.5738 | 1739.988
Devonshire Building | 2016-11-16 12:30 | 48120.0088 | 1739.988
Devonshire Building | 2016-11-16 12:45 | 48120.4238 | 1659.996
Devonshire Building | 2016-11-16 13:00 | 48121.1038 | 2720.016
Devonshire Building | 2016-11-16 13:15 | 48121.4938 | 1559.988
Devonshire Building | 2016-11-16 13:30 | 48121.8888 | 1580.004
Devonshire Building | 2016-11-16 13:45 | 48122.2838 | 1580.004
Devonshire Building | 2016-11-16 14:00 | 48122.6738 | 1559.988
Devonshire Building | 2016-11-16 14:15 | 48123.0688 | 1580.004
Devonshire Building | 2016-11-16 14:30 | 48123.4588 | 1559.988
Devonshire Building | 2016-11-16 14:45 | 48124.0438 | 2340
Devonshire Building | 2016-11-16 15:00 | 48124.4988 | 1820.016
Devonshire Building | 2016-11-16 15:15 | 48124.8838 | 1540.008
Devonshire Building | 2016-11-16 15:30 | 48125.2688 | 1540.008
Devonshire Building | 2016-11-16 15:45 | 48125.6588 | 1559.988
Devonshire Building | 2016-11-16 16:00 | 48126.0388 | 1519.992
Devonshire Building | 2016-11-16 16:15 | 48126.5838 | 2180.016
Devonshire Building | 2016-11-16 16:30 | 48127.0988 | 2059.992
Devonshire Building | 2016-11-16 16:45 | 48127.4888 | 1559.988
Devonshire Building | 2016-11-16 17:00 | 48127.8738 | 1540.008
Devonshire Building | 2016-11-16 17:15 | 48128.2638 | 1559.988
Devonshire Building | 2016-11-16 17:30 | 48128.6538 | 1559.988
Devonshire Building | 2016-11-16 17:45 | 48129.0488 | 1580.004
Devonshire Building | 2016-11-16 18:00 | 48129.4388 | 1559.988
Devonshire Building | 2016-11-16 18:15 | 48129.8188 | 1519.992
Devonshire Building | 2016-11-16 18:30 | 48130.2038 | 1540.008
Devonshire Building | 2016-11-16 18:45 | 48130.5888 | 1540.008
Devonshire Building | 2016-11-16 19:00 | 48130.9638 | 1500.012
Devonshire Building | 2016-11-16 19:15 | 48131.5938 | 2520
Devonshire Building | 2016-11-16 19:30 | 48131.9588 | 1460.016
Devonshire Building | 2016-11-16 19:45 | 48132.3288 | 1479.996
Devonshire Building | 2016-11-16 20:00 | 48132.6938 | 1460.016
Devonshire Building | 2016-11-16 20:15 | 48133.0588 | 1460.016
Devonshire Building | 2016-11-16 20:30 | 48133.4238 | 1460.016
Devonshire Building | 2016-11-16 20:45 | 48133.7888 | 1460.016
Devonshire Building | 2016-11-16 21:00 | 48134.1588 | 1479.996
Devonshire Building | 2016-11-16 21:15 | 48134.5288 | 1479.996
Devonshire Building | 2016-11-16 21:30 | 48134.8988 | 1479.996
Devonshire Building | 2016-11-16 21:45 | 48135.2688 | 1479.996
Devonshire Building | 2016-11-16 22:00 | 48135.6388 | 1479.996
Devonshire Building | 2016-11-16 22:15 | 48136.0088 | 1479.996
Devonshire Building | 2016-11-16 22:30 | 48136.3788 | 1479.996
Devonshire Building | 2016-11-16 22:45 | 48136.7438 | 1460.016
Devonshire Building | 2016-11-16 23:00 | 48137.1138 | 1479.996
Devonshire Building | 2016-11-16 23:15 | 48137.4788 | 1460.016
Devonshire Building | 2016-11-16 23:30 | 48137.8488 | 1479.996
Devonshire Building | 2016-11-16 23:45 | 48138.2138 | 1460.016 | 1460.016
Devonshire Building | 2016-11-17 | 48138.5859 | 1479.996
Devonshire Building | 2016-11-17 00:15 | 48138.9559 | 1479.996
Devonshire Building | 2016-11-17 00:30 | 48139.3259 | 1479.996
Devonshire Building | 2016-11-17 00:45 | 48139.6959 | 1479.996
Devonshire Building | 2016-11-17 01:00 | 48140.0659 | 1479.996
Devonshire Building | 2016-11-17 01:15 | 48140.4359 | 1479.996
Devonshire Building | 2016-11-17 01:30 | 48140.8059 | 1479.996
Devonshire Building | 2016-11-17 01:45 | 48141.1759 | 1479.996
Devonshire Building | 2016-11-17 02:00 | 48141.5459 | 1479.996
Devonshire Building | 2016-11-17 02:15 | 48141.9109 | 1460.016
Devonshire Building | 2016-11-17 02:30 | 48142.2809 | 1479.996
Devonshire Building | 2016-11-17 02:45 | 48142.6509 | 1479.996
Devonshire Building | 2016-11-17 03:00 | 48143.0209 | 1479.996
Devonshire Building | 2016-11-17 03:15 | 48143.3859 | 1460.016
Devonshire Building | 2016-11-17 03:30 | 48143.7559 | 1479.996
Devonshire Building | 2016-11-17 03:45 | 48144.1209 | 1460.016
Devonshire Building | 2016-11-17 04:00 | 48144.4909 | 1479.996
Devonshire Building | 2016-11-17 04:15 | 48144.8559 | 1460.016
Devonshire Building | 2016-11-17 04:30 | 48145.2259 | 1479.996
Devonshire Building | 2016-11-17 04:45 | 48145.5909 | 1460.016
Devonshire Building | 2016-11-17 05:00 | 48145.9609 | 1479.996
Devonshire Building | 2016-11-17 05:15 | 48146.3259 | 1460.016
Devonshire Building | 2016-11-17 05:30 | 48146.691 | 1460.016
Devonshire Building | 2016-11-17 05:45 | 48147.061 | 1479.996
Devonshire Building | 2016-11-17 06:00 | 48147.426 | 1460.016
Devonshire Building | 2016-11-17 06:15 | 48147.796 | 1479.996
Devonshire Building | 2016-11-17 06:30 | 48148.161 | 1460.016
Devonshire Building | 2016-11-17 06:45 | 48148.521 | 1440
Devonshire Building | 2016-11-17 07:00 | 48148.886 | 1460.016
Devonshire Building | 2016-11-17 07:15 | 48149.246 | 1440
Devonshire Building | 2016-11-17 07:30 | 48149.606 | 1440
Devonshire Building | 2016-11-17 07:45 | 48149.981 | 1500.012
Devonshire Building | 2016-11-17 08:00 | 48150.356 | 1500.012
Devonshire Building | 2016-11-17 08:15 | 48150.736 | 1519.992
Devonshire Building | 2016-11-17 08:30 | 48151.116 | 1519.992
Devonshire Building | 2016-11-17 08:45 | 48151.486 | 1479.996
Devonshire Building | 2016-11-17 09:00 | 48151.856 | 1479.996
Devonshire Building | 2016-11-17 09:15 | 48152.481 | 2499.984
Devonshire Building | 2016-11-17 09:30 | 48152.856 | 1500.012
Devonshire Building | 2016-11-17 09:45 | 48153.226 | 1479.996
Devonshire Building | 2016-11-17 10:00 | 48153.596 | 1479.996
Devonshire Building | 2016-11-17 10:15 | 48153.966 | 1479.996
Devonshire Building | 2016-11-17 10:30 | 48154.341 | 1500.012
Devonshire Building | 2016-11-17 10:45 | 48154.721 | 1519.992
Devonshire Building | 2016-11-17 11:00 | 48155.366 | 2580.012
Devonshire Building | 2016-11-17 11:15 | 48155.736 | 1479.996
Devonshire Building | 2016-11-17 11:30 | 48156.131 | 1580.004
Devonshire Building | 2016-11-17 11:45 | 48156.551 | 1680.012
Devonshire Building | 2016-11-17 12:00 | 48156.996 | 1779.984
Devonshire Building | 2016-11-17 12:15 | 48157.486 | 1959.984
Devonshire Building | 2016-11-17 12:30 | 48158.311 | 3300.012
Devonshire Building | 2016-11-17 12:45 | 48158.821 | 2040.012
Devonshire Building | 2016-11-17 13:00 | 48159.306 | 1940.004
Devonshire Building | 2016-11-17 13:15 | 48159.786 | 1919.988
Devonshire Building | 2016-11-17 13:30 | 48160.266 | 1919.988
Devonshire Building | 2016-11-17 13:45 | 48160.741 | 1900.008
Devonshire Building | 2016-11-17 14:00 | 48161.186 | 1779.984
Devonshire Building | 2016-11-17 14:15 | 48161.901 | 2859.984
Devonshire Building | 2016-11-17 14:30 | 48162.356 | 1820.016
Devonshire Building | 2016-11-17 14:45 | 48162.806 | 1800
Devonshire Building | 2016-11-17 15:00 | 48163.256 | 1800
Devonshire Building | 2016-11-17 15:15 | 48163.711 | 1820.016
Devonshire Building | 2016-11-17 15:30 | 48164.161 | 1800
Devonshire Building | 2016-11-17 15:45 | 48164.781 | 2480.004
Devonshire Building | 2016-11-17 16:00 | 48165.291 | 2040.012
Devonshire Building | 2016-11-17 16:15 | 48165.716 | 1699.992
Devonshire Building | 2016-11-17 16:30 | 48166.141 | 1699.992
Devonshire Building | 2016-11-17 16:45 | 48166.561 | 1680.012
Devonshire Building | 2016-11-17 17:00 | 48166.976 | 1659.996
Devonshire Building | 2016-11-17 17:15 | 48167.381 | 1620
Devonshire Building | 2016-11-17 17:30 | 48167.791 | 1640.016
Devonshire Building | 2016-11-17 17:45 | 48168.181 | 1559.988
Devonshire Building | 2016-11-17 18:00 | 48168.831 | 2599.992
Devonshire Building | 2016-11-17 18:15 | 48169.191 | 1440
Devonshire Building | 2016-11-17 18:30 | 48169.556 | 1460.016
Devonshire Building | 2016-11-17 18:45 | 48169.921 | 1460.016
Devonshire Building | 2016-11-17 19:00 | 48170.281 | 1440
Devonshire Building | 2016-11-17 19:15 | 48170.646 | 1460.016
Devonshire Building | 2016-11-17 19:30 | 48171.006 | 1440
Devonshire Building | 2016-11-17 19:45 | 48171.371 | 1460.016
Devonshire Building | 2016-11-17 20:00 | 48171.736 | 1460.016
Devonshire Building | 2016-11-17 20:15 | 48172.106 | 1479.996
Devonshire Building | 2016-11-17 20:30 | 48172.471 | 1460.016
Devonshire Building | 2016-11-17 20:45 | 48172.836 | 1460.016
Devonshire Building | 2016-11-17 21:00 | 48173.201 | 1460.016
Devonshire Building | 2016-11-17 21:15 | 48173.566 | 1460.016
Devonshire Building | 2016-11-17 21:30 | 48173.931 | 1460.016
Devonshire Building | 2016-11-17 21:45 | 48174.301 | 1479.996
Devonshire Building | 2016-11-17 22:00 | 48174.671 | 1479.996
Devonshire Building | 2016-11-17 22:15 | 48175.031 | 1440
Devonshire Building | 2016-11-17 22:30 | 48175.396 | 1460.016
Devonshire Building | 2016-11-17 22:45 | 48175.761 | 1460.016
Devonshire Building | 2016-11-17 23:00 | 48176.126 | 1460.016
Devonshire Building | 2016-11-17 23:15 | 48176.491 | 1460.016
Devonshire Building | 2016-11-17 23:30 | 48176.856 | 1460.016
Devonshire Building | 2016-11-17 23:45 | 48177.221 | 1460.016 | 1440
Devonshire Building | 2016-11-18 | 48177.5898 | 1479.996
Devonshire Building | 2016-11-18 00:15 | 48177.9548 | 1460.016
Devonshire Building | 2016-11-18 00:30 | 48178.3198 | 1460.016
Devonshire Building | 2016-11-18 00:45 | 48178.6898 | 1479.996
Devonshire Building | 2016-11-18 01:00 | 48179.0549 | 1460.016
Devonshire Building | 2016-11-18 01:15 | 48179.4249 | 1479.996
Devonshire Building | 2016-11-18 01:30 | 48179.7899 | 1460.016
Devonshire Building | 2016-11-18 01:45 | 48180.1599 | 1479.996
Devonshire Building | 2016-11-18 02:00 | 48180.5299 | 1479.996
Devonshire Building | 2016-11-18 02:15 | 48180.8999 | 1479.996
Devonshire Building | 2016-11-18 02:30 | 48181.2649 | 1460.016
Devonshire Building | 2016-11-18 02:45 | 48181.6349 | 1479.996
Devonshire Building | 2016-11-18 03:00 | 48182.0049 | 1479.996
Devonshire Building | 2016-11-18 03:15 | 48182.3699 | 1460.016
Devonshire Building | 2016-11-18 03:30 | 48182.7399 | 1479.996
Devonshire Building | 2016-11-18 03:45 | 48183.1049 | 1460.016
Devonshire Building | 2016-11-18 04:00 | 48183.4699 | 1460.016
Devonshire Building | 2016-11-18 04:15 | 48183.8349 | 1460.016
Devonshire Building | 2016-11-18 04:30 | 48184.1999 | 1460.016
Devonshire Building | 2016-11-18 04:45 | 48184.5649 | 1460.016
Devonshire Building | 2016-11-18 05:00 | 48184.9299 | 1460.016
Devonshire Building | 2016-11-18 05:15 | 48185.2949 | 1460.016
Devonshire Building | 2016-11-18 05:30 | 48185.6599 | 1460.016
Devonshire Building | 2016-11-18 05:45 | 48186.0249 | 1460.016
Devonshire Building | 2016-11-18 06:00 | 48186.3949 | 1479.996
Devonshire Building | 2016-11-18 06:15 | 48186.7599 | 1460.016
Devonshire Building | 2016-11-18 06:30 | 48187.1249 | 1460.016
Devonshire Building | 2016-11-18 06:45 | 48187.4849 | 1440
Devonshire Building | 2016-11-18 07:00 | 48187.8499 | 1460.016
Devonshire Building | 2016-11-18 07:15 | 48188.2199 | 1479.996
Devonshire Building | 2016-11-18 07:30 | 48188.5949 | 1500.012
Devonshire Building | 2016-11-18 07:45 | 48188.9699 | 1500.012
Devonshire Building | 2016-11-18 08:00 | 48189.3499 | 1519.992
Devonshire Building | 2016-11-18 08:15 | 48189.7299 | 1519.992
Devonshire Building | 2016-11-18 08:30 | 48190.1099 | 1519.992
Devonshire Building | 2016-11-18 08:45 | 48190.4849 | 1500.012
Devonshire Building | 2016-11-18 09:00 | 48191.1249 | 2559.996
Devonshire Building | 2016-11-18 09:15 | 48191.4949 | 1479.996
Devonshire Building | 2016-11-18 09:30 | 48191.8649 | 1479.996
Devonshire Building | 2016-11-18 09:45 | 48192.2399 | 1500.012
Devonshire Building | 2016-11-18 10:00 | 48192.6249 | 1540.008
Devonshire Building | 2016-11-18 10:15 | 48193.0399 | 1659.996
Devonshire Building | 2016-11-18 10:30 | 48193.6899 | 2599.992
Devonshire Building | 2016-11-18 10:45 | 48194.3199 | 2520
Devonshire Building | 2016-11-18 11:00 | 48194.8349 | 2059.992
Devonshire Building | 2016-11-18 11:15 | 48195.3299 | 1980
Devonshire Building | 2016-11-18 11:30 | 48195.7899 | 1839.996
Devonshire Building | 2016-11-18 11:45 | 48196.4999 | 2840.004
Devonshire Building | 2016-11-18 12:00 | 48196.9199 | 1680.012
Devonshire Building | 2016-11-18 12:15 | 48197.3449 | 1699.992
Devonshire Building | 2016-11-18 12:30 | 48197.7649 | 1680.012
Devonshire Building | 2016-11-18 12:45 | 48198.1949 | 1720.008
Devonshire Building | 2016-11-18 13:00 | 48198.6849 | 1959.984
Devonshire Building | 2016-11-18 13:15 | 48199.4399 | 3020.004
Devonshire Building | 2016-11-18 13:30 | 48200.0199 | 2319.984
Devonshire Building | 2016-11-18 13:45 | 48200.5099 | 1959.984
Devonshire Building | 2016-11-18 14:00 | 48200.9599 | 1800
Devonshire Building | 2016-11-18 14:15 | 48201.3899 | 1720.008
Devonshire Building | 2016-11-18 14:30 | 48201.8149 | 1699.992
Devonshire Building | 2016-11-18 14:45 | 48202.2449 | 1720.008
Devonshire Building | 2016-11-18 15:00 | 48202.6749 | 1720.008
Devonshire Building | 2016-11-18 15:15 | 48203.3399 | 2660.004
Devonshire Building | 2016-11-18 15:30 | 48203.7349 | 1580.004
Devonshire Building | 2016-11-18 15:45 | 48204.1299 | 1580.004
Devonshire Building | 2016-11-18 16:00 | 48204.5199 | 1559.988
Devonshire Building | 2016-11-18 16:15 | 48204.9199 | 1599.984
Devonshire Building | 2016-11-18 16:30 | 48205.3149 | 1580.004
Devonshire Building | 2016-11-18 16:45 | 48205.7349 | 1680.012
Devonshire Building | 2016-11-18 17:00 | 48206.4549 | 2880
Devonshire Building | 2016-11-18 17:15 | 48206.9149 | 1839.996
Devonshire Building | 2016-11-18 17:30 | 48207.3899 | 1900.008
Devonshire Building | 2016-11-18 17:45 | 48207.8649 | 1900.008
Devonshire Building | 2016-11-18 18:00 | 48208.3199 | 1820.016
Devonshire Building | 2016-11-18 18:15 | 48208.7499 | 1720.008
Devonshire Building | 2016-11-18 18:30 | 48209.1549 | 1620
Devonshire Building | 2016-11-18 18:45 | 48209.5549 | 1599.984
Devonshire Building | 2016-11-18 19:00 | 48209.9449 | 1559.988
Devonshire Building | 2016-11-18 19:15 | 48210.3249 | 1519.992
Devonshire Building | 2016-11-18 19:30 | 48210.7049 | 1519.992
Devonshire Building | 2016-11-18 19:45 | 48211.0849 | 1519.992
Devonshire Building | 2016-11-18 20:00 | 48211.4599 | 1500.012
Devonshire Building | 2016-11-18 20:15 | 48211.8349 | 1500.012
Devonshire Building | 2016-11-18 20:30 | 48212.2099 | 1500.012
Devonshire Building | 2016-11-18 20:45 | 48212.5799 | 1479.996
Devonshire Building | 2016-11-18 21:00 | 48212.9499 | 1479.996
Devonshire Building | 2016-11-18 21:15 | 48213.3199 | 1479.996
Devonshire Building | 2016-11-18 21:30 | 48213.6899 | 1479.996
Devonshire Building | 2016-11-18 21:45 | 48214.0599 | 1479.996
Devonshire Building | 2016-11-18 22:00 | 48214.4499 | 1559.988
Devonshire Building | 2016-11-18 22:15 | 48214.8149 | 1460.016
Devonshire Building | 2016-11-18 22:30 | 48215.1799 | 1460.016
Devonshire Building | 2016-11-18 22:45 | 48215.5449 | 1460.016
Devonshire Building | 2016-11-18 23:00 | 48215.9099 | 1460.016
Devonshire Building | 2016-11-18 23:15 | 48216.2749 | 1460.016
Devonshire Building | 2016-11-18 23:30 | 48216.6399 | 1460.016
Devonshire Building | 2016-11-18 23:45 | 48217.0049 | 1460.016 | 1440
Devonshire Building | 2016-11-19 | 48217.375 | 1479.996
Devonshire Building | 2016-11-19 00:15 | 48217.745 | 1479.996
Devonshire Building | 2016-11-19 00:30 | 48218.11 | 1460.016
Devonshire Building | 2016-11-19 00:45 | 48218.48 | 1479.996
Devonshire Building | 2016-11-19 01:00 | 48218.855 | 1500.012
Devonshire Building | 2016-11-19 01:15 | 48219.225 | 1479.996
Devonshire Building | 2016-11-19 01:30 | 48219.595 | 1479.996
Devonshire Building | 2016-11-19 01:45 | 48219.98 | 1540.008
Devonshire Building | 2016-11-19 02:00 | 48220.37 | 1559.988
Devonshire Building | 2016-11-19 02:15 | 48220.76 | 1559.988
Devonshire Building | 2016-11-19 02:30 | 48221.15 | 1559.988
Devonshire Building | 2016-11-19 02:45 | 48221.535 | 1540.008
Devonshire Building | 2016-11-19 03:00 | 48221.925 | 1559.988
Devonshire Building | 2016-11-19 03:15 | 48222.315 | 1559.988
Devonshire Building | 2016-11-19 03:30 | 48222.705 | 1559.988
Devonshire Building | 2016-11-19 03:45 | 48223.085 | 1519.992
Devonshire Building | 2016-11-19 04:00 | 48223.46 | 1500.012
Devonshire Building | 2016-11-19 04:15 | 48223.835 | 1500.012
Devonshire Building | 2016-11-19 04:30 | 48224.21 | 1500.012
Devonshire Building | 2016-11-19 04:45 | 48224.585 | 1500.012
Devonshire Building | 2016-11-19 05:00 | 48224.97 | 1540.008
Devonshire Building | 2016-11-19 05:15 | 48225.35 | 1519.992
Devonshire Building | 2016-11-19 05:30 | 48225.73 | 1519.992
Devonshire Building | 2016-11-19 05:45 | 48226.11 | 1519.992
Devonshire Building | 2016-11-19 06:00 | 48226.49 | 1519.992
Devonshire Building | 2016-11-19 06:15 | 48226.87 | 1519.992
Devonshire Building | 2016-11-19 06:30 | 48227.505 | 2540.016
Devonshire Building | 2016-11-19 06:45 | 48227.885 | 1519.992
Devonshire Building | 2016-11-19 07:00 | 48228.26 | 1500.012
Devonshire Building | 2016-11-19 07:15 | 48228.64 | 1519.992
Devonshire Building | 2016-11-19 07:30 | 48229.02 | 1519.992
Devonshire Building | 2016-11-19 07:45 | 48229.4 | 1519.992
Devonshire Building | 2016-11-19 08:00 | 48229.775 | 1500.012
Devonshire Building | 2016-11-19 08:15 | 48230.15 | 1500.012
Devonshire Building | 2016-11-19 08:30 | 48230.525 | 1500.012
Devonshire Building | 2016-11-19 08:45 | 48230.9 | 1500.012
Devonshire Building | 2016-11-19 09:00 | 48231.275 | 1500.012
Devonshire Building | 2016-11-19 09:15 | 48231.65 | 1500.012
Devonshire Building | 2016-11-19 09:30 | 48232.02 | 1479.996
Devonshire Building | 2016-11-19 09:45 | 48232.395 | 1500.012
Devonshire Building | 2016-11-19 10:00 | 48232.77 | 1500.012
Devonshire Building | 2016-11-19 10:15 | 48233.145 | 1500.012
Devonshire Building | 2016-11-19 10:30 | 48233.52 | 1500.012
Devonshire Building | 2016-11-19 10:45 | 48233.89 | 1479.996
Devonshire Building | 2016-11-19 11:00 | 48234.265 | 1500.012
Devonshire Building | 2016-11-19 11:15 | 48234.64 | 1500.012
Devonshire Building | 2016-11-19 11:30 | 48235.01 | 1479.996
Devonshire Building | 2016-11-19 11:45 | 48235.385 | 1500.012
Devonshire Building | 2016-11-19 12:00 | 48235.755 | 1479.996
Devonshire Building | 2016-11-19 12:15 | 48236.125 | 1479.996
Devonshire Building | 2016-11-19 12:30 | 48236.5 | 1500.012
Devonshire Building | 2016-11-19 12:45 | 48236.87 | 1479.996
Devonshire Building | 2016-11-19 13:00 | 48237.245 | 1500.012
Devonshire Building | 2016-11-19 13:15 | 48237.615 | 1479.996
Devonshire Building | 2016-11-19 13:30 | 48237.99 | 1500.012
Devonshire Building | 2016-11-19 13:45 | 48238.36 | 1479.996
Devonshire Building | 2016-11-19 14:00 | 48238.735 | 1500.012
Devonshire Building | 2016-11-19 14:15 | 48239.11 | 1500.012
Devonshire Building | 2016-11-19 14:30 | 48239.485 | 1500.012
Devonshire Building | 2016-11-19 14:45 | 48239.86 | 1500.012
Devonshire Building | 2016-11-19 15:00 | 48240.235 | 1500.012
Devonshire Building | 2016-11-19 15:15 | 48240.61 | 1500.012
Devonshire Building | 2016-11-19 15:30 | 48240.9851 | 1500.012
Devonshire Building | 2016-11-19 15:45 | 48241.3601 | 1500.012
Devonshire Building | 2016-11-19 16:00 | 48241.7401 | 1519.992
Devonshire Building | 2016-11-19 16:15 | 48242.1151 | 1500.012
Devonshire Building | 2016-11-19 16:30 | 48242.4901 | 1500.012
Devonshire Building | 2016-11-19 16:45 | 48242.8651 | 1500.012
Devonshire Building | 2016-11-19 17:00 | 48243.2401 | 1500.012
Devonshire Building | 2016-11-19 17:15 | 48243.6151 | 1500.012
Devonshire Building | 2016-11-19 17:30 | 48243.9901 | 1500.012
Devonshire Building | 2016-11-19 17:45 | 48244.3651 | 1500.012
Devonshire Building | 2016-11-19 18:00 | 48244.7401 | 1500.012
Devonshire Building | 2016-11-19 18:15 | 48245.1151 | 1500.012
Devonshire Building | 2016-11-19 18:30 | 48245.4901 | 1500.012
Devonshire Building | 2016-11-19 18:45 | 48245.8651 | 1500.012
Devonshire Building | 2016-11-19 19:00 | 48246.2401 | 1500.012
Devonshire Building | 2016-11-19 19:15 | 48246.6101 | 1479.996
Devonshire Building | 2016-11-19 19:30 | 48246.9901 | 1519.992
Devonshire Building | 2016-11-19 19:45 | 48247.3651 | 1500.012
Devonshire Building | 2016-11-19 20:00 | 48247.7401 | 1500.012
Devonshire Building | 2016-11-19 20:15 | 48248.1201 | 1519.992
Devonshire Building | 2016-11-19 20:30 | 48248.4951 | 1500.012
Devonshire Building | 2016-11-19 20:45 | 48248.8701 | 1500.012
Devonshire Building | 2016-11-19 21:00 | 48249.2501 | 1519.992
Devonshire Building | 2016-11-19 21:15 | 48249.6251 | 1500.012
Devonshire Building | 2016-11-19 21:30 | 48250.0051 | 1519.992
Devonshire Building | 2016-11-19 21:45 | 48250.3851 | 1519.992
Devonshire Building | 2016-11-19 22:00 | 48250.7851 | 1599.984
Devonshire Building | 2016-11-19 22:15 | 48251.1651 | 1519.992
Devonshire Building | 2016-11-19 22:30 | 48251.5451 | 1519.992
Devonshire Building | 2016-11-19 22:45 | 48251.9251 | 1519.992
Devonshire Building | 2016-11-19 23:00 | 48252.3051 | 1519.992
Devonshire Building | 2016-11-19 23:15 | 48252.6851 | 1519.992
Devonshire Building | 2016-11-19 23:30 | 48253.0701 | 1540.008
Devonshire Building | 2016-11-19 23:45 | 48253.4501 | 1519.992 | 1460.016
Devonshire Building | 2016-11-20 | 48253.8359 | 1540.008
Devonshire Building | 2016-11-20 00:15 | 48254.2209 | 1540.008
Devonshire Building | 2016-11-20 00:30 | 48254.6059 | 1540.008
Devonshire Building | 2016-11-20 00:45 | 48254.9909 | 1540.008
Devonshire Building | 2016-11-20 01:00 | 48255.3759 | 1540.008
Devonshire Building | 2016-11-20 01:15 | 48255.761 | 1540.008
Devonshire Building | 2016-11-20 01:30 | 48256.1509 | 1559.988
Devonshire Building | 2016-11-20 01:45 | 48256.5559 | 1620
Devonshire Building | 2016-11-20 02:00 | 48256.9559 | 1599.984
Devonshire Building | 2016-11-20 02:15 | 48257.3559 | 1599.984
Devonshire Building | 2016-11-20 02:30 | 48257.7609 | 1620
Devonshire Building | 2016-11-20 02:45 | 48258.1609 | 1599.984
Devonshire Building | 2016-11-20 03:00 | 48258.5609 | 1599.984
Devonshire Building | 2016-11-20 03:15 | 48258.9659 | 1620
Devonshire Building | 2016-11-20 03:30 | 48259.3709 | 1620
Devonshire Building | 2016-11-20 03:45 | 48259.7709 | 1599.984
Devonshire Building | 2016-11-20 04:00 | 48260.1659 | 1580.004
Devonshire Building | 2016-11-20 04:15 | 48260.5559 | 1559.988
Devonshire Building | 2016-11-20 04:30 | 48260.9409 | 1540.008
Devonshire Building | 2016-11-20 04:45 | 48261.3309 | 1559.988
Devonshire Building | 2016-11-20 05:00 | 48261.7209 | 1559.988
Devonshire Building | 2016-11-20 05:15 | 48262.1109 | 1559.988
Devonshire Building | 2016-11-20 05:30 | 48262.5009 | 1559.988
Devonshire Building | 2016-11-20 05:45 | 48262.8859 | 1540.008
Devonshire Building | 2016-11-20 06:00 | 48263.2759 | 1559.988
Devonshire Building | 2016-11-20 06:15 | 48263.6659 | 1559.988
Devonshire Building | 2016-11-20 06:30 | 48264.0509 | 1540.008
Devonshire Building | 2016-11-20 06:45 | 48264.4409 | 1559.988
Devonshire Building | 2016-11-20 07:00 | 48264.8309 | 1559.988
Devonshire Building | 2016-11-20 07:15 | 48265.2159 | 1540.008
Devonshire Building | 2016-11-20 07:30 | 48265.6059 | 1559.988
Devonshire Building | 2016-11-20 07:45 | 48265.9909 | 1540.008
Devonshire Building | 2016-11-20 08:00 | 48266.3759 | 1540.008
Devonshire Building | 2016-11-20 08:15 | 48266.7609 | 1540.008
Devonshire Building | 2016-11-20 08:30 | 48267.1459 | 1540.008
Devonshire Building | 2016-11-20 08:45 | 48267.5309 | 1540.008
Devonshire Building | 2016-11-20 09:00 | 48267.9159 | 1540.008
Devonshire Building | 2016-11-20 09:15 | 48268.3009 | 1540.008
Devonshire Building | 2016-11-20 09:30 | 48268.6809 | 1519.992
Devonshire Building | 2016-11-20 09:45 | 48269.0609 | 1519.992
Devonshire Building | 2016-11-20 10:00 | 48269.4409 | 1519.992
Devonshire Building | 2016-11-20 10:15 | 48269.8209 | 1519.992
Devonshire Building | 2016-11-20 10:30 | 48270.2009 | 1519.992
Devonshire Building | 2016-11-20 10:45 | 48270.5809 | 1519.992
Devonshire Building | 2016-11-20 11:00 | 48270.9609 | 1519.992
Devonshire Building | 2016-11-20 11:15 | 48271.3409 | 1519.992
Devonshire Building | 2016-11-20 11:30 | 48271.7209 | 1519.992
Devonshire Building | 2016-11-20 11:45 | 48272.1059 | 1540.008
Devonshire Building | 2016-11-20 12:00 | 48272.4859 | 1519.992
Devonshire Building | 2016-11-20 12:15 | 48272.9509 | 1860.012
Devonshire Building | 2016-11-20 12:30 | 48273.5109 | 2239.992
Devonshire Building | 2016-11-20 12:45 | 48273.8959 | 1540.008
Devonshire Building | 2016-11-20 13:00 | 48274.2759 | 1519.992
Devonshire Building | 2016-11-20 13:15 | 48274.6659 | 1559.988
Devonshire Building | 2016-11-20 13:30 | 48275.0509 | 1540.008
Devonshire Building | 2016-11-20 13:45 | 48275.4359 | 1540.008
Devonshire Building | 2016-11-20 14:00 | 48275.8259 | 1559.988
Devonshire Building | 2016-11-20 14:15 | 48276.2109 | 1540.008
Devonshire Building | 2016-11-20 14:30 | 48276.6009 | 1559.988
Devonshire Building | 2016-11-20 14:45 | 48276.9909 | 1559.988
Devonshire Building | 2016-11-20 15:00 | 48277.3809 | 1559.988
Devonshire Building | 2016-11-20 15:15 | 48277.7659 | 1540.008
Devonshire Building | 2016-11-20 15:30 | 48278.1559 | 1559.988
Devonshire Building | 2016-11-20 15:45 | 48278.5409 | 1540.008
Devonshire Building | 2016-11-20 16:00 | 48278.9309 | 1559.988
Devonshire Building | 2016-11-20 16:15 | 48279.3159 | 1540.008
Devonshire Building | 2016-11-20 16:30 | 48279.7059 | 1559.988
Devonshire Building | 2016-11-20 16:45 | 48280.0909 | 1540.008
Devonshire Building | 2016-11-20 17:00 | 48280.4809 | 1559.988
Devonshire Building | 2016-11-20 17:15 | 48280.8709 | 1559.988
Devonshire Building | 2016-11-20 17:30 | 48281.2559 | 1540.008
Devonshire Building | 2016-11-20 17:45 | 48281.6409 | 1540.008
Devonshire Building | 2016-11-20 18:00 | 48282.0309 | 1559.988
Devonshire Building | 2016-11-20 18:15 | 48282.4159 | 1540.008
Devonshire Building | 2016-11-20 18:30 | 48282.7959 | 1519.992
Devonshire Building | 2016-11-20 18:45 | 48283.1809 | 1540.008
Devonshire Building | 2016-11-20 19:00 | 48283.5659 | 1540.008
Devonshire Building | 2016-11-20 19:15 | 48283.9509 | 1540.008
Devonshire Building | 2016-11-20 19:30 | 48284.3409 | 1559.988
Devonshire Building | 2016-11-20 19:45 | 48284.7409 | 1599.984
Devonshire Building | 2016-11-20 20:00 | 48285.1409 | 1599.984
Devonshire Building | 2016-11-20 20:15 | 48285.5459 | 1620
Devonshire Building | 2016-11-20 20:30 | 48285.9509 | 1620
Devonshire Building | 2016-11-20 20:45 | 48286.3559 | 1620
Devonshire Building | 2016-11-20 21:00 | 48286.7609 | 1620
Devonshire Building | 2016-11-20 21:15 | 48287.1659 | 1620
Devonshire Building | 2016-11-20 21:30 | 48287.5709 | 1620
Devonshire Building | 2016-11-20 21:45 | 48287.9759 | 1620
Devonshire Building | 2016-11-20 22:00 | 48288.3709 | 1580.004
Devonshire Building | 2016-11-20 22:15 | 48288.7609 | 1559.988
Devonshire Building | 2016-11-20 22:30 | 48289.1509 | 1559.988
Devonshire Building | 2016-11-20 22:45 | 48289.5409 | 1559.988
Devonshire Building | 2016-11-20 23:00 | 48289.9309 | 1559.988
Devonshire Building | 2016-11-20 23:15 | 48290.3259 | 1580.004
Devonshire Building | 2016-11-20 23:30 | 48290.7159 | 1559.988
Devonshire Building | 2016-11-20 23:45 | 48291.1109 | 1580.004 | 1519.992
Devonshire Building | 2016-11-21 | 48291.5039 | 1580.004
Devonshire Building | 2016-11-21 00:15 | 48291.8989 | 1580.004
Devonshire Building | 2016-11-21 00:30 | 48292.2939 | 1580.004
Devonshire Building | 2016-11-21 00:45 | 48292.6889 | 1580.004
Devonshire Building | 2016-11-21 01:00 | 48293.0889 | 1599.984
Devonshire Building | 2016-11-21 01:15 | 48293.4889 | 1599.984
Devonshire Building | 2016-11-21 01:30 | 48293.8889 | 1599.984
Devonshire Building | 2016-11-21 01:45 | 48294.2839 | 1580.004
Devonshire Building | 2016-11-21 02:00 | 48294.6839 | 1599.984
Devonshire Building | 2016-11-21 02:15 | 48295.0839 | 1599.984
Devonshire Building | 2016-11-21 02:30 | 48295.4889 | 1620
Devonshire Building | 2016-11-21 02:45 | 48295.8889 | 1599.984
Devonshire Building | 2016-11-21 03:00 | 48296.2889 | 1599.984
Devonshire Building | 2016-11-21 03:15 | 48296.6939 | 1620
Devonshire Building | 2016-11-21 03:30 | 48297.0939 | 1599.984
Devonshire Building | 2016-11-21 03:45 | 48297.4939 | 1599.984
Devonshire Building | 2016-11-21 04:00 | 48297.8939 | 1599.984
Devonshire Building | 2016-11-21 04:15 | 48298.2939 | 1599.984
Devonshire Building | 2016-11-21 04:30 | 48298.6939 | 1599.984
Devonshire Building | 2016-11-21 04:45 | 48299.0939 | 1599.984
Devonshire Building | 2016-11-21 05:00 | 48299.4939 | 1599.984
Devonshire Building | 2016-11-21 05:15 | 48299.8939 | 1599.984
Devonshire Building | 2016-11-21 05:30 | 48300.2939 | 1599.984
Devonshire Building | 2016-11-21 05:45 | 48300.6889 | 1580.004
Devonshire Building | 2016-11-21 06:00 | 48301.0888 | 1599.984
Devonshire Building | 2016-11-21 06:15 | 48301.4838 | 1580.004
Devonshire Building | 2016-11-21 06:30 | 48301.8838 | 1599.984
Devonshire Building | 2016-11-21 06:45 | 48302.2788 | 1580.004
Devonshire Building | 2016-11-21 07:00 | 48302.6738 | 1580.004
Devonshire Building | 2016-11-21 07:15 | 48303.0788 | 1620
Devonshire Building | 2016-11-21 07:30 | 48303.4688 | 1559.988
Devonshire Building | 2016-11-21 07:45 | 48303.8688 | 1599.984
Devonshire Building | 2016-11-21 08:00 | 48304.2638 | 1580.004
Devonshire Building | 2016-11-21 08:15 | 48304.6588 | 1580.004
Devonshire Building | 2016-11-21 08:30 | 48305.0488 | 1559.988
Devonshire Building | 2016-11-21 08:45 | 48305.4538 | 1620
Devonshire Building | 2016-11-21 09:00 | 48306.1238 | 2679.984
Devonshire Building | 2016-11-21 09:15 | 48306.5238 | 1599.984
Devonshire Building | 2016-11-21 09:30 | 48306.9188 | 1580.004
Devonshire Building | 2016-11-21 09:45 | 48307.3138 | 1580.004
Devonshire Building | 2016-11-21 10:00 | 48307.7138 | 1599.984
Devonshire Building | 2016-11-21 10:15 | 48308.1138 | 1599.984
Devonshire Building | 2016-11-21 10:30 | 48308.8188 | 2819.988
Devonshire Building | 2016-11-21 10:45 | 48309.2988 | 1919.988
Devonshire Building | 2016-11-21 11:00 | 48309.8388 | 2160
Devonshire Building | 2016-11-21 11:15 | 48310.3688 | 2120.004
Devonshire Building | 2016-11-21 11:30 | 48310.8938 | 2099.988
Devonshire Building | 2016-11-21 11:45 | 48311.7238 | 3319.992
Devonshire Building | 2016-11-21 12:00 | 48312.2438 | 2080.008
Devonshire Building | 2016-11-21 12:15 | 48312.7688 | 2099.988
Devonshire Building | 2016-11-21 12:30 | 48313.2538 | 1940.004
Devonshire Building | 2016-11-21 12:45 | 48313.7238 | 1879.992
Devonshire Building | 2016-11-21 13:00 | 48314.2038 | 1919.988
Devonshire Building | 2016-11-21 13:15 | 48314.9738 | 3080.016
Devonshire Building | 2016-11-21 13:30 | 48315.4638 | 1959.984
Devonshire Building | 2016-11-21 13:45 | 48315.9588 | 1980
Devonshire Building | 2016-11-21 14:00 | 48316.4588 | 2000.016
Devonshire Building | 2016-11-21 14:15 | 48316.9488 | 1959.984
Devonshire Building | 2016-11-21 14:30 | 48317.4338 | 1940.004
Devonshire Building | 2016-11-21 14:45 | 48317.9138 | 1919.988
Devonshire Building | 2016-11-21 15:00 | 48318.6588 | 2980.008
Devonshire Building | 2016-11-21 15:15 | 48319.1388 | 1919.988
Devonshire Building | 2016-11-21 15:30 | 48319.6288 | 1959.984
Devonshire Building | 2016-11-21 15:45 | 48320.1288 | 2000.016
Devonshire Building | 2016-11-21 16:00 | 48320.6588 | 2120.004
Devonshire Building | 2016-11-21 16:15 | 48321.1888 | 2120.004
Devonshire Building | 2016-11-21 16:30 | 48321.7038 | 2059.992
Devonshire Building | 2016-11-21 16:45 | 48322.2138 | 2040.012
Devonshire Building | 2016-11-21 17:00 | 48322.9838 | 3080.016
Devonshire Building | 2016-11-21 17:15 | 48323.4838 | 2000.016
Devonshire Building | 2016-11-21 17:30 | 48323.9688 | 1940.004
Devonshire Building | 2016-11-21 17:45 | 48324.4488 | 1919.988
Devonshire Building | 2016-11-21 18:00 | 48324.9138 | 1860.012
Devonshire Building | 2016-11-21 18:15 | 48325.3738 | 1839.996
Devonshire Building | 2016-11-21 18:30 | 48325.8338 | 1839.996
Devonshire Building | 2016-11-21 18:45 | 48326.2888 | 1820.016
Devonshire Building | 2016-11-21 19:00 | 48326.7438 | 1820.016
Devonshire Building | 2016-11-21 19:15 | 48327.1988 | 1820.016
Devonshire Building | 2016-11-21 19:30 | 48327.6488 | 1800
Devonshire Building | 2016-11-21 19:45 | 48328.0888 | 1760.004
Devonshire Building | 2016-11-21 20:00 | 48328.5238 | 1739.988
Devonshire Building | 2016-11-21 20:15 | 48328.9538 | 1720.008
Devonshire Building | 2016-11-21 20:30 | 48329.3738 | 1680.012
Devonshire Building | 2016-11-21 20:45 | 48329.7938 | 1680.012
Devonshire Building | 2016-11-21 21:00 | 48330.2088 | 1659.996
Devonshire Building | 2016-11-21 21:15 | 48330.6288 | 1680.012
Devonshire Building | 2016-11-21 21:30 | 48331.0438 | 1659.996
Devonshire Building | 2016-11-21 21:45 | 48331.4588 | 1659.996
Devonshire Building | 2016-11-21 22:00 | 48331.8938 | 1739.988
Devonshire Building | 2016-11-21 22:15 | 48332.2988 | 1620
Devonshire Building | 2016-11-21 22:30 | 48332.7088 | 1640.016
Devonshire Building | 2016-11-21 22:45 | 48333.1138 | 1620
Devonshire Building | 2016-11-21 23:00 | 48333.5238 | 1640.016
Devonshire Building | 2016-11-21 23:15 | 48333.9288 | 1620
Devonshire Building | 2016-11-21 23:30 | 48334.3388 | 1640.016
Devonshire Building | 2016-11-21 23:45 | 48334.7488 | 1640.016 | 1559.988
Devonshire Building | 2016-11-22 | 48335.1602 | 1640.016
Devonshire Building | 2016-11-22 00:15 | 48335.5702 | 1640.016
Devonshire Building | 2016-11-22 00:30 | 48335.9802 | 1640.016
Devonshire Building | 2016-11-22 00:45 | 48336.3902 | 1640.016
Devonshire Building | 2016-11-22 01:00 | 48336.8002 | 1640.016
Devonshire Building | 2016-11-22 01:15 | 48337.2102 | 1640.016
Devonshire Building | 2016-11-22 01:30 | 48337.6252 | 1659.996
Devonshire Building | 2016-11-22 01:45 | 48338.0352 | 1640.016
Devonshire Building | 2016-11-22 02:00 | 48338.4502 | 1659.996
Devonshire Building | 2016-11-22 02:15 | 48338.8602 | 1640.016
Devonshire Building | 2016-11-22 02:30 | 48339.2752 | 1659.996
Devonshire Building | 2016-11-22 02:45 | 48339.6902 | 1659.996
Devonshire Building | 2016-11-22 03:00 | 48340.1052 | 1659.996
Devonshire Building | 2016-11-22 03:15 | 48340.5202 | 1659.996
Devonshire Building | 2016-11-22 03:30 | 48340.9352 | 1659.996
Devonshire Building | 2016-11-22 03:45 | 48341.3452 | 1640.016
Devonshire Building | 2016-11-22 04:00 | 48341.7602 | 1659.996
Devonshire Building | 2016-11-22 04:15 | 48342.1752 | 1659.996
Devonshire Building | 2016-11-22 04:30 | 48342.5852 | 1640.016
Devonshire Building | 2016-11-22 04:45 | 48343.0002 | 1659.996
Devonshire Building | 2016-11-22 05:00 | 48343.4102 | 1640.016
Devonshire Building | 2016-11-22 05:15 | 48344.0852 | 2700
Devonshire Building | 2016-11-22 05:30 | 48344.5002 | 1659.996
Devonshire Building | 2016-11-22 05:45 | 48344.9102 | 1640.016
Devonshire Building | 2016-11-22 06:00 | 48345.3252 | 1659.996
Devonshire Building | 2016-11-22 06:15 | 48345.7402 | 1659.996
Devonshire Building | 2016-11-22 06:30 | 48346.1502 | 1640.016
Devonshire Building | 2016-11-22 06:45 | 48346.5602 | 1640.016
Devonshire Building | 2016-11-22 07:00 | 48346.9702 | 1640.016
Devonshire Building | 2016-11-22 07:15 | 48347.3802 | 1640.016
Devonshire Building | 2016-11-22 07:30 | 48347.7852 | 1620
Devonshire Building | 2016-11-22 07:45 | 48348.1902 | 1620
Devonshire Building | 2016-11-22 08:00 | 48348.6102 | 1680.012
Devonshire Building | 2016-11-22 08:15 | 48349.0302 | 1680.012
Devonshire Building | 2016-11-22 08:30 | 48349.4502 | 1680.012
Devonshire Building | 2016-11-22 08:45 | 48349.8752 | 1699.992
Devonshire Building | 2016-11-22 09:00 | 48350.3052 | 1720.008
Devonshire Building | 2016-11-22 09:15 | 48350.7452 | 1760.004
Devonshire Building | 2016-11-22 09:30 | 48351.1802 | 1739.988
Devonshire Building | 2016-11-22 09:45 | 48351.6702 | 1959.984
Devonshire Building | 2016-11-22 10:00 | 48352.1602 | 1959.984
Devonshire Building | 2016-11-22 10:15 | 48352.9352 | 3099.996
Devonshire Building | 2016-11-22 10:30 | 48353.4502 | 2059.992
Devonshire Building | 2016-11-22 10:45 | 48353.9702 | 2080.008
Devonshire Building | 2016-11-22 11:00 | 48354.4652 | 1980
Devonshire Building | 2016-11-22 11:15 | 48354.9452 | 1919.988
Devonshire Building | 2016-11-22 11:30 | 48355.4102 | 1860.012
Devonshire Building | 2016-11-22 11:45 | 48355.8602 | 1800
Devonshire Building | 2016-11-22 12:00 | 48356.6052 | 2980.008
Devonshire Building | 2016-11-22 12:15 | 48357.0402 | 1739.988
Devonshire Building | 2016-11-22 12:30 | 48357.4652 | 1699.992
Devonshire Building | 2016-11-22 12:45 | 48357.9002 | 1739.988
Devonshire Building | 2016-11-22 13:00 | 48358.3352 | 1739.988
Devonshire Building | 2016-11-22 13:15 | 48358.7752 | 1760.004
Devonshire Building | 2016-11-22 13:30 | 48359.2152 | 1760.004
Devonshire Building | 2016-11-22 13:45 | 48359.9452 | 2919.996
Devonshire Building | 2016-11-22 14:00 | 48360.3852 | 1760.004
Devonshire Building | 2016-11-22 14:15 | 48360.8252 | 1760.004
Devonshire Building | 2016-11-22 14:30 | 48361.2802 | 1820.016
Devonshire Building | 2016-11-22 14:45 | 48361.7402 | 1839.996
Devonshire Building | 2016-11-22 15:00 | 48362.2152 | 1900.008
Devonshire Building | 2016-11-22 15:15 | 48362.6902 | 1900.008
Devonshire Building | 2016-11-22 15:30 | 48363.4702 | 3120.012
Devonshire Building | 2016-11-22 15:45 | 48363.9702 | 2000.016
Devonshire Building | 2016-11-22 16:00 | 48364.4702 | 2000.016
Devonshire Building | 2016-11-22 16:15 | 48364.9652 | 1980
Devonshire Building | 2016-11-22 16:30 | 48365.4602 | 1980
Devonshire Building | 2016-11-22 16:45 | 48365.9452 | 1940.004
Devonshire Building | 2016-11-22 17:00 | 48366.4152 | 1879.992
Devonshire Building | 2016-11-22 17:15 | 48367.1602 | 2980.008
Devonshire Building | 2016-11-22 17:30 | 48367.6002 | 1760.004
Devonshire Building | 2016-11-22 17:45 | 48368.0452 | 1779.984
Devonshire Building | 2016-11-22 18:00 | 48368.4802 | 1739.988
Devonshire Building | 2016-11-22 18:15 | 48368.9152 | 1739.988
Devonshire Building | 2016-11-22 18:30 | 48369.3402 | 1699.992
Devonshire Building | 2016-11-22 18:45 | 48369.7702 | 1720.008
Devonshire Building | 2016-11-22 19:00 | 48370.1952 | 1699.992
Devonshire Building | 2016-11-22 19:15 | 48370.6202 | 1699.992
Devonshire Building | 2016-11-22 19:30 | 48371.0402 | 1680.012
Devonshire Building | 2016-11-22 19:45 | 48371.4602 | 1680.012
Devonshire Building | 2016-11-22 20:00 | 48371.8802 | 1680.012
Devonshire Building | 2016-11-22 20:15 | 48372.2952 | 1659.996
Devonshire Building | 2016-11-22 20:30 | 48372.7152 | 1680.012
Devonshire Building | 2016-11-22 20:45 | 48373.1302 | 1659.996
Devonshire Building | 2016-11-22 21:00 | 48373.5502 | 1680.012
Devonshire Building | 2016-11-22 21:15 | 48373.9652 | 1659.996
Devonshire Building | 2016-11-22 21:30 | 48374.3852 | 1680.012
Devonshire Building | 2016-11-22 21:45 | 48374.8002 | 1659.996
Devonshire Building | 2016-11-22 22:00 | 48375.2402 | 1760.004
Devonshire Building | 2016-11-22 22:15 | 48375.6502 | 1640.016
Devonshire Building | 2016-11-22 22:30 | 48376.0602 | 1640.016
Devonshire Building | 2016-11-22 22:45 | 48376.4752 | 1659.996
Devonshire Building | 2016-11-22 23:00 | 48376.8852 | 1640.016
Devonshire Building | 2016-11-22 23:15 | 48377.3002 | 1659.996
Devonshire Building | 2016-11-22 23:30 | 48377.7152 | 1659.996
Devonshire Building | 2016-11-22 23:45 | 48378.1302 | 1659.996 | 1620
Devonshire Building | 2016-11-23 | 48378.543 | 1659.996
Devonshire Building | 2016-11-23 00:15 | 48378.963 | 1680.012
Devonshire Building | 2016-11-23 00:30 | 48379.378 | 1659.996
Devonshire Building | 2016-11-23 00:45 | 48379.798 | 1680.012
Devonshire Building | 2016-11-23 01:00 | 48380.218 | 1680.012
Devonshire Building | 2016-11-23 01:15 | 48380.633 | 1659.996
Devonshire Building | 2016-11-23 01:30 | 48381.053 | 1680.012
Devonshire Building | 2016-11-23 01:45 | 48381.473 | 1680.012
Devonshire Building | 2016-11-23 02:00 | 48381.893 | 1680.012
Devonshire Building | 2016-11-23 02:15 | 48382.313 | 1680.012
Devonshire Building | 2016-11-23 02:30 | 48382.738 | 1699.992
Devonshire Building | 2016-11-23 02:45 | 48383.158 | 1680.012
Devonshire Building | 2016-11-23 03:00 | 48383.578 | 1680.012
Devonshire Building | 2016-11-23 03:15 | 48383.998 | 1680.012
Devonshire Building | 2016-11-23 03:30 | 48384.418 | 1680.012
Devonshire Building | 2016-11-23 03:45 | 48384.838 | 1680.012
Devonshire Building | 2016-11-23 04:00 | 48385.258 | 1680.012
Devonshire Building | 2016-11-23 04:15 | 48385.678 | 1680.012
Devonshire Building | 2016-11-23 04:30 | 48386.098 | 1680.012
Devonshire Building | 2016-11-23 04:45 | 48386.518 | 1680.012
Devonshire Building | 2016-11-23 05:00 | 48386.938 | 1680.012
Devonshire Building | 2016-11-23 05:15 | 48387.358 | 1680.012
Devonshire Building | 2016-11-23 05:30 | 48387.778 | 1680.012
Devonshire Building | 2016-11-23 05:45 | 48388.193 | 1659.996
Devonshire Building | 2016-11-23 06:00 | 48388.613 | 1680.012
Devonshire Building | 2016-11-23 06:15 | 48389.033 | 1680.012
Devonshire Building | 2016-11-23 06:30 | 48389.448 | 1659.996
Devonshire Building | 2016-11-23 06:45 | 48389.863 | 1659.996
Devonshire Building | 2016-11-23 07:00 | 48390.278 | 1659.996
Devonshire Building | 2016-11-23 07:15 | 48390.688 | 1640.016
Devonshire Building | 2016-11-23 07:30 | 48391.103 | 1659.996
Devonshire Building | 2016-11-23 07:45 | 48391.528 | 1699.992
Devonshire Building | 2016-11-23 08:00 | 48392.213 | 2739.996
Devonshire Building | 2016-11-23 08:15 | 48392.648 | 1739.988
Devonshire Building | 2016-11-23 08:30 | 48393.073 | 1699.992
Devonshire Building | 2016-11-23 08:45 | 48393.498 | 1699.992
Devonshire Building | 2016-11-23 09:00 | 48393.928 | 1720.008
Devonshire Building | 2016-11-23 09:15 | 48394.358 | 1720.008
Devonshire Building | 2016-11-23 09:30 | 48394.788 | 1720.008
Devonshire Building | 2016-11-23 09:45 | 48395.218 | 1720.008
Devonshire Building | 2016-11-23 10:00 | 48395.658 | 1760.004
Devonshire Building | 2016-11-23 10:15 | 48396.448 | 3160.008
Devonshire Building | 2016-11-23 10:30 | 48396.963 | 2059.992
Devonshire Building | 2016-11-23 10:45 | 48397.463 | 2000.016
Devonshire Building | 2016-11-23 11:00 | 48397.968 | 2019.996
Devonshire Building | 2016-11-23 11:15 | 48398.468 | 2000.016
Devonshire Building | 2016-11-23 11:30 | 48399.238 | 3080.016
Devonshire Building | 2016-11-23 11:45 | 48399.693 | 1820.016
Devonshire Building | 2016-11-23 12:00 | 48400.163 | 1879.992
Devonshire Building | 2016-11-23 12:15 | 48400.613 | 1800
Devonshire Building | 2016-11-23 12:30 | 48401.068 | 1820.016
Devonshire Building | 2016-11-23 12:45 | 48401.518 | 1800
Devonshire Building | 2016-11-23 13:00 | 48401.968 | 1800
Devonshire Building | 2016-11-23 13:15 | 48402.713 | 2980.008
Devonshire Building | 2016-11-23 13:30 | 48403.173 | 1839.996
Devonshire Building | 2016-11-23 13:45 | 48403.633 | 1839.996
Devonshire Building | 2016-11-23 14:00 | 48404.098 | 1860.012
Devonshire Building | 2016-11-23 14:15 | 48404.5531 | 1820.016
Devonshire Building | 2016-11-23 14:30 | 48405.0081 | 1820.016
Devonshire Building | 2016-11-23 14:45 | 48405.4631 | 1820.016
Devonshire Building | 2016-11-23 15:00 | 48406.1931 | 2919.996
Devonshire Building | 2016-11-23 15:15 | 48406.6481 | 1820.016
Devonshire Building | 2016-11-23 15:30 | 48407.0881 | 1760.004
Devonshire Building | 2016-11-23 15:45 | 48407.5331 | 1779.984
Devonshire Building | 2016-11-23 16:00 | 48407.9731 | 1760.004
Devonshire Building | 2016-11-23 16:15 | 48408.4231 | 1800
Devonshire Building | 2016-11-23 16:30 | 48408.8881 | 1860.012
Devonshire Building | 2016-11-23 16:45 | 48409.3531 | 1860.012
Devonshire Building | 2016-11-23 17:00 | 48409.8231 | 1879.992
Devonshire Building | 2016-11-23 17:15 | 48410.5781 | 3020.004
Devonshire Building | 2016-11-23 17:30 | 48411.0331 | 1820.016
Devonshire Building | 2016-11-23 17:45 | 48411.4931 | 1839.996
Devonshire Building | 2016-11-23 18:00 | 48411.9481 | 1820.016
Devonshire Building | 2016-11-23 18:15 | 48412.3981 | 1800
Devonshire Building | 2016-11-23 18:30 | 48412.8381 | 1760.004
Devonshire Building | 2016-11-23 18:45 | 48413.2681 | 1720.008
Devonshire Building | 2016-11-23 19:00 | 48413.6981 | 1720.008
Devonshire Building | 2016-11-23 19:15 | 48414.1231 | 1699.992
Devonshire Building | 2016-11-23 19:30 | 48414.5481 | 1699.992
Devonshire Building | 2016-11-23 19:45 | 48414.9731 | 1699.992
Devonshire Building | 2016-11-23 20:00 | 48415.3981 | 1699.992
Devonshire Building | 2016-11-23 20:15 | 48415.8181 | 1680.012
Devonshire Building | 2016-11-23 20:30 | 48416.2381 | 1680.012
Devonshire Building | 2016-11-23 20:45 | 48416.6631 | 1699.992
Devonshire Building | 2016-11-23 21:00 | 48417.0781 | 1659.996
Devonshire Building | 2016-11-23 21:15 | 48417.4981 | 1680.012
Devonshire Building | 2016-11-23 21:30 | 48417.9181 | 1680.012
Devonshire Building | 2016-11-23 21:45 | 48418.3381 | 1680.012
Devonshire Building | 2016-11-23 22:00 | 48418.7681 | 1720.008
Devonshire Building | 2016-11-23 22:15 | 48419.1781 | 1640.016
Devonshire Building | 2016-11-23 22:30 | 48419.5931 | 1659.996
Devonshire Building | 2016-11-23 22:45 | 48420.0081 | 1659.996
Devonshire Building | 2016-11-23 23:00 | 48420.4231 | 1659.996
Devonshire Building | 2016-11-23 23:15 | 48420.8381 | 1659.996
Devonshire Building | 2016-11-23 23:30 | 48421.2531 | 1659.996
Devonshire Building | 2016-11-23 23:45 | 48421.6681 | 1659.996 | 1640.016
Devonshire Building | 2016-11-24 | 48422.0898 | 1680.012
Devonshire Building | 2016-11-24 00:15 | 48422.5098 | 1680.012
Devonshire Building | 2016-11-24 00:30 | 48422.9298 | 1680.012
Devonshire Building | 2016-11-24 00:45 | 48423.3448 | 1659.996
Devonshire Building | 2016-11-24 01:00 | 48423.7648 | 1680.012
Devonshire Building | 2016-11-24 01:15 | 48424.1849 | 1680.012
Devonshire Building | 2016-11-24 01:30 | 48424.6049 | 1680.012
Devonshire Building | 2016-11-24 01:45 | 48425.0249 | 1680.012
Devonshire Building | 2016-11-24 02:00 | 48425.4499 | 1699.992
Devonshire Building | 2016-11-24 02:15 | 48425.8699 | 1680.012
Devonshire Building | 2016-11-24 02:30 | 48426.2899 | 1680.012
Devonshire Building | 2016-11-24 02:45 | 48426.7099 | 1680.012
Devonshire Building | 2016-11-24 03:00 | 48427.1299 | 1680.012
Devonshire Building | 2016-11-24 03:15 | 48427.5499 | 1680.012
Devonshire Building | 2016-11-24 03:30 | 48427.9699 | 1680.012
Devonshire Building | 2016-11-24 03:45 | 48428.3949 | 1699.992
Devonshire Building | 2016-11-24 04:00 | 48428.8149 | 1680.012
Devonshire Building | 2016-11-24 04:15 | 48429.2349 | 1680.012
Devonshire Building | 2016-11-24 04:30 | 48429.6549 | 1680.012
Devonshire Building | 2016-11-24 04:45 | 48430.0749 | 1680.012
Devonshire Building | 2016-11-24 05:00 | 48430.4949 | 1680.012
Devonshire Building | 2016-11-24 05:15 | 48430.9149 | 1680.012
Devonshire Building | 2016-11-24 05:30 | 48431.3349 | 1680.012
Devonshire Building | 2016-11-24 05:45 | 48431.7549 | 1680.012
Devonshire Building | 2016-11-24 06:00 | 48432.1749 | 1680.012
Devonshire Building | 2016-11-24 06:15 | 48432.5899 | 1659.996
Devonshire Building | 2016-11-24 06:30 | 48433.0099 | 1680.012
Devonshire Building | 2016-11-24 06:45 | 48433.4249 | 1659.996
Devonshire Building | 2016-11-24 07:00 | 48433.8399 | 1659.996
Devonshire Building | 2016-11-24 07:15 | 48434.2499 | 1640.016
Devonshire Building | 2016-11-24 07:30 | 48434.6699 | 1680.012
Devonshire Building | 2016-11-24 07:45 | 48435.1049 | 1739.988
Devonshire Building | 2016-11-24 08:00 | 48435.5349 | 1720.008
Devonshire Building | 2016-11-24 08:15 | 48435.9599 | 1699.992
Devonshire Building | 2016-11-24 08:30 | 48436.3849 | 1699.992
Devonshire Building | 2016-11-24 08:45 | 48436.9199 | 2139.984
Devonshire Building | 2016-11-24 09:00 | 48437.4899 | 2279.988
Devonshire Building | 2016-11-24 09:15 | 48437.9149 | 1699.992
Devonshire Building | 2016-11-24 09:30 | 48438.3449 | 1720.008
Devonshire Building | 2016-11-24 09:45 | 48438.7699 | 1699.992
Devonshire Building | 2016-11-24 10:00 | 48439.1899 | 1680.012
Devonshire Building | 2016-11-24 10:15 | 48439.6149 | 1699.992
Devonshire Building | 2016-11-24 10:30 | 48440.2999 | 2739.996
Devonshire Building | 2016-11-24 10:45 | 48440.7249 | 1699.992
Devonshire Building | 2016-11-24 11:00 | 48441.1549 | 1720.008
Devonshire Building | 2016-11-24 11:15 | 48441.5849 | 1720.008
Devonshire Building | 2016-11-24 11:30 | 48442.0399 | 1820.016
Devonshire Building | 2016-11-24 11:45 | 48442.4999 | 1839.996
Devonshire Building | 2016-11-24 12:00 | 48443.2499 | 2999.988
Devonshire Building | 2016-11-24 12:15 | 48443.7149 | 1860.012
Devonshire Building | 2016-11-24 12:30 | 48444.1849 | 1879.992
Devonshire Building | 2016-11-24 12:45 | 48444.6599 | 1900.008
Devonshire Building | 2016-11-24 13:00 | 48445.1349 | 1900.008
Devonshire Building | 2016-11-24 13:15 | 48445.5999 | 1860.012
Devonshire Building | 2016-11-24 13:30 | 48446.3399 | 2959.992
Devonshire Building | 2016-11-24 13:45 | 48446.8199 | 1919.988
Devonshire Building | 2016-11-24 14:00 | 48447.2899 | 1879.992
Devonshire Building | 2016-11-24 14:15 | 48447.7649 | 1900.008
Devonshire Building | 2016-11-24 14:30 | 48448.2299 | 1860.012
Devonshire Building | 2016-11-24 14:45 | 48448.6999 | 1879.992
Devonshire Building | 2016-11-24 15:00 | 48449.1699 | 1879.992
Devonshire Building | 2016-11-24 15:15 | 48449.9199 | 2999.988
Devonshire Building | 2016-11-24 15:30 | 48450.3849 | 1860.012
Devonshire Building | 2016-11-24 15:45 | 48450.8549 | 1879.992
Devonshire Building | 2016-11-24 16:00 | 48451.3199 | 1860.012
Devonshire Building | 2016-11-24 16:15 | 48451.7799 | 1839.996
Devonshire Building | 2016-11-24 16:30 | 48452.2299 | 1800
Devonshire Building | 2016-11-24 16:45 | 48452.6749 | 1779.984
Devonshire Building | 2016-11-24 17:00 | 48453.1249 | 1800
Devonshire Building | 2016-11-24 17:15 | 48453.8599 | 2940.012
Devonshire Building | 2016-11-24 17:30 | 48454.2899 | 1720.008
Devonshire Building | 2016-11-24 17:45 | 48454.7199 | 1720.008
Devonshire Building | 2016-11-24 18:00 | 48455.1499 | 1720.008
Devonshire Building | 2016-11-24 18:15 | 48455.5849 | 1739.988
Devonshire Building | 2016-11-24 18:30 | 48456.0149 | 1720.008
Devonshire Building | 2016-11-24 18:45 | 48456.4449 | 1720.008
Devonshire Building | 2016-11-24 19:00 | 48456.8749 | 1720.008
Devonshire Building | 2016-11-24 19:15 | 48457.2999 | 1699.992
Devonshire Building | 2016-11-24 19:30 | 48457.7249 | 1699.992
Devonshire Building | 2016-11-24 19:45 | 48458.1449 | 1680.012
Devonshire Building | 2016-11-24 20:00 | 48458.5649 | 1680.012
Devonshire Building | 2016-11-24 20:15 | 48458.9849 | 1680.012
Devonshire Building | 2016-11-24 20:30 | 48459.4049 | 1680.012
Devonshire Building | 2016-11-24 20:45 | 48459.8249 | 1680.012
Devonshire Building | 2016-11-24 21:00 | 48460.2399 | 1659.996
Devonshire Building | 2016-11-24 21:15 | 48460.6599 | 1680.012
Devonshire Building | 2016-11-24 21:30 | 48461.0799 | 1680.012
Devonshire Building | 2016-11-24 21:45 | 48461.4949 | 1659.996
Devonshire Building | 2016-11-24 22:00 | 48461.9249 | 1720.008
Devonshire Building | 2016-11-24 22:15 | 48462.3399 | 1659.996
Devonshire Building | 2016-11-24 22:30 | 48462.7549 | 1659.996
Devonshire Building | 2016-11-24 22:45 | 48463.1749 | 1680.012
Devonshire Building | 2016-11-24 23:00 | 48463.5899 | 1659.996
Devonshire Building | 2016-11-24 23:15 | 48464.0099 | 1680.012
Devonshire Building | 2016-11-24 23:30 | 48464.4249 | 1659.996
Devonshire Building | 2016-11-24 23:45 | 48464.8449 | 1680.012 | 1640.016
Devonshire Building | 2016-11-25 | 48465.2656 | 1680.012
Devonshire Building | 2016-11-25 00:15 | 48465.6856 | 1680.012
Devonshire Building | 2016-11-25 00:30 | 48466.1056 | 1680.012
Devonshire Building | 2016-11-25 00:45 | 48466.5256 | 1680.012
Devonshire Building | 2016-11-25 01:00 | 48466.9456 | 1680.012
Devonshire Building | 2016-11-25 01:15 | 48467.3706 | 1699.992
Devonshire Building | 2016-11-25 01:30 | 48467.8006 | 1720.008
Devonshire Building | 2016-11-25 01:45 | 48468.2356 | 1739.988
Devonshire Building | 2016-11-25 02:00 | 48468.6756 | 1760.004
Devonshire Building | 2016-11-25 02:15 | 48469.1106 | 1739.988
Devonshire Building | 2016-11-25 02:30 | 48469.5506 | 1760.004
Devonshire Building | 2016-11-25 02:45 | 48469.9856 | 1739.988
Devonshire Building | 2016-11-25 03:00 | 48470.4206 | 1739.988
Devonshire Building | 2016-11-25 03:15 | 48470.8606 | 1760.004
Devonshire Building | 2016-11-25 03:30 | 48471.2956 | 1739.988
Devonshire Building | 2016-11-25 03:45 | 48471.7306 | 1739.988
Devonshire Building | 2016-11-25 04:00 | 48472.1656 | 1739.988
Devonshire Building | 2016-11-25 04:15 | 48472.5856 | 1680.012
Devonshire Building | 2016-11-25 04:30 | 48473.0056 | 1680.012
Devonshire Building | 2016-11-25 04:45 | 48473.4256 | 1680.012
Devonshire Building | 2016-11-25 05:00 | 48473.8456 | 1680.012
Devonshire Building | 2016-11-25 05:15 | 48474.2656 | 1680.012
Devonshire Building | 2016-11-25 05:30 | 48474.6856 | 1680.012
Devonshire Building | 2016-11-25 05:45 | 48475.1056 | 1680.012
Devonshire Building | 2016-11-25 06:00 | 48475.5256 | 1680.012
Devonshire Building | 2016-11-25 06:15 | 48475.9457 | 1680.012
Devonshire Building | 2016-11-25 06:30 | 48476.3657 | 1680.012
Devonshire Building | 2016-11-25 06:45 | 48476.7807 | 1659.996
Devonshire Building | 2016-11-25 07:00 | 48477.2007 | 1680.012
Devonshire Building | 2016-11-25 07:15 | 48477.6157 | 1659.996
Devonshire Building | 2016-11-25 07:30 | 48478.0307 | 1659.996
Devonshire Building | 2016-11-25 07:45 | 48478.4457 | 1659.996
Devonshire Building | 2016-11-25 08:00 | 48478.8607 | 1659.996
Devonshire Building | 2016-11-25 08:15 | 48479.2707 | 1640.016
Devonshire Building | 2016-11-25 08:30 | 48479.6857 | 1659.996
Devonshire Building | 2016-11-25 08:45 | 48480.3757 | 2760.012
Devonshire Building | 2016-11-25 09:00 | 48480.7857 | 1640.016
Devonshire Building | 2016-11-25 09:15 | 48481.1907 | 1620
Devonshire Building | 2016-11-25 09:30 | 48481.5957 | 1620
Devonshire Building | 2016-11-25 09:45 | 48482.0007 | 1620
Devonshire Building | 2016-11-25 10:00 | 48482.4107 | 1640.016
Devonshire Building | 2016-11-25 10:15 | 48482.8257 | 1659.996
Devonshire Building | 2016-11-25 10:30 | 48483.2607 | 1739.988
Devonshire Building | 2016-11-25 10:45 | 48483.7857 | 2099.988
Devonshire Building | 2016-11-25 11:00 | 48484.6007 | 3260.016
Devonshire Building | 2016-11-25 11:15 | 48485.1307 | 2120.004
Devonshire Building | 2016-11-25 11:30 | 48485.6357 | 2019.996
Devonshire Building | 2016-11-25 11:45 | 48486.1207 | 1940.004
Devonshire Building | 2016-11-25 12:00 | 48486.6057 | 1940.004
Devonshire Building | 2016-11-25 12:15 | 48487.0807 | 1900.008
Devonshire Building | 2016-11-25 12:30 | 48487.5457 | 1860.012
Devonshire Building | 2016-11-25 12:45 | 48488.2657 | 2880
Devonshire Building | 2016-11-25 13:00 | 48488.7157 | 1800
Devonshire Building | 2016-11-25 13:15 | 48489.1657 | 1800
Devonshire Building | 2016-11-25 13:30 | 48489.6207 | 1820.016
Devonshire Building | 2016-11-25 13:45 | 48490.0857 | 1860.012
Devonshire Building | 2016-11-25 14:00 | 48490.5457 | 1839.996
Devonshire Building | 2016-11-25 14:15 | 48491.0157 | 1879.992
Devonshire Building | 2016-11-25 14:30 | 48491.4757 | 1839.996
Devonshire Building | 2016-11-25 14:45 | 48491.9357 | 1839.996
Devonshire Building | 2016-11-25 15:00 | 48492.6607 | 2900.016
Devonshire Building | 2016-11-25 15:15 | 48493.1207 | 1839.996
Devonshire Building | 2016-11-25 15:30 | 48493.5857 | 1860.012
Devonshire Building | 2016-11-25 15:45 | 48494.0557 | 1879.992
Devonshire Building | 2016-11-25 16:00 | 48494.5207 | 1860.012
Devonshire Building | 2016-11-25 16:15 | 48494.9907 | 1879.992
Devonshire Building | 2016-11-25 16:30 | 48495.4557 | 1860.012
Devonshire Building | 2016-11-25 16:45 | 48495.9307 | 1900.008
Devonshire Building | 2016-11-25 17:00 | 48496.3957 | 1860.012
Devonshire Building | 2016-11-25 17:15 | 48496.8557 | 1839.996
Devonshire Building | 2016-11-25 17:30 | 48497.5857 | 2919.996
Devonshire Building | 2016-11-25 17:45 | 48498.0507 | 1860.012
Devonshire Building | 2016-11-25 18:00 | 48498.5157 | 1860.012
Devonshire Building | 2016-11-25 18:15 | 48498.9807 | 1860.012
Devonshire Building | 2016-11-25 18:30 | 48499.4457 | 1860.012
Devonshire Building | 2016-11-25 18:45 | 48499.9107 | 1860.012
Devonshire Building | 2016-11-25 19:00 | 48500.3707 | 1839.996
Devonshire Building | 2016-11-25 19:15 | 48500.8257 | 1820.016
Devonshire Building | 2016-11-25 19:30 | 48501.2907 | 1860.012
Devonshire Building | 2016-11-25 19:45 | 48501.7457 | 1820.016
Devonshire Building | 2016-11-25 20:00 | 48502.2107 | 1860.012
Devonshire Building | 2016-11-25 20:15 | 48502.6657 | 1820.016
Devonshire Building | 2016-11-25 20:30 | 48503.1257 | 1839.996
Devonshire Building | 2016-11-25 20:45 | 48503.5857 | 1839.996
Devonshire Building | 2016-11-25 21:00 | 48504.0457 | 1839.996
Devonshire Building | 2016-11-25 21:15 | 48504.5007 | 1820.016
Devonshire Building | 2016-11-25 21:30 | 48504.9557 | 1820.016
Devonshire Building | 2016-11-25 21:45 | 48505.4107 | 1820.016
Devonshire Building | 2016-11-25 22:00 | 48505.8657 | 1820.016
Devonshire Building | 2016-11-25 22:15 | 48506.3107 | 1779.984
Devonshire Building | 2016-11-25 22:30 | 48506.7457 | 1739.988
Devonshire Building | 2016-11-25 22:45 | 48507.1757 | 1720.008
Devonshire Building | 2016-11-25 23:00 | 48507.6057 | 1720.008
Devonshire Building | 2016-11-25 23:15 | 48508.0307 | 1699.992
Devonshire Building | 2016-11-25 23:30 | 48508.4607 | 1720.008
Devonshire Building | 2016-11-25 23:45 | 48508.8907 | 1720.008 | 1620
Devonshire Building | 2016-11-26 | 48509.3203 | 1720.008
Devonshire Building | 2016-11-26 00:15 | 48509.7453 | 1699.992
Devonshire Building | 2016-11-26 00:30 | 48510.1753 | 1720.008
Devonshire Building | 2016-11-26 00:45 | 48510.6003 | 1699.992
Devonshire Building | 2016-11-26 01:00 | 48511.0253 | 1699.992
Devonshire Building | 2016-11-26 01:15 | 48511.4553 | 1720.008
Devonshire Building | 2016-11-26 01:30 | 48511.8803 | 1699.992
Devonshire Building | 2016-11-26 01:45 | 48512.3053 | 1699.992
Devonshire Building | 2016-11-26 02:00 | 48512.7303 | 1699.992
Devonshire Building | 2016-11-26 02:15 | 48513.1553 | 1699.992
Devonshire Building | 2016-11-26 02:30 | 48513.5803 | 1699.992
Devonshire Building | 2016-11-26 02:45 | 48514.0053 | 1699.992
Devonshire Building | 2016-11-26 03:00 | 48514.4303 | 1699.992
Devonshire Building | 2016-11-26 03:15 | 48514.8553 | 1699.992
Devonshire Building | 2016-11-26 03:30 | 48515.2853 | 1720.008
Devonshire Building | 2016-11-26 03:45 | 48515.7103 | 1699.992
Devonshire Building | 2016-11-26 04:00 | 48516.1353 | 1699.992
Devonshire Building | 2016-11-26 04:15 | 48516.5603 | 1699.992
Devonshire Building | 2016-11-26 04:30 | 48516.9853 | 1699.992
Devonshire Building | 2016-11-26 04:45 | 48517.4103 | 1699.992
Devonshire Building | 2016-11-26 05:00 | 48517.8403 | 1720.008
Devonshire Building | 2016-11-26 05:15 | 48518.2653 | 1699.992
Devonshire Building | 2016-11-26 05:30 | 48518.6903 | 1699.992
Devonshire Building | 2016-11-26 05:45 | 48519.1203 | 1720.008
Devonshire Building | 2016-11-26 06:00 | 48519.5453 | 1699.992
Devonshire Building | 2016-11-26 06:15 | 48519.9703 | 1699.992
Devonshire Building | 2016-11-26 06:30 | 48520.3953 | 1699.992
Devonshire Building | 2016-11-26 06:45 | 48520.8203 | 1699.992
Devonshire Building | 2016-11-26 07:00 | 48521.2453 | 1699.992
Devonshire Building | 2016-11-26 07:15 | 48521.6703 | 1699.992
Devonshire Building | 2016-11-26 07:30 | 48522.0953 | 1699.992
Devonshire Building | 2016-11-26 07:45 | 48522.5203 | 1699.992
Devonshire Building | 2016-11-26 08:00 | 48522.9403 | 1680.012
Devonshire Building | 2016-11-26 08:15 | 48523.3603 | 1680.012
Devonshire Building | 2016-11-26 08:30 | 48523.7803 | 1680.012
Devonshire Building | 2016-11-26 08:45 | 48524.2003 | 1680.012
Devonshire Building | 2016-11-26 09:00 | 48524.6153 | 1659.996
Devonshire Building | 2016-11-26 09:15 | 48525.0353 | 1680.012
Devonshire Building | 2016-11-26 09:30 | 48525.4553 | 1680.012
Devonshire Building | 2016-11-26 09:45 | 48525.8703 | 1659.996
Devonshire Building | 2016-11-26 10:00 | 48526.2853 | 1659.996
Devonshire Building | 2016-11-26 10:15 | 48526.7003 | 1659.996
Devonshire Building | 2016-11-26 10:30 | 48527.1153 | 1659.996
Devonshire Building | 2016-11-26 10:45 | 48527.5303 | 1659.996
Devonshire Building | 2016-11-26 11:00 | 48527.9453 | 1659.996
Devonshire Building | 2016-11-26 11:15 | 48528.3603 | 1659.996
Devonshire Building | 2016-11-26 11:30 | 48528.7753 | 1659.996
Devonshire Building | 2016-11-26 11:45 | 48529.1903 | 1659.996
Devonshire Building | 2016-11-26 12:00 | 48529.6103 | 1680.012
Devonshire Building | 2016-11-26 12:15 | 48530.0303 | 1680.012
Devonshire Building | 2016-11-26 12:30 | 48530.4503 | 1680.012
Devonshire Building | 2016-11-26 12:45 | 48530.8653 | 1659.996
Devonshire Building | 2016-11-26 13:00 | 48531.5403 | 2700
Devonshire Building | 2016-11-26 13:15 | 48531.9603 | 1680.012
Devonshire Building | 2016-11-26 13:30 | 48532.3803 | 1680.012
Devonshire Building | 2016-11-26 13:45 | 48532.8003 | 1680.012
Devonshire Building | 2016-11-26 14:00 | 48533.2203 | 1680.012
Devonshire Building | 2016-11-26 14:15 | 48533.6453 | 1699.992
Devonshire Building | 2016-11-26 14:30 | 48534.0653 | 1680.012
Devonshire Building | 2016-11-26 14:45 | 48534.4853 | 1680.012
Devonshire Building | 2016-11-26 15:00 | 48534.9003 | 1659.996
Devonshire Building | 2016-11-26 15:15 | 48535.3253 | 1699.992
Devonshire Building | 2016-11-26 15:30 | 48535.7453 | 1680.012
Devonshire Building | 2016-11-26 15:45 | 48536.1653 | 1680.012
Devonshire Building | 2016-11-26 16:00 | 48536.5853 | 1680.012
Devonshire Building | 2016-11-26 16:15 | 48537.0053 | 1680.012
Devonshire Building | 2016-11-26 16:30 | 48537.4253 | 1680.012
Devonshire Building | 2016-11-26 16:45 | 48537.8453 | 1680.012
Devonshire Building | 2016-11-26 17:00 | 48538.2603 | 1659.996
Devonshire Building | 2016-11-26 17:15 | 48538.6753 | 1659.996
Devonshire Building | 2016-11-26 17:30 | 48539.0953 | 1680.012
Devonshire Building | 2016-11-26 17:45 | 48539.5103 | 1659.996
Devonshire Building | 2016-11-26 18:00 | 48539.9303 | 1680.012
Devonshire Building | 2016-11-26 18:15 | 48540.3453 | 1659.996
Devonshire Building | 2016-11-26 18:30 | 48540.7653 | 1680.012
Devonshire Building | 2016-11-26 18:45 | 48541.1853 | 1680.012
Devonshire Building | 2016-11-26 19:00 | 48541.6003 | 1659.996
Devonshire Building | 2016-11-26 19:15 | 48542.0203 | 1680.012
Devonshire Building | 2016-11-26 19:30 | 48542.4503 | 1720.008
Devonshire Building | 2016-11-26 19:45 | 48542.8903 | 1760.004
Devonshire Building | 2016-11-26 20:00 | 48543.3253 | 1739.988
Devonshire Building | 2016-11-26 20:15 | 48543.7653 | 1760.004
Devonshire Building | 2016-11-26 20:30 | 48544.2053 | 1760.004
Devonshire Building | 2016-11-26 20:45 | 48544.6403 | 1739.988
Devonshire Building | 2016-11-26 21:00 | 48545.0803 | 1760.004
Devonshire Building | 2016-11-26 21:15 | 48545.5203 | 1760.004
Devonshire Building | 2016-11-26 21:30 | 48545.9603 | 1760.004
Devonshire Building | 2016-11-26 21:45 | 48546.4053 | 1779.984
Devonshire Building | 2016-11-26 22:00 | 48546.8503 | 1779.984
Devonshire Building | 2016-11-26 22:15 | 48547.2753 | 1699.992
Devonshire Building | 2016-11-26 22:30 | 48547.7003 | 1699.992
Devonshire Building | 2016-11-26 22:45 | 48548.1303 | 1720.008
Devonshire Building | 2016-11-26 23:00 | 48548.5553 | 1699.992
Devonshire Building | 2016-11-26 23:15 | 48548.9853 | 1720.008
Devonshire Building | 2016-11-26 23:30 | 48549.4103 | 1699.992
Devonshire Building | 2016-11-26 23:45 | 48549.8403 | 1720.008 | 1659.996
Devonshire Building | 2016-11-27 | 48550.2695 | 1720.008
Devonshire Building | 2016-11-27 00:15 | 48550.6995 | 1720.008
Devonshire Building | 2016-11-27 00:30 | 48551.1295 | 1720.008
Devonshire Building | 2016-11-27 00:45 | 48551.5595 | 1720.008
Devonshire Building | 2016-11-27 01:00 | 48551.9895 | 1720.008
Devonshire Building | 2016-11-27 01:15 | 48552.4195 | 1720.008
Devonshire Building | 2016-11-27 01:30 | 48552.8545 | 1739.988
Devonshire Building | 2016-11-27 01:45 | 48553.2845 | 1720.008
Devonshire Building | 2016-11-27 02:00 | 48553.7145 | 1720.008
Devonshire Building | 2016-11-27 02:15 | 48554.1445 | 1720.008
Devonshire Building | 2016-11-27 02:30 | 48554.5795 | 1739.988
Devonshire Building | 2016-11-27 02:45 | 48555.0095 | 1720.008
Devonshire Building | 2016-11-27 03:00 | 48555.4395 | 1720.008
Devonshire Building | 2016-11-27 03:15 | 48555.8695 | 1720.008
Devonshire Building | 2016-11-27 03:30 | 48556.2995 | 1720.008
Devonshire Building | 2016-11-27 03:45 | 48556.7345 | 1739.988
Devonshire Building | 2016-11-27 04:00 | 48557.1645 | 1720.008
Devonshire Building | 2016-11-27 04:15 | 48557.5895 | 1699.992
Devonshire Building | 2016-11-27 04:30 | 48558.0195 | 1720.008
Devonshire Building | 2016-11-27 04:45 | 48558.4495 | 1720.008
Devonshire Building | 2016-11-27 05:00 | 48558.8796 | 1720.008
Devonshire Building | 2016-11-27 05:15 | 48559.3096 | 1720.008
Devonshire Building | 2016-11-27 05:30 | 48559.7396 | 1720.008
Devonshire Building | 2016-11-27 05:45 | 48560.1696 | 1720.008
Devonshire Building | 2016-11-27 06:00 | 48560.5996 | 1720.008
Devonshire Building | 2016-11-27 06:15 | 48561.0296 | 1720.008
Devonshire Building | 2016-11-27 06:30 | 48561.4596 | 1720.008
Devonshire Building | 2016-11-27 06:45 | 48561.8896 | 1720.008
Devonshire Building | 2016-11-27 07:00 | 48562.3196 | 1720.008
Devonshire Building | 2016-11-27 07:15 | 48562.7496 | 1720.008
Devonshire Building | 2016-11-27 07:30 | 48563.1846 | 1739.988
Devonshire Building | 2016-11-27 07:45 | 48563.6146 | 1720.008
Devonshire Building | 2016-11-27 08:00 | 48564.0396 | 1699.992
Devonshire Building | 2016-11-27 08:15 | 48564.4696 | 1720.008
Devonshire Building | 2016-11-27 08:30 | 48564.8946 | 1699.992
Devonshire Building | 2016-11-27 08:45 | 48565.3196 | 1699.992
Devonshire Building | 2016-11-27 09:00 | 48565.7496 | 1720.008
Devonshire Building | 2016-11-27 09:15 | 48566.1746 | 1699.992
Devonshire Building | 2016-11-27 09:30 | 48566.5996 | 1699.992
Devonshire Building | 2016-11-27 09:45 | 48567.0196 | 1680.012
Devonshire Building | 2016-11-27 10:00 | 48567.4446 | 1699.992
Devonshire Building | 2016-11-27 10:15 | 48567.8696 | 1699.992
Devonshire Building | 2016-11-27 10:30 | 48568.2946 | 1699.992
Devonshire Building | 2016-11-27 10:45 | 48568.7146 | 1680.012
Devonshire Building | 2016-11-27 11:00 | 48569.1346 | 1680.012
Devonshire Building | 2016-11-27 11:15 | 48569.5596 | 1699.992
Devonshire Building | 2016-11-27 11:30 | 48569.9796 | 1680.012
Devonshire Building | 2016-11-27 11:45 | 48570.3996 | 1680.012
Devonshire Building | 2016-11-27 12:00 | 48570.8196 | 1680.012
Devonshire Building | 2016-11-27 12:15 | 48571.2446 | 1699.992
Devonshire Building | 2016-11-27 12:30 | 48571.6646 | 1680.012
Devonshire Building | 2016-11-27 12:45 | 48572.0896 | 1699.992
Devonshire Building | 2016-11-27 13:00 | 48572.5096 | 1680.012
Devonshire Building | 2016-11-27 13:15 | 48572.9346 | 1699.992
Devonshire Building | 2016-11-27 13:30 | 48573.3546 | 1680.012
Devonshire Building | 2016-11-27 13:45 | 48573.7796 | 1699.992
Devonshire Building | 2016-11-27 14:00 | 48574.2046 | 1699.992
Devonshire Building | 2016-11-27 14:15 | 48574.6346 | 1720.008
Devonshire Building | 2016-11-27 14:30 | 48575.0596 | 1699.992
Devonshire Building | 2016-11-27 14:45 | 48575.4846 | 1699.992
Devonshire Building | 2016-11-27 15:00 | 48576.1696 | 2739.996
Devonshire Building | 2016-11-27 15:15 | 48576.5996 | 1720.008
Devonshire Building | 2016-11-27 15:30 | 48577.0296 | 1720.008
Devonshire Building | 2016-11-27 15:45 | 48577.4596 | 1720.008
Devonshire Building | 2016-11-27 16:00 | 48577.8846 | 1699.992
Devonshire Building | 2016-11-27 16:15 | 48578.3146 | 1720.008
Devonshire Building | 2016-11-27 16:30 | 48578.7446 | 1720.008
Devonshire Building | 2016-11-27 16:45 | 48579.1696 | 1699.992
Devonshire Building | 2016-11-27 17:00 | 48579.6096 | 1760.004
Devonshire Building | 2016-11-27 17:15 | 48580.0496 | 1760.004
Devonshire Building | 2016-11-27 17:30 | 48580.4946 | 1779.984
Devonshire Building | 2016-11-27 17:45 | 48580.9346 | 1760.004
Devonshire Building | 2016-11-27 18:00 | 48581.3746 | 1760.004
Devonshire Building | 2016-11-27 18:15 | 48581.8146 | 1760.004
Devonshire Building | 2016-11-27 18:30 | 48582.2546 | 1760.004
Devonshire Building | 2016-11-27 18:45 | 48582.6946 | 1760.004
Devonshire Building | 2016-11-27 19:00 | 48583.1346 | 1760.004
Devonshire Building | 2016-11-27 19:15 | 48583.5746 | 1760.004
Devonshire Building | 2016-11-27 19:30 | 48584.0146 | 1760.004
Devonshire Building | 2016-11-27 19:45 | 48584.4546 | 1760.004
Devonshire Building | 2016-11-27 20:00 | 48584.8946 | 1760.004
Devonshire Building | 2016-11-27 20:15 | 48585.3346 | 1760.004
Devonshire Building | 2016-11-27 20:30 | 48585.7746 | 1760.004
Devonshire Building | 2016-11-27 20:45 | 48586.2196 | 1779.984
Devonshire Building | 2016-11-27 21:00 | 48586.6496 | 1720.008
Devonshire Building | 2016-11-27 21:15 | 48587.0796 | 1720.008
Devonshire Building | 2016-11-27 21:30 | 48587.5046 | 1699.992
Devonshire Building | 2016-11-27 21:45 | 48587.9296 | 1699.992
Devonshire Building | 2016-11-27 22:00 | 48588.3746 | 1779.984
Devonshire Building | 2016-11-27 22:15 | 48588.8046 | 1720.008
Devonshire Building | 2016-11-27 22:30 | 48589.2346 | 1720.008
Devonshire Building | 2016-11-27 22:45 | 48589.6596 | 1699.992
Devonshire Building | 2016-11-27 23:00 | 48590.0896 | 1720.008
Devonshire Building | 2016-11-27 23:15 | 48590.5196 | 1720.008
Devonshire Building | 2016-11-27 23:30 | 48590.9496 | 1720.008
Devonshire Building | 2016-11-27 23:45 | 48591.3796 | 1720.008 | 1680.012
Devonshire Building | 2016-11-28 | 48591.8125 | 1739.988
Devonshire Building | 2016-11-28 00:15 | 48592.2425 | 1720.008
Devonshire Building | 2016-11-28 00:30 | 48592.6775 | 1739.988
Devonshire Building | 2016-11-28 00:45 | 48593.1075 | 1720.008
Devonshire Building | 2016-11-28 01:00 | 48593.5425 | 1739.988
Devonshire Building | 2016-11-28 01:15 | 48593.9775 | 1739.988
Devonshire Building | 2016-11-28 01:30 | 48594.4125 | 1739.988
Devonshire Building | 2016-11-28 01:45 | 48594.8425 | 1720.008
Devonshire Building | 2016-11-28 02:00 | 48595.2775 | 1739.988
Devonshire Building | 2016-11-28 02:15 | 48595.7125 | 1739.988
Devonshire Building | 2016-11-28 02:30 | 48596.1475 | 1739.988
Devonshire Building | 2016-11-28 02:45 | 48596.5825 | 1739.988
Devonshire Building | 2016-11-28 03:00 | 48597.0175 | 1739.988
Devonshire Building | 2016-11-28 03:15 | 48597.4525 | 1739.988
Devonshire Building | 2016-11-28 03:30 | 48597.8875 | 1739.988
Devonshire Building | 2016-11-28 03:45 | 48598.3225 | 1739.988
Devonshire Building | 2016-11-28 04:00 | 48598.7575 | 1739.988
Devonshire Building | 2016-11-28 04:15 | 48599.1875 | 1720.008
Devonshire Building | 2016-11-28 04:30 | 48599.6225 | 1739.988
Devonshire Building | 2016-11-28 04:45 | 48600.0575 | 1739.988
Devonshire Building | 2016-11-28 05:00 | 48600.4875 | 1720.008
Devonshire Building | 2016-11-28 05:15 | 48600.9225 | 1739.988
Devonshire Building | 2016-11-28 05:30 | 48601.3525 | 1720.008
Devonshire Building | 2016-11-28 05:45 | 48601.7875 | 1739.988
Devonshire Building | 2016-11-28 06:00 | 48602.2175 | 1720.008
Devonshire Building | 2016-11-28 06:15 | 48602.6475 | 1720.008
Devonshire Building | 2016-11-28 06:30 | 48603.0775 | 1720.008
Devonshire Building | 2016-11-28 06:45 | 48603.5075 | 1720.008
Devonshire Building | 2016-11-28 07:00 | 48603.9375 | 1720.008
Devonshire Building | 2016-11-28 07:15 | 48604.3625 | 1699.992
Devonshire Building | 2016-11-28 07:30 | 48604.7925 | 1720.008
Devonshire Building | 2016-11-28 07:45 | 48605.2225 | 1720.008
Devonshire Building | 2016-11-28 08:00 | 48605.6475 | 1699.992
Devonshire Building | 2016-11-28 08:15 | 48606.0675 | 1680.012
Devonshire Building | 2016-11-28 08:30 | 48606.4925 | 1699.992
Devonshire Building | 2016-11-28 08:45 | 48606.9325 | 1760.004
Devonshire Building | 2016-11-28 09:00 | 48607.6275 | 2779.992
Devonshire Building | 2016-11-28 09:15 | 48608.0525 | 1699.992
Devonshire Building | 2016-11-28 09:30 | 48608.4775 | 1699.992
Devonshire Building | 2016-11-28 09:45 | 48608.9075 | 1720.008
Devonshire Building | 2016-11-28 10:00 | 48609.3325 | 1699.992
Devonshire Building | 2016-11-28 10:15 | 48610.0725 | 2959.992
Devonshire Building | 2016-11-28 10:30 | 48610.5175 | 1779.984
Devonshire Building | 2016-11-28 10:45 | 48610.9625 | 1779.984
Devonshire Building | 2016-11-28 11:00 | 48611.4175 | 1820.016
Devonshire Building | 2016-11-28 11:15 | 48611.8925 | 1900.008
Devonshire Building | 2016-11-28 11:30 | 48612.3875 | 1980
Devonshire Building | 2016-11-28 11:45 | 48613.2825 | 3579.984
Devonshire Building | 2016-11-28 12:00 | 48613.9675 | 2739.996
Devonshire Building | 2016-11-28 12:15 | 48614.5975 | 2520
Devonshire Building | 2016-11-28 12:30 | 48615.1875 | 2360.016
Devonshire Building | 2016-11-28 12:45 | 48615.7725 | 2340
Devonshire Building | 2016-11-28 13:00 | 48616.6175 | 3380.004
Devonshire Building | 2016-11-28 13:15 | 48617.1425 | 2099.988
Devonshire Building | 2016-11-28 13:30 | 48617.6525 | 2040.012
Devonshire Building | 2016-11-28 13:45 | 48618.1625 | 2040.012
Devonshire Building | 2016-11-28 14:00 | 48618.6675 | 2019.996
Devonshire Building | 2016-11-28 14:15 | 48619.1725 | 2019.996
Devonshire Building | 2016-11-28 14:30 | 48619.9325 | 3039.984
Devonshire Building | 2016-11-28 14:45 | 48620.3925 | 1839.996
Devonshire Building | 2016-11-28 15:00 | 48620.8675 | 1900.008
Devonshire Building | 2016-11-28 15:15 | 48621.3675 | 2000.016
Devonshire Building | 2016-11-28 15:30 | 48621.8675 | 2000.016
Devonshire Building | 2016-11-28 15:45 | 48622.3775 | 2040.012
Devonshire Building | 2016-11-28 16:00 | 48623.1675 | 3160.008
Devonshire Building | 2016-11-28 16:15 | 48623.6875 | 2080.008
Devonshire Building | 2016-11-28 16:30 | 48624.1925 | 2019.996
Devonshire Building | 2016-11-28 16:45 | 48624.6825 | 1959.984
Devonshire Building | 2016-11-28 17:00 | 48625.1525 | 1879.992
Devonshire Building | 2016-11-28 17:15 | 48625.6125 | 1839.996
Devonshire Building | 2016-11-28 17:30 | 48626.0825 | 1879.992
Devonshire Building | 2016-11-28 17:45 | 48626.6025 | 2080.008
Devonshire Building | 2016-11-28 18:00 | 48627.2975 | 2779.992
Devonshire Building | 2016-11-28 18:15 | 48627.7725 | 1900.008
Devonshire Building | 2016-11-28 18:30 | 48628.2475 | 1900.008
Devonshire Building | 2016-11-28 18:45 | 48628.7175 | 1879.992
Devonshire Building | 2016-11-28 19:00 | 48629.1875 | 1879.992
Devonshire Building | 2016-11-28 19:15 | 48629.6575 | 1879.992
Devonshire Building | 2016-11-28 19:30 | 48630.1225 | 1860.012
Devonshire Building | 2016-11-28 19:45 | 48630.5825 | 1839.996
Devonshire Building | 2016-11-28 20:00 | 48631.0375 | 1820.016
Devonshire Building | 2016-11-28 20:15 | 48631.4825 | 1779.984
Devonshire Building | 2016-11-28 20:30 | 48631.9275 | 1779.984
Devonshire Building | 2016-11-28 20:45 | 48632.3675 | 1760.004
Devonshire Building | 2016-11-28 21:00 | 48632.8075 | 1760.004
Devonshire Building | 2016-11-28 21:15 | 48633.2425 | 1739.988
Devonshire Building | 2016-11-28 21:30 | 48633.6775 | 1739.988
Devonshire Building | 2016-11-28 21:45 | 48634.1125 | 1739.988
Devonshire Building | 2016-11-28 22:00 | 48634.5525 | 1760.004
Devonshire Building | 2016-11-28 22:15 | 48634.9825 | 1720.008
Devonshire Building | 2016-11-28 22:30 | 48635.4125 | 1720.008
Devonshire Building | 2016-11-28 22:45 | 48635.8425 | 1720.008
Devonshire Building | 2016-11-28 23:00 | 48636.2775 | 1739.988
Devonshire Building | 2016-11-28 23:15 | 48636.7075 | 1720.008
Devonshire Building | 2016-11-28 23:30 | 48637.1425 | 1739.988
Devonshire Building | 2016-11-28 23:45 | 48637.5775 | 1739.988 | 1680.012
Devonshire Building | 2016-11-29 | 48638.0078 | 1720.008
Devonshire Building | 2016-11-29 00:15 | 48638.4428 | 1739.988
Devonshire Building | 2016-11-29 00:30 | 48638.8778 | 1739.988
Devonshire Building | 2016-11-29 00:45 | 48639.3128 | 1739.988
Devonshire Building | 2016-11-29 01:00 | 48639.7478 | 1739.988
Devonshire Building | 2016-11-29 01:15 | 48640.1828 | 1739.988
Devonshire Building | 2016-11-29 01:30 | 48640.6228 | 1760.004
Devonshire Building | 2016-11-29 01:45 | 48641.0578 | 1739.988
Devonshire Building | 2016-11-29 02:00 | 48641.4928 | 1739.988
Devonshire Building | 2016-11-29 02:15 | 48641.9278 | 1739.988
Devonshire Building | 2016-11-29 02:30 | 48642.3678 | 1760.004
Devonshire Building | 2016-11-29 02:45 | 48642.8028 | 1739.988
Devonshire Building | 2016-11-29 03:00 | 48643.2378 | 1739.988
Devonshire Building | 2016-11-29 03:15 | 48643.6728 | 1739.988
Devonshire Building | 2016-11-29 03:30 | 48644.1078 | 1739.988
Devonshire Building | 2016-11-29 03:45 | 48644.5428 | 1739.988
Devonshire Building | 2016-11-29 04:00 | 48644.9778 | 1739.988
Devonshire Building | 2016-11-29 04:15 | 48645.4128 | 1739.988
Devonshire Building | 2016-11-29 04:30 | 48645.8428 | 1720.008
Devonshire Building | 2016-11-29 04:45 | 48646.2778 | 1739.988
Devonshire Building | 2016-11-29 05:00 | 48646.7128 | 1739.988
Devonshire Building | 2016-11-29 05:15 | 48647.1428 | 1720.008
Devonshire Building | 2016-11-29 05:30 | 48647.5728 | 1720.008
Devonshire Building | 2016-11-29 05:45 | 48648.0028 | 1720.008
Devonshire Building | 2016-11-29 06:00 | 48648.4378 | 1739.988
Devonshire Building | 2016-11-29 06:15 | 48648.8678 | 1720.008
Devonshire Building | 2016-11-29 06:30 | 48649.2978 | 1720.008
Devonshire Building | 2016-11-29 06:45 | 48649.7228 | 1699.992
Devonshire Building | 2016-11-29 07:00 | 48650.1528 | 1720.008
Devonshire Building | 2016-11-29 07:15 | 48650.5778 | 1699.992
Devonshire Building | 2016-11-29 07:30 | 48651.0128 | 1739.988
Devonshire Building | 2016-11-29 07:45 | 48651.4528 | 1760.004
Devonshire Building | 2016-11-29 08:00 | 48651.8978 | 1779.984
Devonshire Building | 2016-11-29 08:15 | 48652.3328 | 1739.988
Devonshire Building | 2016-11-29 08:30 | 48652.7728 | 1760.004
Devonshire Building | 2016-11-29 08:45 | 48653.2128 | 1760.004
Devonshire Building | 2016-11-29 09:00 | 48653.9378 | 2900.016
Devonshire Building | 2016-11-29 09:15 | 48654.3728 | 1739.988
Devonshire Building | 2016-11-29 09:30 | 48654.8128 | 1760.004
Devonshire Building | 2016-11-29 09:45 | 48655.2528 | 1760.004
Devonshire Building | 2016-11-29 10:00 | 48655.6928 | 1760.004
Devonshire Building | 2016-11-29 10:15 | 48656.1478 | 1820.016
Devonshire Building | 2016-11-29 10:30 | 48656.9078 | 3039.984
Devonshire Building | 2016-11-29 10:45 | 48657.4628 | 2220.012
Devonshire Building | 2016-11-29 11:00 | 48658.0178 | 2220.012
Devonshire Building | 2016-11-29 11:15 | 48658.5678 | 2199.996
Devonshire Building | 2016-11-29 11:30 | 48659.1028 | 2139.984
Devonshire Building | 2016-11-29 11:45 | 48659.6278 | 2099.988
Devonshire Building | 2016-11-29 12:00 | 48660.4428 | 3260.016
Devonshire Building | 2016-11-29 12:15 | 48660.9728 | 2120.004
Devonshire Building | 2016-11-29 12:30 | 48661.5028 | 2120.004
Devonshire Building | 2016-11-29 12:45 | 48662.0228 | 2080.008
Devonshire Building | 2016-11-29 13:00 | 48662.5328 | 2040.012
Devonshire Building | 2016-11-29 13:15 | 48663.0378 | 2019.996
Devonshire Building | 2016-11-29 13:30 | 48663.5578 | 2080.008
Devonshire Building | 2016-11-29 13:45 | 48664.3078 | 2999.988
Devonshire Building | 2016-11-29 14:00 | 48664.7928 | 1940.004
Devonshire Building | 2016-11-29 14:15 | 48665.2828 | 1959.984
Devonshire Building | 2016-11-29 14:30 | 48665.7678 | 1940.004
Devonshire Building | 2016-11-29 14:45 | 48666.2428 | 1900.008
Devonshire Building | 2016-11-29 15:00 | 48666.7178 | 1900.008
Devonshire Building | 2016-11-29 15:15 | 48667.1978 | 1919.988
Devonshire Building | 2016-11-29 15:30 | 48667.9478 | 2999.988
Devonshire Building | 2016-11-29 15:45 | 48668.4178 | 1879.992
Devonshire Building | 2016-11-29 16:00 | 48668.8878 | 1879.992
Devonshire Building | 2016-11-29 16:15 | 48669.3628 | 1900.008
Devonshire Building | 2016-11-29 16:30 | 48669.8328 | 1879.992
Devonshire Building | 2016-11-29 16:45 | 48670.3078 | 1900.008
Devonshire Building | 2016-11-29 17:00 | 48670.7778 | 1879.992
Devonshire Building | 2016-11-29 17:15 | 48671.5228 | 2980.008
Devonshire Building | 2016-11-29 17:30 | 48671.9928 | 1879.992
Devonshire Building | 2016-11-29 17:45 | 48672.4578 | 1860.012
Devonshire Building | 2016-11-29 18:00 | 48672.9278 | 1879.992
Devonshire Building | 2016-11-29 18:15 | 48673.3828 | 1820.016
Devonshire Building | 2016-11-29 18:30 | 48673.8428 | 1839.996
Devonshire Building | 2016-11-29 18:45 | 48674.2978 | 1820.016
Devonshire Building | 2016-11-29 19:00 | 48674.7528 | 1820.016
Devonshire Building | 2016-11-29 19:15 | 48675.2078 | 1820.016
Devonshire Building | 2016-11-29 19:30 | 48675.6578 | 1800
Devonshire Building | 2016-11-29 19:45 | 48676.1028 | 1779.984
Devonshire Building | 2016-11-29 20:00 | 48676.5478 | 1779.984
Devonshire Building | 2016-11-29 20:15 | 48676.9878 | 1760.004
Devonshire Building | 2016-11-29 20:30 | 48677.4278 | 1760.004
Devonshire Building | 2016-11-29 20:45 | 48677.8628 | 1739.988
Devonshire Building | 2016-11-29 21:00 | 48678.2978 | 1739.988
Devonshire Building | 2016-11-29 21:15 | 48678.7378 | 1760.004
Devonshire Building | 2016-11-29 21:30 | 48679.1728 | 1739.988
Devonshire Building | 2016-11-29 21:45 | 48679.6078 | 1739.988
Devonshire Building | 2016-11-29 22:00 | 48680.0578 | 1800
Devonshire Building | 2016-11-29 22:15 | 48680.4878 | 1720.008
Devonshire Building | 2016-11-29 22:30 | 48680.9178 | 1720.008
Devonshire Building | 2016-11-29 22:45 | 48681.3478 | 1720.008
Devonshire Building | 2016-11-29 23:00 | 48681.7778 | 1720.008
Devonshire Building | 2016-11-29 23:15 | 48682.2078 | 1720.008
Devonshire Building | 2016-11-29 23:30 | 48682.6378 | 1720.008
Devonshire Building | 2016-11-29 23:45 | 48683.0678 | 1720.008 | 1699.992
Devonshire Building | 2016-11-30 | 48683.5039 | 1739.988
Devonshire Building | 2016-11-30 00:15 | 48683.9389 | 1739.988
Devonshire Building | 2016-11-30 00:30 | 48684.3739 | 1739.988
Devonshire Building | 2016-11-30 00:45 | 48684.8039 | 1720.008
Devonshire Building | 2016-11-30 01:00 | 48685.2389 | 1739.988
Devonshire Building | 2016-11-30 01:15 | 48685.6739 | 1739.988
Devonshire Building | 2016-11-30 01:30 | 48686.1089 | 1739.988
Devonshire Building | 2016-11-30 01:45 | 48686.5439 | 1739.988
Devonshire Building | 2016-11-30 02:00 | 48686.9789 | 1739.988
Devonshire Building | 2016-11-30 02:15 | 48687.4189 | 1760.004
Devonshire Building | 2016-11-30 02:30 | 48687.8539 | 1739.988
Devonshire Building | 2016-11-30 02:45 | 48688.2939 | 1760.004
Devonshire Building | 2016-11-30 03:00 | 48688.7289 | 1739.988
Devonshire Building | 2016-11-30 03:15 | 48689.1639 | 1739.988
Devonshire Building | 2016-11-30 03:30 | 48689.5989 | 1739.988
Devonshire Building | 2016-11-30 03:45 | 48690.0339 | 1739.988
Devonshire Building | 2016-11-30 04:00 | 48690.4689 | 1739.988
Devonshire Building | 2016-11-30 04:15 | 48690.8989 | 1720.008
Devonshire Building | 2016-11-30 04:30 | 48691.3339 | 1739.988
Devonshire Building | 2016-11-30 04:45 | 48691.7689 | 1739.988
Devonshire Building | 2016-11-30 05:00 | 48692.1989 | 1720.008
Devonshire Building | 2016-11-30 05:15 | 48692.6339 | 1739.988
Devonshire Building | 2016-11-30 05:30 | 48693.0689 | 1739.988
Devonshire Building | 2016-11-30 05:45 | 48693.5039 | 1739.988
Devonshire Building | 2016-11-30 06:00 | 48693.9389 | 1739.988
Devonshire Building | 2016-11-30 06:15 | 48694.3689 | 1720.008
Devonshire Building | 2016-11-30 06:30 | 48694.8039 | 1739.988
Devonshire Building | 2016-11-30 06:45 | 48695.2389 | 1739.988
Devonshire Building | 2016-11-30 07:00 | 48695.6689 | 1720.008
Devonshire Building | 2016-11-30 07:15 | 48696.0989 | 1720.008
Devonshire Building | 2016-11-30 07:30 | 48696.5289 | 1720.008
Devonshire Building | 2016-11-30 07:45 | 48696.9689 | 1760.004
Devonshire Building | 2016-11-30 08:00 | 48697.4139 | 1779.984
Devonshire Building | 2016-11-30 08:15 | 48697.8539 | 1760.004
Devonshire Building | 2016-11-30 08:30 | 48698.5789 | 2900.016
Devonshire Building | 2016-11-30 08:45 | 48699.0239 | 1779.984
Devonshire Building | 2016-11-30 09:00 | 48699.4789 | 1820.016
Devonshire Building | 2016-11-30 09:15 | 48699.9239 | 1779.984
Devonshire Building | 2016-11-30 09:30 | 48700.3889 | 1860.012
Devonshire Building | 2016-11-30 09:45 | 48700.8889 | 2000.016
Devonshire Building | 2016-11-30 10:00 | 48701.4239 | 2139.984
Devonshire Building | 2016-11-30 10:15 | 48701.9639 | 2160
Devonshire Building | 2016-11-30 10:30 | 48702.5089 | 2180.016
Devonshire Building | 2016-11-30 10:45 | 48703.2989 | 3160.008
Devonshire Building | 2016-11-30 11:00 | 48703.8189 | 2080.008
Devonshire Building | 2016-11-30 11:15 | 48704.3339 | 2059.992
Devonshire Building | 2016-11-30 11:30 | 48704.8239 | 1959.984
Devonshire Building | 2016-11-30 11:45 | 48705.3139 | 1959.984
Devonshire Building | 2016-11-30 12:00 | 48706.0889 | 3099.996
Devonshire Building | 2016-11-30 12:15 | 48706.5439 | 1820.016
Devonshire Building | 2016-11-30 12:30 | 48706.9989 | 1820.016
Devonshire Building | 2016-11-30 12:45 | 48707.4589 | 1839.996
Devonshire Building | 2016-11-30 13:00 | 48707.9289 | 1879.992
Devonshire Building | 2016-11-30 13:15 | 48708.3939 | 1860.012
Devonshire Building | 2016-11-30 13:30 | 48708.8639 | 1879.992
Devonshire Building | 2016-11-30 13:45 | 48709.3239 | 1839.996
Devonshire Building | 2016-11-30 14:00 | 48710.1039 | 3120.012
Devonshire Building | 2016-11-30 14:15 | 48710.5789 | 1900.008
Devonshire Building | 2016-11-30 14:30 | 48711.0489 | 1879.992
Devonshire Building | 2016-11-30 14:45 | 48711.5289 | 1919.988
Devonshire Building | 2016-11-30 15:00 | 48712.0039 | 1900.008
Devonshire Building | 2016-11-30 15:15 | 48712.4789 | 1900.008
Devonshire Building | 2016-11-30 15:30 | 48712.9539 | 1900.008
Devonshire Building | 2016-11-30 15:45 | 48713.7139 | 3039.984
Devonshire Building | 2016-11-30 16:00 | 48714.1839 | 1879.992
Devonshire Building | 2016-11-30 16:15 | 48714.6889 | 2019.996
Devonshire Building | 2016-11-30 16:30 | 48715.2589 | 2279.988
Devonshire Building | 2016-11-30 16:45 | 48715.8339 | 2300.004
Devonshire Building | 2016-11-30 17:00 | 48716.4189 | 2340
Devonshire Building | 2016-11-30 17:15 | 48717.1039 | 2739.996
Devonshire Building | 2016-11-30 17:30 | 48717.6989 | 2379.996
Devonshire Building | 2016-11-30 17:45 | 48718.4589 | 3039.984
Devonshire Building | 2016-11-30 18:00 | 48718.9639 | 2019.996
Devonshire Building | 2016-11-30 18:15 | 48719.4439 | 1919.988
Devonshire Building | 2016-11-30 18:30 | 48719.9238 | 1919.988
Devonshire Building | 2016-11-30 18:45 | 48720.3989 | 1900.008
Devonshire Building | 2016-11-30 19:00 | 48720.8688 | 1879.992
Devonshire Building | 2016-11-30 19:15 | 48721.3288 | 1839.996
Devonshire Building | 2016-11-30 19:30 | 48721.7839 | 1820.016
Devonshire Building | 2016-11-30 19:45 | 48722.2389 | 1820.016
Devonshire Building | 2016-11-30 20:00 | 48722.6939 | 1820.016
Devonshire Building | 2016-11-30 20:15 | 48723.1389 | 1779.984
Devonshire Building | 2016-11-30 20:30 | 48723.5839 | 1779.984
Devonshire Building | 2016-11-30 20:45 | 48724.0288 | 1779.984
Devonshire Building | 2016-11-30 21:00 | 48724.4738 | 1779.984
Devonshire Building | 2016-11-30 21:15 | 48724.9138 | 1760.004
Devonshire Building | 2016-11-30 21:30 | 48725.3588 | 1779.984
Devonshire Building | 2016-11-30 21:45 | 48725.7988 | 1760.004
Devonshire Building | 2016-11-30 22:00 | 48726.2488 | 1800
Devonshire Building | 2016-11-30 22:15 | 48726.6788 | 1720.008
Devonshire Building | 2016-11-30 22:30 | 48727.1188 | 1760.004
Devonshire Building | 2016-11-30 22:45 | 48727.5538 | 1739.988
Devonshire Building | 2016-11-30 23:00 | 48727.9888 | 1739.988
Devonshire Building | 2016-11-30 23:15 | 48728.4288 | 1760.004
Devonshire Building | 2016-11-30 23:30 | 48728.8638 | 1739.988
Devonshire Building | 2016-11-30 23:45 | 48729.3038 | 1760.004 | 1720.008
Devonshire Building | 2016-12-01 | 48729.7461 | 1760.004
Devonshire Building | 2016-12-01 00:15 | 48730.1811 | 1739.988
Devonshire Building | 2016-12-01 00:30 | 48730.6211 | 1760.004
Devonshire Building | 2016-12-01 00:45 | 48731.0611 | 1760.004
Devonshire Building | 2016-12-01 01:00 | 48731.5011 | 1760.004
Devonshire Building | 2016-12-01 01:15 | 48731.9411 | 1760.004
Devonshire Building | 2016-12-01 01:30 | 48732.3811 | 1760.004
Devonshire Building | 2016-12-01 01:45 | 48732.8211 | 1760.004
Devonshire Building | 2016-12-01 02:00 | 48733.2661 | 1779.984
Devonshire Building | 2016-12-01 02:15 | 48733.7061 | 1760.004
Devonshire Building | 2016-12-01 02:30 | 48734.1461 | 1760.004
Devonshire Building | 2016-12-01 02:45 | 48734.5861 | 1760.004
Devonshire Building | 2016-12-01 03:00 | 48735.0261 | 1760.004
Devonshire Building | 2016-12-01 03:15 | 48735.4711 | 1779.984
Devonshire Building | 2016-12-01 03:30 | 48735.9111 | 1760.004
Devonshire Building | 2016-12-01 03:45 | 48736.3511 | 1760.004
Devonshire Building | 2016-12-01 04:00 | 48736.7961 | 1779.984
Devonshire Building | 2016-12-01 04:15 | 48737.2361 | 1760.004
Devonshire Building | 2016-12-01 04:30 | 48737.6761 | 1760.004
Devonshire Building | 2016-12-01 04:45 | 48738.1211 | 1779.984
Devonshire Building | 2016-12-01 05:00 | 48738.5611 | 1760.004
Devonshire Building | 2016-12-01 05:15 | 48739.0011 | 1760.004
Devonshire Building | 2016-12-01 05:30 | 48739.4411 | 1760.004
Devonshire Building | 2016-12-01 05:45 | 48739.8811 | 1760.004
Devonshire Building | 2016-12-01 06:00 | 48740.3211 | 1760.004
Devonshire Building | 2016-12-01 06:15 | 48740.7611 | 1760.004
Devonshire Building | 2016-12-01 06:30 | 48741.1961 | 1739.988
Devonshire Building | 2016-12-01 06:45 | 48741.6361 | 1760.004
Devonshire Building | 2016-12-01 07:00 | 48742.0711 | 1739.988
Devonshire Building | 2016-12-01 07:15 | 48742.5011 | 1720.008
Devonshire Building | 2016-12-01 07:30 | 48742.9361 | 1739.988
Devonshire Building | 2016-12-01 07:45 | 48743.6511 | 2859.984
Devonshire Building | 2016-12-01 08:00 | 48744.0961 | 1779.984
Devonshire Building | 2016-12-01 08:15 | 48744.5411 | 1779.984
Devonshire Building | 2016-12-01 08:30 | 48744.9911 | 1800
Devonshire Building | 2016-12-01 08:45 | 48745.4311 | 1760.004
Devonshire Building | 2016-12-01 09:00 | 48745.8811 | 1800
Devonshire Building | 2016-12-01 09:15 | 48746.3261 | 1779.984
Devonshire Building | 2016-12-01 09:30 | 48746.7711 | 1779.984
Devonshire Building | 2016-12-01 09:45 | 48747.2211 | 1800
Devonshire Building | 2016-12-01 10:00 | 48747.6761 | 1820.016
Devonshire Building | 2016-12-01 10:15 | 48748.4411 | 3060
Devonshire Building | 2016-12-01 10:30 | 48748.9211 | 1919.988
Devonshire Building | 2016-12-01 10:45 | 48749.4061 | 1940.004
Devonshire Building | 2016-12-01 11:00 | 48749.9361 | 2120.004
Devonshire Building | 2016-12-01 11:15 | 48750.4761 | 2160
Devonshire Building | 2016-12-01 11:30 | 48750.9961 | 2080.008
Devonshire Building | 2016-12-01 11:45 | 48751.7711 | 3099.996
Devonshire Building | 2016-12-01 12:00 | 48752.2711 | 2000.016
Devonshire Building | 2016-12-01 12:15 | 48752.7661 | 1980
Devonshire Building | 2016-12-01 12:30 | 48753.2661 | 2000.016
Devonshire Building | 2016-12-01 12:45 | 48753.7711 | 2019.996
Devonshire Building | 2016-12-01 13:00 | 48754.2711 | 2000.016
Devonshire Building | 2016-12-01 13:15 | 48754.9061 | 2540.016
Devonshire Building | 2016-12-01 13:30 | 48755.5661 | 2639.988
Devonshire Building | 2016-12-01 13:45 | 48756.0811 | 2059.992
Devonshire Building | 2016-12-01 14:00 | 48756.5961 | 2059.992
Devonshire Building | 2016-12-01 14:15 | 48757.1011 | 2019.996
Devonshire Building | 2016-12-01 14:30 | 48757.5961 | 1980
Devonshire Building | 2016-12-01 14:45 | 48758.0911 | 1980
Devonshire Building | 2016-12-01 15:00 | 48758.5811 | 1959.984
Devonshire Building | 2016-12-01 15:15 | 48759.3461 | 3060
Devonshire Building | 2016-12-01 15:30 | 48759.8361 | 1959.984
Devonshire Building | 2016-12-01 15:45 | 48760.3311 | 1980
Devonshire Building | 2016-12-01 16:00 | 48760.8211 | 1959.984
Devonshire Building | 2016-12-01 16:15 | 48761.3011 | 1919.988
Devonshire Building | 2016-12-01 16:30 | 48761.7911 | 1959.984
Devonshire Building | 2016-12-01 16:45 | 48762.2711 | 1919.988
Devonshire Building | 2016-12-01 17:00 | 48762.7561 | 1940.004
Devonshire Building | 2016-12-01 17:15 | 48763.5311 | 3099.996
Devonshire Building | 2016-12-01 17:30 | 48764.0261 | 1980
Devonshire Building | 2016-12-01 17:45 | 48764.5361 | 2040.012
Devonshire Building | 2016-12-01 18:00 | 48765.0361 | 2000.016
Devonshire Building | 2016-12-01 18:15 | 48765.5261 | 1959.984
Devonshire Building | 2016-12-01 18:30 | 48766.0111 | 1940.004
Devonshire Building | 2016-12-01 18:45 | 48766.4911 | 1919.988
Devonshire Building | 2016-12-01 19:00 | 48766.9711 | 1919.988
Devonshire Building | 2016-12-01 19:15 | 48767.4511 | 1919.988
Devonshire Building | 2016-12-01 19:30 | 48767.921 | 1879.992
Devonshire Building | 2016-12-01 19:45 | 48768.3861 | 1860.012
Devonshire Building | 2016-12-01 20:00 | 48768.8461 | 1839.996
Devonshire Building | 2016-12-01 20:15 | 48769.3011 | 1820.016
Devonshire Building | 2016-12-01 20:30 | 48769.7511 | 1800
Devonshire Building | 2016-12-01 20:45 | 48770.196 | 1779.984
Devonshire Building | 2016-12-01 21:00 | 48770.641 | 1779.984
Devonshire Building | 2016-12-01 21:15 | 48771.091 | 1800
Devonshire Building | 2016-12-01 21:30 | 48771.531 | 1760.004
Devonshire Building | 2016-12-01 21:45 | 48771.976 | 1779.984
Devonshire Building | 2016-12-01 22:00 | 48772.431 | 1820.016
Devonshire Building | 2016-12-01 22:15 | 48772.866 | 1739.988
Devonshire Building | 2016-12-01 22:30 | 48773.306 | 1760.004
Devonshire Building | 2016-12-01 22:45 | 48773.741 | 1739.988
Devonshire Building | 2016-12-01 23:00 | 48774.181 | 1760.004
Devonshire Building | 2016-12-01 23:15 | 48774.616 | 1739.988
Devonshire Building | 2016-12-01 23:30 | 48775.056 | 1760.004
Devonshire Building | 2016-12-01 23:45 | 48775.491 | 1739.988 | 1720.008
Devonshire Building | 2016-12-02 | 48775.9297 | 1760.004
Devonshire Building | 2016-12-02 00:15 | 48776.3697 | 1760.004
Devonshire Building | 2016-12-02 00:30 | 48776.8097 | 1760.004
Devonshire Building | 2016-12-02 00:45 | 48777.2497 | 1760.004
Devonshire Building | 2016-12-02 01:00 | 48777.6897 | 1760.004
Devonshire Building | 2016-12-02 01:15 | 48778.1297 | 1760.004
Devonshire Building | 2016-12-02 01:30 | 48778.5747 | 1779.984
Devonshire Building | 2016-12-02 01:45 | 48779.0147 | 1760.004
Devonshire Building | 2016-12-02 02:00 | 48779.4547 | 1760.004
Devonshire Building | 2016-12-02 02:15 | 48779.8947 | 1760.004
Devonshire Building | 2016-12-02 02:30 | 48780.3397 | 1779.984
Devonshire Building | 2016-12-02 02:45 | 48780.7797 | 1760.004
Devonshire Building | 2016-12-02 03:00 | 48781.2197 | 1760.004
Devonshire Building | 2016-12-02 03:15 | 48781.6647 | 1779.984
Devonshire Building | 2016-12-02 03:30 | 48782.1047 | 1760.004
Devonshire Building | 2016-12-02 03:45 | 48782.5497 | 1779.984
Devonshire Building | 2016-12-02 04:00 | 48782.9897 | 1760.004
Devonshire Building | 2016-12-02 04:15 | 48783.4297 | 1760.004
Devonshire Building | 2016-12-02 04:30 | 48783.8697 | 1760.004
Devonshire Building | 2016-12-02 04:45 | 48784.3097 | 1760.004
Devonshire Building | 2016-12-02 05:00 | 48784.7497 | 1760.004
Devonshire Building | 2016-12-02 05:15 | 48785.1897 | 1760.004
Devonshire Building | 2016-12-02 05:30 | 48785.6297 | 1760.004
Devonshire Building | 2016-12-02 05:45 | 48786.0697 | 1760.004
Devonshire Building | 2016-12-02 06:00 | 48786.5047 | 1739.988
Devonshire Building | 2016-12-02 06:15 | 48786.9447 | 1760.004
Devonshire Building | 2016-12-02 06:30 | 48787.3797 | 1739.988
Devonshire Building | 2016-12-02 06:45 | 48787.8147 | 1739.988
Devonshire Building | 2016-12-02 07:00 | 48788.2497 | 1739.988
Devonshire Building | 2016-12-02 07:15 | 48788.6797 | 1720.008
Devonshire Building | 2016-12-02 07:30 | 48789.1147 | 1739.988
Devonshire Building | 2016-12-02 07:45 | 48789.5597 | 1779.984
Devonshire Building | 2016-12-02 08:00 | 48790.0047 | 1779.984
Devonshire Building | 2016-12-02 08:15 | 48790.7047 | 2800.008
Devonshire Building | 2016-12-02 08:30 | 48791.1497 | 1779.984
Devonshire Building | 2016-12-02 08:45 | 48791.6097 | 1839.996
Devonshire Building | 2016-12-02 09:00 | 48792.0547 | 1779.984
Devonshire Building | 2016-12-02 09:15 | 48792.4997 | 1779.984
Devonshire Building | 2016-12-02 09:30 | 48792.9497 | 1800
Devonshire Building | 2016-12-02 09:45 | 48793.3997 | 1800
Devonshire Building | 2016-12-02 10:00 | 48793.8447 | 1779.984
Devonshire Building | 2016-12-02 10:15 | 48794.3147 | 1879.992
Devonshire Building | 2016-12-02 10:30 | 48794.8047 | 1959.984
Devonshire Building | 2016-12-02 10:45 | 48795.6647 | 3440.016
Devonshire Building | 2016-12-02 11:00 | 48796.2597 | 2379.996
Devonshire Building | 2016-12-02 11:15 | 48796.7847 | 2099.988
Devonshire Building | 2016-12-02 11:30 | 48797.2847 | 2000.016
Devonshire Building | 2016-12-02 11:45 | 48797.7597 | 1900.008
Devonshire Building | 2016-12-02 12:00 | 48798.2297 | 1879.992
Devonshire Building | 2016-12-02 12:15 | 48798.6997 | 1879.992
Devonshire Building | 2016-12-02 12:30 | 48799.1747 | 1900.008
Devonshire Building | 2016-12-02 12:45 | 48799.6497 | 1900.008
Devonshire Building | 2016-12-02 13:00 | 48800.3847 | 2940.012
Devonshire Building | 2016-12-02 13:15 | 48800.8597 | 1900.008
Devonshire Building | 2016-12-02 13:30 | 48801.3747 | 2059.992
Devonshire Building | 2016-12-02 13:45 | 48801.9197 | 2180.016
Devonshire Building | 2016-12-02 14:00 | 48802.4597 | 2160
Devonshire Building | 2016-12-02 14:15 | 48802.9947 | 2139.984
Devonshire Building | 2016-12-02 14:30 | 48803.5047 | 2040.012
Devonshire Building | 2016-12-02 14:45 | 48804.0197 | 2059.992
Devonshire Building | 2016-12-02 15:00 | 48804.5047 | 1940.004
Devonshire Building | 2016-12-02 15:15 | 48805.2597 | 3020.004
Devonshire Building | 2016-12-02 15:30 | 48805.7147 | 1820.016
Devonshire Building | 2016-12-02 15:45 | 48806.1697 | 1820.016
Devonshire Building | 2016-12-02 16:00 | 48806.6197 | 1800
Devonshire Building | 2016-12-02 16:15 | 48807.0747 | 1820.016
Devonshire Building | 2016-12-02 16:30 | 48807.5347 | 1839.996
Devonshire Building | 2016-12-02 16:45 | 48807.9947 | 1839.996
Devonshire Building | 2016-12-02 17:00 | 48808.4497 | 1820.016
Devonshire Building | 2016-12-02 17:15 | 48808.9097 | 1839.996
Devonshire Building | 2016-12-02 17:30 | 48809.6297 | 2880
Devonshire Building | 2016-12-02 17:45 | 48810.0697 | 1760.004
Devonshire Building | 2016-12-02 18:00 | 48810.5097 | 1760.004
Devonshire Building | 2016-12-02 18:15 | 48810.9497 | 1760.004
Devonshire Building | 2016-12-02 18:30 | 48811.3847 | 1739.988
Devonshire Building | 2016-12-02 18:45 | 48811.8247 | 1760.004
Devonshire Building | 2016-12-02 19:00 | 48812.2647 | 1760.004
Devonshire Building | 2016-12-02 19:15 | 48812.7047 | 1760.004
Devonshire Building | 2016-12-02 19:30 | 48813.1497 | 1779.984
Devonshire Building | 2016-12-02 19:45 | 48813.5847 | 1739.988
Devonshire Building | 2016-12-02 20:00 | 48814.0247 | 1760.004
Devonshire Building | 2016-12-02 20:15 | 48814.4647 | 1760.004
Devonshire Building | 2016-12-02 20:30 | 48814.9047 | 1760.004
Devonshire Building | 2016-12-02 20:45 | 48815.3447 | 1760.004
Devonshire Building | 2016-12-02 21:00 | 48815.7797 | 1739.988
Devonshire Building | 2016-12-02 21:15 | 48816.2197 | 1760.004
Devonshire Building | 2016-12-02 21:30 | 48816.6597 | 1760.004
Devonshire Building | 2016-12-02 21:45 | 48817.0947 | 1739.988
Devonshire Building | 2016-12-02 22:00 | 48817.5397 | 1779.984
Devonshire Building | 2016-12-02 22:15 | 48817.9697 | 1720.008
Devonshire Building | 2016-12-02 22:30 | 48818.4097 | 1760.004
Devonshire Building | 2016-12-02 22:45 | 48818.8447 | 1739.988
Devonshire Building | 2016-12-02 23:00 | 48819.2797 | 1739.988
Devonshire Building | 2016-12-02 23:15 | 48819.7147 | 1739.988
Devonshire Building | 2016-12-02 23:30 | 48820.1497 | 1739.988
Devonshire Building | 2016-12-02 23:45 | 48820.5847 | 1739.988 | 1720.008
Devonshire Building | 2016-12-03 | 48821.0234 | 1760.004
Devonshire Building | 2016-12-03 00:15 | 48821.4584 | 1739.988
Devonshire Building | 2016-12-03 00:30 | 48821.8984 | 1760.004
Devonshire Building | 2016-12-03 00:45 | 48822.3334 | 1739.988
Devonshire Building | 2016-12-03 01:00 | 48822.7734 | 1760.004
Devonshire Building | 2016-12-03 01:15 | 48823.2084 | 1739.988
Devonshire Building | 2016-12-03 01:30 | 48823.6434 | 1739.988
Devonshire Building | 2016-12-03 01:45 | 48824.0834 | 1760.004
Devonshire Building | 2016-12-03 02:00 | 48824.5184 | 1739.988
Devonshire Building | 2016-12-03 02:15 | 48824.9534 | 1739.988
Devonshire Building | 2016-12-03 02:30 | 48825.3934 | 1760.004
Devonshire Building | 2016-12-03 02:45 | 48825.8284 | 1739.988
Devonshire Building | 2016-12-03 03:00 | 48826.2634 | 1739.988
Devonshire Building | 2016-12-03 03:15 | 48826.6984 | 1739.988
Devonshire Building | 2016-12-03 03:30 | 48827.1334 | 1739.988
Devonshire Building | 2016-12-03 03:45 | 48827.5684 | 1739.988
Devonshire Building | 2016-12-03 04:00 | 48828.0034 | 1739.988
Devonshire Building | 2016-12-03 04:15 | 48828.4384 | 1739.988
Devonshire Building | 2016-12-03 04:30 | 48828.8734 | 1739.988
Devonshire Building | 2016-12-03 04:45 | 48829.3034 | 1720.008
Devonshire Building | 2016-12-03 05:00 | 48829.7384 | 1739.988
Devonshire Building | 2016-12-03 05:15 | 48830.1734 | 1739.988
Devonshire Building | 2016-12-03 05:30 | 48830.6084 | 1739.988
Devonshire Building | 2016-12-03 05:45 | 48831.0384 | 1720.008
Devonshire Building | 2016-12-03 06:00 | 48831.4734 | 1739.988
Devonshire Building | 2016-12-03 06:15 | 48831.9034 | 1720.008
Devonshire Building | 2016-12-03 06:30 | 48832.3384 | 1739.988
Devonshire Building | 2016-12-03 06:45 | 48832.7734 | 1739.988
Devonshire Building | 2016-12-03 07:00 | 48833.2034 | 1720.008
Devonshire Building | 2016-12-03 07:15 | 48833.6334 | 1720.008
Devonshire Building | 2016-12-03 07:30 | 48834.0684 | 1739.988
Devonshire Building | 2016-12-03 07:45 | 48834.5084 | 1760.004
Devonshire Building | 2016-12-03 08:00 | 48834.9534 | 1779.984
Devonshire Building | 2016-12-03 08:15 | 48835.3984 | 1779.984
Devonshire Building | 2016-12-03 08:30 | 48835.8434 | 1779.984
Devonshire Building | 2016-12-03 08:45 | 48836.2884 | 1779.984
Devonshire Building | 2016-12-03 09:00 | 48836.7284 | 1760.004
Devonshire Building | 2016-12-03 09:15 | 48837.1684 | 1760.004
Devonshire Building | 2016-12-03 09:30 | 48837.6134 | 1779.984
Devonshire Building | 2016-12-03 09:45 | 48838.0534 | 1760.004
Devonshire Building | 2016-12-03 10:00 | 48838.4884 | 1739.988
Devonshire Building | 2016-12-03 10:15 | 48838.9234 | 1739.988
Devonshire Building | 2016-12-03 10:30 | 48839.3534 | 1720.008
Devonshire Building | 2016-12-03 10:45 | 48839.7834 | 1720.008
Devonshire Building | 2016-12-03 11:00 | 48840.2084 | 1699.992
Devonshire Building | 2016-12-03 11:15 | 48840.6334 | 1699.992
Devonshire Building | 2016-12-03 11:30 | 48841.0634 | 1720.008
Devonshire Building | 2016-12-03 11:45 | 48841.4984 | 1739.988
Devonshire Building | 2016-12-03 12:00 | 48841.9334 | 1739.988
Devonshire Building | 2016-12-03 12:15 | 48842.6434 | 2840.004
Devonshire Building | 2016-12-03 12:30 | 48843.0784 | 1739.988
Devonshire Building | 2016-12-03 12:45 | 48843.5084 | 1720.008
Devonshire Building | 2016-12-03 13:00 | 48843.9484 | 1760.004
Devonshire Building | 2016-12-03 13:15 | 48844.3834 | 1739.988
Devonshire Building | 2016-12-03 13:30 | 48844.8084 | 1699.992
Devonshire Building | 2016-12-03 13:45 | 48845.2334 | 1699.992
Devonshire Building | 2016-12-03 14:00 | 48845.6684 | 1739.988
Devonshire Building | 2016-12-03 14:15 | 48846.0984 | 1720.008
Devonshire Building | 2016-12-03 14:30 | 48846.5384 | 1760.004
Devonshire Building | 2016-12-03 14:45 | 48846.9734 | 1739.988
Devonshire Building | 2016-12-03 15:00 | 48847.4084 | 1739.988
Devonshire Building | 2016-12-03 15:15 | 48847.8384 | 1720.008
Devonshire Building | 2016-12-03 15:30 | 48848.2684 | 1720.008
Devonshire Building | 2016-12-03 15:45 | 48848.8934 | 2499.984
Devonshire Building | 2016-12-03 16:00 | 48849.3934 | 2000.016
Devonshire Building | 2016-12-03 16:15 | 48849.8284 | 1739.988
Devonshire Building | 2016-12-03 16:30 | 48850.2634 | 1739.988
Devonshire Building | 2016-12-03 16:45 | 48850.6983 | 1739.988
Devonshire Building | 2016-12-03 17:00 | 48851.1283 | 1720.008
Devonshire Building | 2016-12-03 17:15 | 48851.5533 | 1699.992
Devonshire Building | 2016-12-03 17:30 | 48851.9783 | 1699.992
Devonshire Building | 2016-12-03 17:45 | 48852.4083 | 1720.008
Devonshire Building | 2016-12-03 18:00 | 48852.8333 | 1699.992
Devonshire Building | 2016-12-03 18:15 | 48853.2583 | 1699.992
Devonshire Building | 2016-12-03 18:30 | 48853.6833 | 1699.992
Devonshire Building | 2016-12-03 18:45 | 48854.1083 | 1699.992
Devonshire Building | 2016-12-03 19:00 | 48854.5383 | 1720.008
Devonshire Building | 2016-12-03 19:15 | 48854.9633 | 1699.992
Devonshire Building | 2016-12-03 19:30 | 48855.3933 | 1720.008
Devonshire Building | 2016-12-03 19:45 | 48855.8183 | 1699.992
Devonshire Building | 2016-12-03 20:00 | 48856.2483 | 1720.008
Devonshire Building | 2016-12-03 20:15 | 48856.6783 | 1720.008
Devonshire Building | 2016-12-03 20:30 | 48857.1033 | 1699.992
Devonshire Building | 2016-12-03 20:45 | 48857.5333 | 1720.008
Devonshire Building | 2016-12-03 21:00 | 48857.9633 | 1720.008
Devonshire Building | 2016-12-03 21:15 | 48858.3933 | 1720.008
Devonshire Building | 2016-12-03 21:30 | 48858.8183 | 1699.992
Devonshire Building | 2016-12-03 21:45 | 48859.2483 | 1720.008
Devonshire Building | 2016-12-03 22:00 | 48859.6983 | 1800
Devonshire Building | 2016-12-03 22:15 | 48860.1283 | 1720.008
Devonshire Building | 2016-12-03 22:30 | 48860.5533 | 1699.992
Devonshire Building | 2016-12-03 22:45 | 48860.9834 | 1720.008
Devonshire Building | 2016-12-03 23:00 | 48861.4134 | 1720.008
Devonshire Building | 2016-12-03 23:15 | 48861.8383 | 1699.992
Devonshire Building | 2016-12-03 23:30 | 48862.2684 | 1720.008
Devonshire Building | 2016-12-03 23:45 | 48862.6984 | 1720.008 | 1699.992
Devonshire Building | 2016-12-04 | 48863.1289 | 1720.008
Devonshire Building | 2016-12-04 00:15 | 48863.5639 | 1739.988
Devonshire Building | 2016-12-04 00:30 | 48863.9939 | 1720.008
Devonshire Building | 2016-12-04 00:45 | 48864.4239 | 1720.008
Devonshire Building | 2016-12-04 01:00 | 48864.8589 | 1739.988
Devonshire Building | 2016-12-04 01:15 | 48865.2889 | 1720.008
Devonshire Building | 2016-12-04 01:30 | 48865.7239 | 1739.988
Devonshire Building | 2016-12-04 01:45 | 48866.1539 | 1720.008
Devonshire Building | 2016-12-04 02:00 | 48866.5889 | 1739.988
Devonshire Building | 2016-12-04 02:15 | 48867.0239 | 1739.988
Devonshire Building | 2016-12-04 02:30 | 48867.4539 | 1720.008
Devonshire Building | 2016-12-04 02:45 | 48867.8889 | 1739.988
Devonshire Building | 2016-12-04 03:00 | 48868.3239 | 1739.988
Devonshire Building | 2016-12-04 03:15 | 48868.7539 | 1720.008
Devonshire Building | 2016-12-04 03:30 | 48869.1889 | 1739.988
Devonshire Building | 2016-12-04 03:45 | 48869.6189 | 1720.008
Devonshire Building | 2016-12-04 04:00 | 48870.0489 | 1720.008
Devonshire Building | 2016-12-04 04:15 | 48870.4839 | 1739.988
Devonshire Building | 2016-12-04 04:30 | 48870.9139 | 1720.008
Devonshire Building | 2016-12-04 04:45 | 48871.3439 | 1720.008
Devonshire Building | 2016-12-04 05:00 | 48871.7789 | 1739.988
Devonshire Building | 2016-12-04 05:15 | 48872.2089 | 1720.008
Devonshire Building | 2016-12-04 05:30 | 48872.8839 | 2700
Devonshire Building | 2016-12-04 05:45 | 48873.3139 | 1720.008
Devonshire Building | 2016-12-04 06:00 | 48873.7489 | 1739.988
Devonshire Building | 2016-12-04 06:15 | 48874.1789 | 1720.008
Devonshire Building | 2016-12-04 06:30 | 48874.6139 | 1739.988
Devonshire Building | 2016-12-04 06:45 | 48875.0439 | 1720.008
Devonshire Building | 2016-12-04 07:00 | 48875.4789 | 1739.988
Devonshire Building | 2016-12-04 07:15 | 48875.9089 | 1720.008
Devonshire Building | 2016-12-04 07:30 | 48876.3389 | 1720.008
Devonshire Building | 2016-12-04 07:45 | 48876.7839 | 1779.984
Devonshire Building | 2016-12-04 08:00 | 48877.2289 | 1779.984
Devonshire Building | 2016-12-04 08:15 | 48877.6739 | 1779.984
Devonshire Building | 2016-12-04 08:30 | 48878.1189 | 1779.984
Devonshire Building | 2016-12-04 08:45 | 48878.5639 | 1779.984
Devonshire Building | 2016-12-04 09:00 | 48879.0039 | 1760.004
Devonshire Building | 2016-12-04 09:15 | 48879.4439 | 1760.004
Devonshire Building | 2016-12-04 09:30 | 48879.8839 | 1760.004
Devonshire Building | 2016-12-04 09:45 | 48880.3239 | 1760.004
Devonshire Building | 2016-12-04 10:00 | 48880.7639 | 1760.004
Devonshire Building | 2016-12-04 10:15 | 48881.2039 | 1760.004
Devonshire Building | 2016-12-04 10:30 | 48881.6289 | 1699.992
Devonshire Building | 2016-12-04 10:45 | 48882.0489 | 1680.012
Devonshire Building | 2016-12-04 11:00 | 48882.4739 | 1699.992
Devonshire Building | 2016-12-04 11:15 | 48882.8939 | 1680.012
Devonshire Building | 2016-12-04 11:30 | 48883.3139 | 1680.012
Devonshire Building | 2016-12-04 11:45 | 48883.7389 | 1699.992
Devonshire Building | 2016-12-04 12:00 | 48884.1639 | 1699.992
Devonshire Building | 2016-12-04 12:15 | 48884.5839 | 1680.012
Devonshire Building | 2016-12-04 12:30 | 48885.0089 | 1699.992
Devonshire Building | 2016-12-04 12:45 | 48885.4339 | 1699.992
Devonshire Building | 2016-12-04 13:00 | 48885.8589 | 1699.992
Devonshire Building | 2016-12-04 13:15 | 48886.2839 | 1699.992
Devonshire Building | 2016-12-04 13:30 | 48886.7039 | 1680.012
Devonshire Building | 2016-12-04 13:45 | 48887.1289 | 1699.992
Devonshire Building | 2016-12-04 14:00 | 48887.5539 | 1699.992
Devonshire Building | 2016-12-04 14:15 | 48887.9789 | 1699.992
Devonshire Building | 2016-12-04 14:30 | 48888.4039 | 1699.992
Devonshire Building | 2016-12-04 14:45 | 48888.8289 | 1699.992
Devonshire Building | 2016-12-04 15:00 | 48889.2589 | 1720.008
Devonshire Building | 2016-12-04 15:15 | 48889.6839 | 1699.992
Devonshire Building | 2016-12-04 15:30 | 48890.1089 | 1699.992
Devonshire Building | 2016-12-04 15:45 | 48890.5339 | 1699.992
Devonshire Building | 2016-12-04 16:00 | 48890.9589 | 1699.992
Devonshire Building | 2016-12-04 16:15 | 48891.3839 | 1699.992
Devonshire Building | 2016-12-04 16:30 | 48891.8089 | 1699.992
Devonshire Building | 2016-12-04 16:45 | 48892.2339 | 1699.992
Devonshire Building | 2016-12-04 17:00 | 48892.6589 | 1699.992
Devonshire Building | 2016-12-04 17:15 | 48893.0789 | 1680.012
Devonshire Building | 2016-12-04 17:30 | 48893.5039 | 1699.992
Devonshire Building | 2016-12-04 17:45 | 48893.9289 | 1699.992
Devonshire Building | 2016-12-04 18:00 | 48894.3539 | 1699.992
Devonshire Building | 2016-12-04 18:15 | 48894.7739 | 1680.012
Devonshire Building | 2016-12-04 18:30 | 48895.1989 | 1699.992
Devonshire Building | 2016-12-04 18:45 | 48895.6239 | 1699.992
Devonshire Building | 2016-12-04 19:00 | 48896.0439 | 1680.012
Devonshire Building | 2016-12-04 19:15 | 48896.4689 | 1699.992
Devonshire Building | 2016-12-04 19:30 | 48896.8889 | 1680.012
Devonshire Building | 2016-12-04 19:45 | 48897.3139 | 1699.992
Devonshire Building | 2016-12-04 20:00 | 48897.7389 | 1699.992
Devonshire Building | 2016-12-04 20:15 | 48898.1639 | 1699.992
Devonshire Building | 2016-12-04 20:30 | 48898.5889 | 1699.992
Devonshire Building | 2016-12-04 20:45 | 48899.0139 | 1699.992
Devonshire Building | 2016-12-04 21:00 | 48899.4389 | 1699.992
Devonshire Building | 2016-12-04 21:15 | 48899.8639 | 1699.992
Devonshire Building | 2016-12-04 21:30 | 48900.2888 | 1699.992
Devonshire Building | 2016-12-04 21:45 | 48900.7188 | 1720.008
Devonshire Building | 2016-12-04 22:00 | 48901.1689 | 1800
Devonshire Building | 2016-12-04 22:15 | 48901.5938 | 1699.992
Devonshire Building | 2016-12-04 22:30 | 48902.0238 | 1720.008
Devonshire Building | 2016-12-04 22:45 | 48902.4488 | 1699.992
Devonshire Building | 2016-12-04 23:00 | 48902.8738 | 1699.992
Devonshire Building | 2016-12-04 23:15 | 48903.3038 | 1720.008
Devonshire Building | 2016-12-04 23:30 | 48903.7338 | 1720.008
Devonshire Building | 2016-12-04 23:45 | 48904.1588 | 1699.992 | 1680.012
Devonshire Building | 2016-12-05 | 48904.5898 | 1720.008
Devonshire Building | 2016-12-05 00:15 | 48905.0198 | 1720.008
Devonshire Building | 2016-12-05 00:30 | 48905.4498 | 1720.008
Devonshire Building | 2016-12-05 00:45 | 48905.8748 | 1699.992
Devonshire Building | 2016-12-05 01:00 | 48906.3048 | 1720.008
Devonshire Building | 2016-12-05 01:15 | 48906.7398 | 1739.988
Devonshire Building | 2016-12-05 01:30 | 48907.1698 | 1720.008
Devonshire Building | 2016-12-05 01:45 | 48907.5998 | 1720.008
Devonshire Building | 2016-12-05 02:00 | 48908.0298 | 1720.008
Devonshire Building | 2016-12-05 02:15 | 48908.4598 | 1720.008
Devonshire Building | 2016-12-05 02:30 | 48908.8948 | 1739.988
Devonshire Building | 2016-12-05 02:45 | 48909.3248 | 1720.008
Devonshire Building | 2016-12-05 03:00 | 48909.7598 | 1739.988
Devonshire Building | 2016-12-05 03:15 | 48910.1898 | 1720.008
Devonshire Building | 2016-12-05 03:30 | 48910.6248 | 1739.988
Devonshire Building | 2016-12-05 03:45 | 48911.0548 | 1720.008
Devonshire Building | 2016-12-05 04:00 | 48911.4898 | 1739.988
Devonshire Building | 2016-12-05 04:15 | 48911.9198 | 1720.008
Devonshire Building | 2016-12-05 04:30 | 48912.3548 | 1739.988
Devonshire Building | 2016-12-05 04:45 | 48912.7848 | 1720.008
Devonshire Building | 2016-12-05 05:00 | 48913.2148 | 1720.008
Devonshire Building | 2016-12-05 05:15 | 48913.6498 | 1739.988
Devonshire Building | 2016-12-05 05:30 | 48914.0798 | 1720.008
Devonshire Building | 2016-12-05 05:45 | 48914.5098 | 1720.008
Devonshire Building | 2016-12-05 06:00 | 48914.9348 | 1699.992
Devonshire Building | 2016-12-05 06:15 | 48915.3648 | 1720.008
Devonshire Building | 2016-12-05 06:30 | 48915.7948 | 1720.008
Devonshire Building | 2016-12-05 06:45 | 48916.2249 | 1720.008
Devonshire Building | 2016-12-05 07:00 | 48916.6498 | 1699.992
Devonshire Building | 2016-12-05 07:15 | 48917.0748 | 1699.992
Devonshire Building | 2016-12-05 07:30 | 48917.7748 | 2800.008
Devonshire Building | 2016-12-05 07:45 | 48918.2148 | 1760.004
Devonshire Building | 2016-12-05 08:00 | 48918.6549 | 1760.004
Devonshire Building | 2016-12-05 08:15 | 48919.0949 | 1760.004
Devonshire Building | 2016-12-05 08:30 | 48919.5449 | 1800
Devonshire Building | 2016-12-05 08:45 | 48919.9798 | 1739.988
Devonshire Building | 2016-12-05 09:00 | 48920.4248 | 1779.984
Devonshire Building | 2016-12-05 09:15 | 48920.8698 | 1779.984
Devonshire Building | 2016-12-05 09:30 | 48921.3248 | 1820.016
Devonshire Building | 2016-12-05 09:45 | 48921.7898 | 1860.012
Devonshire Building | 2016-12-05 10:00 | 48922.5699 | 3120.012
Devonshire Building | 2016-12-05 10:15 | 48923.0948 | 2099.988
Devonshire Building | 2016-12-05 10:30 | 48923.6198 | 2099.988
Devonshire Building | 2016-12-05 10:45 | 48924.1498 | 2120.004
Devonshire Building | 2016-12-05 11:00 | 48924.6748 | 2099.988
Devonshire Building | 2016-12-05 11:15 | 48925.4798 | 3219.984
Devonshire Building | 2016-12-05 11:30 | 48925.9948 | 2059.992
Devonshire Building | 2016-12-05 11:45 | 48926.5248 | 2120.004
Devonshire Building | 2016-12-05 12:00 | 48927.0598 | 2139.984
Devonshire Building | 2016-12-05 12:15 | 48927.7498 | 2760.012
Devonshire Building | 2016-12-05 12:30 | 48928.3948 | 2580.012
Devonshire Building | 2016-12-05 12:45 | 48929.2148 | 3279.996
Devonshire Building | 2016-12-05 13:00 | 48929.6998 | 1940.004
Devonshire Building | 2016-12-05 13:15 | 48930.1898 | 1959.984
Devonshire Building | 2016-12-05 13:30 | 48930.6748 | 1940.004
Devonshire Building | 2016-12-05 13:45 | 48931.1598 | 1940.004
Devonshire Building | 2016-12-05 14:00 | 48931.9098 | 2999.988
Devonshire Building | 2016-12-05 14:15 | 48932.3898 | 1919.988
Devonshire Building | 2016-12-05 14:30 | 48932.8698 | 1919.988
Devonshire Building | 2016-12-05 14:45 | 48933.3548 | 1940.004
Devonshire Building | 2016-12-05 15:00 | 48933.8298 | 1900.008
Devonshire Building | 2016-12-05 15:15 | 48934.3048 | 1900.008
Devonshire Building | 2016-12-05 15:30 | 48934.7848 | 1919.988
Devonshire Building | 2016-12-05 15:45 | 48935.2548 | 1879.992
Devonshire Building | 2016-12-05 16:00 | 48936.0248 | 3080.016
Devonshire Building | 2016-12-05 16:15 | 48936.4798 | 1820.016
Devonshire Building | 2016-12-05 16:30 | 48936.9348 | 1820.016
Devonshire Building | 2016-12-05 16:45 | 48937.3848 | 1800
Devonshire Building | 2016-12-05 17:00 | 48937.8398 | 1820.016
Devonshire Building | 2016-12-05 17:15 | 48938.2898 | 1800
Devonshire Building | 2016-12-05 17:30 | 48938.7398 | 1800
Devonshire Building | 2016-12-05 17:45 | 48939.1948 | 1820.016
Devonshire Building | 2016-12-05 18:00 | 48939.6398 | 1779.984
Devonshire Building | 2016-12-05 18:15 | 48940.3698 | 2919.996
Devonshire Building | 2016-12-05 18:30 | 48940.8148 | 1779.984
Devonshire Building | 2016-12-05 18:45 | 48941.2548 | 1760.004
Devonshire Building | 2016-12-05 19:00 | 48941.6948 | 1760.004
Devonshire Building | 2016-12-05 19:15 | 48942.1398 | 1779.984
Devonshire Building | 2016-12-05 19:30 | 48942.5848 | 1779.984
Devonshire Building | 2016-12-05 19:45 | 48943.0248 | 1760.004
Devonshire Building | 2016-12-05 20:00 | 48943.4648 | 1760.004
Devonshire Building | 2016-12-05 20:15 | 48943.8998 | 1739.988
Devonshire Building | 2016-12-05 20:30 | 48944.3348 | 1739.988
Devonshire Building | 2016-12-05 20:45 | 48944.7698 | 1739.988
Devonshire Building | 2016-12-05 21:00 | 48945.2098 | 1760.004
Devonshire Building | 2016-12-05 21:15 | 48945.6398 | 1720.008
Devonshire Building | 2016-12-05 21:30 | 48946.0748 | 1739.988
Devonshire Building | 2016-12-05 21:45 | 48946.5048 | 1720.008
Devonshire Building | 2016-12-05 22:00 | 48946.9398 | 1739.988
Devonshire Building | 2016-12-05 22:15 | 48947.3698 | 1720.008
Devonshire Building | 2016-12-05 22:30 | 48947.7948 | 1699.992
Devonshire Building | 2016-12-05 22:45 | 48948.2248 | 1720.008
Devonshire Building | 2016-12-05 23:00 | 48948.6598 | 1739.988
Devonshire Building | 2016-12-05 23:15 | 48949.0848 | 1699.992
Devonshire Building | 2016-12-05 23:30 | 48949.5198 | 1739.988
Devonshire Building | 2016-12-05 23:45 | 48949.9498 | 1720.008 | 1699.992
Devonshire Building | 2016-12-06 | 48950.3789 | 1720.008
Devonshire Building | 2016-12-06 00:15 | 48950.8139 | 1739.988
Devonshire Building | 2016-12-06 00:30 | 48951.2489 | 1739.988
Devonshire Building | 2016-12-06 00:45 | 48951.6789 | 1720.008
Devonshire Building | 2016-12-06 01:00 | 48952.1139 | 1739.988
Devonshire Building | 2016-12-06 01:15 | 48952.5489 | 1739.988
Devonshire Building | 2016-12-06 01:30 | 48952.9839 | 1739.988
Devonshire Building | 2016-12-06 01:45 | 48953.4189 | 1739.988
Devonshire Building | 2016-12-06 02:00 | 48953.8539 | 1739.988
Devonshire Building | 2016-12-06 02:15 | 48954.2889 | 1739.988
Devonshire Building | 2016-12-06 02:30 | 48954.7239 | 1739.988
Devonshire Building | 2016-12-06 02:45 | 48955.1589 | 1739.988
Devonshire Building | 2016-12-06 03:00 | 48955.5939 | 1739.988
Devonshire Building | 2016-12-06 03:15 | 48956.0289 | 1739.988
Devonshire Building | 2016-12-06 03:30 | 48956.4639 | 1739.988
Devonshire Building | 2016-12-06 03:45 | 48956.8989 | 1739.988
Devonshire Building | 2016-12-06 04:00 | 48957.3339 | 1739.988
Devonshire Building | 2016-12-06 04:15 | 48957.7689 | 1739.988
Devonshire Building | 2016-12-06 04:30 | 48958.1989 | 1720.008
Devonshire Building | 2016-12-06 04:45 | 48958.6339 | 1739.988
Devonshire Building | 2016-12-06 05:00 | 48959.0689 | 1739.988
Devonshire Building | 2016-12-06 05:15 | 48959.5039 | 1739.988
Devonshire Building | 2016-12-06 05:30 | 48959.9339 | 1720.008
Devonshire Building | 2016-12-06 05:45 | 48960.3689 | 1739.988
Devonshire Building | 2016-12-06 06:00 | 48960.7989 | 1720.008
Devonshire Building | 2016-12-06 06:15 | 48961.2339 | 1739.988
Devonshire Building | 2016-12-06 06:30 | 48961.6639 | 1720.008
Devonshire Building | 2016-12-06 06:45 | 48962.0939 | 1720.008
Devonshire Building | 2016-12-06 07:00 | 48962.5239 | 1720.008
Devonshire Building | 2016-12-06 07:15 | 48962.9489 | 1699.992
Devonshire Building | 2016-12-06 07:30 | 48963.3889 | 1760.004
Devonshire Building | 2016-12-06 07:45 | 48963.8289 | 1760.004
Devonshire Building | 2016-12-06 08:00 | 48964.2689 | 1760.004
Devonshire Building | 2016-12-06 08:15 | 48964.7089 | 1760.004
Devonshire Building | 2016-12-06 08:30 | 48965.1489 | 1760.004
Devonshire Building | 2016-12-06 08:45 | 48965.5939 | 1779.984
Devonshire Building | 2016-12-06 09:00 | 48966.2939 | 2800.008
Devonshire Building | 2016-12-06 09:15 | 48966.7339 | 1760.004
Devonshire Building | 2016-12-06 09:30 | 48967.1739 | 1760.004
Devonshire Building | 2016-12-06 09:45 | 48967.6239 | 1800
Devonshire Building | 2016-12-06 10:00 | 48968.0839 | 1839.996
Devonshire Building | 2016-12-06 10:15 | 48968.5889 | 2019.996
Devonshire Building | 2016-12-06 10:30 | 48969.4089 | 3279.996
Devonshire Building | 2016-12-06 10:45 | 48969.9389 | 2120.004
Devonshire Building | 2016-12-06 11:00 | 48970.4589 | 2080.008
Devonshire Building | 2016-12-06 11:15 | 48970.9739 | 2059.992
Devonshire Building | 2016-12-06 11:30 | 48971.4939 | 2080.008
Devonshire Building | 2016-12-06 11:45 | 48972.0039 | 2040.012
Devonshire Building | 2016-12-06 12:00 | 48972.5389 | 2139.984
Devonshire Building | 2016-12-06 12:15 | 48973.2939 | 3020.004
Devonshire Building | 2016-12-06 12:30 | 48973.7889 | 1980
Devonshire Building | 2016-12-06 12:45 | 48974.2789 | 1959.984
Devonshire Building | 2016-12-06 13:00 | 48974.7639 | 1940.004
Devonshire Building | 2016-12-06 13:15 | 48975.2489 | 1940.004
Devonshire Building | 2016-12-06 13:30 | 48975.7239 | 1900.008
Devonshire Building | 2016-12-06 13:45 | 48976.4989 | 3099.996
Devonshire Building | 2016-12-06 14:00 | 48976.9689 | 1879.992
Devonshire Building | 2016-12-06 14:15 | 48977.4439 | 1900.008
Devonshire Building | 2016-12-06 14:30 | 48977.9189 | 1900.008
Devonshire Building | 2016-12-06 14:45 | 48978.4039 | 1940.004
Devonshire Building | 2016-12-06 15:00 | 48978.9139 | 2040.012
Devonshire Building | 2016-12-06 15:15 | 48979.6189 | 2819.988
Devonshire Building | 2016-12-06 15:30 | 48980.4289 | 3240
Devonshire Building | 2016-12-06 15:45 | 48980.9689 | 2160
Devonshire Building | 2016-12-06 16:00 | 48981.4839 | 2059.992
Devonshire Building | 2016-12-06 16:15 | 48981.9989 | 2059.992
Devonshire Building | 2016-12-06 16:30 | 48982.5139 | 2059.992
Devonshire Building | 2016-12-06 16:45 | 48983.0289 | 2059.992
Devonshire Building | 2016-12-06 17:00 | 48983.7289 | 2800.008
Devonshire Building | 2016-12-06 17:15 | 48984.3589 | 2520
Devonshire Building | 2016-12-06 17:30 | 48984.8839 | 2099.988
Devonshire Building | 2016-12-06 17:45 | 48985.3939 | 2040.012
Devonshire Building | 2016-12-06 18:00 | 48985.8789 | 1940.004
Devonshire Building | 2016-12-06 18:15 | 48986.3439 | 1860.012
Devonshire Building | 2016-12-06 18:30 | 48986.7989 | 1820.016
Devonshire Building | 2016-12-06 18:45 | 48987.2439 | 1779.984
Devonshire Building | 2016-12-06 19:00 | 48987.6889 | 1779.984
Devonshire Building | 2016-12-06 19:15 | 48988.1289 | 1760.004
Devonshire Building | 2016-12-06 19:30 | 48988.5689 | 1760.004
Devonshire Building | 2016-12-06 19:45 | 48989.0039 | 1739.988
Devonshire Building | 2016-12-06 20:00 | 48989.4439 | 1760.004
Devonshire Building | 2016-12-06 20:15 | 48989.8739 | 1720.008
Devonshire Building | 2016-12-06 20:30 | 48990.3089 | 1739.988
Devonshire Building | 2016-12-06 20:45 | 48990.7389 | 1720.008
Devonshire Building | 2016-12-06 21:00 | 48991.1739 | 1739.988
Devonshire Building | 2016-12-06 21:15 | 48991.6039 | 1720.008
Devonshire Building | 2016-12-06 21:30 | 48992.0389 | 1739.988
Devonshire Building | 2016-12-06 21:45 | 48992.4739 | 1739.988
Devonshire Building | 2016-12-06 22:00 | 48992.9289 | 1820.016
Devonshire Building | 2016-12-06 22:15 | 48993.3589 | 1720.008
Devonshire Building | 2016-12-06 22:30 | 48993.7889 | 1720.008
Devonshire Building | 2016-12-06 22:45 | 48994.2239 | 1739.988
Devonshire Building | 2016-12-06 23:00 | 48994.6539 | 1720.008
Devonshire Building | 2016-12-06 23:15 | 48995.0889 | 1739.988
Devonshire Building | 2016-12-06 23:30 | 48995.5239 | 1739.988
Devonshire Building | 2016-12-06 23:45 | 48995.9589 | 1739.988 | 1699.992
Devonshire Building | 2016-12-07 | 48996.3945 | 1739.988
Devonshire Building | 2016-12-07 00:15 | 48996.8295 | 1739.988
Devonshire Building | 2016-12-07 00:30 | 48997.2695 | 1760.004
Devonshire Building | 2016-12-07 00:45 | 48997.7045 | 1739.988
Devonshire Building | 2016-12-07 01:00 | 48998.1445 | 1760.004
Devonshire Building | 2016-12-07 01:15 | 48998.5795 | 1739.988
Devonshire Building | 2016-12-07 01:30 | 48999.0195 | 1760.004
Devonshire Building | 2016-12-07 01:45 | 48999.4695 | 1800
Devonshire Building | 2016-12-07 02:00 | 48999.9245 | 1820.016
Devonshire Building | 2016-12-07 02:15 | 49000.3795 | 1820.016
Devonshire Building | 2016-12-07 02:30 | 49000.8395 | 1839.996
Devonshire Building | 2016-12-07 02:45 | 49001.2945 | 1820.016
Devonshire Building | 2016-12-07 03:00 | 49001.7495 | 1820.016
Devonshire Building | 2016-12-07 03:15 | 49002.2045 | 1820.016
Devonshire Building | 2016-12-07 03:30 | 49002.6595 | 1820.016
Devonshire Building | 2016-12-07 03:45 | 49003.1146 | 1820.016
Devonshire Building | 2016-12-07 04:00 | 49003.5546 | 1760.004
Devonshire Building | 2016-12-07 04:15 | 49003.9946 | 1760.004
Devonshire Building | 2016-12-07 04:30 | 49004.4346 | 1760.004
Devonshire Building | 2016-12-07 04:45 | 49004.8696 | 1739.988
Devonshire Building | 2016-12-07 05:00 | 49005.3096 | 1760.004
Devonshire Building | 2016-12-07 05:15 | 49005.7496 | 1760.004
Devonshire Building | 2016-12-07 05:30 | 49006.1896 | 1760.004
Devonshire Building | 2016-12-07 05:45 | 49006.6296 | 1760.004
Devonshire Building | 2016-12-07 06:00 | 49007.0696 | 1760.004
Devonshire Building | 2016-12-07 06:15 | 49007.5046 | 1739.988
Devonshire Building | 2016-12-07 06:30 | 49007.9446 | 1760.004
Devonshire Building | 2016-12-07 06:45 | 49008.3796 | 1739.988
Devonshire Building | 2016-12-07 07:00 | 49008.8145 | 1739.988
Devonshire Building | 2016-12-07 07:15 | 49009.2446 | 1720.008
Devonshire Building | 2016-12-07 07:30 | 49009.6795 | 1739.988
Devonshire Building | 2016-12-07 07:45 | 49010.3745 | 2779.992
Devonshire Building | 2016-12-07 08:00 | 49010.8145 | 1760.004
Devonshire Building | 2016-12-07 08:15 | 49011.2595 | 1779.984
Devonshire Building | 2016-12-07 08:30 | 49011.6945 | 1739.988
Devonshire Building | 2016-12-07 08:45 | 49012.1195 | 1699.992
Devonshire Building | 2016-12-07 09:00 | 49012.5545 | 1739.988
Devonshire Building | 2016-12-07 09:15 | 49012.9995 | 1779.984
Devonshire Building | 2016-12-07 09:30 | 49013.4545 | 1820.016
Devonshire Building | 2016-12-07 09:45 | 49013.9345 | 1919.988
Devonshire Building | 2016-12-07 10:00 | 49014.4395 | 2019.996
Devonshire Building | 2016-12-07 10:15 | 49015.2545 | 3260.016
Devonshire Building | 2016-12-07 10:30 | 49015.7645 | 2040.012
Devonshire Building | 2016-12-07 10:45 | 49016.2945 | 2120.004
Devonshire Building | 2016-12-07 11:00 | 49016.8395 | 2180.016
Devonshire Building | 2016-12-07 11:15 | 49017.3695 | 2120.004
Devonshire Building | 2016-12-07 11:30 | 49017.8795 | 2040.012
Devonshire Building | 2016-12-07 11:45 | 49018.3695 | 1959.984
Devonshire Building | 2016-12-07 12:00 | 49018.8495 | 1919.988
Devonshire Building | 2016-12-07 12:15 | 49019.6245 | 3099.996
Devonshire Building | 2016-12-07 12:30 | 49020.0845 | 1839.996
Devonshire Building | 2016-12-07 12:45 | 49020.5545 | 1879.992
Devonshire Building | 2016-12-07 13:00 | 49021.0245 | 1879.992
Devonshire Building | 2016-12-07 13:15 | 49021.4895 | 1860.012
Devonshire Building | 2016-12-07 13:30 | 49022.2295 | 2959.992
Devonshire Building | 2016-12-07 13:45 | 49022.7045 | 1900.008
Devonshire Building | 2016-12-07 14:00 | 49023.1795 | 1900.008
Devonshire Building | 2016-12-07 14:15 | 49023.6695 | 1959.984
Devonshire Building | 2016-12-07 14:30 | 49024.1645 | 1980
Devonshire Building | 2016-12-07 14:45 | 49024.6595 | 1980
Devonshire Building | 2016-12-07 15:00 | 49025.4395 | 3120.012
Devonshire Building | 2016-12-07 15:15 | 49025.9445 | 2019.996
Devonshire Building | 2016-12-07 15:30 | 49026.4645 | 2080.008
Devonshire Building | 2016-12-07 15:45 | 49026.9695 | 2019.996
Devonshire Building | 2016-12-07 16:00 | 49027.4645 | 1980
Devonshire Building | 2016-12-07 16:15 | 49027.9495 | 1940.004
Devonshire Building | 2016-12-07 16:30 | 49028.4395 | 1959.984
Devonshire Building | 2016-12-07 16:45 | 49028.9295 | 1959.984
Devonshire Building | 2016-12-07 17:00 | 49029.4195 | 1959.984
Devonshire Building | 2016-12-07 17:15 | 49030.2345 | 3260.016
Devonshire Building | 2016-12-07 17:30 | 49030.8995 | 2660.004
Devonshire Building | 2016-12-07 17:45 | 49031.5545 | 2620.008
Devonshire Building | 2016-12-07 18:00 | 49032.1495 | 2379.996
Devonshire Building | 2016-12-07 18:15 | 49032.6745 | 2099.988
Devonshire Building | 2016-12-07 18:30 | 49033.1595 | 1940.004
Devonshire Building | 2016-12-07 18:45 | 49033.6295 | 1879.992
Devonshire Building | 2016-12-07 19:00 | 49034.0845 | 1820.016
Devonshire Building | 2016-12-07 19:15 | 49034.5395 | 1820.016
Devonshire Building | 2016-12-07 19:30 | 49034.9845 | 1779.984
Devonshire Building | 2016-12-07 19:45 | 49035.4445 | 1839.996
Devonshire Building | 2016-12-07 20:00 | 49035.9045 | 1839.996
Devonshire Building | 2016-12-07 20:15 | 49036.3645 | 1839.996
Devonshire Building | 2016-12-07 20:30 | 49036.8245 | 1839.996
Devonshire Building | 2016-12-07 20:45 | 49037.2795 | 1820.016
Devonshire Building | 2016-12-07 21:00 | 49037.7395 | 1839.996
Devonshire Building | 2016-12-07 21:15 | 49038.1945 | 1820.016
Devonshire Building | 2016-12-07 21:30 | 49038.6545 | 1839.996
Devonshire Building | 2016-12-07 21:45 | 49039.1095 | 1820.016
Devonshire Building | 2016-12-07 22:00 | 49039.5845 | 1900.008
Devonshire Building | 2016-12-07 22:15 | 49040.0245 | 1760.004
Devonshire Building | 2016-12-07 22:30 | 49040.4595 | 1739.988
Devonshire Building | 2016-12-07 22:45 | 49040.8945 | 1739.988
Devonshire Building | 2016-12-07 23:00 | 49041.3345 | 1760.004
Devonshire Building | 2016-12-07 23:15 | 49041.7745 | 1760.004
Devonshire Building | 2016-12-07 23:30 | 49042.2095 | 1739.988
Devonshire Building | 2016-12-07 23:45 | 49042.6495 | 1760.004 | 1699.992
Devonshire Building | 2016-12-08 | 49043.0898 | 1760.004
Devonshire Building | 2016-12-08 00:15 | 49043.5298 | 1760.004
Devonshire Building | 2016-12-08 00:30 | 49043.9748 | 1779.984
Devonshire Building | 2016-12-08 00:45 | 49044.4148 | 1760.004
Devonshire Building | 2016-12-08 01:00 | 49044.8548 | 1760.004
Devonshire Building | 2016-12-08 01:15 | 49045.2998 | 1779.984
Devonshire Building | 2016-12-08 01:30 | 49045.7398 | 1760.004
Devonshire Building | 2016-12-08 01:45 | 49046.1848 | 1779.984
Devonshire Building | 2016-12-08 02:00 | 49046.6248 | 1760.004
Devonshire Building | 2016-12-08 02:15 | 49047.0698 | 1779.984
Devonshire Building | 2016-12-08 02:30 | 49047.5148 | 1779.984
Devonshire Building | 2016-12-08 02:45 | 49047.9548 | 1760.004
Devonshire Building | 2016-12-08 03:00 | 49048.3998 | 1779.984
Devonshire Building | 2016-12-08 03:15 | 49048.8398 | 1760.004
Devonshire Building | 2016-12-08 03:30 | 49049.2798 | 1760.004
Devonshire Building | 2016-12-08 03:45 | 49049.7198 | 1760.004
Devonshire Building | 2016-12-08 04:00 | 49050.1598 | 1760.004
Devonshire Building | 2016-12-08 04:15 | 49050.6048 | 1779.984
Devonshire Building | 2016-12-08 04:30 | 49051.0448 | 1760.004
Devonshire Building | 2016-12-08 04:45 | 49051.4798 | 1739.988
Devonshire Building | 2016-12-08 05:00 | 49051.9198 | 1760.004
Devonshire Building | 2016-12-08 05:15 | 49052.3598 | 1760.004
Devonshire Building | 2016-12-08 05:30 | 49052.8048 | 1779.984
Devonshire Building | 2016-12-08 05:45 | 49053.2448 | 1760.004
Devonshire Building | 2016-12-08 06:00 | 49053.6848 | 1760.004
Devonshire Building | 2016-12-08 06:15 | 49054.1198 | 1739.988
Devonshire Building | 2016-12-08 06:30 | 49054.5598 | 1760.004
Devonshire Building | 2016-12-08 06:45 | 49054.9948 | 1739.988
Devonshire Building | 2016-12-08 07:00 | 49055.4348 | 1760.004
Devonshire Building | 2016-12-08 07:15 | 49055.8698 | 1739.988
Devonshire Building | 2016-12-08 07:30 | 49056.2998 | 1720.008
Devonshire Building | 2016-12-08 07:45 | 49057.0198 | 2880
Devonshire Building | 2016-12-08 08:00 | 49057.4498 | 1720.008
Devonshire Building | 2016-12-08 08:15 | 49057.8848 | 1739.988
Devonshire Building | 2016-12-08 08:30 | 49058.3248 | 1760.004
Devonshire Building | 2016-12-08 08:45 | 49058.7598 | 1739.988
Devonshire Building | 2016-12-08 09:00 | 49059.1948 | 1739.988
Devonshire Building | 2016-12-08 09:15 | 49059.6348 | 1760.004
Devonshire Building | 2016-12-08 09:30 | 49060.0748 | 1760.004
Devonshire Building | 2016-12-08 09:45 | 49060.5198 | 1779.984
Devonshire Building | 2016-12-08 10:00 | 49060.9698 | 1800
Devonshire Building | 2016-12-08 10:15 | 49061.7298 | 3039.984
Devonshire Building | 2016-12-08 10:30 | 49062.3198 | 2360.016
Devonshire Building | 2016-12-08 10:45 | 49062.9648 | 2580.012
Devonshire Building | 2016-12-08 11:00 | 49063.5348 | 2279.988
Devonshire Building | 2016-12-08 11:15 | 49064.0598 | 2099.988
Devonshire Building | 2016-12-08 11:30 | 49064.5598 | 2000.016
Devonshire Building | 2016-12-08 11:45 | 49065.2998 | 2959.992
Devonshire Building | 2016-12-08 12:00 | 49065.7498 | 1800
Devonshire Building | 2016-12-08 12:15 | 49066.2048 | 1820.016
Devonshire Building | 2016-12-08 12:30 | 49066.6598 | 1820.016
Devonshire Building | 2016-12-08 12:45 | 49067.1148 | 1820.016
Devonshire Building | 2016-12-08 13:00 | 49067.5948 | 1919.988
Devonshire Building | 2016-12-08 13:15 | 49068.0898 | 1980
Devonshire Building | 2016-12-08 13:30 | 49069.0098 | 3679.992
Devonshire Building | 2016-12-08 13:45 | 49069.6648 | 2620.008
Devonshire Building | 2016-12-08 14:00 | 49070.2348 | 2279.988
Devonshire Building | 2016-12-08 14:15 | 49070.7698 | 2139.984
Devonshire Building | 2016-12-08 14:30 | 49071.2948 | 2099.988
Devonshire Building | 2016-12-08 14:45 | 49071.8048 | 2040.012
Devonshire Building | 2016-12-08 15:00 | 49072.6148 | 3240
Devonshire Building | 2016-12-08 15:15 | 49073.1098 | 1980
Devonshire Building | 2016-12-08 15:30 | 49073.6148 | 2019.996
Devonshire Building | 2016-12-08 15:45 | 49074.1098 | 1980
Devonshire Building | 2016-12-08 16:00 | 49074.6048 | 1980
Devonshire Building | 2016-12-08 16:15 | 49075.0998 | 1980
Devonshire Building | 2016-12-08 16:30 | 49075.5898 | 1959.984
Devonshire Building | 2016-12-08 16:45 | 49076.3698 | 3120.012
Devonshire Building | 2016-12-08 17:00 | 49076.8698 | 2000.016
Devonshire Building | 2016-12-08 17:15 | 49077.3698 | 2000.016
Devonshire Building | 2016-12-08 17:30 | 49077.8698 | 2000.016
Devonshire Building | 2016-12-08 17:45 | 49078.3598 | 1959.984
Devonshire Building | 2016-12-08 18:00 | 49078.8348 | 1900.008
Devonshire Building | 2016-12-08 18:15 | 49079.3048 | 1879.992
Devonshire Building | 2016-12-08 18:30 | 49079.7698 | 1860.012
Devonshire Building | 2016-12-08 18:45 | 49080.2298 | 1839.996
Devonshire Building | 2016-12-08 19:00 | 49080.6898 | 1839.996
Devonshire Building | 2016-12-08 19:15 | 49081.1398 | 1800
Devonshire Building | 2016-12-08 19:30 | 49081.5798 | 1760.004
Devonshire Building | 2016-12-08 19:45 | 49082.0248 | 1779.984
Devonshire Building | 2016-12-08 20:00 | 49082.4498 | 1699.992
Devonshire Building | 2016-12-08 20:15 | 49082.8748 | 1699.992
Devonshire Building | 2016-12-08 20:30 | 49083.3098 | 1739.988
Devonshire Building | 2016-12-08 20:45 | 49083.7448 | 1739.988
Devonshire Building | 2016-12-08 21:00 | 49084.1798 | 1739.988
Devonshire Building | 2016-12-08 21:15 | 49084.6098 | 1720.008
Devonshire Building | 2016-12-08 21:30 | 49085.0348 | 1699.992
Devonshire Building | 2016-12-08 21:45 | 49085.4598 | 1699.992
Devonshire Building | 2016-12-08 22:00 | 49085.9048 | 1779.984
Devonshire Building | 2016-12-08 22:15 | 49086.3248 | 1680.012
Devonshire Building | 2016-12-08 22:30 | 49086.7498 | 1699.992
Devonshire Building | 2016-12-08 22:45 | 49087.1698 | 1680.012
Devonshire Building | 2016-12-08 23:00 | 49087.5898 | 1680.012
Devonshire Building | 2016-12-08 23:15 | 49088.0148 | 1699.992
Devonshire Building | 2016-12-08 23:30 | 49088.4348 | 1680.012
Devonshire Building | 2016-12-08 23:45 | 49088.8598 | 1699.992 | 1680.012
Devonshire Building | 2016-12-09 | 49089.2852 | 1699.992
Devonshire Building | 2016-12-09 00:15 | 49089.7102 | 1699.992
Devonshire Building | 2016-12-09 00:30 | 49090.1352 | 1699.992
Devonshire Building | 2016-12-09 00:45 | 49090.5602 | 1699.992
Devonshire Building | 2016-12-09 01:00 | 49090.9902 | 1720.008
Devonshire Building | 2016-12-09 01:15 | 49091.4152 | 1699.992
Devonshire Building | 2016-12-09 01:30 | 49091.8452 | 1720.008
Devonshire Building | 2016-12-09 01:45 | 49092.2702 | 1699.992
Devonshire Building | 2016-12-09 02:00 | 49092.7002 | 1720.008
Devonshire Building | 2016-12-09 02:15 | 49093.1302 | 1720.008
Devonshire Building | 2016-12-09 02:30 | 49093.5552 | 1699.992
Devonshire Building | 2016-12-09 02:45 | 49093.9802 | 1699.992
Devonshire Building | 2016-12-09 03:00 | 49094.4102 | 1720.008
Devonshire Building | 2016-12-09 03:15 | 49094.8402 | 1720.008
Devonshire Building | 2016-12-09 03:30 | 49095.2652 | 1699.992
Devonshire Building | 2016-12-09 03:45 | 49095.6902 | 1699.992
Devonshire Building | 2016-12-09 04:00 | 49096.1202 | 1720.008
Devonshire Building | 2016-12-09 04:15 | 49096.5452 | 1699.992
Devonshire Building | 2016-12-09 04:30 | 49096.9702 | 1699.992
Devonshire Building | 2016-12-09 04:45 | 49097.4002 | 1720.008
Devonshire Building | 2016-12-09 05:00 | 49097.8252 | 1699.992
Devonshire Building | 2016-12-09 05:15 | 49098.5052 | 2720.016
Devonshire Building | 2016-12-09 05:30 | 49098.9302 | 1699.992
Devonshire Building | 2016-12-09 05:45 | 49099.3502 | 1680.012
Devonshire Building | 2016-12-09 06:00 | 49099.7752 | 1699.992
Devonshire Building | 2016-12-09 06:15 | 49100.1952 | 1680.012
Devonshire Building | 2016-12-09 06:30 | 49100.6102 | 1659.996
Devonshire Building | 2016-12-09 06:45 | 49101.0302 | 1680.012
Devonshire Building | 2016-12-09 07:00 | 49101.4402 | 1640.016
Devonshire Building | 2016-12-09 07:15 | 49101.8502 | 1640.016
Devonshire Building | 2016-12-09 07:30 | 49102.2602 | 1640.016
Devonshire Building | 2016-12-09 07:45 | 49102.6702 | 1640.016
Devonshire Building | 2016-12-09 08:00 | 49103.0902 | 1680.012
Devonshire Building | 2016-12-09 08:15 | 49103.5252 | 1739.988
Devonshire Building | 2016-12-09 08:30 | 49103.9552 | 1720.008
Devonshire Building | 2016-12-09 08:45 | 49104.3802 | 1699.992
Devonshire Building | 2016-12-09 09:00 | 49104.8152 | 1739.988
Devonshire Building | 2016-12-09 09:15 | 49105.2452 | 1720.008
Devonshire Building | 2016-12-09 09:30 | 49105.6802 | 1739.988
Devonshire Building | 2016-12-09 09:45 | 49106.3752 | 2779.992
Devonshire Building | 2016-12-09 10:00 | 49106.8202 | 1779.984
Devonshire Building | 2016-12-09 10:15 | 49107.4502 | 2520
Devonshire Building | 2016-12-09 10:30 | 49108.0252 | 2300.004
Devonshire Building | 2016-12-09 10:45 | 49108.5852 | 2239.992
Devonshire Building | 2016-12-09 11:00 | 49109.3752 | 3160.008
Devonshire Building | 2016-12-09 11:15 | 49109.8352 | 1839.996
Devonshire Building | 2016-12-09 11:30 | 49110.3002 | 1860.012
Devonshire Building | 2016-12-09 11:45 | 49110.7702 | 1879.992
Devonshire Building | 2016-12-09 12:00 | 49111.2352 | 1860.012
Devonshire Building | 2016-12-09 12:15 | 49111.6902 | 1820.016
Devonshire Building | 2016-12-09 12:30 | 49112.1402 | 1800
Devonshire Building | 2016-12-09 12:45 | 49112.5852 | 1779.984
Devonshire Building | 2016-12-09 13:00 | 49113.3202 | 2940.012
Devonshire Building | 2016-12-09 13:15 | 49113.7502 | 1720.008
Devonshire Building | 2016-12-09 13:30 | 49114.1752 | 1699.992
Devonshire Building | 2016-12-09 13:45 | 49114.6052 | 1720.008
Devonshire Building | 2016-12-09 14:00 | 49115.0402 | 1739.988
Devonshire Building | 2016-12-09 14:15 | 49115.4702 | 1720.008
Devonshire Building | 2016-12-09 14:30 | 49115.9102 | 1760.004
Devonshire Building | 2016-12-09 14:45 | 49116.6502 | 2959.992
Devonshire Building | 2016-12-09 15:00 | 49117.1102 | 1839.996
Devonshire Building | 2016-12-09 15:15 | 49117.5802 | 1879.992
Devonshire Building | 2016-12-09 15:30 | 49118.0602 | 1919.988
Devonshire Building | 2016-12-09 15:45 | 49118.5352 | 1900.008
Devonshire Building | 2016-12-09 16:00 | 49119.0102 | 1900.008
Devonshire Building | 2016-12-09 16:15 | 49119.5902 | 2319.984
Devonshire Building | 2016-12-09 16:30 | 49120.2452 | 2620.008
Devonshire Building | 2016-12-09 16:45 | 49120.7202 | 1900.008
Devonshire Building | 2016-12-09 17:00 | 49121.1902 | 1879.992
Devonshire Building | 2016-12-09 17:15 | 49121.6502 | 1839.996
Devonshire Building | 2016-12-09 17:30 | 49122.1052 | 1820.016
Devonshire Building | 2016-12-09 17:45 | 49122.5502 | 1779.984
Devonshire Building | 2016-12-09 18:00 | 49122.9902 | 1760.004
Devonshire Building | 2016-12-09 18:15 | 49123.4252 | 1739.988
Devonshire Building | 2016-12-09 18:30 | 49123.8552 | 1720.008
Devonshire Building | 2016-12-09 18:45 | 49124.2852 | 1720.008
Devonshire Building | 2016-12-09 19:00 | 49124.7152 | 1720.008
Devonshire Building | 2016-12-09 19:15 | 49125.1352 | 1680.012
Devonshire Building | 2016-12-09 19:30 | 49125.5602 | 1699.992
Devonshire Building | 2016-12-09 19:45 | 49125.9852 | 1699.992
Devonshire Building | 2016-12-09 20:00 | 49126.6652 | 2720.016
Devonshire Building | 2016-12-09 20:15 | 49127.0852 | 1680.012
Devonshire Building | 2016-12-09 20:30 | 49127.5002 | 1659.996
Devonshire Building | 2016-12-09 20:45 | 49127.9152 | 1659.996
Devonshire Building | 2016-12-09 21:00 | 49128.3302 | 1659.996
Devonshire Building | 2016-12-09 21:15 | 49128.7502 | 1680.012
Devonshire Building | 2016-12-09 21:30 | 49129.1652 | 1659.996
Devonshire Building | 2016-12-09 21:45 | 49129.5802 | 1659.996
Devonshire Building | 2016-12-09 22:00 | 49130.0002 | 1680.012
Devonshire Building | 2016-12-09 22:15 | 49130.4152 | 1659.996
Devonshire Building | 2016-12-09 22:30 | 49130.8352 | 1680.012
Devonshire Building | 2016-12-09 22:45 | 49131.2502 | 1659.996
Devonshire Building | 2016-12-09 23:00 | 49131.6702 | 1680.012
Devonshire Building | 2016-12-09 23:15 | 49132.0852 | 1659.996
Devonshire Building | 2016-12-09 23:30 | 49132.5052 | 1680.012
Devonshire Building | 2016-12-09 23:45 | 49132.9252 | 1680.012 | 1640.016
Devonshire Building | 2016-12-10 | 49133.3438 | 1680.012
Devonshire Building | 2016-12-10 00:15 | 49133.7687 | 1699.992
Devonshire Building | 2016-12-10 00:30 | 49134.1888 | 1680.012
Devonshire Building | 2016-12-10 00:45 | 49134.6088 | 1680.012
Devonshire Building | 2016-12-10 01:00 | 49135.0338 | 1699.992
Devonshire Building | 2016-12-10 01:15 | 49135.4587 | 1699.992
Devonshire Building | 2016-12-10 01:30 | 49135.8837 | 1699.992
Devonshire Building | 2016-12-10 01:45 | 49136.3087 | 1699.992
Devonshire Building | 2016-12-10 02:00 | 49136.7337 | 1699.992
Devonshire Building | 2016-12-10 02:15 | 49137.1587 | 1699.992
Devonshire Building | 2016-12-10 02:30 | 49137.5837 | 1699.992
Devonshire Building | 2016-12-10 02:45 | 49138.0037 | 1680.012
Devonshire Building | 2016-12-10 03:00 | 49138.4287 | 1699.992
Devonshire Building | 2016-12-10 03:15 | 49138.8537 | 1699.992
Devonshire Building | 2016-12-10 03:30 | 49139.2737 | 1680.012
Devonshire Building | 2016-12-10 03:45 | 49139.6987 | 1699.992
Devonshire Building | 2016-12-10 04:00 | 49140.1187 | 1680.012
Devonshire Building | 2016-12-10 04:15 | 49140.5437 | 1699.992
Devonshire Building | 2016-12-10 04:30 | 49140.9637 | 1680.012
Devonshire Building | 2016-12-10 04:45 | 49141.3887 | 1699.992
Devonshire Building | 2016-12-10 05:00 | 49141.8087 | 1680.012
Devonshire Building | 2016-12-10 05:15 | 49142.2287 | 1680.012
Devonshire Building | 2016-12-10 05:30 | 49142.6537 | 1699.992
Devonshire Building | 2016-12-10 05:45 | 49143.0737 | 1680.012
Devonshire Building | 2016-12-10 06:00 | 49143.4987 | 1699.992
Devonshire Building | 2016-12-10 06:15 | 49143.9187 | 1680.012
Devonshire Building | 2016-12-10 06:30 | 49144.3388 | 1680.012
Devonshire Building | 2016-12-10 06:45 | 49144.7588 | 1680.012
Devonshire Building | 2016-12-10 07:00 | 49145.1788 | 1680.012
Devonshire Building | 2016-12-10 07:15 | 49145.5938 | 1659.996
Devonshire Building | 2016-12-10 07:30 | 49146.0088 | 1659.996
Devonshire Building | 2016-12-10 07:45 | 49146.4288 | 1680.012
Devonshire Building | 2016-12-10 08:00 | 49146.8588 | 1720.008
Devonshire Building | 2016-12-10 08:15 | 49147.2838 | 1699.992
Devonshire Building | 2016-12-10 08:30 | 49147.7038 | 1680.012
Devonshire Building | 2016-12-10 08:45 | 49148.1288 | 1699.992
Devonshire Building | 2016-12-10 09:00 | 49148.5488 | 1680.012
Devonshire Building | 2016-12-10 09:15 | 49148.9638 | 1659.996
Devonshire Building | 2016-12-10 09:30 | 49149.3838 | 1680.012
Devonshire Building | 2016-12-10 09:45 | 49149.7988 | 1659.996
Devonshire Building | 2016-12-10 10:00 | 49150.2138 | 1659.996
Devonshire Building | 2016-12-10 10:15 | 49150.6138 | 1599.984
Devonshire Building | 2016-12-10 10:30 | 49151.0188 | 1620
Devonshire Building | 2016-12-10 10:45 | 49151.4188 | 1599.984
Devonshire Building | 2016-12-10 11:00 | 49151.8188 | 1599.984
Devonshire Building | 2016-12-10 11:15 | 49152.2238 | 1620
Devonshire Building | 2016-12-10 11:30 | 49152.6237 | 1599.984
Devonshire Building | 2016-12-10 11:45 | 49153.0287 | 1620
Devonshire Building | 2016-12-10 12:00 | 49153.4337 | 1620
Devonshire Building | 2016-12-10 12:15 | 49153.8337 | 1599.984
Devonshire Building | 2016-12-10 12:30 | 49154.2387 | 1620
Devonshire Building | 2016-12-10 12:45 | 49154.6437 | 1620
Devonshire Building | 2016-12-10 13:00 | 49155.0487 | 1620
Devonshire Building | 2016-12-10 13:15 | 49155.4487 | 1599.984
Devonshire Building | 2016-12-10 13:30 | 49155.8587 | 1640.016
Devonshire Building | 2016-12-10 13:45 | 49156.2637 | 1620
Devonshire Building | 2016-12-10 14:00 | 49156.6687 | 1620
Devonshire Building | 2016-12-10 14:15 | 49157.0737 | 1620
Devonshire Building | 2016-12-10 14:30 | 49157.4787 | 1620
Devonshire Building | 2016-12-10 14:45 | 49157.8887 | 1640.016
Devonshire Building | 2016-12-10 15:00 | 49158.2937 | 1620
Devonshire Building | 2016-12-10 15:15 | 49158.6987 | 1620
Devonshire Building | 2016-12-10 15:30 | 49159.1037 | 1620
Devonshire Building | 2016-12-10 15:45 | 49159.5138 | 1640.016
Devonshire Building | 2016-12-10 16:00 | 49159.9188 | 1620
Devonshire Building | 2016-12-10 16:15 | 49160.3238 | 1620
Devonshire Building | 2016-12-10 16:30 | 49160.9888 | 2660.004
Devonshire Building | 2016-12-10 16:45 | 49161.3938 | 1620
Devonshire Building | 2016-12-10 17:00 | 49161.7988 | 1620
Devonshire Building | 2016-12-10 17:15 | 49162.1987 | 1599.984
Devonshire Building | 2016-12-10 17:30 | 49162.6037 | 1620
Devonshire Building | 2016-12-10 17:45 | 49163.0087 | 1620
Devonshire Building | 2016-12-10 18:00 | 49163.4137 | 1620
Devonshire Building | 2016-12-10 18:15 | 49163.8137 | 1599.984
Devonshire Building | 2016-12-10 18:30 | 49164.2187 | 1620
Devonshire Building | 2016-12-10 18:45 | 49164.6187 | 1599.984
Devonshire Building | 2016-12-10 19:00 | 49165.0237 | 1620
Devonshire Building | 2016-12-10 19:15 | 49165.4287 | 1620
Devonshire Building | 2016-12-10 19:30 | 49165.8337 | 1620
Devonshire Building | 2016-12-10 19:45 | 49166.2387 | 1620
Devonshire Building | 2016-12-10 20:00 | 49166.6437 | 1620
Devonshire Building | 2016-12-10 20:15 | 49167.0487 | 1620
Devonshire Building | 2016-12-10 20:30 | 49167.4537 | 1620
Devonshire Building | 2016-12-10 20:45 | 49167.8587 | 1620
Devonshire Building | 2016-12-10 21:00 | 49168.2687 | 1640.016
Devonshire Building | 2016-12-10 21:15 | 49168.6737 | 1620
Devonshire Building | 2016-12-10 21:30 | 49169.0837 | 1640.016
Devonshire Building | 2016-12-10 21:45 | 49169.4938 | 1640.016
Devonshire Building | 2016-12-10 22:00 | 49169.9088 | 1659.996
Devonshire Building | 2016-12-10 22:15 | 49170.3138 | 1620
Devonshire Building | 2016-12-10 22:30 | 49170.7238 | 1640.016
Devonshire Building | 2016-12-10 22:45 | 49171.1338 | 1640.016
Devonshire Building | 2016-12-10 23:00 | 49171.5388 | 1620
Devonshire Building | 2016-12-10 23:15 | 49171.9488 | 1640.016
Devonshire Building | 2016-12-10 23:30 | 49172.3588 | 1640.016
Devonshire Building | 2016-12-10 23:45 | 49172.7688 | 1640.016 | 1599.984
Devonshire Building | 2016-12-11 | 49173.1797 | 1640.016
Devonshire Building | 2016-12-11 00:15 | 49173.5897 | 1640.016
Devonshire Building | 2016-12-11 00:30 | 49173.9997 | 1640.016
Devonshire Building | 2016-12-11 00:45 | 49174.4097 | 1640.016
Devonshire Building | 2016-12-11 01:00 | 49174.8197 | 1640.016
Devonshire Building | 2016-12-11 01:15 | 49175.2347 | 1659.996
Devonshire Building | 2016-12-11 01:30 | 49175.6447 | 1640.016
Devonshire Building | 2016-12-11 01:45 | 49176.0597 | 1659.996
Devonshire Building | 2016-12-11 02:00 | 49176.4697 | 1640.016
Devonshire Building | 2016-12-11 02:15 | 49176.8847 | 1659.996
Devonshire Building | 2016-12-11 02:30 | 49177.2947 | 1640.016
Devonshire Building | 2016-12-11 02:45 | 49177.7097 | 1659.996
Devonshire Building | 2016-12-11 03:00 | 49178.1197 | 1640.016
Devonshire Building | 2016-12-11 03:15 | 49178.5297 | 1640.016
Devonshire Building | 2016-12-11 03:30 | 49178.9447 | 1659.996
Devonshire Building | 2016-12-11 03:45 | 49179.3547 | 1640.016
Devonshire Building | 2016-12-11 04:00 | 49179.7697 | 1659.996
Devonshire Building | 2016-12-11 04:15 | 49180.1797 | 1640.016
Devonshire Building | 2016-12-11 04:30 | 49180.5947 | 1659.996
Devonshire Building | 2016-12-11 04:45 | 49181.0047 | 1640.016
Devonshire Building | 2016-12-11 05:00 | 49181.4197 | 1659.996
Devonshire Building | 2016-12-11 05:15 | 49181.8297 | 1640.016
Devonshire Building | 2016-12-11 05:30 | 49182.2397 | 1640.016
Devonshire Building | 2016-12-11 05:45 | 49182.6547 | 1659.996
Devonshire Building | 2016-12-11 06:00 | 49183.0647 | 1640.016
Devonshire Building | 2016-12-11 06:15 | 49183.4747 | 1640.016
Devonshire Building | 2016-12-11 06:30 | 49183.8847 | 1640.016
Devonshire Building | 2016-12-11 06:45 | 49184.2997 | 1659.996
Devonshire Building | 2016-12-11 07:00 | 49184.7098 | 1640.016
Devonshire Building | 2016-12-11 07:15 | 49185.1198 | 1640.016
Devonshire Building | 2016-12-11 07:30 | 49185.5298 | 1640.016
Devonshire Building | 2016-12-11 07:45 | 49185.9498 | 1680.012
Devonshire Building | 2016-12-11 08:00 | 49186.3748 | 1699.992
Devonshire Building | 2016-12-11 08:15 | 49186.7998 | 1699.992
Devonshire Building | 2016-12-11 08:30 | 49187.2198 | 1680.012
Devonshire Building | 2016-12-11 08:45 | 49187.6398 | 1680.012
Devonshire Building | 2016-12-11 09:00 | 49188.0548 | 1659.996
Devonshire Building | 2016-12-11 09:15 | 49188.4698 | 1659.996
Devonshire Building | 2016-12-11 09:30 | 49188.8798 | 1640.016
Devonshire Building | 2016-12-11 09:45 | 49189.2948 | 1659.996
Devonshire Building | 2016-12-11 10:00 | 49189.7048 | 1640.016
Devonshire Building | 2016-12-11 10:15 | 49190.0998 | 1580.004
Devonshire Building | 2016-12-11 10:30 | 49190.4948 | 1580.004
Devonshire Building | 2016-12-11 10:45 | 49190.8898 | 1580.004
Devonshire Building | 2016-12-11 11:00 | 49191.2848 | 1580.004
Devonshire Building | 2016-12-11 11:15 | 49191.6748 | 1559.988
Devonshire Building | 2016-12-11 11:30 | 49192.0698 | 1580.004
Devonshire Building | 2016-12-11 11:45 | 49192.4698 | 1599.984
Devonshire Building | 2016-12-11 12:00 | 49192.8648 | 1580.004
Devonshire Building | 2016-12-11 12:15 | 49193.2598 | 1580.004
Devonshire Building | 2016-12-11 12:30 | 49193.6548 | 1580.004
Devonshire Building | 2016-12-11 12:45 | 49194.0498 | 1580.004
Devonshire Building | 2016-12-11 13:00 | 49194.4498 | 1599.984
Devonshire Building | 2016-12-11 13:15 | 49194.8448 | 1580.004
Devonshire Building | 2016-12-11 13:30 | 49195.2448 | 1599.984
Devonshire Building | 2016-12-11 13:45 | 49195.6448 | 1599.984
Devonshire Building | 2016-12-11 14:00 | 49196.0448 | 1599.984
Devonshire Building | 2016-12-11 14:15 | 49196.4398 | 1580.004
Devonshire Building | 2016-12-11 14:30 | 49196.8398 | 1599.984
Devonshire Building | 2016-12-11 14:45 | 49197.2448 | 1620
Devonshire Building | 2016-12-11 15:00 | 49197.6447 | 1599.984
Devonshire Building | 2016-12-11 15:15 | 49198.0447 | 1599.984
Devonshire Building | 2016-12-11 15:30 | 49198.4447 | 1599.984
Devonshire Building | 2016-12-11 15:45 | 49198.8447 | 1599.984
Devonshire Building | 2016-12-11 16:00 | 49199.2447 | 1599.984
Devonshire Building | 2016-12-11 16:15 | 49199.6447 | 1599.984
Devonshire Building | 2016-12-11 16:30 | 49200.0447 | 1599.984
Devonshire Building | 2016-12-11 16:45 | 49200.4397 | 1580.004
Devonshire Building | 2016-12-11 17:00 | 49200.8397 | 1599.984
Devonshire Building | 2016-12-11 17:15 | 49201.2347 | 1580.004
Devonshire Building | 2016-12-11 17:30 | 49201.6297 | 1580.004
Devonshire Building | 2016-12-11 17:45 | 49202.0247 | 1580.004
Devonshire Building | 2016-12-11 18:00 | 49202.4197 | 1580.004
Devonshire Building | 2016-12-11 18:15 | 49202.8147 | 1580.004
Devonshire Building | 2016-12-11 18:30 | 49203.2097 | 1580.004
Devonshire Building | 2016-12-11 18:45 | 49203.5997 | 1559.988
Devonshire Building | 2016-12-11 19:00 | 49203.9947 | 1580.004
Devonshire Building | 2016-12-11 19:15 | 49204.3897 | 1580.004
Devonshire Building | 2016-12-11 19:30 | 49204.8397 | 1800
Devonshire Building | 2016-12-11 19:45 | 49205.4347 | 2379.996
Devonshire Building | 2016-12-11 20:00 | 49205.8297 | 1580.004
Devonshire Building | 2016-12-11 20:15 | 49206.2247 | 1580.004
Devonshire Building | 2016-12-11 20:30 | 49206.6247 | 1599.984
Devonshire Building | 2016-12-11 20:45 | 49207.0247 | 1599.984
Devonshire Building | 2016-12-11 21:00 | 49207.4197 | 1580.004
Devonshire Building | 2016-12-11 21:15 | 49207.8197 | 1599.984
Devonshire Building | 2016-12-11 21:30 | 49208.2147 | 1580.004
Devonshire Building | 2016-12-11 21:45 | 49208.6147 | 1599.984
Devonshire Building | 2016-12-11 22:00 | 49209.0197 | 1620
Devonshire Building | 2016-12-11 22:15 | 49209.4197 | 1599.984
Devonshire Building | 2016-12-11 22:30 | 49209.8147 | 1580.004
Devonshire Building | 2016-12-11 22:45 | 49210.2147 | 1599.984
Devonshire Building | 2016-12-11 23:00 | 49210.6147 | 1599.984
Devonshire Building | 2016-12-11 23:15 | 49211.0147 | 1599.984
Devonshire Building | 2016-12-11 23:30 | 49211.4197 | 1620
Devonshire Building | 2016-12-11 23:45 | 49211.8197 | 1599.984 | 1559.988
Devonshire Building | 2016-12-12 | 49212.2227 | 1620
Devonshire Building | 2016-12-12 00:15 | 49212.6277 | 1620
Devonshire Building | 2016-12-12 00:30 | 49213.0327 | 1620
Devonshire Building | 2016-12-12 00:45 | 49213.4377 | 1620
Devonshire Building | 2016-12-12 01:00 | 49213.8477 | 1640.016
Devonshire Building | 2016-12-12 01:15 | 49214.2527 | 1620
Devonshire Building | 2016-12-12 01:30 | 49214.6627 | 1640.016
Devonshire Building | 2016-12-12 01:45 | 49215.0677 | 1620
Devonshire Building | 2016-12-12 02:00 | 49215.4777 | 1640.016
Devonshire Building | 2016-12-12 02:15 | 49215.8877 | 1640.016
Devonshire Building | 2016-12-12 02:30 | 49216.2927 | 1620
Devonshire Building | 2016-12-12 02:45 | 49216.7027 | 1640.016
Devonshire Building | 2016-12-12 03:00 | 49217.1127 | 1640.016
Devonshire Building | 2016-12-12 03:15 | 49217.5177 | 1620
Devonshire Building | 2016-12-12 03:30 | 49217.9277 | 1640.016
Devonshire Building | 2016-12-12 03:45 | 49218.3327 | 1620
Devonshire Building | 2016-12-12 04:00 | 49218.7427 | 1640.016
Devonshire Building | 2016-12-12 04:15 | 49219.1527 | 1640.016
Devonshire Building | 2016-12-12 04:30 | 49219.5577 | 1620
Devonshire Building | 2016-12-12 04:45 | 49219.9677 | 1640.016
Devonshire Building | 2016-12-12 05:00 | 49220.3777 | 1640.016
Devonshire Building | 2016-12-12 05:15 | 49220.7827 | 1620
Devonshire Building | 2016-12-12 05:30 | 49221.1927 | 1640.016
Devonshire Building | 2016-12-12 05:45 | 49221.5977 | 1620
Devonshire Building | 2016-12-12 06:00 | 49222.0027 | 1620
Devonshire Building | 2016-12-12 06:15 | 49222.4077 | 1620
Devonshire Building | 2016-12-12 06:30 | 49222.8077 | 1599.984
Devonshire Building | 2016-12-12 06:45 | 49223.2077 | 1599.984
Devonshire Building | 2016-12-12 07:00 | 49223.6077 | 1599.984
Devonshire Building | 2016-12-12 07:15 | 49224.0027 | 1580.004
Devonshire Building | 2016-12-12 07:30 | 49224.3927 | 1559.988
Devonshire Building | 2016-12-12 07:45 | 49224.8027 | 1640.016
Devonshire Building | 2016-12-12 08:00 | 49225.2227 | 1680.012
Devonshire Building | 2016-12-12 08:15 | 49225.6327 | 1640.016
Devonshire Building | 2016-12-12 08:30 | 49226.0477 | 1659.996
Devonshire Building | 2016-12-12 08:45 | 49226.4677 | 1680.012
Devonshire Building | 2016-12-12 09:00 | 49226.8877 | 1680.012
Devonshire Building | 2016-12-12 09:15 | 49227.5777 | 2760.012
Devonshire Building | 2016-12-12 09:30 | 49227.9877 | 1640.016
Devonshire Building | 2016-12-12 09:45 | 49228.4027 | 1659.996
Devonshire Building | 2016-12-12 10:00 | 49228.8177 | 1659.996
Devonshire Building | 2016-12-12 10:15 | 49229.2427 | 1699.992
Devonshire Building | 2016-12-12 10:30 | 49229.7127 | 1879.992
Devonshire Building | 2016-12-12 10:45 | 49230.3377 | 2499.984
Devonshire Building | 2016-12-12 11:00 | 49230.7377 | 1599.984
Devonshire Building | 2016-12-12 11:15 | 49231.1327 | 1580.004
Devonshire Building | 2016-12-12 11:30 | 49231.8127 | 2720.016
Devonshire Building | 2016-12-12 11:45 | 49232.2177 | 1620
Devonshire Building | 2016-12-12 12:00 | 49232.6277 | 1640.016
Devonshire Building | 2016-12-12 12:15 | 49233.0727 | 1779.984
Devonshire Building | 2016-12-12 12:30 | 49233.5527 | 1919.988
Devonshire Building | 2016-12-12 12:45 | 49234.0427 | 1959.984
Devonshire Building | 2016-12-12 13:00 | 49234.8227 | 3120.012
Devonshire Building | 2016-12-12 13:15 | 49235.3727 | 2199.996
Devonshire Building | 2016-12-12 13:30 | 49235.9627 | 2360.016
Devonshire Building | 2016-12-12 13:45 | 49236.4877 | 2099.988
Devonshire Building | 2016-12-12 14:00 | 49236.9777 | 1959.984
Devonshire Building | 2016-12-12 14:15 | 49237.4377 | 1839.996
Devonshire Building | 2016-12-12 14:30 | 49237.8927 | 1820.016
Devonshire Building | 2016-12-12 14:45 | 49238.5977 | 2819.988
Devonshire Building | 2016-12-12 15:00 | 49239.0227 | 1699.992
Devonshire Building | 2016-12-12 15:15 | 49239.4477 | 1699.992
Devonshire Building | 2016-12-12 15:30 | 49239.8827 | 1739.988
Devonshire Building | 2016-12-12 15:45 | 49240.3677 | 1940.004
Devonshire Building | 2016-12-12 16:00 | 49240.8577 | 1959.984
Devonshire Building | 2016-12-12 16:15 | 49241.6377 | 3120.012
Devonshire Building | 2016-12-12 16:30 | 49242.1227 | 1940.004
Devonshire Building | 2016-12-12 16:45 | 49242.6127 | 1959.984
Devonshire Building | 2016-12-12 17:00 | 49243.1027 | 1959.984
Devonshire Building | 2016-12-12 17:15 | 49243.5827 | 1919.988
Devonshire Building | 2016-12-12 17:30 | 49244.0577 | 1900.008
Devonshire Building | 2016-12-12 17:45 | 49244.5277 | 1879.992
Devonshire Building | 2016-12-12 18:00 | 49244.9977 | 1879.992
Devonshire Building | 2016-12-12 18:15 | 49245.4527 | 1820.016
Devonshire Building | 2016-12-12 18:30 | 49245.8927 | 1760.004
Devonshire Building | 2016-12-12 18:45 | 49246.5877 | 2779.992
Devonshire Building | 2016-12-12 19:00 | 49247.0027 | 1659.996
Devonshire Building | 2016-12-12 19:15 | 49247.4127 | 1640.016
Devonshire Building | 2016-12-12 19:30 | 49247.8327 | 1680.012
Devonshire Building | 2016-12-12 19:45 | 49248.2477 | 1659.996
Devonshire Building | 2016-12-12 20:00 | 49248.6577 | 1640.016
Devonshire Building | 2016-12-12 20:15 | 49249.0677 | 1640.016
Devonshire Building | 2016-12-12 20:30 | 49249.4777 | 1640.016
Devonshire Building | 2016-12-12 20:45 | 49249.8877 | 1640.016
Devonshire Building | 2016-12-12 21:00 | 49250.2977 | 1640.016
Devonshire Building | 2016-12-12 21:15 | 49250.7027 | 1620
Devonshire Building | 2016-12-12 21:30 | 49251.1077 | 1620
Devonshire Building | 2016-12-12 21:45 | 49251.5127 | 1620
Devonshire Building | 2016-12-12 22:00 | 49251.9227 | 1640.016
Devonshire Building | 2016-12-12 22:15 | 49252.3277 | 1620
Devonshire Building | 2016-12-12 22:30 | 49252.7327 | 1620
Devonshire Building | 2016-12-12 22:45 | 49253.1427 | 1640.016
Devonshire Building | 2016-12-12 23:00 | 49253.5477 | 1620
Devonshire Building | 2016-12-12 23:15 | 49253.9527 | 1620
Devonshire Building | 2016-12-12 23:30 | 49254.3627 | 1640.016
Devonshire Building | 2016-12-12 23:45 | 49254.7677 | 1620 | 1559.988
Devonshire Building | 2016-12-13 | 49255.1797 | 1640.016
Devonshire Building | 2016-12-13 00:15 | 49255.5897 | 1640.016
Devonshire Building | 2016-12-13 00:30 | 49255.9997 | 1640.016
Devonshire Building | 2016-12-13 00:45 | 49256.4147 | 1659.996
Devonshire Building | 2016-12-13 01:00 | 49256.8247 | 1640.016
Devonshire Building | 2016-12-13 01:15 | 49257.2397 | 1659.996
Devonshire Building | 2016-12-13 01:30 | 49257.6497 | 1640.016
Devonshire Building | 2016-12-13 01:45 | 49258.0647 | 1659.996
Devonshire Building | 2016-12-13 02:00 | 49258.4747 | 1640.016
Devonshire Building | 2016-12-13 02:15 | 49258.8897 | 1659.996
Devonshire Building | 2016-12-13 02:30 | 49259.2997 | 1640.016
Devonshire Building | 2016-12-13 02:45 | 49259.7147 | 1659.996
Devonshire Building | 2016-12-13 03:00 | 49260.1247 | 1640.016
Devonshire Building | 2016-12-13 03:15 | 49260.5397 | 1659.996
Devonshire Building | 2016-12-13 03:30 | 49260.9497 | 1640.016
Devonshire Building | 2016-12-13 03:45 | 49261.3597 | 1640.016
Devonshire Building | 2016-12-13 04:00 | 49261.7697 | 1640.016
Devonshire Building | 2016-12-13 04:15 | 49262.1797 | 1640.016
Devonshire Building | 2016-12-13 04:30 | 49262.5897 | 1640.016
Devonshire Building | 2016-12-13 04:45 | 49262.9997 | 1640.016
Devonshire Building | 2016-12-13 05:00 | 49263.4097 | 1640.016
Devonshire Building | 2016-12-13 05:15 | 49263.8197 | 1640.016
Devonshire Building | 2016-12-13 05:30 | 49264.2297 | 1640.016
Devonshire Building | 2016-12-13 05:45 | 49264.6347 | 1620
Devonshire Building | 2016-12-13 06:00 | 49265.0347 | 1599.984
Devonshire Building | 2016-12-13 06:15 | 49265.4397 | 1620
Devonshire Building | 2016-12-13 06:30 | 49265.8397 | 1599.984
Devonshire Building | 2016-12-13 06:45 | 49266.2347 | 1580.004
Devonshire Building | 2016-12-13 07:00 | 49266.6297 | 1580.004
Devonshire Building | 2016-12-13 07:15 | 49267.0247 | 1580.004
Devonshire Building | 2016-12-13 07:30 | 49267.4147 | 1559.988
Devonshire Building | 2016-12-13 07:45 | 49267.8297 | 1659.996
Devonshire Building | 2016-12-13 08:00 | 49268.2347 | 1620
Devonshire Building | 2016-12-13 08:15 | 49268.6497 | 1659.996
Devonshire Building | 2016-12-13 08:30 | 49269.0597 | 1640.016
Devonshire Building | 2016-12-13 08:45 | 49269.4797 | 1680.012
Devonshire Building | 2016-12-13 09:00 | 49270.1947 | 2859.984
Devonshire Building | 2016-12-13 09:15 | 49270.6147 | 1680.012
Devonshire Building | 2016-12-13 09:30 | 49271.0247 | 1640.016
Devonshire Building | 2016-12-13 09:45 | 49271.4448 | 1680.012
Devonshire Building | 2016-12-13 10:00 | 49271.8598 | 1659.996
Devonshire Building | 2016-12-13 10:15 | 49272.3047 | 1779.984
Devonshire Building | 2016-12-13 10:30 | 49272.7547 | 1800
Devonshire Building | 2016-12-13 10:45 | 49273.5247 | 3080.016
Devonshire Building | 2016-12-13 11:00 | 49274.0147 | 1959.984
Devonshire Building | 2016-12-13 11:15 | 49274.5197 | 2019.996
Devonshire Building | 2016-12-13 11:30 | 49275.0197 | 2000.016
Devonshire Building | 2016-12-13 11:45 | 49275.5347 | 2059.992
Devonshire Building | 2016-12-13 12:00 | 49276.2697 | 2940.012
Devonshire Building | 2016-12-13 12:15 | 49276.7348 | 1860.012
Devonshire Building | 2016-12-13 12:30 | 49277.1948 | 1839.996
Devonshire Building | 2016-12-13 12:45 | 49277.6548 | 1839.996
Devonshire Building | 2016-12-13 13:00 | 49278.2848 | 2520
Devonshire Building | 2016-12-13 13:15 | 49278.8447 | 2239.992
Devonshire Building | 2016-12-13 13:30 | 49279.3098 | 1860.012
Devonshire Building | 2016-12-13 13:45 | 49279.7698 | 1839.996
Devonshire Building | 2016-12-13 14:00 | 49280.2198 | 1800
Devonshire Building | 2016-12-13 14:15 | 49280.6698 | 1800
Devonshire Building | 2016-12-13 14:30 | 49281.1198 | 1800
Devonshire Building | 2016-12-13 14:45 | 49281.8548 | 2940.012
Devonshire Building | 2016-12-13 15:00 | 49282.2948 | 1760.004
Devonshire Building | 2016-12-13 15:15 | 49282.7398 | 1779.984
Devonshire Building | 2016-12-13 15:30 | 49283.1948 | 1820.016
Devonshire Building | 2016-12-13 15:45 | 49283.6698 | 1900.008
Devonshire Building | 2016-12-13 16:00 | 49284.1848 | 2059.992
Devonshire Building | 2016-12-13 16:15 | 49284.9598 | 3099.996
Devonshire Building | 2016-12-13 16:30 | 49285.4698 | 2040.012
Devonshire Building | 2016-12-13 16:45 | 49285.9748 | 2019.996
Devonshire Building | 2016-12-13 17:00 | 49286.4598 | 1940.004
Devonshire Building | 2016-12-13 17:15 | 49286.9248 | 1860.012
Devonshire Building | 2016-12-13 17:30 | 49287.3798 | 1820.016
Devonshire Building | 2016-12-13 17:45 | 49287.8248 | 1779.984
Devonshire Building | 2016-12-13 18:00 | 49288.5398 | 2859.984
Devonshire Building | 2016-12-13 18:15 | 49288.9748 | 1739.988
Devonshire Building | 2016-12-13 18:30 | 49289.4048 | 1720.008
Devonshire Building | 2016-12-13 18:45 | 49289.8398 | 1739.988
Devonshire Building | 2016-12-13 19:00 | 49290.2598 | 1680.012
Devonshire Building | 2016-12-13 19:15 | 49290.6848 | 1699.992
Devonshire Building | 2016-12-13 19:30 | 49291.0998 | 1659.996
Devonshire Building | 2016-12-13 19:45 | 49291.5148 | 1659.996
Devonshire Building | 2016-12-13 20:00 | 49291.9248 | 1640.016
Devonshire Building | 2016-12-13 20:15 | 49292.3348 | 1640.016
Devonshire Building | 2016-12-13 20:30 | 49292.7448 | 1640.016
Devonshire Building | 2016-12-13 20:45 | 49293.1548 | 1640.016
Devonshire Building | 2016-12-13 21:00 | 49293.5598 | 1620
Devonshire Building | 2016-12-13 21:15 | 49293.9698 | 1640.016
Devonshire Building | 2016-12-13 21:30 | 49294.3748 | 1620
Devonshire Building | 2016-12-13 21:45 | 49294.7848 | 1640.016
Devonshire Building | 2016-12-13 22:00 | 49295.1948 | 1640.016
Devonshire Building | 2016-12-13 22:15 | 49295.5998 | 1620
Devonshire Building | 2016-12-13 22:30 | 49296.0048 | 1620
Devonshire Building | 2016-12-13 22:45 | 49296.4148 | 1640.016
Devonshire Building | 2016-12-13 23:00 | 49296.8198 | 1620
Devonshire Building | 2016-12-13 23:15 | 49297.2298 | 1640.016
Devonshire Building | 2016-12-13 23:30 | 49297.6398 | 1640.016
Devonshire Building | 2016-12-13 23:45 | 49298.0498 | 1640.016 | 1559.988
Devonshire Building | 2016-12-14 | 49298.4609 | 1640.016
Devonshire Building | 2016-12-14 00:15 | 49298.8709 | 1640.016
Devonshire Building | 2016-12-14 00:30 | 49299.2809 | 1640.016
Devonshire Building | 2016-12-14 00:45 | 49299.691 | 1640.016
Devonshire Building | 2016-12-14 01:00 | 49300.101 | 1640.016
Devonshire Building | 2016-12-14 01:15 | 49300.511 | 1640.016
Devonshire Building | 2016-12-14 01:30 | 49300.926 | 1659.996
Devonshire Building | 2016-12-14 01:45 | 49301.351 | 1699.992
Devonshire Building | 2016-12-14 02:00 | 49301.776 | 1699.992
Devonshire Building | 2016-12-14 02:15 | 49302.201 | 1699.992
Devonshire Building | 2016-12-14 02:30 | 49302.626 | 1699.992
Devonshire Building | 2016-12-14 02:45 | 49303.0509 | 1699.992
Devonshire Building | 2016-12-14 03:00 | 49303.4759 | 1699.992
Devonshire Building | 2016-12-14 03:15 | 49303.9009 | 1699.992
Devonshire Building | 2016-12-14 03:30 | 49304.3259 | 1699.992
Devonshire Building | 2016-12-14 03:45 | 49304.7509 | 1699.992
Devonshire Building | 2016-12-14 04:00 | 49305.1659 | 1659.996
Devonshire Building | 2016-12-14 04:15 | 49305.5709 | 1620
Devonshire Building | 2016-12-14 04:30 | 49305.9809 | 1640.016
Devonshire Building | 2016-12-14 04:45 | 49306.3909 | 1640.016
Devonshire Building | 2016-12-14 05:00 | 49306.7959 | 1620
Devonshire Building | 2016-12-14 05:15 | 49307.206 | 1640.016
Devonshire Building | 2016-12-14 05:30 | 49307.616 | 1640.016
Devonshire Building | 2016-12-14 05:45 | 49308.021 | 1620
Devonshire Building | 2016-12-14 06:00 | 49308.431 | 1640.016
Devonshire Building | 2016-12-14 06:15 | 49308.836 | 1620
Devonshire Building | 2016-12-14 06:30 | 49309.241 | 1620
Devonshire Building | 2016-12-14 06:45 | 49309.646 | 1620
Devonshire Building | 2016-12-14 07:00 | 49310.046 | 1599.984
Devonshire Building | 2016-12-14 07:15 | 49310.446 | 1599.984
Devonshire Building | 2016-12-14 07:30 | 49310.8459 | 1599.984
Devonshire Building | 2016-12-14 07:45 | 49311.2459 | 1599.984
Devonshire Building | 2016-12-14 08:00 | 49311.6459 | 1599.984
Devonshire Building | 2016-12-14 08:15 | 49312.0459 | 1599.984
Devonshire Building | 2016-12-14 08:30 | 49312.4459 | 1599.984
Devonshire Building | 2016-12-14 08:45 | 49312.8459 | 1599.984
Devonshire Building | 2016-12-14 09:00 | 49313.2609 | 1659.996
Devonshire Building | 2016-12-14 09:15 | 49313.6659 | 1620
Devonshire Building | 2016-12-14 09:30 | 49314.3559 | 2760.012
Devonshire Building | 2016-12-14 09:45 | 49314.7659 | 1640.016
Devonshire Building | 2016-12-14 10:00 | 49315.1709 | 1620
Devonshire Building | 2016-12-14 10:15 | 49315.5759 | 1620
Devonshire Building | 2016-12-14 10:30 | 49316.0459 | 1879.992
Devonshire Building | 2016-12-14 10:45 | 49316.5659 | 2080.008
Devonshire Building | 2016-12-14 11:00 | 49317.3559 | 3160.008
Devonshire Building | 2016-12-14 11:15 | 49317.8559 | 2000.016
Devonshire Building | 2016-12-14 11:30 | 49318.3609 | 2019.996
Devonshire Building | 2016-12-14 11:45 | 49318.8559 | 1980
Devonshire Building | 2016-12-14 12:00 | 49319.3359 | 1919.988
Devonshire Building | 2016-12-14 12:15 | 49319.8109 | 1900.008
Devonshire Building | 2016-12-14 12:30 | 49320.5409 | 2919.996
Devonshire Building | 2016-12-14 12:45 | 49320.9909 | 1800
Devonshire Building | 2016-12-14 13:00 | 49321.4759 | 1940.004
Devonshire Building | 2016-12-14 13:15 | 49321.9809 | 2019.996
Devonshire Building | 2016-12-14 13:30 | 49322.4759 | 1980
Devonshire Building | 2016-12-14 13:45 | 49322.9609 | 1940.004
Devonshire Building | 2016-12-14 14:00 | 49323.7259 | 3060
Devonshire Building | 2016-12-14 14:15 | 49324.1809 | 1820.016
Devonshire Building | 2016-12-14 14:30 | 49324.6359 | 1820.016
Devonshire Building | 2016-12-14 14:45 | 49325.1159 | 1919.988
Devonshire Building | 2016-12-14 15:00 | 49325.5859 | 1879.992
Devonshire Building | 2016-12-14 15:15 | 49326.0509 | 1860.012
Devonshire Building | 2016-12-14 15:30 | 49326.5159 | 1860.012
Devonshire Building | 2016-12-14 15:45 | 49326.9809 | 1860.012
Devonshire Building | 2016-12-14 16:00 | 49327.7659 | 3139.992
Devonshire Building | 2016-12-14 16:15 | 49328.2809 | 2059.992
Devonshire Building | 2016-12-14 16:30 | 49328.8059 | 2099.988
Devonshire Building | 2016-12-14 16:45 | 49329.3209 | 2059.992
Devonshire Building | 2016-12-14 17:00 | 49329.8459 | 2099.988
Devonshire Building | 2016-12-14 17:15 | 49330.3659 | 2080.008
Devonshire Building | 2016-12-14 17:30 | 49330.8809 | 2059.992
Devonshire Building | 2016-12-14 17:45 | 49331.3859 | 2019.996
Devonshire Building | 2016-12-14 18:00 | 49331.8709 | 1940.004
Devonshire Building | 2016-12-14 18:15 | 49332.3309 | 1839.996
Devonshire Building | 2016-12-14 18:30 | 49333.0159 | 2739.996
Devonshire Building | 2016-12-14 18:45 | 49333.4259 | 1640.016
Devonshire Building | 2016-12-14 19:00 | 49333.8409 | 1659.996
Devonshire Building | 2016-12-14 19:15 | 49334.2559 | 1659.996
Devonshire Building | 2016-12-14 19:30 | 49334.6709 | 1659.996
Devonshire Building | 2016-12-14 19:45 | 49335.0859 | 1659.996
Devonshire Building | 2016-12-14 20:00 | 49335.5009 | 1659.996
Devonshire Building | 2016-12-14 20:15 | 49335.9109 | 1640.016
Devonshire Building | 2016-12-14 20:30 | 49336.3259 | 1659.996
Devonshire Building | 2016-12-14 20:45 | 49336.7359 | 1640.016
Devonshire Building | 2016-12-14 21:00 | 49337.1509 | 1659.996
Devonshire Building | 2016-12-14 21:15 | 49337.5609 | 1640.016
Devonshire Building | 2016-12-14 21:30 | 49337.9759 | 1659.996
Devonshire Building | 2016-12-14 21:45 | 49338.3859 | 1640.016
Devonshire Building | 2016-12-14 22:00 | 49338.8009 | 1659.996
Devonshire Building | 2016-12-14 22:15 | 49339.2059 | 1620
Devonshire Building | 2016-12-14 22:30 | 49339.616 | 1640.016
Devonshire Building | 2016-12-14 22:45 | 49340.026 | 1640.016
Devonshire Building | 2016-12-14 23:00 | 49340.436 | 1640.016
Devonshire Building | 2016-12-14 23:15 | 49340.846 | 1640.016
Devonshire Building | 2016-12-14 23:30 | 49341.256 | 1640.016
Devonshire Building | 2016-12-14 23:45 | 49341.666 | 1640.016 | 1599.984
Devonshire Building | 2016-12-15 | 49342.0742 | 1640.016
Devonshire Building | 2016-12-15 00:15 | 49342.4892 | 1659.996
Devonshire Building | 2016-12-15 00:30 | 49342.8992 | 1640.016
Devonshire Building | 2016-12-15 00:45 | 49343.3092 | 1640.016
Devonshire Building | 2016-12-15 01:00 | 49343.7192 | 1640.016
Devonshire Building | 2016-12-15 01:15 | 49344.1292 | 1640.016
Devonshire Building | 2016-12-15 01:30 | 49344.5392 | 1640.016
Devonshire Building | 2016-12-15 01:45 | 49344.9442 | 1620
Devonshire Building | 2016-12-15 02:00 | 49345.3542 | 1640.016
Devonshire Building | 2016-12-15 02:15 | 49345.7642 | 1640.016
Devonshire Building | 2016-12-15 02:30 | 49346.1743 | 1640.016
Devonshire Building | 2016-12-15 02:45 | 49346.5843 | 1640.016
Devonshire Building | 2016-12-15 03:00 | 49346.9943 | 1640.016
Devonshire Building | 2016-12-15 03:15 | 49347.3993 | 1620
Devonshire Building | 2016-12-15 03:30 | 49347.8093 | 1640.016
Devonshire Building | 2016-12-15 03:45 | 49348.2143 | 1620
Devonshire Building | 2016-12-15 04:00 | 49348.6243 | 1640.016
Devonshire Building | 2016-12-15 04:15 | 49349.0293 | 1620
Devonshire Building | 2016-12-15 04:30 | 49349.4343 | 1620
Devonshire Building | 2016-12-15 04:45 | 49349.8393 | 1620
Devonshire Building | 2016-12-15 05:00 | 49350.2493 | 1640.016
Devonshire Building | 2016-12-15 05:15 | 49350.6543 | 1620
Devonshire Building | 2016-12-15 05:30 | 49351.0593 | 1620
Devonshire Building | 2016-12-15 05:45 | 49351.4643 | 1620
Devonshire Building | 2016-12-15 06:00 | 49351.8693 | 1620
Devonshire Building | 2016-12-15 06:15 | 49352.2693 | 1599.984
Devonshire Building | 2016-12-15 06:30 | 49352.6693 | 1599.984
Devonshire Building | 2016-12-15 06:45 | 49353.0693 | 1599.984
Devonshire Building | 2016-12-15 07:00 | 49353.4693 | 1599.984
Devonshire Building | 2016-12-15 07:15 | 49353.8743 | 1620
Devonshire Building | 2016-12-15 07:30 | 49354.2693 | 1580.004
Devonshire Building | 2016-12-15 07:45 | 49354.6793 | 1640.016
Devonshire Building | 2016-12-15 08:00 | 49355.0743 | 1580.004
Devonshire Building | 2016-12-15 08:15 | 49355.4843 | 1640.016
Devonshire Building | 2016-12-15 08:30 | 49356.0943 | 2440.008
Devonshire Building | 2016-12-15 08:45 | 49356.5543 | 1839.996
Devonshire Building | 2016-12-15 09:00 | 49356.9693 | 1659.996
Devonshire Building | 2016-12-15 09:15 | 49357.3743 | 1620
Devonshire Building | 2016-12-15 09:30 | 49357.7793 | 1620
Devonshire Building | 2016-12-15 09:45 | 49358.1743 | 1580.004
Devonshire Building | 2016-12-15 10:00 | 49358.5743 | 1599.984
Devonshire Building | 2016-12-15 10:15 | 49358.9943 | 1680.012
Devonshire Building | 2016-12-15 10:30 | 49359.4143 | 1680.012
Devonshire Building | 2016-12-15 10:45 | 49360.1493 | 2940.012
Devonshire Building | 2016-12-15 11:00 | 49360.6393 | 1959.984
Devonshire Building | 2016-12-15 11:15 | 49361.2393 | 2400.012
Devonshire Building | 2016-12-15 11:30 | 49361.7943 | 2220.012
Devonshire Building | 2016-12-15 11:45 | 49362.5543 | 3039.984
Devonshire Building | 2016-12-15 12:00 | 49363.0293 | 1900.008
Devonshire Building | 2016-12-15 12:15 | 49363.5393 | 2040.012
Devonshire Building | 2016-12-15 12:30 | 49364.0743 | 2139.984
Devonshire Building | 2016-12-15 12:45 | 49364.5893 | 2059.992
Devonshire Building | 2016-12-15 13:00 | 49365.0943 | 2019.996
Devonshire Building | 2016-12-15 13:15 | 49365.8493 | 3020.004
Devonshire Building | 2016-12-15 13:30 | 49366.2993 | 1800
Devonshire Building | 2016-12-15 13:45 | 49366.7593 | 1839.996
Devonshire Building | 2016-12-15 14:00 | 49367.2193 | 1839.996
Devonshire Building | 2016-12-15 14:15 | 49367.6843 | 1860.012
Devonshire Building | 2016-12-15 14:30 | 49368.1443 | 1839.996
Devonshire Building | 2016-12-15 14:45 | 49368.5993 | 1820.016
Devonshire Building | 2016-12-15 15:00 | 49369.3443 | 2980.008
Devonshire Building | 2016-12-15 15:15 | 49369.7943 | 1800
Devonshire Building | 2016-12-15 15:30 | 49370.2343 | 1760.004
Devonshire Building | 2016-12-15 15:45 | 49370.6743 | 1760.004
Devonshire Building | 2016-12-15 16:00 | 49371.1143 | 1760.004
Devonshire Building | 2016-12-15 16:15 | 49371.5543 | 1760.004
Devonshire Building | 2016-12-15 16:30 | 49371.9893 | 1739.988
Devonshire Building | 2016-12-15 16:45 | 49372.4193 | 1720.008
Devonshire Building | 2016-12-15 17:00 | 49373.1293 | 2840.004
Devonshire Building | 2016-12-15 17:15 | 49373.5443 | 1659.996
Devonshire Building | 2016-12-15 17:30 | 49373.9843 | 1760.004
Devonshire Building | 2016-12-15 17:45 | 49374.6293 | 2580.012
Devonshire Building | 2016-12-15 18:00 | 49375.2343 | 2419.992
Devonshire Building | 2016-12-15 18:15 | 49375.8043 | 2279.988
Devonshire Building | 2016-12-15 18:30 | 49376.3293 | 2099.988
Devonshire Building | 2016-12-15 18:45 | 49376.8493 | 2080.008
Devonshire Building | 2016-12-15 19:00 | 49377.3243 | 1900.008
Devonshire Building | 2016-12-15 19:15 | 49377.7743 | 1800
Devonshire Building | 2016-12-15 19:30 | 49378.2093 | 1739.988
Devonshire Building | 2016-12-15 19:45 | 49378.6293 | 1680.012
Devonshire Building | 2016-12-15 20:00 | 49379.0543 | 1699.992
Devonshire Building | 2016-12-15 20:15 | 49379.4693 | 1659.996
Devonshire Building | 2016-12-15 20:30 | 49379.8893 | 1680.012
Devonshire Building | 2016-12-15 20:45 | 49380.2993 | 1640.016
Devonshire Building | 2016-12-15 21:00 | 49380.7093 | 1640.016
Devonshire Building | 2016-12-15 21:15 | 49381.1143 | 1620
Devonshire Building | 2016-12-15 21:30 | 49381.5243 | 1640.016
Devonshire Building | 2016-12-15 21:45 | 49381.9293 | 1620
Devonshire Building | 2016-12-15 22:00 | 49382.3543 | 1699.992
Devonshire Building | 2016-12-15 22:15 | 49382.7493 | 1580.004
Devonshire Building | 2016-12-15 22:30 | 49383.1493 | 1599.984
Devonshire Building | 2016-12-15 22:45 | 49383.5543 | 1620
Devonshire Building | 2016-12-15 23:00 | 49383.9543 | 1599.984
Devonshire Building | 2016-12-15 23:15 | 49384.3543 | 1599.984
Devonshire Building | 2016-12-15 23:30 | 49384.7543 | 1599.984
Devonshire Building | 2016-12-15 23:45 | 49385.1593 | 1620 | 1580.004
Devonshire Building | 2016-12-16 | 49385.5586 | 1599.984
Devonshire Building | 2016-12-16 00:15 | 49385.9636 | 1620
Devonshire Building | 2016-12-16 00:30 | 49386.3686 | 1620
Devonshire Building | 2016-12-16 00:45 | 49386.7736 | 1620
Devonshire Building | 2016-12-16 01:00 | 49387.1786 | 1620
Devonshire Building | 2016-12-16 01:15 | 49387.5836 | 1620
Devonshire Building | 2016-12-16 01:30 | 49387.9886 | 1620
Devonshire Building | 2016-12-16 01:45 | 49388.3936 | 1620
Devonshire Building | 2016-12-16 02:00 | 49388.7986 | 1620
Devonshire Building | 2016-12-16 02:15 | 49389.2036 | 1620
Devonshire Building | 2016-12-16 02:30 | 49389.8636 | 2639.988
Devonshire Building | 2016-12-16 02:45 | 49390.2686 | 1620
Devonshire Building | 2016-12-16 03:00 | 49390.6736 | 1620
Devonshire Building | 2016-12-16 03:15 | 49391.0786 | 1620
Devonshire Building | 2016-12-16 03:30 | 49391.4836 | 1620
Devonshire Building | 2016-12-16 03:45 | 49391.8886 | 1620
Devonshire Building | 2016-12-16 04:00 | 49392.2936 | 1620
Devonshire Building | 2016-12-16 04:15 | 49392.6936 | 1599.984
Devonshire Building | 2016-12-16 04:30 | 49393.0986 | 1620
Devonshire Building | 2016-12-16 04:45 | 49393.4986 | 1599.984
Devonshire Building | 2016-12-16 05:00 | 49393.9036 | 1620
Devonshire Building | 2016-12-16 05:15 | 49394.3086 | 1620
Devonshire Building | 2016-12-16 05:30 | 49394.7136 | 1620
Devonshire Building | 2016-12-16 05:45 | 49395.1136 | 1599.984
Devonshire Building | 2016-12-16 06:00 | 49395.5186 | 1620
Devonshire Building | 2016-12-16 06:15 | 49395.9186 | 1599.984
Devonshire Building | 2016-12-16 06:30 | 49396.3186 | 1599.984
Devonshire Building | 2016-12-16 06:45 | 49396.7186 | 1599.984
Devonshire Building | 2016-12-16 07:00 | 49397.1186 | 1599.984
Devonshire Building | 2016-12-16 07:15 | 49397.5186 | 1599.984
Devonshire Building | 2016-12-16 07:30 | 49397.9236 | 1620
Devonshire Building | 2016-12-16 07:45 | 49398.3186 | 1580.004
Devonshire Building | 2016-12-16 08:00 | 49398.7386 | 1680.012
Devonshire Building | 2016-12-16 08:15 | 49399.1536 | 1659.996
Devonshire Building | 2016-12-16 08:30 | 49399.5636 | 1640.016
Devonshire Building | 2016-12-16 08:45 | 49399.9886 | 1699.992
Devonshire Building | 2016-12-16 09:00 | 49400.4136 | 1699.992
Devonshire Building | 2016-12-16 09:15 | 49401.0086 | 2379.996
Devonshire Building | 2016-12-16 09:30 | 49401.6486 | 2559.996
Devonshire Building | 2016-12-16 09:45 | 49402.5736 | 3700.008
Devonshire Building | 2016-12-16 10:00 | 49403.1686 | 2379.996
Devonshire Building | 2016-12-16 10:15 | 49403.7186 | 2199.996
Devonshire Building | 2016-12-16 10:30 | 49404.2586 | 2160
Devonshire Building | 2016-12-16 10:45 | 49404.7736 | 2059.992
Devonshire Building | 2016-12-16 11:00 | 49405.2736 | 2000.016
Devonshire Building | 2016-12-16 11:15 | 49405.7786 | 2019.996
Devonshire Building | 2016-12-16 11:30 | 49406.5436 | 3060
Devonshire Building | 2016-12-16 11:45 | 49406.9986 | 1820.016
Devonshire Building | 2016-12-16 12:00 | 49407.4736 | 1900.008
Devonshire Building | 2016-12-16 12:15 | 49408.0186 | 2180.016
Devonshire Building | 2016-12-16 12:30 | 49408.5636 | 2180.016
Devonshire Building | 2016-12-16 12:45 | 49409.3386 | 3099.996
Devonshire Building | 2016-12-16 13:00 | 49409.8086 | 1879.992
Devonshire Building | 2016-12-16 13:15 | 49410.2636 | 1820.016
Devonshire Building | 2016-12-16 13:30 | 49410.7186 | 1820.016
Devonshire Building | 2016-12-16 13:45 | 49411.1686 | 1800
Devonshire Building | 2016-12-16 14:00 | 49411.6186 | 1800
Devonshire Building | 2016-12-16 14:15 | 49412.0686 | 1800
Devonshire Building | 2016-12-16 14:30 | 49412.7886 | 2880
Devonshire Building | 2016-12-16 14:45 | 49413.2086 | 1680.012
Devonshire Building | 2016-12-16 15:00 | 49413.6436 | 1739.988
Devonshire Building | 2016-12-16 15:15 | 49414.0836 | 1760.004
Devonshire Building | 2016-12-16 15:30 | 49414.5186 | 1739.988
Devonshire Building | 2016-12-16 15:45 | 49414.9536 | 1739.988
Devonshire Building | 2016-12-16 16:00 | 49415.3886 | 1739.988
Devonshire Building | 2016-12-16 16:15 | 49415.8236 | 1739.988
Devonshire Building | 2016-12-16 16:30 | 49416.5386 | 2859.984
Devonshire Building | 2016-12-16 16:45 | 49416.9686 | 1720.008
Devonshire Building | 2016-12-16 17:00 | 49417.4186 | 1800
Devonshire Building | 2016-12-16 17:15 | 49417.9386 | 2080.008
Devonshire Building | 2016-12-16 17:30 | 49418.4636 | 2099.988
Devonshire Building | 2016-12-16 17:45 | 49418.9736 | 2040.012
Devonshire Building | 2016-12-16 18:00 | 49419.4886 | 2059.992
Devonshire Building | 2016-12-16 18:15 | 49419.9886 | 2000.016
Devonshire Building | 2016-12-16 18:30 | 49420.4636 | 1900.008
Devonshire Building | 2016-12-16 18:45 | 49420.9236 | 1839.996
Devonshire Building | 2016-12-16 19:00 | 49421.3686 | 1779.984
Devonshire Building | 2016-12-16 19:15 | 49421.8136 | 1779.984
Devonshire Building | 2016-12-16 19:30 | 49422.2436 | 1720.008
Devonshire Building | 2016-12-16 19:45 | 49422.6636 | 1680.012
Devonshire Building | 2016-12-16 20:00 | 49423.0836 | 1680.012
Devonshire Building | 2016-12-16 20:15 | 49423.4986 | 1659.996
Devonshire Building | 2016-12-16 20:30 | 49423.9136 | 1659.996
Devonshire Building | 2016-12-16 20:45 | 49424.3236 | 1640.016
Devonshire Building | 2016-12-16 21:00 | 49424.7336 | 1640.016
Devonshire Building | 2016-12-16 21:15 | 49425.1386 | 1620
Devonshire Building | 2016-12-16 21:30 | 49425.5486 | 1640.016
Devonshire Building | 2016-12-16 21:45 | 49425.9536 | 1620
Devonshire Building | 2016-12-16 22:00 | 49426.3786 | 1699.992
Devonshire Building | 2016-12-16 22:15 | 49426.7786 | 1599.984
Devonshire Building | 2016-12-16 22:30 | 49427.1786 | 1599.984
Devonshire Building | 2016-12-16 22:45 | 49427.5786 | 1599.984
Devonshire Building | 2016-12-16 23:00 | 49427.9786 | 1599.984
Devonshire Building | 2016-12-16 23:15 | 49428.3786 | 1599.984
Devonshire Building | 2016-12-16 23:30 | 49428.7786 | 1599.984
Devonshire Building | 2016-12-16 23:45 | 49429.1836 | 1620 | 1580.004
Devonshire Building | 2016-12-17 | 49429.5859 | 1599.984
Devonshire Building | 2016-12-17 00:15 | 49429.9909 | 1620
Devonshire Building | 2016-12-17 00:30 | 49430.3909 | 1599.984
Devonshire Building | 2016-12-17 00:45 | 49430.7959 | 1620
Devonshire Building | 2016-12-17 01:00 | 49431.1959 | 1599.984
Devonshire Building | 2016-12-17 01:15 | 49431.6009 | 1620
Devonshire Building | 2016-12-17 01:30 | 49432.0059 | 1620
Devonshire Building | 2016-12-17 01:45 | 49432.4059 | 1599.984
Devonshire Building | 2016-12-17 02:00 | 49432.8109 | 1620
Devonshire Building | 2016-12-17 02:15 | 49433.2159 | 1620
Devonshire Building | 2016-12-17 02:30 | 49433.6159 | 1599.984
Devonshire Building | 2016-12-17 02:45 | 49434.0209 | 1620
Devonshire Building | 2016-12-17 03:00 | 49434.4259 | 1620
Devonshire Building | 2016-12-17 03:15 | 49434.8259 | 1599.984
Devonshire Building | 2016-12-17 03:30 | 49435.2309 | 1620
Devonshire Building | 2016-12-17 03:45 | 49435.8909 | 2639.988
Devonshire Building | 2016-12-17 04:00 | 49436.2909 | 1599.984
Devonshire Building | 2016-12-17 04:15 | 49436.6959 | 1620
Devonshire Building | 2016-12-17 04:30 | 49437.0959 | 1599.984
Devonshire Building | 2016-12-17 04:45 | 49437.5009 | 1620
Devonshire Building | 2016-12-17 05:00 | 49437.9059 | 1620
Devonshire Building | 2016-12-17 05:15 | 49438.3059 | 1599.984
Devonshire Building | 2016-12-17 05:30 | 49438.7109 | 1620
Devonshire Building | 2016-12-17 05:45 | 49439.1159 | 1620
Devonshire Building | 2016-12-17 06:00 | 49439.5209 | 1620
Devonshire Building | 2016-12-17 06:15 | 49439.9259 | 1620
Devonshire Building | 2016-12-17 06:30 | 49440.3309 | 1620
Devonshire Building | 2016-12-17 06:45 | 49440.7409 | 1640.016
Devonshire Building | 2016-12-17 07:00 | 49441.1459 | 1620
Devonshire Building | 2016-12-17 07:15 | 49441.5509 | 1620
Devonshire Building | 2016-12-17 07:30 | 49441.9559 | 1620
Devonshire Building | 2016-12-17 07:45 | 49442.3609 | 1620
Devonshire Building | 2016-12-17 08:00 | 49442.7759 | 1659.996
Devonshire Building | 2016-12-17 08:15 | 49443.1909 | 1659.996
Devonshire Building | 2016-12-17 08:30 | 49443.6109 | 1680.012
Devonshire Building | 2016-12-17 08:45 | 49444.0309 | 1680.012
Devonshire Building | 2016-12-17 09:00 | 49444.4459 | 1659.996
Devonshire Building | 2016-12-17 09:15 | 49444.8609 | 1659.996
Devonshire Building | 2016-12-17 09:30 | 49445.2809 | 1680.012
Devonshire Building | 2016-12-17 09:45 | 49445.7009 | 1680.012
Devonshire Building | 2016-12-17 10:00 | 49446.1109 | 1640.016
Devonshire Building | 2016-12-17 10:15 | 49446.5109 | 1599.984
Devonshire Building | 2016-12-17 10:30 | 49446.9159 | 1620
Devonshire Building | 2016-12-17 10:45 | 49447.3209 | 1620
Devonshire Building | 2016-12-17 11:00 | 49447.7259 | 1620
Devonshire Building | 2016-12-17 11:15 | 49448.1259 | 1599.984
Devonshire Building | 2016-12-17 11:30 | 49448.5309 | 1620
Devonshire Building | 2016-12-17 11:45 | 49448.9359 | 1620
Devonshire Building | 2016-12-17 12:00 | 49449.3359 | 1599.984
Devonshire Building | 2016-12-17 12:15 | 49449.7459 | 1640.016
Devonshire Building | 2016-12-17 12:30 | 49450.1559 | 1640.016
Devonshire Building | 2016-12-17 12:45 | 49450.5709 | 1659.996
Devonshire Building | 2016-12-17 13:00 | 49451.2609 | 2760.012
Devonshire Building | 2016-12-17 13:15 | 49451.6659 | 1620
Devonshire Building | 2016-12-17 13:30 | 49452.0709 | 1620
Devonshire Building | 2016-12-17 13:45 | 49452.4759 | 1620
Devonshire Building | 2016-12-17 14:00 | 49452.8809 | 1620
Devonshire Building | 2016-12-17 14:15 | 49453.2859 | 1620
Devonshire Building | 2016-12-17 14:30 | 49453.6959 | 1640.016
Devonshire Building | 2016-12-17 14:45 | 49454.1059 | 1640.016
Devonshire Building | 2016-12-17 15:00 | 49454.5109 | 1620
Devonshire Building | 2016-12-17 15:15 | 49454.9209 | 1640.016
Devonshire Building | 2016-12-17 15:30 | 49455.3309 | 1640.016
Devonshire Building | 2016-12-17 15:45 | 49455.7409 | 1640.016
Devonshire Building | 2016-12-17 16:00 | 49456.1409 | 1599.984
Devonshire Building | 2016-12-17 16:15 | 49456.5509 | 1640.016
Devonshire Building | 2016-12-17 16:30 | 49457.2459 | 2779.992
Devonshire Building | 2016-12-17 16:45 | 49457.6509 | 1620
Devonshire Building | 2016-12-17 17:00 | 49458.0609 | 1640.016
Devonshire Building | 2016-12-17 17:15 | 49458.4709 | 1640.016
Devonshire Building | 2016-12-17 17:30 | 49458.8809 | 1640.016
Devonshire Building | 2016-12-17 17:45 | 49459.291 | 1640.016
Devonshire Building | 2016-12-17 18:00 | 49459.706 | 1659.996
Devonshire Building | 2016-12-17 18:15 | 49460.116 | 1640.016
Devonshire Building | 2016-12-17 18:30 | 49460.531 | 1659.996
Devonshire Building | 2016-12-17 18:45 | 49460.946 | 1659.996
Devonshire Building | 2016-12-17 19:00 | 49461.361 | 1659.996
Devonshire Building | 2016-12-17 19:15 | 49461.776 | 1659.996
Devonshire Building | 2016-12-17 19:30 | 49462.196 | 1680.012
Devonshire Building | 2016-12-17 19:45 | 49462.611 | 1659.996
Devonshire Building | 2016-12-17 20:00 | 49463.026 | 1659.996
Devonshire Building | 2016-12-17 20:15 | 49463.441 | 1659.996
Devonshire Building | 2016-12-17 20:30 | 49463.856 | 1659.996
Devonshire Building | 2016-12-17 20:45 | 49464.2709 | 1659.996
Devonshire Building | 2016-12-17 21:00 | 49464.6859 | 1659.996
Devonshire Building | 2016-12-17 21:15 | 49465.1009 | 1659.996
Devonshire Building | 2016-12-17 21:30 | 49465.5159 | 1659.996
Devonshire Building | 2016-12-17 21:45 | 49465.9309 | 1659.996
Devonshire Building | 2016-12-17 22:00 | 49466.3659 | 1739.988
Devonshire Building | 2016-12-17 22:15 | 49466.7759 | 1640.016
Devonshire Building | 2016-12-17 22:30 | 49467.186 | 1640.016
Devonshire Building | 2016-12-17 22:45 | 49467.601 | 1659.996
Devonshire Building | 2016-12-17 23:00 | 49468.011 | 1640.016
Devonshire Building | 2016-12-17 23:15 | 49468.421 | 1640.016
Devonshire Building | 2016-12-17 23:30 | 49468.831 | 1640.016
Devonshire Building | 2016-12-17 23:45 | 49469.241 | 1640.016 | 1599.984
Devonshire Building | 2016-12-18 | 49469.6484 | 1640.016
Devonshire Building | 2016-12-18 00:15 | 49470.0584 | 1640.016
Devonshire Building | 2016-12-18 00:30 | 49470.4684 | 1640.016
Devonshire Building | 2016-12-18 00:45 | 49470.8834 | 1659.996
Devonshire Building | 2016-12-18 01:00 | 49471.2935 | 1640.016
Devonshire Building | 2016-12-18 01:15 | 49471.7084 | 1659.996
Devonshire Building | 2016-12-18 01:30 | 49472.1185 | 1640.016
Devonshire Building | 2016-12-18 01:45 | 49472.5335 | 1659.996
Devonshire Building | 2016-12-18 02:00 | 49472.9435 | 1640.016
Devonshire Building | 2016-12-18 02:15 | 49473.3585 | 1659.996
Devonshire Building | 2016-12-18 02:30 | 49473.7685 | 1640.016
Devonshire Building | 2016-12-18 02:45 | 49474.1785 | 1640.016
Devonshire Building | 2016-12-18 03:00 | 49474.5935 | 1659.996
Devonshire Building | 2016-12-18 03:15 | 49475.0035 | 1640.016
Devonshire Building | 2016-12-18 03:30 | 49475.4185 | 1659.996
Devonshire Building | 2016-12-18 03:45 | 49475.8285 | 1640.016
Devonshire Building | 2016-12-18 04:00 | 49476.2435 | 1659.996
Devonshire Building | 2016-12-18 04:15 | 49476.6535 | 1640.016
Devonshire Building | 2016-12-18 04:30 | 49477.0685 | 1659.996
Devonshire Building | 2016-12-18 04:45 | 49477.4785 | 1640.016
Devonshire Building | 2016-12-18 05:00 | 49477.8935 | 1659.996
Devonshire Building | 2016-12-18 05:15 | 49478.3085 | 1659.996
Devonshire Building | 2016-12-18 05:30 | 49478.7185 | 1640.016
Devonshire Building | 2016-12-18 05:45 | 49479.1335 | 1659.996
Devonshire Building | 2016-12-18 06:00 | 49479.5435 | 1640.016
Devonshire Building | 2016-12-18 06:15 | 49479.9585 | 1659.996
Devonshire Building | 2016-12-18 06:30 | 49480.3685 | 1640.016
Devonshire Building | 2016-12-18 06:45 | 49480.7785 | 1640.016
Devonshire Building | 2016-12-18 07:00 | 49481.1885 | 1640.016
Devonshire Building | 2016-12-18 07:15 | 49481.5985 | 1640.016
Devonshire Building | 2016-12-18 07:30 | 49482.0085 | 1640.016
Devonshire Building | 2016-12-18 07:45 | 49482.4335 | 1699.992
Devonshire Building | 2016-12-18 08:00 | 49482.8535 | 1680.012
Devonshire Building | 2016-12-18 08:15 | 49483.2785 | 1699.992
Devonshire Building | 2016-12-18 08:30 | 49483.6985 | 1680.012
Devonshire Building | 2016-12-18 08:45 | 49484.1185 | 1680.012
Devonshire Building | 2016-12-18 09:00 | 49484.5385 | 1680.012
Devonshire Building | 2016-12-18 09:15 | 49484.9585 | 1680.012
Devonshire Building | 2016-12-18 09:30 | 49485.3735 | 1659.996
Devonshire Building | 2016-12-18 09:45 | 49485.7885 | 1659.996
Devonshire Building | 2016-12-18 10:00 | 49486.2035 | 1659.996
Devonshire Building | 2016-12-18 10:15 | 49486.6185 | 1659.996
Devonshire Building | 2016-12-18 10:30 | 49487.0185 | 1599.984
Devonshire Building | 2016-12-18 10:45 | 49487.4235 | 1620
Devonshire Building | 2016-12-18 11:00 | 49487.8235 | 1599.984
Devonshire Building | 2016-12-18 11:15 | 49488.2235 | 1599.984
Devonshire Building | 2016-12-18 11:30 | 49488.6285 | 1620
Devonshire Building | 2016-12-18 11:45 | 49489.0285 | 1599.984
Devonshire Building | 2016-12-18 12:00 | 49489.4335 | 1620
Devonshire Building | 2016-12-18 12:15 | 49489.8385 | 1620
Devonshire Building | 2016-12-18 12:30 | 49490.2435 | 1620
Devonshire Building | 2016-12-18 12:45 | 49490.6485 | 1620
Devonshire Building | 2016-12-18 13:00 | 49491.0535 | 1620
Devonshire Building | 2016-12-18 13:15 | 49491.4585 | 1620
Devonshire Building | 2016-12-18 13:30 | 49491.8685 | 1640.016
Devonshire Building | 2016-12-18 13:45 | 49492.2785 | 1640.016
Devonshire Building | 2016-12-18 14:00 | 49492.6885 | 1640.016
Devonshire Building | 2016-12-18 14:15 | 49493.0935 | 1620
Devonshire Building | 2016-12-18 14:30 | 49493.7135 | 2480.004
Devonshire Building | 2016-12-18 14:45 | 49494.1685 | 1820.016
Devonshire Building | 2016-12-18 15:00 | 49494.5735 | 1620
Devonshire Building | 2016-12-18 15:15 | 49494.9835 | 1640.016
Devonshire Building | 2016-12-18 15:30 | 49495.3885 | 1620
Devonshire Building | 2016-12-18 15:45 | 49495.7985 | 1640.016
Devonshire Building | 2016-12-18 16:00 | 49496.2035 | 1620
Devonshire Building | 2016-12-18 16:15 | 49496.6135 | 1640.016
Devonshire Building | 2016-12-18 16:30 | 49497.0185 | 1620
Devonshire Building | 2016-12-18 16:45 | 49497.4285 | 1640.016
Devonshire Building | 2016-12-18 17:00 | 49497.8335 | 1620
Devonshire Building | 2016-12-18 17:15 | 49498.2435 | 1640.016
Devonshire Building | 2016-12-18 17:30 | 49498.6485 | 1620
Devonshire Building | 2016-12-18 17:45 | 49499.0535 | 1620
Devonshire Building | 2016-12-18 18:00 | 49499.4585 | 1620
Devonshire Building | 2016-12-18 18:15 | 49499.8685 | 1640.016
Devonshire Building | 2016-12-18 18:30 | 49500.2735 | 1620
Devonshire Building | 2016-12-18 18:45 | 49500.6785 | 1620
Devonshire Building | 2016-12-18 19:00 | 49501.0835 | 1620
Devonshire Building | 2016-12-18 19:15 | 49501.4885 | 1620
Devonshire Building | 2016-12-18 19:30 | 49501.8935 | 1620
Devonshire Building | 2016-12-18 19:45 | 49502.2985 | 1620
Devonshire Building | 2016-12-18 20:00 | 49502.7035 | 1620
Devonshire Building | 2016-12-18 20:15 | 49503.1085 | 1620
Devonshire Building | 2016-12-18 20:30 | 49503.5135 | 1620
Devonshire Building | 2016-12-18 20:45 | 49503.9185 | 1620
Devonshire Building | 2016-12-18 21:00 | 49504.3285 | 1640.016
Devonshire Building | 2016-12-18 21:15 | 49504.7335 | 1620
Devonshire Building | 2016-12-18 21:30 | 49505.1435 | 1640.016
Devonshire Building | 2016-12-18 21:45 | 49505.5485 | 1620
Devonshire Building | 2016-12-18 22:00 | 49505.9635 | 1659.996
Devonshire Building | 2016-12-18 22:15 | 49506.3685 | 1620
Devonshire Building | 2016-12-18 22:30 | 49506.7785 | 1640.016
Devonshire Building | 2016-12-18 22:45 | 49507.1885 | 1640.016
Devonshire Building | 2016-12-18 23:00 | 49507.5986 | 1640.016
Devonshire Building | 2016-12-18 23:15 | 49508.0086 | 1640.016
Devonshire Building | 2016-12-18 23:30 | 49508.4186 | 1640.016
Devonshire Building | 2016-12-18 23:45 | 49508.8336 | 1659.996 | 1599.984
Devonshire Building | 2016-12-19 | 49509.2461 | 1640.016
Devonshire Building | 2016-12-19 00:15 | 49509.6611 | 1659.996
Devonshire Building | 2016-12-19 00:30 | 49510.0711 | 1640.016
Devonshire Building | 2016-12-19 00:45 | 49510.4811 | 1640.016
Devonshire Building | 2016-12-19 01:00 | 49510.8961 | 1659.996
Devonshire Building | 2016-12-19 01:15 | 49511.3061 | 1640.016
Devonshire Building | 2016-12-19 01:30 | 49511.7161 | 1640.016
Devonshire Building | 2016-12-19 01:45 | 49512.1311 | 1659.996
Devonshire Building | 2016-12-19 02:00 | 49512.5411 | 1640.016
Devonshire Building | 2016-12-19 02:15 | 49512.9561 | 1659.996
Devonshire Building | 2016-12-19 02:30 | 49513.3661 | 1640.016
Devonshire Building | 2016-12-19 02:45 | 49513.7761 | 1640.016
Devonshire Building | 2016-12-19 03:00 | 49514.1861 | 1640.016
Devonshire Building | 2016-12-19 03:15 | 49514.6011 | 1659.996
Devonshire Building | 2016-12-19 03:30 | 49515.0111 | 1640.016
Devonshire Building | 2016-12-19 03:45 | 49515.4211 | 1640.016
Devonshire Building | 2016-12-19 04:00 | 49515.8311 | 1640.016
Devonshire Building | 2016-12-19 04:15 | 49516.2411 | 1640.016
Devonshire Building | 2016-12-19 04:30 | 49516.6511 | 1640.016
Devonshire Building | 2016-12-19 04:45 | 49517.0611 | 1640.016
Devonshire Building | 2016-12-19 05:00 | 49517.4711 | 1640.016
Devonshire Building | 2016-12-19 05:15 | 49517.8811 | 1640.016
Devonshire Building | 2016-12-19 05:30 | 49518.2912 | 1640.016
Devonshire Building | 2016-12-19 05:45 | 49518.7062 | 1659.996
Devonshire Building | 2016-12-19 06:00 | 49519.1162 | 1640.016
Devonshire Building | 2016-12-19 06:15 | 49519.5212 | 1620
Devonshire Building | 2016-12-19 06:30 | 49519.9312 | 1640.016
Devonshire Building | 2016-12-19 06:45 | 49520.3412 | 1640.016
Devonshire Building | 2016-12-19 07:00 | 49520.7462 | 1620
Devonshire Building | 2016-12-19 07:15 | 49521.1562 | 1640.016
Devonshire Building | 2016-12-19 07:30 | 49521.5612 | 1620
Devonshire Building | 2016-12-19 07:45 | 49521.9812 | 1680.012
Devonshire Building | 2016-12-19 08:00 | 49522.4062 | 1699.992
Devonshire Building | 2016-12-19 08:15 | 49522.8212 | 1659.996
Devonshire Building | 2016-12-19 08:30 | 49523.2412 | 1680.012
Devonshire Building | 2016-12-19 08:45 | 49523.6712 | 1720.008
Devonshire Building | 2016-12-19 09:00 | 49524.1262 | 1820.016
Devonshire Building | 2016-12-19 09:15 | 49524.8162 | 2760.012
Devonshire Building | 2016-12-19 09:30 | 49525.2362 | 1680.012
Devonshire Building | 2016-12-19 09:45 | 49525.6512 | 1659.996
Devonshire Building | 2016-12-19 10:00 | 49526.0712 | 1680.012
Devonshire Building | 2016-12-19 10:15 | 49526.4962 | 1699.992
Devonshire Building | 2016-12-19 10:30 | 49526.9612 | 1860.012
Devonshire Building | 2016-12-19 10:45 | 49527.7962 | 3340.008
Devonshire Building | 2016-12-19 11:00 | 49528.3462 | 2199.996
Devonshire Building | 2016-12-19 11:15 | 49528.8512 | 2019.996
Devonshire Building | 2016-12-19 11:30 | 49529.3362 | 1940.004
Devonshire Building | 2016-12-19 11:45 | 49529.8262 | 1959.984
Devonshire Building | 2016-12-19 12:00 | 49530.4512 | 2499.984
Devonshire Building | 2016-12-19 12:15 | 49531.1012 | 2599.992
Devonshire Building | 2016-12-19 12:30 | 49531.6762 | 2300.004
Devonshire Building | 2016-12-19 12:45 | 49532.2412 | 2260.008
Devonshire Building | 2016-12-19 13:00 | 49532.7712 | 2120.004
Devonshire Building | 2016-12-19 13:15 | 49533.2812 | 2040.012
Devonshire Building | 2016-12-19 13:30 | 49533.7562 | 1900.008
Devonshire Building | 2016-12-19 13:45 | 49534.4712 | 2859.984
Devonshire Building | 2016-12-19 14:00 | 49534.8912 | 1680.012
Devonshire Building | 2016-12-19 14:15 | 49535.3112 | 1680.012
Devonshire Building | 2016-12-19 14:30 | 49535.7462 | 1739.988
Devonshire Building | 2016-12-19 14:45 | 49536.1812 | 1739.988
Devonshire Building | 2016-12-19 15:00 | 49536.6162 | 1739.988
Devonshire Building | 2016-12-19 15:15 | 49537.0512 | 1739.988
Devonshire Building | 2016-12-19 15:30 | 49537.4862 | 1739.988
Devonshire Building | 2016-12-19 15:45 | 49538.2212 | 2940.012
Devonshire Building | 2016-12-19 16:00 | 49538.6562 | 1739.988
Devonshire Building | 2016-12-19 16:15 | 49539.0962 | 1760.004
Devonshire Building | 2016-12-19 16:30 | 49539.5462 | 1800
Devonshire Building | 2016-12-19 16:45 | 49539.9962 | 1800
Devonshire Building | 2016-12-19 17:00 | 49540.4412 | 1779.984
Devonshire Building | 2016-12-19 17:15 | 49540.8862 | 1779.984
Devonshire Building | 2016-12-19 17:30 | 49541.3212 | 1739.988
Devonshire Building | 2016-12-19 17:45 | 49541.9912 | 2679.984
Devonshire Building | 2016-12-19 18:00 | 49542.5112 | 2080.008
Devonshire Building | 2016-12-19 18:15 | 49542.9512 | 1760.004
Devonshire Building | 2016-12-19 18:30 | 49543.3512 | 1599.984
Devonshire Building | 2016-12-19 18:45 | 49544.2262 | 3499.992
Devonshire Building | 2016-12-19 19:00 | 49544.9462 | 2880
Devonshire Building | 2016-12-19 19:15 | 49545.4812 | 2139.984
Devonshire Building | 2016-12-19 19:30 | 49545.9512 | 1879.992
Devonshire Building | 2016-12-19 19:45 | 49546.4062 | 1820.016
Devonshire Building | 2016-12-19 20:00 | 49546.8462 | 1760.004
Devonshire Building | 2016-12-19 20:15 | 49547.2812 | 1739.988
Devonshire Building | 2016-12-19 20:30 | 49547.7161 | 1739.988
Devonshire Building | 2016-12-19 20:45 | 49548.1462 | 1720.008
Devonshire Building | 2016-12-19 21:00 | 49548.5711 | 1699.992
Devonshire Building | 2016-12-19 21:15 | 49548.9961 | 1699.992
Devonshire Building | 2016-12-19 21:30 | 49549.4211 | 1699.992
Devonshire Building | 2016-12-19 21:45 | 49549.8461 | 1699.992
Devonshire Building | 2016-12-19 22:00 | 49550.2711 | 1699.992
Devonshire Building | 2016-12-19 22:15 | 49550.6911 | 1680.012
Devonshire Building | 2016-12-19 22:30 | 49551.1111 | 1680.012
Devonshire Building | 2016-12-19 22:45 | 49551.5361 | 1699.992
Devonshire Building | 2016-12-19 23:00 | 49551.9561 | 1680.012
Devonshire Building | 2016-12-19 23:15 | 49552.3762 | 1680.012
Devonshire Building | 2016-12-19 23:30 | 49552.7962 | 1680.012
Devonshire Building | 2016-12-19 23:45 | 49553.2162 | 1680.012 | 1599.984
Devonshire Building | 2016-12-20 | 49553.6328 | 1680.012
Devonshire Building | 2016-12-20 00:15 | 49554.0578 | 1699.992
Devonshire Building | 2016-12-20 00:30 | 49554.4778 | 1680.012
Devonshire Building | 2016-12-20 00:45 | 49554.9028 | 1699.992
Devonshire Building | 2016-12-20 01:00 | 49555.3228 | 1680.012
Devonshire Building | 2016-12-20 01:15 | 49555.7478 | 1699.992
Devonshire Building | 2016-12-20 01:30 | 49556.1678 | 1680.012
Devonshire Building | 2016-12-20 01:45 | 49556.5878 | 1680.012
Devonshire Building | 2016-12-20 02:00 | 49557.0128 | 1699.992
Devonshire Building | 2016-12-20 02:15 | 49557.4328 | 1680.012
Devonshire Building | 2016-12-20 02:30 | 49557.8528 | 1680.012
Devonshire Building | 2016-12-20 02:45 | 49558.2728 | 1680.012
Devonshire Building | 2016-12-20 03:00 | 49558.6978 | 1699.992
Devonshire Building | 2016-12-20 03:15 | 49559.1178 | 1680.012
Devonshire Building | 2016-12-20 03:30 | 49559.5378 | 1680.012
Devonshire Building | 2016-12-20 03:45 | 49559.9578 | 1680.012
Devonshire Building | 2016-12-20 04:00 | 49560.3778 | 1680.012
Devonshire Building | 2016-12-20 04:15 | 49560.7978 | 1680.012
Devonshire Building | 2016-12-20 04:30 | 49561.2178 | 1680.012
Devonshire Building | 2016-12-20 04:45 | 49561.6378 | 1680.012
Devonshire Building | 2016-12-20 05:00 | 49562.0578 | 1680.012
Devonshire Building | 2016-12-20 05:15 | 49562.4778 | 1680.012
Devonshire Building | 2016-12-20 05:30 | 49562.8979 | 1680.012
Devonshire Building | 2016-12-20 05:45 | 49563.3179 | 1680.012
Devonshire Building | 2016-12-20 06:00 | 49563.7329 | 1659.996
Devonshire Building | 2016-12-20 06:15 | 49564.1529 | 1680.012
Devonshire Building | 2016-12-20 06:30 | 49564.5729 | 1680.012
Devonshire Building | 2016-12-20 06:45 | 49564.9929 | 1680.012
Devonshire Building | 2016-12-20 07:00 | 49565.4079 | 1659.996
Devonshire Building | 2016-12-20 07:15 | 49565.8229 | 1659.996
Devonshire Building | 2016-12-20 07:30 | 49566.2429 | 1680.012
Devonshire Building | 2016-12-20 07:45 | 49566.6729 | 1720.008
Devonshire Building | 2016-12-20 08:00 | 49567.1079 | 1739.988
Devonshire Building | 2016-12-20 08:15 | 49567.5429 | 1739.988
Devonshire Building | 2016-12-20 08:30 | 49567.9779 | 1739.988
Devonshire Building | 2016-12-20 08:45 | 49568.4079 | 1720.008
Devonshire Building | 2016-12-20 09:00 | 49568.8429 | 1739.988
Devonshire Building | 2016-12-20 09:15 | 49569.2679 | 1699.992
Devonshire Building | 2016-12-20 09:30 | 49569.9629 | 2779.992
Devonshire Building | 2016-12-20 09:45 | 49570.3929 | 1720.008
Devonshire Building | 2016-12-20 10:00 | 49570.8179 | 1699.992
Devonshire Building | 2016-12-20 10:15 | 49571.2428 | 1699.992
Devonshire Building | 2016-12-20 10:30 | 49571.6629 | 1680.012
Devonshire Building | 2016-12-20 10:45 | 49572.0729 | 1640.016
Devonshire Building | 2016-12-20 11:00 | 49572.4929 | 1680.012
Devonshire Building | 2016-12-20 11:15 | 49573.2179 | 2900.016
Devonshire Building | 2016-12-20 11:30 | 49573.6329 | 1659.996
Devonshire Building | 2016-12-20 11:45 | 49574.0629 | 1720.008
Devonshire Building | 2016-12-20 12:00 | 49574.5079 | 1779.984
Devonshire Building | 2016-12-20 12:15 | 49574.9679 | 1839.996
Devonshire Building | 2016-12-20 12:30 | 49575.4329 | 1860.012
Devonshire Building | 2016-12-20 12:45 | 49575.8929 | 1839.996
Devonshire Building | 2016-12-20 13:00 | 49576.6379 | 2980.008
Devonshire Building | 2016-12-20 13:15 | 49577.1079 | 1879.992
Devonshire Building | 2016-12-20 13:30 | 49577.5929 | 1940.004
Devonshire Building | 2016-12-20 13:45 | 49578.0829 | 1959.984
Devonshire Building | 2016-12-20 14:00 | 49578.5979 | 2059.992
Devonshire Building | 2016-12-20 14:15 | 49579.1079 | 2040.012
Devonshire Building | 2016-12-20 14:30 | 49579.6229 | 2059.992
Devonshire Building | 2016-12-20 14:45 | 49580.1229 | 2000.016
Devonshire Building | 2016-12-20 15:00 | 49580.8129 | 2760.012
Devonshire Building | 2016-12-20 15:15 | 49581.3479 | 2139.984
Devonshire Building | 2016-12-20 15:30 | 49581.8129 | 1860.012
Devonshire Building | 2016-12-20 15:45 | 49582.2729 | 1839.996
Devonshire Building | 2016-12-20 16:00 | 49582.7179 | 1779.984
Devonshire Building | 2016-12-20 16:15 | 49583.1629 | 1779.984
Devonshire Building | 2016-12-20 16:30 | 49583.6029 | 1760.004
Devonshire Building | 2016-12-20 16:45 | 49584.0529 | 1800
Devonshire Building | 2016-12-20 17:00 | 49584.4929 | 1760.004
Devonshire Building | 2016-12-20 17:15 | 49584.9379 | 1779.984
Devonshire Building | 2016-12-20 17:30 | 49585.6629 | 2900.016
Devonshire Building | 2016-12-20 17:45 | 49586.1029 | 1760.004
Devonshire Building | 2016-12-20 18:00 | 49586.5429 | 1760.004
Devonshire Building | 2016-12-20 18:15 | 49586.9829 | 1760.004
Devonshire Building | 2016-12-20 18:30 | 49587.4279 | 1779.984
Devonshire Building | 2016-12-20 18:45 | 49587.8629 | 1739.988
Devonshire Building | 2016-12-20 19:00 | 49588.3029 | 1760.004
Devonshire Building | 2016-12-20 19:15 | 49588.7378 | 1739.988
Devonshire Building | 2016-12-20 19:30 | 49589.1728 | 1739.988
Devonshire Building | 2016-12-20 19:45 | 49589.6028 | 1720.008
Devonshire Building | 2016-12-20 20:00 | 49590.0329 | 1720.008
Devonshire Building | 2016-12-20 20:15 | 49590.4578 | 1699.992
Devonshire Building | 2016-12-20 20:30 | 49590.8879 | 1720.008
Devonshire Building | 2016-12-20 20:45 | 49591.3128 | 1699.992
Devonshire Building | 2016-12-20 21:00 | 49591.7378 | 1699.992
Devonshire Building | 2016-12-20 21:15 | 49592.1628 | 1699.992
Devonshire Building | 2016-12-20 21:30 | 49592.5878 | 1699.992
Devonshire Building | 2016-12-20 21:45 | 49593.0128 | 1699.992
Devonshire Building | 2016-12-20 22:00 | 49593.4428 | 1720.008
Devonshire Building | 2016-12-20 22:15 | 49593.8628 | 1680.012
Devonshire Building | 2016-12-20 22:30 | 49594.2828 | 1680.012
Devonshire Building | 2016-12-20 22:45 | 49594.7029 | 1680.012
Devonshire Building | 2016-12-20 23:00 | 49595.1229 | 1680.012
Devonshire Building | 2016-12-20 23:15 | 49595.5429 | 1680.012
Devonshire Building | 2016-12-20 23:30 | 49595.9629 | 1680.012
Devonshire Building | 2016-12-20 23:45 | 49596.3829 | 1680.012 | 1640.016
Devonshire Building | 2016-12-21 | 49596.8086 | 1699.992
Devonshire Building | 2016-12-21 00:15 | 49597.2286 | 1680.012
Devonshire Building | 2016-12-21 00:30 | 49597.6536 | 1699.992
Devonshire Building | 2016-12-21 00:45 | 49598.0736 | 1680.012
Devonshire Building | 2016-12-21 01:00 | 49598.4986 | 1699.992
Devonshire Building | 2016-12-21 01:15 | 49598.9186 | 1680.012
Devonshire Building | 2016-12-21 01:30 | 49599.3436 | 1699.992
Devonshire Building | 2016-12-21 01:45 | 49599.7636 | 1680.012
Devonshire Building | 2016-12-21 02:00 | 49600.1886 | 1699.992
Devonshire Building | 2016-12-21 02:15 | 49600.6086 | 1680.012
Devonshire Building | 2016-12-21 02:30 | 49601.0336 | 1699.992
Devonshire Building | 2016-12-21 02:45 | 49601.4536 | 1680.012
Devonshire Building | 2016-12-21 03:00 | 49601.8786 | 1699.992
Devonshire Building | 2016-12-21 03:15 | 49602.2986 | 1680.012
Devonshire Building | 2016-12-21 03:30 | 49602.7236 | 1699.992
Devonshire Building | 2016-12-21 03:45 | 49603.1436 | 1680.012
Devonshire Building | 2016-12-21 04:00 | 49603.5686 | 1699.992
Devonshire Building | 2016-12-21 04:15 | 49603.9936 | 1699.992
Devonshire Building | 2016-12-21 04:30 | 49604.4136 | 1680.012
Devonshire Building | 2016-12-21 04:45 | 49604.8336 | 1680.012
Devonshire Building | 2016-12-21 05:00 | 49605.2586 | 1699.992
Devonshire Building | 2016-12-21 05:15 | 49605.6786 | 1680.012
Devonshire Building | 2016-12-21 05:30 | 49606.0986 | 1680.012
Devonshire Building | 2016-12-21 05:45 | 49606.5186 | 1680.012
Devonshire Building | 2016-12-21 06:00 | 49606.9386 | 1680.012
Devonshire Building | 2016-12-21 06:15 | 49607.3586 | 1680.012
Devonshire Building | 2016-12-21 06:30 | 49607.7786 | 1680.012
Devonshire Building | 2016-12-21 06:45 | 49608.1986 | 1680.012
Devonshire Building | 2016-12-21 07:00 | 49608.6136 | 1659.996
Devonshire Building | 2016-12-21 07:15 | 49609.0286 | 1659.996
Devonshire Building | 2016-12-21 07:30 | 49609.4486 | 1680.012
Devonshire Building | 2016-12-21 07:45 | 49609.8786 | 1720.008
Devonshire Building | 2016-12-21 08:00 | 49610.3086 | 1720.008
Devonshire Building | 2016-12-21 08:15 | 49610.7536 | 1779.984
Devonshire Building | 2016-12-21 08:30 | 49611.1886 | 1739.988
Devonshire Building | 2016-12-21 08:45 | 49611.6136 | 1699.992
Devonshire Building | 2016-12-21 09:00 | 49612.0436 | 1720.008
Devonshire Building | 2016-12-21 09:15 | 49612.7436 | 2800.008
Devonshire Building | 2016-12-21 09:30 | 49613.1686 | 1699.992
Devonshire Building | 2016-12-21 09:45 | 49613.5986 | 1720.008
Devonshire Building | 2016-12-21 10:00 | 49614.0286 | 1720.008
Devonshire Building | 2016-12-21 10:15 | 49614.4536 | 1699.992
Devonshire Building | 2016-12-21 10:30 | 49614.8786 | 1699.992
Devonshire Building | 2016-12-21 10:45 | 49615.2886 | 1640.016
Devonshire Building | 2016-12-21 11:00 | 49615.6986 | 1640.016
Devonshire Building | 2016-12-21 11:15 | 49616.1086 | 1640.016
Devonshire Building | 2016-12-21 11:30 | 49616.8086 | 2800.008
Devonshire Building | 2016-12-21 11:45 | 49617.2186 | 1640.016
Devonshire Building | 2016-12-21 12:00 | 49617.6336 | 1659.996
Devonshire Building | 2016-12-21 12:15 | 49618.0486 | 1659.996
Devonshire Building | 2016-12-21 12:30 | 49618.4586 | 1640.016
Devonshire Building | 2016-12-21 12:45 | 49618.8786 | 1680.012
Devonshire Building | 2016-12-21 13:00 | 49619.3086 | 1720.008
Devonshire Building | 2016-12-21 13:15 | 49620.0486 | 2959.992
Devonshire Building | 2016-12-21 13:30 | 49620.5136 | 1860.012
Devonshire Building | 2016-12-21 13:45 | 49620.9786 | 1860.012
Devonshire Building | 2016-12-21 14:00 | 49621.4386 | 1839.996
Devonshire Building | 2016-12-21 14:15 | 49621.8937 | 1820.016
Devonshire Building | 2016-12-21 14:30 | 49622.3487 | 1820.016
Devonshire Building | 2016-12-21 14:45 | 49622.8037 | 1820.016
Devonshire Building | 2016-12-21 15:00 | 49623.2537 | 1800
Devonshire Building | 2016-12-21 15:15 | 49623.7037 | 1800
Devonshire Building | 2016-12-21 15:30 | 49624.1537 | 1800
Devonshire Building | 2016-12-21 15:45 | 49624.6087 | 1820.016
Devonshire Building | 2016-12-21 16:00 | 49625.0687 | 1839.996
Devonshire Building | 2016-12-21 16:15 | 49625.8237 | 3020.004
Devonshire Building | 2016-12-21 16:30 | 49626.3237 | 2000.016
Devonshire Building | 2016-12-21 16:45 | 49626.8187 | 1980
Devonshire Building | 2016-12-21 17:00 | 49627.3087 | 1959.984
Devonshire Building | 2016-12-21 17:15 | 49627.7937 | 1940.004
Devonshire Building | 2016-12-21 17:30 | 49628.2587 | 1860.012
Devonshire Building | 2016-12-21 17:45 | 49628.7187 | 1839.996
Devonshire Building | 2016-12-21 18:00 | 49629.1687 | 1800
Devonshire Building | 2016-12-21 18:15 | 49629.6137 | 1779.984
Devonshire Building | 2016-12-21 18:30 | 49630.0487 | 1739.988
Devonshire Building | 2016-12-21 18:45 | 49630.4837 | 1739.988
Devonshire Building | 2016-12-21 19:00 | 49630.9137 | 1720.008
Devonshire Building | 2016-12-21 19:15 | 49631.3437 | 1720.008
Devonshire Building | 2016-12-21 19:30 | 49631.7737 | 1720.008
Devonshire Building | 2016-12-21 19:45 | 49632.2037 | 1720.008
Devonshire Building | 2016-12-21 20:00 | 49632.6287 | 1699.992
Devonshire Building | 2016-12-21 20:15 | 49633.0537 | 1699.992
Devonshire Building | 2016-12-21 20:30 | 49633.4837 | 1720.008
Devonshire Building | 2016-12-21 20:45 | 49633.9087 | 1699.992
Devonshire Building | 2016-12-21 21:00 | 49634.3337 | 1699.992
Devonshire Building | 2016-12-21 21:15 | 49634.7587 | 1699.992
Devonshire Building | 2016-12-21 21:30 | 49635.1887 | 1720.008
Devonshire Building | 2016-12-21 21:45 | 49635.6137 | 1699.992
Devonshire Building | 2016-12-21 22:00 | 49636.0587 | 1779.984
Devonshire Building | 2016-12-21 22:15 | 49636.4787 | 1680.012
Devonshire Building | 2016-12-21 22:30 | 49637.3137 | 3340.008
Devonshire Building | 2016-12-21 22:45 | 49637.7387 | 1699.992
Devonshire Building | 2016-12-21 23:00 | 49638.1587 | 1680.012
Devonshire Building | 2016-12-21 23:15 | 49638.5837 | 1699.992
Devonshire Building | 2016-12-21 23:30 | 49639.0037 | 1680.012
Devonshire Building | 2016-12-21 23:45 | 49639.4287 | 1699.992 | 1640.016
Devonshire Building | 2016-12-22 | 49639.8555 | 1699.992
Devonshire Building | 2016-12-22 00:15 | 49640.2755 | 1680.012
Devonshire Building | 2016-12-22 00:30 | 49640.7005 | 1699.992
Devonshire Building | 2016-12-22 00:45 | 49641.1255 | 1699.992
Devonshire Building | 2016-12-22 01:00 | 49641.5505 | 1699.992
Devonshire Building | 2016-12-22 01:15 | 49641.9755 | 1699.992
Devonshire Building | 2016-12-22 01:30 | 49642.4005 | 1699.992
Devonshire Building | 2016-12-22 01:45 | 49642.8255 | 1699.992
Devonshire Building | 2016-12-22 02:00 | 49643.2505 | 1699.992
Devonshire Building | 2016-12-22 02:15 | 49643.6755 | 1699.992
Devonshire Building | 2016-12-22 02:30 | 49644.1005 | 1699.992
Devonshire Building | 2016-12-22 02:45 | 49644.5255 | 1699.992
Devonshire Building | 2016-12-22 03:00 | 49644.9505 | 1699.992
Devonshire Building | 2016-12-22 03:15 | 49645.3705 | 1680.012
Devonshire Building | 2016-12-22 03:30 | 49645.7955 | 1699.992
Devonshire Building | 2016-12-22 03:45 | 49646.2205 | 1699.992
Devonshire Building | 2016-12-22 04:00 | 49646.6405 | 1680.012
Devonshire Building | 2016-12-22 04:15 | 49647.0655 | 1699.992
Devonshire Building | 2016-12-22 04:30 | 49647.4904 | 1699.992
Devonshire Building | 2016-12-22 04:45 | 49647.9154 | 1699.992
Devonshire Building | 2016-12-22 05:00 | 49648.3404 | 1699.992
Devonshire Building | 2016-12-22 05:15 | 49648.7654 | 1699.992
Devonshire Building | 2016-12-22 05:30 | 49649.1904 | 1699.992
Devonshire Building | 2016-12-22 05:45 | 49649.6154 | 1699.992
Devonshire Building | 2016-12-22 06:00 | 49650.0404 | 1699.992
Devonshire Building | 2016-12-22 06:15 | 49650.4604 | 1680.012
Devonshire Building | 2016-12-22 06:30 | 49650.8854 | 1699.992
Devonshire Building | 2016-12-22 06:45 | 49651.3054 | 1680.012
Devonshire Building | 2016-12-22 07:00 | 49651.7304 | 1699.992
Devonshire Building | 2016-12-22 07:15 | 49652.1454 | 1659.996
Devonshire Building | 2016-12-22 07:30 | 49652.5704 | 1699.992
Devonshire Building | 2016-12-22 07:45 | 49653.0154 | 1779.984
Devonshire Building | 2016-12-22 08:00 | 49653.4554 | 1760.004
Devonshire Building | 2016-12-22 08:15 | 49653.8954 | 1760.004
Devonshire Building | 2016-12-22 08:30 | 49654.3204 | 1699.992
Devonshire Building | 2016-12-22 08:45 | 49654.7454 | 1699.992
Devonshire Building | 2016-12-22 09:00 | 49655.1704 | 1699.992
Devonshire Building | 2016-12-22 09:15 | 49655.5954 | 1699.992
Devonshire Building | 2016-12-22 09:30 | 49656.0204 | 1699.992
Devonshire Building | 2016-12-22 09:45 | 49656.4504 | 1720.008
Devonshire Building | 2016-12-22 10:00 | 49657.4054 | 3819.996
Devonshire Building | 2016-12-22 10:15 | 49657.8354 | 1720.008
Devonshire Building | 2016-12-22 10:30 | 49658.2554 | 1680.012
Devonshire Building | 2016-12-22 10:45 | 49658.6654 | 1640.016
Devonshire Building | 2016-12-22 11:00 | 49659.0904 | 1699.992
Devonshire Building | 2016-12-22 11:15 | 49659.6254 | 2139.984
Devonshire Building | 2016-12-22 11:30 | 49660.2404 | 2459.988
Devonshire Building | 2016-12-22 11:45 | 49660.7854 | 2180.016
Devonshire Building | 2016-12-22 12:00 | 49661.2804 | 1980
Devonshire Building | 2016-12-22 12:15 | 49661.7504 | 1879.992
Devonshire Building | 2016-12-22 12:30 | 49662.2104 | 1839.996
Devonshire Building | 2016-12-22 12:45 | 49663.2104 | 3999.996
Devonshire Building | 2016-12-22 13:00 | 49663.6754 | 1860.012
Devonshire Building | 2016-12-22 13:15 | 49664.1504 | 1900.008
Devonshire Building | 2016-12-22 13:30 | 49664.6304 | 1919.988
Devonshire Building | 2016-12-22 13:45 | 49665.1154 | 1940.004
Devonshire Building | 2016-12-22 14:00 | 49665.6254 | 2040.012
Devonshire Building | 2016-12-22 14:15 | 49666.1354 | 2040.012
Devonshire Building | 2016-12-22 14:30 | 49666.6354 | 2000.016
Devonshire Building | 2016-12-22 14:45 | 49667.1204 | 1940.004
Devonshire Building | 2016-12-22 15:00 | 49667.5904 | 1879.992
Devonshire Building | 2016-12-22 15:15 | 49668.0604 | 1879.992
Devonshire Building | 2016-12-22 15:30 | 49669.0504 | 3960
Devonshire Building | 2016-12-22 15:45 | 49669.5054 | 1820.016
Devonshire Building | 2016-12-22 16:00 | 49669.9604 | 1820.016
Devonshire Building | 2016-12-22 16:15 | 49670.4104 | 1800
Devonshire Building | 2016-12-22 16:30 | 49670.8604 | 1800
Devonshire Building | 2016-12-22 16:45 | 49671.3254 | 1860.012
Devonshire Building | 2016-12-22 17:00 | 49671.7804 | 1820.016
Devonshire Building | 2016-12-22 17:15 | 49672.2355 | 1820.016
Devonshire Building | 2016-12-22 17:30 | 49672.6804 | 1779.984
Devonshire Building | 2016-12-22 17:45 | 49673.1254 | 1779.984
Devonshire Building | 2016-12-22 18:00 | 49673.5654 | 1760.004
Devonshire Building | 2016-12-22 18:15 | 49674.0004 | 1739.988
Devonshire Building | 2016-12-22 18:30 | 49674.4354 | 1739.988
Devonshire Building | 2016-12-22 18:45 | 49674.8654 | 1720.008
Devonshire Building | 2016-12-22 19:00 | 49675.2954 | 1720.008
Devonshire Building | 2016-12-22 19:15 | 49675.7204 | 1699.992
Devonshire Building | 2016-12-22 19:30 | 49676.1504 | 1720.008
Devonshire Building | 2016-12-22 19:45 | 49676.5754 | 1699.992
Devonshire Building | 2016-12-22 20:00 | 49677.0004 | 1699.992
Devonshire Building | 2016-12-22 20:15 | 49677.4304 | 1720.008
Devonshire Building | 2016-12-22 20:30 | 49677.8554 | 1699.992
Devonshire Building | 2016-12-22 20:45 | 49678.2804 | 1699.992
Devonshire Building | 2016-12-22 21:00 | 49678.7054 | 1699.992
Devonshire Building | 2016-12-22 21:15 | 49679.1304 | 1699.992
Devonshire Building | 2016-12-22 21:30 | 49679.5604 | 1720.008
Devonshire Building | 2016-12-22 21:45 | 49679.9854 | 1699.992
Devonshire Building | 2016-12-22 22:00 | 49680.4354 | 1800
Devonshire Building | 2016-12-22 22:15 | 49680.8604 | 1699.992
Devonshire Building | 2016-12-22 22:30 | 49681.2854 | 1699.992
Devonshire Building | 2016-12-22 22:45 | 49681.7104 | 1699.992
Devonshire Building | 2016-12-22 23:00 | 49682.1404 | 1720.008
Devonshire Building | 2016-12-22 23:15 | 49682.5654 | 1699.992
Devonshire Building | 2016-12-22 23:30 | 49682.9904 | 1699.992
Devonshire Building | 2016-12-22 23:45 | 49683.4204 | 1720.008 | 1640.016
Devonshire Building | 2016-12-23 | 49683.8438 | 1699.992
Devonshire Building | 2016-12-23 00:15 | 49684.2738 | 1720.008
Devonshire Building | 2016-12-23 00:30 | 49684.7038 | 1720.008
Devonshire Building | 2016-12-23 00:45 | 49685.1288 | 1699.992
Devonshire Building | 2016-12-23 01:00 | 49685.5588 | 1720.008
Devonshire Building | 2016-12-23 01:15 | 49685.9888 | 1720.008
Devonshire Building | 2016-12-23 01:30 | 49686.4188 | 1720.008
Devonshire Building | 2016-12-23 01:45 | 49686.8488 | 1720.008
Devonshire Building | 2016-12-23 02:00 | 49687.2738 | 1699.992
Devonshire Building | 2016-12-23 02:15 | 49687.7038 | 1720.008
Devonshire Building | 2016-12-23 02:30 | 49688.1288 | 1699.992
Devonshire Building | 2016-12-23 02:45 | 49688.5588 | 1720.008
Devonshire Building | 2016-12-23 03:00 | 49688.9888 | 1720.008
Devonshire Building | 2016-12-23 03:15 | 49689.4188 | 1720.008
Devonshire Building | 2016-12-23 03:30 | 49689.8488 | 1720.008
Devonshire Building | 2016-12-23 03:45 | 49690.2788 | 1720.008
Devonshire Building | 2016-12-23 04:00 | 49690.7038 | 1699.992
Devonshire Building | 2016-12-23 04:15 | 49691.1338 | 1720.008
Devonshire Building | 2016-12-23 04:30 | 49691.5588 | 1699.992
Devonshire Building | 2016-12-23 04:45 | 49691.9888 | 1720.008
Devonshire Building | 2016-12-23 05:00 | 49692.4138 | 1699.992
Devonshire Building | 2016-12-23 05:15 | 49692.8438 | 1720.008
Devonshire Building | 2016-12-23 05:30 | 49693.7738 | 3719.988
Devonshire Building | 2016-12-23 05:45 | 49694.1988 | 1699.992
Devonshire Building | 2016-12-23 06:00 | 49694.6288 | 1720.008
Devonshire Building | 2016-12-23 06:15 | 49695.0538 | 1699.992
Devonshire Building | 2016-12-23 06:30 | 49695.4788 | 1699.992
Devonshire Building | 2016-12-23 06:45 | 49695.9038 | 1699.992
Devonshire Building | 2016-12-23 07:00 | 49696.3288 | 1699.992
Devonshire Building | 2016-12-23 07:15 | 49696.7538 | 1699.992
Devonshire Building | 2016-12-23 07:30 | 49697.1788 | 1699.992
Devonshire Building | 2016-12-23 07:45 | 49697.6088 | 1720.008
Devonshire Building | 2016-12-23 08:00 | 49698.0488 | 1760.004
Devonshire Building | 2016-12-23 08:15 | 49698.4838 | 1739.988
Devonshire Building | 2016-12-23 08:30 | 49698.9238 | 1760.004
Devonshire Building | 2016-12-23 08:45 | 49699.3588 | 1739.988
Devonshire Building | 2016-12-23 09:00 | 49699.7888 | 1720.008
Devonshire Building | 2016-12-23 09:15 | 49700.2237 | 1739.988
Devonshire Building | 2016-12-23 09:30 | 49700.6587 | 1739.988
Devonshire Building | 2016-12-23 09:45 | 49701.0937 | 1739.988
Devonshire Building | 2016-12-23 10:00 | 49701.5287 | 1739.988
Devonshire Building | 2016-12-23 10:15 | 49701.9587 | 1720.008
Devonshire Building | 2016-12-23 10:30 | 49702.3837 | 1699.992
Devonshire Building | 2016-12-23 10:45 | 49702.8037 | 1680.012
Devonshire Building | 2016-12-23 11:00 | 49703.2237 | 1680.012
Devonshire Building | 2016-12-23 11:15 | 49703.6487 | 1699.992
Devonshire Building | 2016-12-23 11:30 | 49704.1037 | 1820.016
Devonshire Building | 2016-12-23 11:45 | 49704.6537 | 2199.996
Devonshire Building | 2016-12-23 12:00 | 49704.9087 | 1019.988
Devonshire Building | 2016-12-23 12:15 | 49704.9287 | 79.992
Devonshire Building | 2016-12-23 12:30 | 49704.9287 | 0
Devonshire Building | 2016-12-23 12:45 | 49704.9287 | 0
Devonshire Building | 2016-12-23 13:00 | 49704.9287 | 0
Devonshire Building | 2016-12-23 13:15 | 49704.9337 | 20.016
Devonshire Building | 2016-12-23 13:30 | 49704.9337 | 0
Devonshire Building | 2016-12-23 13:45 | 49704.9337 | 0
Devonshire Building | 2016-12-23 14:00 | 49704.9388 | 20.016
Devonshire Building | 2016-12-23 14:15 | 49704.9388 | 0
Devonshire Building | 2016-12-23 14:30 | 49704.9388 | 0
Devonshire Building | 2016-12-23 14:45 | 49704.9388 | 0
Devonshire Building | 2016-12-23 15:00 | 49704.9388 | 0
Devonshire Building | 2016-12-23 15:15 | 49704.9438 | 20.016
Devonshire Building | 2016-12-23 15:30 | 49704.9438 | 0
Devonshire Building | 2016-12-23 15:45 | 49704.9438 | 0
Devonshire Building | 2016-12-23 16:00 | 49704.9438 | 0
Devonshire Building | 2016-12-23 16:15 | 49704.9438 | 0
Devonshire Building | 2016-12-23 16:30 | 49704.9488 | 20.016
Devonshire Building | 2016-12-23 16:45 | 49704.9488 | 0
Devonshire Building | 2016-12-23 17:00 | 49704.9488 | 0
Devonshire Building | 2016-12-23 17:15 | 49704.9488 | 0
Devonshire Building | 2016-12-23 17:30 | 49704.9488 | 0
Devonshire Building | 2016-12-23 17:45 | 49704.9538 | 20.016
Devonshire Building | 2016-12-23 18:00 | 49704.9538 | 0
Devonshire Building | 2016-12-23 18:15 | 49704.9538 | 0
Devonshire Building | 2016-12-23 18:30 | 49704.9538 | 0
Devonshire Building | 2016-12-23 18:45 | 49704.9588 | 20.016
Devonshire Building | 2016-12-23 19:00 | 49704.9588 | 0
Devonshire Building | 2016-12-23 19:15 | 49704.9588 | 0
Devonshire Building | 2016-12-23 19:30 | 49704.9588 | 0
Devonshire Building | 2016-12-23 19:45 | 49704.9638 | 20.016
Devonshire Building | 2016-12-23 20:00 | 49704.9638 | 0
Devonshire Building | 2016-12-23 20:15 | 49704.9638 | 0
Devonshire Building | 2016-12-23 20:30 | 49704.9638 | 0
Devonshire Building | 2016-12-23 20:45 | 49704.9638 | 0
Devonshire Building | 2016-12-23 21:00 | 49704.9688 | 20.016
Devonshire Building | 2016-12-23 21:15 | 49704.9688 | 0
Devonshire Building | 2016-12-23 21:30 | 49704.9688 | 0
Devonshire Building | 2016-12-23 21:45 | 49704.9688 | 0
Devonshire Building | 2016-12-23 22:00 | 49704.9938 | 100.008
Devonshire Building | 2016-12-23 22:15 | 49704.9938 | 0
Devonshire Building | 2016-12-23 22:30 | 49704.9938 | 0
Devonshire Building | 2016-12-23 22:45 | 49704.9988 | 20.016
Devonshire Building | 2016-12-23 23:00 | 49704.9988 | 0
Devonshire Building | 2016-12-23 23:15 | 49704.9988 | 0
Devonshire Building | 2016-12-23 23:30 | 49704.9988 | 0
Devonshire Building | 2016-12-23 23:45 | 49705.0038 | 20.016 | 0
Devonshire Building | 2016-12-24 | 49705.0039 | 0
Devonshire Building | 2016-12-24 00:15 | 49705.0039 | 0
Devonshire Building | 2016-12-24 00:30 | 49705.0039 | 0
Devonshire Building | 2016-12-24 00:45 | 49705.0039 | 0
Devonshire Building | 2016-12-24 01:00 | 49705.0089 | 20.016
Devonshire Building | 2016-12-24 01:15 | 49705.0089 | 0
Devonshire Building | 2016-12-24 01:30 | 49705.0089 | 0
Devonshire Building | 2016-12-24 01:45 | 49705.0089 | 0
Devonshire Building | 2016-12-24 02:00 | 49705.0139 | 20.016
Devonshire Building | 2016-12-24 02:15 | 49705.0139 | 0
Devonshire Building | 2016-12-24 02:30 | 49705.0139 | 0
Devonshire Building | 2016-12-24 02:45 | 49705.0139 | 0
Devonshire Building | 2016-12-24 03:00 | 49705.0189 | 20.016
Devonshire Building | 2016-12-24 03:15 | 49705.0189 | 0
Devonshire Building | 2016-12-24 03:30 | 49705.0189 | 0
Devonshire Building | 2016-12-24 03:45 | 49705.0189 | 0
Devonshire Building | 2016-12-24 04:00 | 49705.0239 | 20.016
Devonshire Building | 2016-12-24 04:15 | 49705.0239 | 0
Devonshire Building | 2016-12-24 04:30 | 49705.0239 | 0
Devonshire Building | 2016-12-24 04:45 | 49705.0239 | 0
Devonshire Building | 2016-12-24 05:00 | 49705.0289 | 20.016
Devonshire Building | 2016-12-24 05:15 | 49705.0289 | 0
Devonshire Building | 2016-12-24 05:30 | 49705.0289 | 0
Devonshire Building | 2016-12-24 05:45 | 49705.0289 | 0
Devonshire Building | 2016-12-24 06:00 | 49705.0289 | 0
Devonshire Building | 2016-12-24 06:15 | 49705.0339 | 20.016
Devonshire Building | 2016-12-24 06:30 | 49705.0339 | 0
Devonshire Building | 2016-12-24 06:45 | 49705.0339 | 0
Devonshire Building | 2016-12-24 07:00 | 49705.0339 | 0
Devonshire Building | 2016-12-24 07:15 | 49705.0389 | 20.016
Devonshire Building | 2016-12-24 07:30 | 49705.0389 | 0
Devonshire Building | 2016-12-24 07:45 | 49705.0589 | 79.992
Devonshire Building | 2016-12-24 08:00 | 49705.0739 | 60.012
Devonshire Building | 2016-12-24 08:15 | 49705.0939 | 79.992
Devonshire Building | 2016-12-24 08:30 | 49705.1089 | 60.012
Devonshire Building | 2016-12-24 08:45 | 49705.1289 | 79.992
Devonshire Building | 2016-12-24 09:00 | 49705.1489 | 79.992
Devonshire Building | 2016-12-24 09:15 | 49705.1639 | 60.012
Devonshire Building | 2016-12-24 09:30 | 49705.1839 | 79.992
Devonshire Building | 2016-12-24 09:45 | 49705.1989 | 60.012
Devonshire Building | 2016-12-24 10:00 | 49705.2189 | 79.992
Devonshire Building | 2016-12-24 10:15 | 49705.2189 | 0
Devonshire Building | 2016-12-24 10:30 | 49705.2239 | 20.016
Devonshire Building | 2016-12-24 10:45 | 49705.2239 | 0
Devonshire Building | 2016-12-24 11:00 | 49705.2239 | 0
Devonshire Building | 2016-12-24 11:15 | 49705.2239 | 0
Devonshire Building | 2016-12-24 11:30 | 49705.2289 | 20.016
Devonshire Building | 2016-12-24 11:45 | 49705.2289 | 0
Devonshire Building | 2016-12-24 12:00 | 49705.2289 | 0
Devonshire Building | 2016-12-24 12:15 | 49705.2289 | 0
Devonshire Building | 2016-12-24 12:30 | 49705.234 | 20.016
Devonshire Building | 2016-12-24 12:45 | 49705.234 | 0
Devonshire Building | 2016-12-24 13:00 | 49705.234 | 0
Devonshire Building | 2016-12-24 13:15 | 49705.234 | 0
Devonshire Building | 2016-12-24 13:30 | 49705.234 | 0
Devonshire Building | 2016-12-24 13:45 | 49705.239 | 20.016
Devonshire Building | 2016-12-24 14:00 | 49705.239 | 0
Devonshire Building | 2016-12-24 14:15 | 49705.239 | 0
Devonshire Building | 2016-12-24 14:30 | 49705.239 | 0
Devonshire Building | 2016-12-24 14:45 | 49705.244 | 20.016
Devonshire Building | 2016-12-24 15:00 | 49705.244 | 0
Devonshire Building | 2016-12-24 15:15 | 49705.244 | 0
Devonshire Building | 2016-12-24 15:30 | 49705.244 | 0
Devonshire Building | 2016-12-24 15:45 | 49705.244 | 0
Devonshire Building | 2016-12-24 16:00 | 49705.249 | 20.016
Devonshire Building | 2016-12-24 16:15 | 49705.249 | 0
Devonshire Building | 2016-12-24 16:30 | 49705.249 | 0
Devonshire Building | 2016-12-24 16:45 | 49705.249 | 0
Devonshire Building | 2016-12-24 17:00 | 49705.254 | 20.016
Devonshire Building | 2016-12-24 17:15 | 49705.254 | 0
Devonshire Building | 2016-12-24 17:30 | 49705.254 | 0
Devonshire Building | 2016-12-24 17:45 | 49705.254 | 0
Devonshire Building | 2016-12-24 18:00 | 49705.569 | 1260
Devonshire Building | 2016-12-24 18:15 | 49705.774 | 820.008
Devonshire Building | 2016-12-24 18:30 | 49705.779 | 20.016
Devonshire Building | 2016-12-24 18:45 | 49705.779 | 0
Devonshire Building | 2016-12-24 19:00 | 49705.779 | 0
Devonshire Building | 2016-12-24 19:15 | 49705.779 | 0
Devonshire Building | 2016-12-24 19:30 | 49705.779 | 0
Devonshire Building | 2016-12-24 19:45 | 49705.784 | 20.016
Devonshire Building | 2016-12-24 20:00 | 49705.784 | 0
Devonshire Building | 2016-12-24 20:15 | 49705.784 | 0
Devonshire Building | 2016-12-24 20:30 | 49705.784 | 0
Devonshire Building | 2016-12-24 20:45 | 49705.789 | 20.016
Devonshire Building | 2016-12-24 21:00 | 49705.789 | 0
Devonshire Building | 2016-12-24 21:15 | 49705.789 | 0
Devonshire Building | 2016-12-24 21:30 | 49705.789 | 0
Devonshire Building | 2016-12-24 21:45 | 49705.794 | 20.016
Devonshire Building | 2016-12-24 22:00 | 49705.799 | 20.016
Devonshire Building | 2016-12-24 22:15 | 49705.799 | 0
Devonshire Building | 2016-12-24 22:30 | 49705.799 | 0
Devonshire Building | 2016-12-24 22:45 | 49705.799 | 0
Devonshire Building | 2016-12-24 23:00 | 49705.804 | 20.016
Devonshire Building | 2016-12-24 23:15 | 49705.804 | 0
Devonshire Building | 2016-12-24 23:30 | 49705.804 | 0
Devonshire Building | 2016-12-24 23:45 | 49705.804 | 0 | 0
Devonshire Building | 2016-12-25 | 49705.8047 | 0
Devonshire Building | 2016-12-25 00:15 | 49705.8097 | 20.016
Devonshire Building | 2016-12-25 00:30 | 49705.8097 | 0
Devonshire Building | 2016-12-25 00:45 | 49705.8097 | 0
Devonshire Building | 2016-12-25 01:00 | 49705.8097 | 0
Devonshire Building | 2016-12-25 01:15 | 49705.8147 | 20.016
Devonshire Building | 2016-12-25 01:30 | 49705.8147 | 0
Devonshire Building | 2016-12-25 01:45 | 49705.8147 | 0
Devonshire Building | 2016-12-25 02:00 | 49705.8147 | 0
Devonshire Building | 2016-12-25 02:15 | 49705.8197 | 20.016
Devonshire Building | 2016-12-25 02:30 | 49705.8197 | 0
Devonshire Building | 2016-12-25 02:45 | 49705.8197 | 0
Devonshire Building | 2016-12-25 03:00 | 49705.8197 | 0
Devonshire Building | 2016-12-25 03:15 | 49705.8197 | 0
Devonshire Building | 2016-12-25 03:30 | 49705.8197 | 0
Devonshire Building | 2016-12-25 03:45 | 49705.8247 | 20.016
Devonshire Building | 2016-12-25 04:00 | 49705.8247 | 0
Devonshire Building | 2016-12-25 04:15 | 49705.8247 | 0
Devonshire Building | 2016-12-25 04:30 | 49705.8247 | 0
Devonshire Building | 2016-12-25 04:45 | 49705.8247 | 0
Devonshire Building | 2016-12-25 05:00 | 49705.8247 | 0
Devonshire Building | 2016-12-25 05:15 | 49705.8297 | 20.016
Devonshire Building | 2016-12-25 05:30 | 49705.8297 | 0
Devonshire Building | 2016-12-25 05:45 | 49705.8297 | 0
Devonshire Building | 2016-12-25 06:00 | 49705.8297 | 0
Devonshire Building | 2016-12-25 06:15 | 49705.8297 | 0
Devonshire Building | 2016-12-25 06:30 | 49705.8297 | 0
Devonshire Building | 2016-12-25 06:45 | 49705.8347 | 20.016
Devonshire Building | 2016-12-25 07:00 | 49705.8347 | 0
Devonshire Building | 2016-12-25 07:15 | 49705.8347 | 0
Devonshire Building | 2016-12-25 07:30 | 49705.8347 | 0
Devonshire Building | 2016-12-25 07:45 | 49705.8497 | 60.012
Devonshire Building | 2016-12-25 08:00 | 49705.8647 | 60.012
Devonshire Building | 2016-12-25 08:15 | 49705.8847 | 79.992
Devonshire Building | 2016-12-25 08:30 | 49705.8997 | 60.012
Devonshire Building | 2016-12-25 08:45 | 49705.9197 | 79.992
Devonshire Building | 2016-12-25 09:00 | 49705.9347 | 60.012
Devonshire Building | 2016-12-25 09:15 | 49705.9547 | 79.992
Devonshire Building | 2016-12-25 09:30 | 49705.9697 | 60.012
Devonshire Building | 2016-12-25 09:45 | 49705.9897 | 79.992
Devonshire Building | 2016-12-25 10:00 | 49705.9997 | 39.996
Devonshire Building | 2016-12-25 10:15 | 49705.9997 | 0
Devonshire Building | 2016-12-25 10:30 | 49706.0047 | 20.016
Devonshire Building | 2016-12-25 10:45 | 49706.0047 | 0
Devonshire Building | 2016-12-25 11:00 | 49706.0047 | 0
Devonshire Building | 2016-12-25 11:15 | 49706.0047 | 0
Devonshire Building | 2016-12-25 11:30 | 49706.0047 | 0
Devonshire Building | 2016-12-25 11:45 | 49706.0047 | 0
Devonshire Building | 2016-12-25 12:00 | 49706.0097 | 20.016
Devonshire Building | 2016-12-25 12:15 | 49706.0097 | 0
Devonshire Building | 2016-12-25 12:30 | 49706.0097 | 0
Devonshire Building | 2016-12-25 12:45 | 49706.0097 | 0
Devonshire Building | 2016-12-25 13:00 | 49706.0097 | 0
Devonshire Building | 2016-12-25 13:15 | 49706.0097 | 0
Devonshire Building | 2016-12-25 13:30 | 49706.0147 | 20.016
Devonshire Building | 2016-12-25 13:45 | 49706.0147 | 0
Devonshire Building | 2016-12-25 14:00 | 49706.0147 | 0
Devonshire Building | 2016-12-25 14:15 | 49706.0147 | 0
Devonshire Building | 2016-12-25 14:30 | 49706.0147 | 0
Devonshire Building | 2016-12-25 14:45 | 49706.0297 | 60.012
Devonshire Building | 2016-12-25 15:00 | 49706.0497 | 79.992
Devonshire Building | 2016-12-25 15:15 | 49706.0647 | 60.012
Devonshire Building | 2016-12-25 15:30 | 49706.0797 | 60.012
Devonshire Building | 2016-12-25 15:45 | 49706.0997 | 79.992
Devonshire Building | 2016-12-25 16:00 | 49706.1147 | 60.012
Devonshire Building | 2016-12-25 16:15 | 49706.1347 | 79.992
Devonshire Building | 2016-12-25 16:30 | 49706.1497 | 60.012
Devonshire Building | 2016-12-25 16:45 | 49706.1697 | 79.992
Devonshire Building | 2016-12-25 17:00 | 49706.1847 | 60.012
Devonshire Building | 2016-12-25 17:15 | 49706.1997 | 60.012
Devonshire Building | 2016-12-25 17:30 | 49706.2197 | 79.992
Devonshire Building | 2016-12-25 17:45 | 49706.2347 | 60.012
Devonshire Building | 2016-12-25 18:00 | 49706.2547 | 79.992
Devonshire Building | 2016-12-25 18:15 | 49706.2697 | 60.012
Devonshire Building | 2016-12-25 18:30 | 49706.2897 | 79.992
Devonshire Building | 2016-12-25 18:45 | 49706.3047 | 60.012
Devonshire Building | 2016-12-25 19:00 | 49706.3247 | 79.992
Devonshire Building | 2016-12-25 19:15 | 49706.3347 | 39.996
Devonshire Building | 2016-12-25 19:30 | 49706.3397 | 20.016
Devonshire Building | 2016-12-25 19:45 | 49706.3397 | 0
Devonshire Building | 2016-12-25 20:00 | 49706.3397 | 0
Devonshire Building | 2016-12-25 20:15 | 49706.3397 | 0
Devonshire Building | 2016-12-25 20:30 | 49706.3397 | 0
Devonshire Building | 2016-12-25 20:45 | 49706.3397 | 0
Devonshire Building | 2016-12-25 21:00 | 49706.3448 | 20.016
Devonshire Building | 2016-12-25 21:15 | 49706.3448 | 0
Devonshire Building | 2016-12-25 21:30 | 49706.3448 | 0
Devonshire Building | 2016-12-25 21:45 | 49706.3448 | 0
Devonshire Building | 2016-12-25 22:00 | 49706.3698 | 100.008
Devonshire Building | 2016-12-25 22:15 | 49706.3698 | 0
Devonshire Building | 2016-12-25 22:30 | 49706.3698 | 0
Devonshire Building | 2016-12-25 22:45 | 49706.3698 | 0
Devonshire Building | 2016-12-25 23:00 | 49706.3748 | 20.016
Devonshire Building | 2016-12-25 23:15 | 49706.3748 | 0
Devonshire Building | 2016-12-25 23:30 | 49706.3748 | 0
Devonshire Building | 2016-12-25 23:45 | 49706.3748 | 0 | 0
Devonshire Building | 2016-12-26 | 49706.375 | 0
Devonshire Building | 2016-12-26 00:15 | 49706.38 | 20.016
Devonshire Building | 2016-12-26 00:30 | 49706.38 | 0
Devonshire Building | 2016-12-26 00:45 | 49706.38 | 0
Devonshire Building | 2016-12-26 01:00 | 49706.38 | 0
Devonshire Building | 2016-12-26 01:15 | 49706.385 | 20.016
Devonshire Building | 2016-12-26 01:30 | 49706.385 | 0
Devonshire Building | 2016-12-26 01:45 | 49706.385 | 0
Devonshire Building | 2016-12-26 02:00 | 49706.385 | 0
Devonshire Building | 2016-12-26 02:15 | 49706.385 | 0
Devonshire Building | 2016-12-26 02:30 | 49706.39 | 20.016
Devonshire Building | 2016-12-26 02:45 | 49706.39 | 0
Devonshire Building | 2016-12-26 03:00 | 49706.39 | 0
Devonshire Building | 2016-12-26 03:15 | 49706.39 | 0
Devonshire Building | 2016-12-26 03:30 | 49706.39 | 0
Devonshire Building | 2016-12-26 03:45 | 49706.395 | 20.016
Devonshire Building | 2016-12-26 04:00 | 49706.395 | 0
Devonshire Building | 2016-12-26 04:15 | 49706.395 | 0
Devonshire Building | 2016-12-26 04:30 | 49706.395 | 0
Devonshire Building | 2016-12-26 04:45 | 49706.395 | 0
Devonshire Building | 2016-12-26 05:00 | 49706.4 | 20.016
Devonshire Building | 2016-12-26 05:15 | 49706.4 | 0
Devonshire Building | 2016-12-26 05:30 | 49706.4 | 0
Devonshire Building | 2016-12-26 05:45 | 49706.4 | 0
Devonshire Building | 2016-12-26 06:00 | 49706.4 | 0
Devonshire Building | 2016-12-26 06:15 | 49706.405 | 20.016
Devonshire Building | 2016-12-26 06:30 | 49706.665 | 1040.004
Devonshire Building | 2016-12-26 06:45 | 49706.665 | 0
Devonshire Building | 2016-12-26 07:00 | 49706.665 | 0
Devonshire Building | 2016-12-26 07:15 | 49706.67 | 20.016
Devonshire Building | 2016-12-26 07:30 | 49706.67 | 0
Devonshire Building | 2016-12-26 07:45 | 49706.67 | 0
Devonshire Building | 2016-12-26 08:00 | 49706.67 | 0
Devonshire Building | 2016-12-26 08:15 | 49706.675 | 20.016
Devonshire Building | 2016-12-26 08:30 | 49706.675 | 0
Devonshire Building | 2016-12-26 08:45 | 49706.675 | 0
Devonshire Building | 2016-12-26 09:00 | 49706.675 | 0
Devonshire Building | 2016-12-26 09:15 | 49706.675 | 0
Devonshire Building | 2016-12-26 09:30 | 49706.68 | 20.016
Devonshire Building | 2016-12-26 09:45 | 49706.68 | 0
Devonshire Building | 2016-12-26 10:00 | 49706.68 | 0
Devonshire Building | 2016-12-26 10:15 | 49706.68 | 0
Devonshire Building | 2016-12-26 10:30 | 49706.68 | 0
Devonshire Building | 2016-12-26 10:45 | 49706.685 | 20.016
Devonshire Building | 2016-12-26 11:00 | 49706.685 | 0
Devonshire Building | 2016-12-26 11:15 | 49706.685 | 0
Devonshire Building | 2016-12-26 11:30 | 49706.685 | 0
Devonshire Building | 2016-12-26 11:45 | 49706.69 | 20.016
Devonshire Building | 2016-12-26 12:00 | 49706.69 | 0
Devonshire Building | 2016-12-26 12:15 | 49706.69 | 0
Devonshire Building | 2016-12-26 12:30 | 49706.69 | 0
Devonshire Building | 2016-12-26 12:45 | 49706.69 | 0
Devonshire Building | 2016-12-26 13:00 | 49706.695 | 20.016
Devonshire Building | 2016-12-26 13:15 | 49706.695 | 0
Devonshire Building | 2016-12-26 13:30 | 49706.705 | 39.996
Devonshire Building | 2016-12-26 13:45 | 49706.7201 | 60.012
Devonshire Building | 2016-12-26 14:00 | 49706.74 | 79.992
Devonshire Building | 2016-12-26 14:15 | 49706.7651 | 100.008
Devonshire Building | 2016-12-26 14:30 | 49706.7801 | 60.012
Devonshire Building | 2016-12-26 14:45 | 49706.8001 | 79.992
Devonshire Building | 2016-12-26 15:00 | 49706.8151 | 60.012
Devonshire Building | 2016-12-26 15:15 | 49706.8351 | 79.992
Devonshire Building | 2016-12-26 15:30 | 49706.8501 | 60.012
Devonshire Building | 2016-12-26 15:45 | 49706.8701 | 79.992
Devonshire Building | 2016-12-26 16:00 | 49706.8751 | 20.016
Devonshire Building | 2016-12-26 16:15 | 49706.8801 | 20.016
Devonshire Building | 2016-12-26 16:30 | 49706.8801 | 0
Devonshire Building | 2016-12-26 16:45 | 49706.8801 | 0
Devonshire Building | 2016-12-26 17:00 | 49706.8801 | 0
Devonshire Building | 2016-12-26 17:15 | 49706.8801 | 0
Devonshire Building | 2016-12-26 17:30 | 49706.8851 | 20.016
Devonshire Building | 2016-12-26 17:45 | 49706.8851 | 0
Devonshire Building | 2016-12-26 18:00 | 49706.8851 | 0
Devonshire Building | 2016-12-26 18:15 | 49706.8851 | 0
Devonshire Building | 2016-12-26 18:30 | 49706.8901 | 20.016
Devonshire Building | 2016-12-26 18:45 | 49706.8901 | 0
Devonshire Building | 2016-12-26 19:00 | 49706.8901 | 0
Devonshire Building | 2016-12-26 19:15 | 49706.8901 | 0
Devonshire Building | 2016-12-26 19:30 | 49706.8901 | 0
Devonshire Building | 2016-12-26 19:45 | 49706.8951 | 20.016
Devonshire Building | 2016-12-26 20:00 | 49706.8951 | 0
Devonshire Building | 2016-12-26 20:15 | 49706.8951 | 0
Devonshire Building | 2016-12-26 20:30 | 49706.8951 | 0
Devonshire Building | 2016-12-26 20:45 | 49706.8951 | 0
Devonshire Building | 2016-12-26 21:00 | 49706.9001 | 20.016
Devonshire Building | 2016-12-26 21:15 | 49706.9001 | 0
Devonshire Building | 2016-12-26 21:30 | 49706.9001 | 0
Devonshire Building | 2016-12-26 21:45 | 49706.9001 | 0
Devonshire Building | 2016-12-26 22:00 | 49706.9151 | 60.012
Devonshire Building | 2016-12-26 22:15 | 49706.9151 | 0
Devonshire Building | 2016-12-26 22:30 | 49706.9151 | 0
Devonshire Building | 2016-12-26 22:45 | 49706.9151 | 0
Devonshire Building | 2016-12-26 23:00 | 49706.9201 | 20.016
Devonshire Building | 2016-12-26 23:15 | 49706.9201 | 0
Devonshire Building | 2016-12-26 23:30 | 49706.9201 | 0
Devonshire Building | 2016-12-26 23:45 | 49706.9201 | 0 | 0
Devonshire Building | 2016-12-27 | 49706.9258 | 20.016
Devonshire Building | 2016-12-27 00:15 | 49706.9258 | 0
Devonshire Building | 2016-12-27 00:30 | 49706.9258 | 0
Devonshire Building | 2016-12-27 00:45 | 49706.9258 | 0
Devonshire Building | 2016-12-27 01:00 | 49706.9258 | 0
Devonshire Building | 2016-12-27 01:15 | 49706.9308 | 20.016
Devonshire Building | 2016-12-27 01:30 | 49706.9308 | 0
Devonshire Building | 2016-12-27 01:45 | 49706.9308 | 0
Devonshire Building | 2016-12-27 02:00 | 49706.9308 | 0
Devonshire Building | 2016-12-27 02:15 | 49706.9358 | 20.016
Devonshire Building | 2016-12-27 02:30 | 49706.9358 | 0
Devonshire Building | 2016-12-27 02:45 | 49706.9358 | 0
Devonshire Building | 2016-12-27 03:00 | 49706.9358 | 0
Devonshire Building | 2016-12-27 03:15 | 49706.9358 | 0
Devonshire Building | 2016-12-27 03:30 | 49706.9408 | 20.016
Devonshire Building | 2016-12-27 03:45 | 49706.9408 | 0
Devonshire Building | 2016-12-27 04:00 | 49706.9408 | 0
Devonshire Building | 2016-12-27 04:15 | 49706.9408 | 0
Devonshire Building | 2016-12-27 04:30 | 49706.9458 | 20.016
Devonshire Building | 2016-12-27 04:45 | 49706.9458 | 0
Devonshire Building | 2016-12-27 05:00 | 49706.9458 | 0
Devonshire Building | 2016-12-27 05:15 | 49706.9458 | 0
Devonshire Building | 2016-12-27 05:30 | 49706.9508 | 20.016
Devonshire Building | 2016-12-27 05:45 | 49706.9508 | 0
Devonshire Building | 2016-12-27 06:00 | 49706.9508 | 0
Devonshire Building | 2016-12-27 06:15 | 49706.9508 | 0
Devonshire Building | 2016-12-27 06:30 | 49706.9508 | 0
Devonshire Building | 2016-12-27 06:45 | 49706.9558 | 20.016
Devonshire Building | 2016-12-27 07:00 | 49706.9558 | 0
Devonshire Building | 2016-12-27 07:15 | 49706.9558 | 0
Devonshire Building | 2016-12-27 07:30 | 49706.9558 | 0
Devonshire Building | 2016-12-27 07:45 | 49706.9608 | 20.016
Devonshire Building | 2016-12-27 08:00 | 49706.9708 | 39.996
Devonshire Building | 2016-12-27 08:15 | 49706.9908 | 79.992
Devonshire Building | 2016-12-27 08:30 | 49707.0058 | 60.012
Devonshire Building | 2016-12-27 08:45 | 49707.0258 | 79.992
Devonshire Building | 2016-12-27 09:00 | 49707.0408 | 60.012
Devonshire Building | 2016-12-27 09:15 | 49707.0608 | 79.992
Devonshire Building | 2016-12-27 09:30 | 49707.0758 | 60.012
Devonshire Building | 2016-12-27 09:45 | 49707.0958 | 79.992
Devonshire Building | 2016-12-27 10:00 | 49707.0958 | 0
Devonshire Building | 2016-12-27 10:15 | 49707.1008 | 20.016
Devonshire Building | 2016-12-27 10:30 | 49707.1008 | 0
Devonshire Building | 2016-12-27 10:45 | 49707.1008 | 0
Devonshire Building | 2016-12-27 11:00 | 49707.1008 | 0
Devonshire Building | 2016-12-27 11:15 | 49707.1058 | 20.016
Devonshire Building | 2016-12-27 11:30 | 49707.1058 | 0
Devonshire Building | 2016-12-27 11:45 | 49707.1058 | 0
Devonshire Building | 2016-12-27 12:00 | 49707.1108 | 20.016
Devonshire Building | 2016-12-27 12:15 | 49707.1108 | 0
Devonshire Building | 2016-12-27 12:30 | 49707.1108 | 0
Devonshire Building | 2016-12-27 12:45 | 49707.1158 | 20.016
Devonshire Building | 2016-12-27 13:00 | 49707.1158 | 0
Devonshire Building | 2016-12-27 13:15 | 49707.1158 | 0
Devonshire Building | 2016-12-27 13:30 | 49707.1258 | 39.996
Devonshire Building | 2016-12-27 13:45 | 49707.1258 | 0
Devonshire Building | 2016-12-27 14:00 | 49707.1258 | 0
Devonshire Building | 2016-12-27 14:15 | 49707.1258 | 0
Devonshire Building | 2016-12-27 14:30 | 49707.4008 | 1100.016
Devonshire Building | 2016-12-27 14:45 | 49707.4008 | 0
Devonshire Building | 2016-12-27 15:00 | 49707.4008 | 0
Devonshire Building | 2016-12-27 15:15 | 49707.4058 | 20.016
Devonshire Building | 2016-12-27 15:30 | 49707.4058 | 0
Devonshire Building | 2016-12-27 15:45 | 49707.4058 | 0
Devonshire Building | 2016-12-27 16:00 | 49707.4108 | 20.016
Devonshire Building | 2016-12-27 16:15 | 49707.4108 | 0
Devonshire Building | 2016-12-27 16:30 | 49707.4108 | 0
Devonshire Building | 2016-12-27 16:45 | 49707.4108 | 0
Devonshire Building | 2016-12-27 17:00 | 49707.4158 | 20.016
Devonshire Building | 2016-12-27 17:15 | 49707.4158 | 0
Devonshire Building | 2016-12-27 17:30 | 49707.4158 | 0
Devonshire Building | 2016-12-27 17:45 | 49707.4208 | 20.016
Devonshire Building | 2016-12-27 18:00 | 49707.4208 | 0
Devonshire Building | 2016-12-27 18:15 | 49707.4208 | 0
Devonshire Building | 2016-12-27 18:30 | 49707.4208 | 0
Devonshire Building | 2016-12-27 18:45 | 49707.4258 | 20.016
Devonshire Building | 2016-12-27 19:00 | 49707.4258 | 0
Devonshire Building | 2016-12-27 19:15 | 49707.4258 | 0
Devonshire Building | 2016-12-27 19:30 | 49707.4258 | 0
Devonshire Building | 2016-12-27 19:45 | 49707.4309 | 20.016
Devonshire Building | 2016-12-27 20:00 | 49707.4309 | 0
Devonshire Building | 2016-12-27 20:15 | 49707.4309 | 0
Devonshire Building | 2016-12-27 20:30 | 49707.4359 | 20.016
Devonshire Building | 2016-12-27 20:45 | 49707.4359 | 0
Devonshire Building | 2016-12-27 21:00 | 49707.4359 | 0
Devonshire Building | 2016-12-27 21:15 | 49707.4359 | 0
Devonshire Building | 2016-12-27 21:30 | 49707.4409 | 20.016
Devonshire Building | 2016-12-27 21:45 | 49707.4409 | 0
Devonshire Building | 2016-12-27 22:00 | 49707.4459 | 20.016
Devonshire Building | 2016-12-27 22:15 | 49707.4509 | 20.016
Devonshire Building | 2016-12-27 22:30 | 49707.4509 | 0
Devonshire Building | 2016-12-27 22:45 | 49707.4509 | 0
Devonshire Building | 2016-12-27 23:00 | 49707.4509 | 0
Devonshire Building | 2016-12-27 23:15 | 49707.4559 | 20.016
Devonshire Building | 2016-12-27 23:30 | 49707.4559 | 0
Devonshire Building | 2016-12-27 23:45 | 49707.4559 | 0 | 0
Devonshire Building | 2016-12-28 | 49707.4609 | 20.016
Devonshire Building | 2016-12-28 00:15 | 49707.4609 | 0
Devonshire Building | 2016-12-28 00:30 | 49707.4609 | 0
Devonshire Building | 2016-12-28 00:45 | 49707.4609 | 0
Devonshire Building | 2016-12-28 01:00 | 49707.4659 | 20.016
Devonshire Building | 2016-12-28 01:15 | 49707.4659 | 0
Devonshire Building | 2016-12-28 01:30 | 49707.4659 | 0
Devonshire Building | 2016-12-28 01:45 | 49707.4659 | 0
Devonshire Building | 2016-12-28 02:00 | 49707.4709 | 20.016
Devonshire Building | 2016-12-28 02:15 | 49707.4709 | 0
Devonshire Building | 2016-12-28 02:30 | 49707.4709 | 0
Devonshire Building | 2016-12-28 02:45 | 49707.4709 | 0
Devonshire Building | 2016-12-28 03:00 | 49707.4709 | 0
Devonshire Building | 2016-12-28 03:15 | 49707.476 | 20.016
Devonshire Building | 2016-12-28 03:30 | 49707.476 | 0
Devonshire Building | 2016-12-28 03:45 | 49707.476 | 0
Devonshire Building | 2016-12-28 04:00 | 49707.476 | 0
Devonshire Building | 2016-12-28 04:15 | 49707.481 | 20.016
Devonshire Building | 2016-12-28 04:30 | 49707.481 | 0
Devonshire Building | 2016-12-28 04:45 | 49707.481 | 0
Devonshire Building | 2016-12-28 05:00 | 49707.481 | 0
Devonshire Building | 2016-12-28 05:15 | 49707.486 | 20.016
Devonshire Building | 2016-12-28 05:30 | 49707.486 | 0
Devonshire Building | 2016-12-28 05:45 | 49707.486 | 0
Devonshire Building | 2016-12-28 06:00 | 49707.486 | 0
Devonshire Building | 2016-12-28 06:15 | 49707.491 | 20.016
Devonshire Building | 2016-12-28 06:30 | 49707.491 | 0
Devonshire Building | 2016-12-28 06:45 | 49707.491 | 0
Devonshire Building | 2016-12-28 07:00 | 49707.491 | 0
Devonshire Building | 2016-12-28 07:15 | 49707.496 | 20.016
Devonshire Building | 2016-12-28 07:30 | 49707.496 | 0
Devonshire Building | 2016-12-28 07:45 | 49707.511 | 60.012
Devonshire Building | 2016-12-28 08:00 | 49707.531 | 79.992
Devonshire Building | 2016-12-28 08:15 | 49707.546 | 60.012
Devonshire Building | 2016-12-28 08:30 | 49707.566 | 79.992
Devonshire Building | 2016-12-28 08:45 | 49707.581 | 60.012
Devonshire Building | 2016-12-28 09:00 | 49707.601 | 79.992
Devonshire Building | 2016-12-28 09:15 | 49707.616 | 60.012
Devonshire Building | 2016-12-28 09:30 | 49707.636 | 79.992
Devonshire Building | 2016-12-28 09:45 | 49707.651 | 60.012
Devonshire Building | 2016-12-28 10:00 | 49707.671 | 79.992
Devonshire Building | 2016-12-28 10:15 | 49707.676 | 20.016
Devonshire Building | 2016-12-28 10:30 | 49707.676 | 0
Devonshire Building | 2016-12-28 10:45 | 49707.681 | 20.016
Devonshire Building | 2016-12-28 11:00 | 49707.681 | 0
Devonshire Building | 2016-12-28 11:15 | 49707.681 | 0
Devonshire Building | 2016-12-28 11:30 | 49707.686 | 20.016
Devonshire Building | 2016-12-28 11:45 | 49707.686 | 0
Devonshire Building | 2016-12-28 12:00 | 49707.686 | 0
Devonshire Building | 2016-12-28 12:15 | 49707.686 | 0
Devonshire Building | 2016-12-28 12:30 | 49707.691 | 20.016
Devonshire Building | 2016-12-28 12:45 | 49707.691 | 0
Devonshire Building | 2016-12-28 13:00 | 49707.696 | 20.016
Devonshire Building | 2016-12-28 13:15 | 49707.701 | 20.016
Devonshire Building | 2016-12-28 13:30 | 49707.701 | 0
Devonshire Building | 2016-12-28 13:45 | 49707.701 | 0
Devonshire Building | 2016-12-28 14:00 | 49707.706 | 20.016
Devonshire Building | 2016-12-28 14:15 | 49707.706 | 0
Devonshire Building | 2016-12-28 14:30 | 49707.706 | 0
Devonshire Building | 2016-12-28 14:45 | 49707.711 | 20.016
Devonshire Building | 2016-12-28 15:00 | 49707.716 | 20.016
Devonshire Building | 2016-12-28 15:15 | 49707.716 | 0
Devonshire Building | 2016-12-28 15:30 | 49707.721 | 20.016
Devonshire Building | 2016-12-28 15:45 | 49707.721 | 0
Devonshire Building | 2016-12-28 16:00 | 49707.721 | 0
Devonshire Building | 2016-12-28 16:15 | 49707.721 | 0
Devonshire Building | 2016-12-28 16:30 | 49707.726 | 20.016
Devonshire Building | 2016-12-28 16:45 | 49708.001 | 1100.016
Devonshire Building | 2016-12-28 17:00 | 49708.001 | 0
Devonshire Building | 2016-12-28 17:15 | 49708.001 | 0
Devonshire Building | 2016-12-28 17:30 | 49708.006 | 20.016
Devonshire Building | 2016-12-28 17:45 | 49708.006 | 0
Devonshire Building | 2016-12-28 18:00 | 49708.006 | 0
Devonshire Building | 2016-12-28 18:15 | 49708.006 | 0
Devonshire Building | 2016-12-28 18:30 | 49708.011 | 20.016
Devonshire Building | 2016-12-28 18:45 | 49708.011 | 0
Devonshire Building | 2016-12-28 19:00 | 49708.011 | 0
Devonshire Building | 2016-12-28 19:15 | 49708.011 | 0
Devonshire Building | 2016-12-28 19:30 | 49708.016 | 20.016
Devonshire Building | 2016-12-28 19:45 | 49708.016 | 0
Devonshire Building | 2016-12-28 20:00 | 49708.016 | 0
Devonshire Building | 2016-12-28 20:15 | 49708.021 | 20.016
Devonshire Building | 2016-12-28 20:30 | 49708.021 | 0
Devonshire Building | 2016-12-28 20:45 | 49708.021 | 0
Devonshire Building | 2016-12-28 21:00 | 49708.021 | 0
Devonshire Building | 2016-12-28 21:15 | 49708.026 | 20.016
Devonshire Building | 2016-12-28 21:30 | 49708.026 | 0
Devonshire Building | 2016-12-28 21:45 | 49708.026 | 0
Devonshire Building | 2016-12-28 22:00 | 49708.036 | 39.996
Devonshire Building | 2016-12-28 22:15 | 49708.036 | 0
Devonshire Building | 2016-12-28 22:30 | 49708.041 | 20.016
Devonshire Building | 2016-12-28 22:45 | 49708.041 | 0
Devonshire Building | 2016-12-28 23:00 | 49708.041 | 0
Devonshire Building | 2016-12-28 23:15 | 49708.041 | 0
Devonshire Building | 2016-12-28 23:30 | 49708.046 | 20.016
Devonshire Building | 2016-12-28 23:45 | 49708.046 | 0 | 0
Devonshire Building | 2016-12-29 | 49708.0469 | 0
Devonshire Building | 2016-12-29 00:15 | 49708.0519 | 20.016
Devonshire Building | 2016-12-29 00:30 | 49708.0519 | 0
Devonshire Building | 2016-12-29 00:45 | 49708.0519 | 0
Devonshire Building | 2016-12-29 01:00 | 49708.0519 | 0
Devonshire Building | 2016-12-29 01:15 | 49708.0569 | 20.016
Devonshire Building | 2016-12-29 01:30 | 49708.0569 | 0
Devonshire Building | 2016-12-29 01:45 | 49708.0569 | 0
Devonshire Building | 2016-12-29 02:00 | 49708.0569 | 0
Devonshire Building | 2016-12-29 02:15 | 49708.0619 | 20.016
Devonshire Building | 2016-12-29 02:30 | 49708.0619 | 0
Devonshire Building | 2016-12-29 02:45 | 49708.0619 | 0
Devonshire Building | 2016-12-29 03:00 | 49708.0619 | 0
Devonshire Building | 2016-12-29 03:15 | 49708.0669 | 20.016
Devonshire Building | 2016-12-29 03:30 | 49708.0669 | 0
Devonshire Building | 2016-12-29 03:45 | 49708.0669 | 0
Devonshire Building | 2016-12-29 04:00 | 49708.0719 | 20.016
Devonshire Building | 2016-12-29 04:15 | 49708.0719 | 0
Devonshire Building | 2016-12-29 04:30 | 49708.0719 | 0
Devonshire Building | 2016-12-29 04:45 | 49708.0719 | 0
Devonshire Building | 2016-12-29 05:00 | 49708.0719 | 0
Devonshire Building | 2016-12-29 05:15 | 49708.0769 | 20.016
Devonshire Building | 2016-12-29 05:30 | 49708.0769 | 0
Devonshire Building | 2016-12-29 05:45 | 49708.0769 | 0
Devonshire Building | 2016-12-29 06:00 | 49708.0769 | 0
Devonshire Building | 2016-12-29 06:15 | 49708.0819 | 20.016
Devonshire Building | 2016-12-29 06:30 | 49708.0819 | 0
Devonshire Building | 2016-12-29 06:45 | 49708.0819 | 0
Devonshire Building | 2016-12-29 07:00 | 49708.0819 | 0
Devonshire Building | 2016-12-29 07:15 | 49708.0869 | 20.016
Devonshire Building | 2016-12-29 07:30 | 49708.0869 | 0
Devonshire Building | 2016-12-29 07:45 | 49708.1019 | 60.012
Devonshire Building | 2016-12-29 08:00 | 49708.1219 | 79.992
Devonshire Building | 2016-12-29 08:15 | 49708.1369 | 60.012
Devonshire Building | 2016-12-29 08:30 | 49708.1569 | 79.992
Devonshire Building | 2016-12-29 08:45 | 49708.1719 | 60.012
Devonshire Building | 2016-12-29 09:00 | 49708.1919 | 79.992
Devonshire Building | 2016-12-29 09:15 | 49708.2069 | 60.012
Devonshire Building | 2016-12-29 09:30 | 49708.2269 | 79.992
Devonshire Building | 2016-12-29 09:45 | 49708.2419 | 60.012
Devonshire Building | 2016-12-29 10:00 | 49708.2619 | 79.992
Devonshire Building | 2016-12-29 10:15 | 49708.2719 | 39.996
Devonshire Building | 2016-12-29 10:30 | 49708.2719 | 0
Devonshire Building | 2016-12-29 10:45 | 49708.2719 | 0
Devonshire Building | 2016-12-29 11:00 | 49708.2769 | 20.016
Devonshire Building | 2016-12-29 11:15 | 49708.2769 | 0
Devonshire Building | 2016-12-29 11:30 | 49708.2769 | 0
Devonshire Building | 2016-12-29 11:45 | 49708.2819 | 20.016
Devonshire Building | 2016-12-29 12:00 | 49708.2819 | 0
Devonshire Building | 2016-12-29 12:15 | 49708.2819 | 0
Devonshire Building | 2016-12-29 12:30 | 49708.2819 | 0
Devonshire Building | 2016-12-29 12:45 | 49708.2869 | 20.016
Devonshire Building | 2016-12-29 13:00 | 49708.2869 | 0
Devonshire Building | 2016-12-29 13:15 | 49708.2919 | 20.016
Devonshire Building | 2016-12-29 13:30 | 49708.2919 | 0
Devonshire Building | 2016-12-29 13:45 | 49708.2919 | 0
Devonshire Building | 2016-12-29 14:00 | 49708.2969 | 20.016
Devonshire Building | 2016-12-29 14:15 | 49708.2969 | 0
Devonshire Building | 2016-12-29 14:30 | 49708.2969 | 0
Devonshire Building | 2016-12-29 14:45 | 49708.3019 | 20.016
Devonshire Building | 2016-12-29 15:00 | 49708.3019 | 0
Devonshire Building | 2016-12-29 15:15 | 49708.3019 | 0
Devonshire Building | 2016-12-29 15:30 | 49708.3019 | 0
Devonshire Building | 2016-12-29 15:45 | 49708.3069 | 20.016
Devonshire Building | 2016-12-29 16:00 | 49708.5569 | 1000.008
Devonshire Building | 2016-12-29 16:15 | 49708.562 | 20.016
Devonshire Building | 2016-12-29 16:30 | 49708.562 | 0
Devonshire Building | 2016-12-29 16:45 | 49708.567 | 20.016
Devonshire Building | 2016-12-29 17:00 | 49708.567 | 0
Devonshire Building | 2016-12-29 17:15 | 49708.567 | 0
Devonshire Building | 2016-12-29 17:30 | 49708.572 | 20.016
Devonshire Building | 2016-12-29 17:45 | 49708.587 | 60.012
Devonshire Building | 2016-12-29 18:00 | 49708.602 | 60.012
Devonshire Building | 2016-12-29 18:15 | 49708.622 | 79.992
Devonshire Building | 2016-12-29 18:30 | 49708.637 | 60.012
Devonshire Building | 2016-12-29 18:45 | 49708.657 | 79.992
Devonshire Building | 2016-12-29 19:00 | 49708.682 | 100.008
Devonshire Building | 2016-12-29 19:15 | 49708.707 | 100.008
Devonshire Building | 2016-12-29 19:30 | 49708.732 | 100.008
Devonshire Building | 2016-12-29 19:45 | 49708.752 | 79.992
Devonshire Building | 2016-12-29 20:00 | 49708.777 | 100.008
Devonshire Building | 2016-12-29 20:15 | 49708.797 | 79.992
Devonshire Building | 2016-12-29 20:30 | 49708.817 | 79.992
Devonshire Building | 2016-12-29 20:45 | 49708.837 | 79.992
Devonshire Building | 2016-12-29 21:00 | 49708.852 | 60.012
Devonshire Building | 2016-12-29 21:15 | 49708.867 | 60.012
Devonshire Building | 2016-12-29 21:30 | 49708.882 | 60.012
Devonshire Building | 2016-12-29 21:45 | 49708.892 | 39.996
Devonshire Building | 2016-12-29 22:00 | 49708.917 | 100.008
Devonshire Building | 2016-12-29 22:15 | 49708.922 | 20.016
Devonshire Building | 2016-12-29 22:30 | 49708.927 | 20.016
Devonshire Building | 2016-12-29 22:45 | 49708.932 | 20.016
Devonshire Building | 2016-12-29 23:00 | 49708.942 | 39.996
Devonshire Building | 2016-12-29 23:15 | 49708.947 | 20.016
Devonshire Building | 2016-12-29 23:30 | 49708.952 | 20.016
Devonshire Building | 2016-12-29 23:45 | 49708.957 | 20.016 | 0
Devonshire Building | 2016-12-30 | 49708.9609 | 20.016
Devonshire Building | 2016-12-30 00:15 | 49708.9659 | 20.016
Devonshire Building | 2016-12-30 00:30 | 49708.9709 | 20.016
Devonshire Building | 2016-12-30 00:45 | 49708.9809 | 39.996
Devonshire Building | 2016-12-30 01:00 | 49708.986 | 20.016
Devonshire Building | 2016-12-30 01:15 | 49708.991 | 20.016
Devonshire Building | 2016-12-30 01:30 | 49708.996 | 20.016
Devonshire Building | 2016-12-30 01:45 | 49709.001 | 20.016
Devonshire Building | 2016-12-30 02:00 | 49709.006 | 20.016
Devonshire Building | 2016-12-30 02:15 | 49709.011 | 20.016
Devonshire Building | 2016-12-30 02:30 | 49709.016 | 20.016
Devonshire Building | 2016-12-30 02:45 | 49709.021 | 20.016
Devonshire Building | 2016-12-30 03:00 | 49709.026 | 20.016
Devonshire Building | 2016-12-30 03:15 | 49709.026 | 0
Devonshire Building | 2016-12-30 03:30 | 49709.031 | 20.016
Devonshire Building | 2016-12-30 03:45 | 49709.036 | 20.016
Devonshire Building | 2016-12-30 04:00 | 49709.041 | 20.016
Devonshire Building | 2016-12-30 04:15 | 49709.046 | 20.016
Devonshire Building | 2016-12-30 04:30 | 49709.046 | 0
Devonshire Building | 2016-12-30 04:45 | 49709.051 | 20.016
Devonshire Building | 2016-12-30 05:00 | 49709.056 | 20.016
Devonshire Building | 2016-12-30 05:15 | 49709.056 | 0
Devonshire Building | 2016-12-30 05:30 | 49709.061 | 20.016
Devonshire Building | 2016-12-30 05:45 | 49709.066 | 20.016
Devonshire Building | 2016-12-30 06:00 | 49709.066 | 0
Devonshire Building | 2016-12-30 06:15 | 49709.071 | 20.016
Devonshire Building | 2016-12-30 06:30 | 49709.071 | 0
Devonshire Building | 2016-12-30 06:45 | 49709.076 | 20.016
Devonshire Building | 2016-12-30 07:00 | 49709.081 | 20.016
Devonshire Building | 2016-12-30 07:15 | 49709.081 | 0
Devonshire Building | 2016-12-30 07:30 | 49709.086 | 20.016
Devonshire Building | 2016-12-30 07:45 | 49709.101 | 60.012
Devonshire Building | 2016-12-30 08:00 | 49709.121 | 79.992
Devonshire Building | 2016-12-30 08:15 | 49709.141 | 79.992
Devonshire Building | 2016-12-30 08:30 | 49709.156 | 60.012
Devonshire Building | 2016-12-30 08:45 | 49709.176 | 79.992
Devonshire Building | 2016-12-30 09:00 | 49709.196 | 79.992
Devonshire Building | 2016-12-30 09:15 | 49709.211 | 60.012
Devonshire Building | 2016-12-30 09:30 | 49709.231 | 79.992
Devonshire Building | 2016-12-30 09:45 | 49709.251 | 79.992
Devonshire Building | 2016-12-30 10:00 | 49709.266 | 60.012
Devonshire Building | 2016-12-30 10:15 | 49709.286 | 79.992
Devonshire Building | 2016-12-30 10:30 | 49709.296 | 39.996
Devonshire Building | 2016-12-30 10:45 | 49709.296 | 0
Devonshire Building | 2016-12-30 11:00 | 49709.296 | 0
Devonshire Building | 2016-12-30 11:15 | 49709.301 | 20.016
Devonshire Building | 2016-12-30 11:30 | 49709.301 | 0
Devonshire Building | 2016-12-30 11:45 | 49709.306 | 20.016
Devonshire Building | 2016-12-30 12:00 | 49709.306 | 0
Devonshire Building | 2016-12-30 12:15 | 49709.311 | 20.016
Devonshire Building | 2016-12-30 12:30 | 49709.311 | 0
Devonshire Building | 2016-12-30 12:45 | 49709.311 | 0
Devonshire Building | 2016-12-30 13:00 | 49709.316 | 20.016
Devonshire Building | 2016-12-30 13:15 | 49709.316 | 0
Devonshire Building | 2016-12-30 13:30 | 49709.321 | 20.016
Devonshire Building | 2016-12-30 13:45 | 49709.321 | 0
Devonshire Building | 2016-12-30 14:00 | 49709.3261 | 20.016
Devonshire Building | 2016-12-30 14:15 | 49709.3261 | 0
Devonshire Building | 2016-12-30 14:30 | 49709.3311 | 20.016
Devonshire Building | 2016-12-30 14:45 | 49709.3311 | 0
Devonshire Building | 2016-12-30 15:00 | 49709.3311 | 0
Devonshire Building | 2016-12-30 15:15 | 49709.3361 | 20.016
Devonshire Building | 2016-12-30 15:30 | 49709.3361 | 0
Devonshire Building | 2016-12-30 15:45 | 49709.3411 | 20.016
Devonshire Building | 2016-12-30 16:00 | 49709.6011 | 1040.004
Devonshire Building | 2016-12-30 16:15 | 49709.6011 | 0
Devonshire Building | 2016-12-30 16:30 | 49709.6061 | 20.016
Devonshire Building | 2016-12-30 16:45 | 49709.6061 | 0
Devonshire Building | 2016-12-30 17:00 | 49709.6061 | 0
Devonshire Building | 2016-12-30 17:15 | 49709.6111 | 20.016
Devonshire Building | 2016-12-30 17:30 | 49709.6111 | 0
Devonshire Building | 2016-12-30 17:45 | 49709.6161 | 20.016
Devonshire Building | 2016-12-30 18:00 | 49709.6161 | 0
Devonshire Building | 2016-12-30 18:15 | 49709.6161 | 0
Devonshire Building | 2016-12-30 18:30 | 49709.6211 | 20.016
Devonshire Building | 2016-12-30 18:45 | 49709.6211 | 0
Devonshire Building | 2016-12-30 19:00 | 49709.6261 | 20.016
Devonshire Building | 2016-12-30 19:15 | 49709.6261 | 0
Devonshire Building | 2016-12-30 19:30 | 49709.6261 | 0
Devonshire Building | 2016-12-30 19:45 | 49709.6311 | 20.016
Devonshire Building | 2016-12-30 20:00 | 49709.6311 | 0
Devonshire Building | 2016-12-30 20:15 | 49709.6361 | 20.016
Devonshire Building | 2016-12-30 20:30 | 49709.6361 | 0
Devonshire Building | 2016-12-30 20:45 | 49709.6361 | 0
Devonshire Building | 2016-12-30 21:00 | 49709.6411 | 20.016
Devonshire Building | 2016-12-30 21:15 | 49709.6411 | 0
Devonshire Building | 2016-12-30 21:30 | 49709.6461 | 20.016
Devonshire Building | 2016-12-30 21:45 | 49709.6461 | 0
Devonshire Building | 2016-12-30 22:00 | 49709.6561 | 39.996
Devonshire Building | 2016-12-30 22:15 | 49709.6561 | 0
Devonshire Building | 2016-12-30 22:30 | 49709.6611 | 20.016
Devonshire Building | 2016-12-30 22:45 | 49709.6611 | 0
Devonshire Building | 2016-12-30 23:00 | 49709.6661 | 20.016
Devonshire Building | 2016-12-30 23:15 | 49709.6661 | 0
Devonshire Building | 2016-12-30 23:30 | 49709.6661 | 0
Devonshire Building | 2016-12-30 23:45 | 49709.6711 | 20.016 | 0
Devonshire Building | 2016-12-31 | 49709.668 | 0
Devonshire Building | 2016-12-31 00:15 | 49709.668 | 0
Devonshire Building | 2016-12-31 00:30 | 49709.673 | 20.016
Devonshire Building | 2016-12-31 00:45 | 49709.673 | 0
Devonshire Building | 2016-12-31 01:00 | 49709.678 | 20.016
Devonshire Building | 2016-12-31 01:15 | 49709.678 | 0
Devonshire Building | 2016-12-31 01:30 | 49709.678 | 0
Devonshire Building | 2016-12-31 01:45 | 49709.683 | 20.016
Devonshire Building | 2016-12-31 02:00 | 49709.683 | 0
Devonshire Building | 2016-12-31 02:15 | 49709.688 | 20.016
Devonshire Building | 2016-12-31 02:30 | 49709.688 | 0
Devonshire Building | 2016-12-31 02:45 | 49709.693 | 20.016
Devonshire Building | 2016-12-31 03:00 | 49709.693 | 0
Devonshire Building | 2016-12-31 03:15 | 49709.693 | 0
Devonshire Building | 2016-12-31 03:30 | 49709.698 | 20.016
Devonshire Building | 2016-12-31 03:45 | 49709.698 | 0
Devonshire Building | 2016-12-31 04:00 | 49709.698 | 0
Devonshire Building | 2016-12-31 04:15 | 49709.703 | 20.016
Devonshire Building | 2016-12-31 04:30 | 49709.703 | 0
Devonshire Building | 2016-12-31 04:45 | 49709.708 | 20.016
Devonshire Building | 2016-12-31 05:00 | 49709.708 | 0
Devonshire Building | 2016-12-31 05:15 | 49709.708 | 0
Devonshire Building | 2016-12-31 05:30 | 49709.713 | 20.016
Devonshire Building | 2016-12-31 05:45 | 49709.713 | 0
Devonshire Building | 2016-12-31 06:00 | 49709.718 | 20.016
Devonshire Building | 2016-12-31 06:15 | 49709.718 | 0
Devonshire Building | 2016-12-31 06:30 | 49709.718 | 0
Devonshire Building | 2016-12-31 06:45 | 49709.723 | 20.016
Devonshire Building | 2016-12-31 07:00 | 49709.723 | 0
Devonshire Building | 2016-12-31 07:15 | 49709.723 | 0
Devonshire Building | 2016-12-31 07:30 | 49709.728 | 20.016
Devonshire Building | 2016-12-31 07:45 | 49709.743 | 60.012
Devonshire Building | 2016-12-31 08:00 | 49709.763 | 79.992
Devonshire Building | 2016-12-31 08:15 | 49709.783 | 79.992
Devonshire Building | 2016-12-31 08:30 | 49709.798 | 60.012
Devonshire Building | 2016-12-31 08:45 | 49709.818 | 79.992
Devonshire Building | 2016-12-31 09:00 | 49709.838 | 79.992
Devonshire Building | 2016-12-31 09:15 | 49709.853 | 60.012
Devonshire Building | 2016-12-31 09:30 | 49709.873 | 79.992
Devonshire Building | 2016-12-31 09:45 | 49709.893 | 79.992
Devonshire Building | 2016-12-31 10:00 | 49709.908 | 60.012
Devonshire Building | 2016-12-31 10:15 | 49709.918 | 39.996
Devonshire Building | 2016-12-31 10:30 | 49709.918 | 0
Devonshire Building | 2016-12-31 10:45 | 49709.923 | 20.016
Devonshire Building | 2016-12-31 11:00 | 49709.923 | 0
Devonshire Building | 2016-12-31 11:15 | 49709.928 | 20.016
Devonshire Building | 2016-12-31 11:30 | 49709.928 | 0
Devonshire Building | 2016-12-31 11:45 | 49709.928 | 0
Devonshire Building | 2016-12-31 12:00 | 49709.933 | 20.016
Devonshire Building | 2016-12-31 12:15 | 49709.933 | 0
Devonshire Building | 2016-12-31 12:30 | 49709.938 | 20.016
Devonshire Building | 2016-12-31 12:45 | 49709.938 | 0
Devonshire Building | 2016-12-31 13:00 | 49709.943 | 20.016
Devonshire Building | 2016-12-31 13:15 | 49709.943 | 0
Devonshire Building | 2016-12-31 13:30 | 49709.943 | 0
Devonshire Building | 2016-12-31 13:45 | 49709.948 | 20.016
Devonshire Building | 2016-12-31 14:00 | 49709.948 | 0
Devonshire Building | 2016-12-31 14:15 | 49709.953 | 20.016
Devonshire Building | 2016-12-31 14:30 | 49709.953 | 0
Devonshire Building | 2016-12-31 14:45 | 49709.958 | 20.016
Devonshire Building | 2016-12-31 15:00 | 49709.958 | 0
Devonshire Building | 2016-12-31 15:15 | 49709.958 | 0
Devonshire Building | 2016-12-31 15:30 | 49709.9631 | 20.016
Devonshire Building | 2016-12-31 15:45 | 49709.9631 | 0
Devonshire Building | 2016-12-31 16:00 | 49709.9681 | 20.016
Devonshire Building | 2016-12-31 16:15 | 49709.9681 | 0
Devonshire Building | 2016-12-31 16:30 | 49709.9681 | 0
Devonshire Building | 2016-12-31 16:45 | 49709.9731 | 20.016
Devonshire Building | 2016-12-31 17:00 | 49709.9781 | 20.016
Devonshire Building | 2016-12-31 17:15 | 49710.2381 | 1040.004
Devonshire Building | 2016-12-31 17:30 | 49710.2431 | 20.016
Devonshire Building | 2016-12-31 17:45 | 49710.2431 | 0
Devonshire Building | 2016-12-31 18:00 | 49710.2431 | 0
Devonshire Building | 2016-12-31 18:15 | 49710.2481 | 20.016
Devonshire Building | 2016-12-31 18:30 | 49710.2481 | 0
Devonshire Building | 2016-12-31 18:45 | 49710.2531 | 20.016
Devonshire Building | 2016-12-31 19:00 | 49710.2531 | 0
Devonshire Building | 2016-12-31 19:15 | 49710.2531 | 0
Devonshire Building | 2016-12-31 19:30 | 49710.2581 | 20.016
Devonshire Building | 2016-12-31 19:45 | 49710.2581 | 0
Devonshire Building | 2016-12-31 20:00 | 49710.2631 | 20.016
Devonshire Building | 2016-12-31 20:15 | 49710.2631 | 0
Devonshire Building | 2016-12-31 20:30 | 49710.2631 | 0
Devonshire Building | 2016-12-31 20:45 | 49710.2681 | 20.016
Devonshire Building | 2016-12-31 21:00 | 49710.2681 | 0
Devonshire Building | 2016-12-31 21:15 | 49710.2731 | 20.016
Devonshire Building | 2016-12-31 21:30 | 49710.2731 | 0
Devonshire Building | 2016-12-31 21:45 | 49710.2781 | 20.016
Devonshire Building | 2016-12-31 22:00 | 49710.2831 | 20.016
Devonshire Building | 2016-12-31 22:15 | 49710.2881 | 20.016
Devonshire Building | 2016-12-31 22:30 | 49710.2881 | 0
Devonshire Building | 2016-12-31 22:45 | 49710.2881 | 0
Devonshire Building | 2016-12-31 23:00 | 49710.2931 | 20.016
Devonshire Building | 2016-12-31 23:15 | 49710.2931 | 0
Devonshire Building | 2016-12-31 23:30 | 49710.2981 | 20.016
Devonshire Building | 2016-12-31 23:45 | 49710.2981 | 0 | 0
Devonshire Building | 2017-01-01 | 49710.3047 | 20.016
Devonshire Building | 2017-01-01 00:15 | 49710.3047 | 0
Devonshire Building | 2017-01-01 00:30 | 49710.3047 | 0
Devonshire Building | 2017-01-01 00:45 | 49710.3097 | 20.016
Devonshire Building | 2017-01-01 01:00 | 49710.3097 | 0
Devonshire Building | 2017-01-01 01:15 | 49710.3147 | 20.016
Devonshire Building | 2017-01-01 01:30 | 49710.3147 | 0
Devonshire Building | 2017-01-01 01:45 | 49710.3147 | 0
Devonshire Building | 2017-01-01 02:00 | 49710.3197 | 20.016
Devonshire Building | 2017-01-01 02:15 | 49710.3197 | 0
Devonshire Building | 2017-01-01 02:30 | 49710.3247 | 20.016
Devonshire Building | 2017-01-01 02:45 | 49710.3247 | 0
Devonshire Building | 2017-01-01 03:00 | 49710.3297 | 20.016
Devonshire Building | 2017-01-01 03:15 | 49710.3297 | 0
Devonshire Building | 2017-01-01 03:30 | 49710.3297 | 0
Devonshire Building | 2017-01-01 03:45 | 49710.3347 | 20.016
Devonshire Building | 2017-01-01 04:00 | 49710.3347 | 0
Devonshire Building | 2017-01-01 04:15 | 49710.3397 | 20.016
Devonshire Building | 2017-01-01 04:30 | 49710.3397 | 0
Devonshire Building | 2017-01-01 04:45 | 49710.3447 | 20.016
Devonshire Building | 2017-01-01 05:00 | 49710.3447 | 0
Devonshire Building | 2017-01-01 05:15 | 49710.3447 | 0
Devonshire Building | 2017-01-01 05:30 | 49710.3497 | 20.016
Devonshire Building | 2017-01-01 05:45 | 49710.3497 | 0
Devonshire Building | 2017-01-01 06:00 | 49710.3547 | 20.016
Devonshire Building | 2017-01-01 06:15 | 49710.3547 | 0
Devonshire Building | 2017-01-01 06:30 | 49710.3547 | 0
Devonshire Building | 2017-01-01 06:45 | 49710.3597 | 20.016
Devonshire Building | 2017-01-01 07:00 | 49710.3597 | 0
Devonshire Building | 2017-01-01 07:15 | 49710.3647 | 20.016
Devonshire Building | 2017-01-01 07:30 | 49710.3647 | 0
Devonshire Building | 2017-01-01 07:45 | 49710.3847 | 79.992
Devonshire Building | 2017-01-01 08:00 | 49710.3997 | 60.012
Devonshire Building | 2017-01-01 08:15 | 49710.4197 | 79.992
Devonshire Building | 2017-01-01 08:30 | 49710.4397 | 79.992
Devonshire Building | 2017-01-01 08:45 | 49710.4547 | 60.012
Devonshire Building | 2017-01-01 09:00 | 49710.4747 | 79.992
Devonshire Building | 2017-01-01 09:15 | 49710.4947 | 79.992
Devonshire Building | 2017-01-01 09:30 | 49710.5097 | 60.012
Devonshire Building | 2017-01-01 09:45 | 49710.5297 | 79.992
Devonshire Building | 2017-01-01 10:00 | 49710.5497 | 79.992
Devonshire Building | 2017-01-01 10:15 | 49710.5597 | 39.996
Devonshire Building | 2017-01-01 10:30 | 49710.5597 | 0
Devonshire Building | 2017-01-01 10:45 | 49710.5597 | 0
Devonshire Building | 2017-01-01 11:00 | 49710.5647 | 20.016
Devonshire Building | 2017-01-01 11:15 | 49710.5647 | 0
Devonshire Building | 2017-01-01 11:30 | 49710.5697 | 20.016
Devonshire Building | 2017-01-01 11:45 | 49710.5697 | 0
Devonshire Building | 2017-01-01 12:00 | 49710.5747 | 20.016
Devonshire Building | 2017-01-01 12:15 | 49710.5797 | 20.016
Devonshire Building | 2017-01-01 12:30 | 49710.5797 | 0
Devonshire Building | 2017-01-01 12:45 | 49710.5797 | 0
Devonshire Building | 2017-01-01 13:00 | 49710.5848 | 20.016
Devonshire Building | 2017-01-01 13:15 | 49710.5848 | 0
Devonshire Building | 2017-01-01 13:30 | 49710.5898 | 20.016
Devonshire Building | 2017-01-01 13:45 | 49710.5898 | 0
Devonshire Building | 2017-01-01 14:00 | 49710.5948 | 20.016
Devonshire Building | 2017-01-01 14:15 | 49710.5948 | 0
Devonshire Building | 2017-01-01 14:30 | 49710.5948 | 0
Devonshire Building | 2017-01-01 14:45 | 49710.5998 | 20.016
Devonshire Building | 2017-01-01 15:00 | 49710.5998 | 0
Devonshire Building | 2017-01-01 15:15 | 49710.6048 | 20.016
Devonshire Building | 2017-01-01 15:30 | 49710.6048 | 0
Devonshire Building | 2017-01-01 15:45 | 49710.6098 | 20.016
Devonshire Building | 2017-01-01 16:00 | 49710.6098 | 0
Devonshire Building | 2017-01-01 16:15 | 49710.6098 | 0
Devonshire Building | 2017-01-01 16:30 | 49710.6148 | 20.016
Devonshire Building | 2017-01-01 16:45 | 49710.6148 | 0
Devonshire Building | 2017-01-01 17:00 | 49710.6198 | 20.016
Devonshire Building | 2017-01-01 17:15 | 49710.6198 | 0
Devonshire Building | 2017-01-01 17:30 | 49710.6198 | 0
Devonshire Building | 2017-01-01 17:45 | 49710.6248 | 20.016
Devonshire Building | 2017-01-01 18:00 | 49710.6248 | 0
Devonshire Building | 2017-01-01 18:15 | 49710.6298 | 20.016
Devonshire Building | 2017-01-01 18:30 | 49710.6298 | 0
Devonshire Building | 2017-01-01 18:45 | 49710.6298 | 0
Devonshire Building | 2017-01-01 19:00 | 49710.6348 | 20.016
Devonshire Building | 2017-01-01 19:15 | 49710.6348 | 0
Devonshire Building | 2017-01-01 19:30 | 49710.6398 | 20.016
Devonshire Building | 2017-01-01 19:45 | 49710.6398 | 0
Devonshire Building | 2017-01-01 20:00 | 49710.6448 | 20.016
Devonshire Building | 2017-01-01 20:15 | 49710.6448 | 0
Devonshire Building | 2017-01-01 20:30 | 49710.6448 | 0
Devonshire Building | 2017-01-01 20:45 | 49710.6498 | 20.016
Devonshire Building | 2017-01-01 21:00 | 49710.6498 | 0
Devonshire Building | 2017-01-01 21:15 | 49710.6548 | 20.016
Devonshire Building | 2017-01-01 21:30 | 49710.6548 | 0
Devonshire Building | 2017-01-01 21:45 | 49710.6548 | 0
Devonshire Building | 2017-01-01 22:00 | 49710.6798 | 100.008
Devonshire Building | 2017-01-01 22:15 | 49710.6848 | 20.016
Devonshire Building | 2017-01-01 22:30 | 49710.6848 | 0
Devonshire Building | 2017-01-01 22:45 | 49710.6898 | 20.016
Devonshire Building | 2017-01-01 23:00 | 49710.6898 | 0
Devonshire Building | 2017-01-01 23:15 | 49710.6898 | 0
Devonshire Building | 2017-01-01 23:30 | 49710.6948 | 20.016
Devonshire Building | 2017-01-01 23:45 | 49710.6948 | 0 | 0
Devonshire Building | 2017-01-02 | 49710.6992 | 20.016
Devonshire Building | 2017-01-02 00:15 | 49710.6992 | 0
Devonshire Building | 2017-01-02 00:30 | 49710.7042 | 20.016
Devonshire Building | 2017-01-02 00:45 | 49710.7042 | 0
Devonshire Building | 2017-01-02 01:00 | 49710.7042 | 0
Devonshire Building | 2017-01-02 01:15 | 49710.7092 | 20.016
Devonshire Building | 2017-01-02 01:30 | 49710.7092 | 0
Devonshire Building | 2017-01-02 01:45 | 49710.7142 | 20.016
Devonshire Building | 2017-01-02 02:00 | 49710.7142 | 0
Devonshire Building | 2017-01-02 02:15 | 49710.7142 | 0
Devonshire Building | 2017-01-02 02:30 | 49710.7192 | 20.016
Devonshire Building | 2017-01-02 02:45 | 49710.7192 | 0
Devonshire Building | 2017-01-02 03:00 | 49710.7242 | 20.016
Devonshire Building | 2017-01-02 03:15 | 49710.7242 | 0
Devonshire Building | 2017-01-02 03:30 | 49710.7292 | 20.016
Devonshire Building | 2017-01-02 03:45 | 49710.7292 | 0
Devonshire Building | 2017-01-02 04:00 | 49710.7292 | 0
Devonshire Building | 2017-01-02 04:15 | 49710.7342 | 20.016
Devonshire Building | 2017-01-02 04:30 | 49710.7342 | 0
Devonshire Building | 2017-01-02 04:45 | 49710.7393 | 20.016
Devonshire Building | 2017-01-02 05:00 | 49710.7393 | 0
Devonshire Building | 2017-01-02 05:15 | 49710.7393 | 0
Devonshire Building | 2017-01-02 05:30 | 49710.7443 | 20.016
Devonshire Building | 2017-01-02 05:45 | 49710.7443 | 0
Devonshire Building | 2017-01-02 06:00 | 49710.7493 | 20.016
Devonshire Building | 2017-01-02 06:15 | 49710.7493 | 0
Devonshire Building | 2017-01-02 06:30 | 49710.7493 | 0
Devonshire Building | 2017-01-02 06:45 | 49710.7543 | 20.016
Devonshire Building | 2017-01-02 07:00 | 49710.7543 | 0
Devonshire Building | 2017-01-02 07:15 | 49710.7593 | 20.016
Devonshire Building | 2017-01-02 07:30 | 49710.7593 | 0
Devonshire Building | 2017-01-02 07:45 | 49710.7743 | 60.012
Devonshire Building | 2017-01-02 08:00 | 49710.7943 | 79.992
Devonshire Building | 2017-01-02 08:15 | 49710.8143 | 79.992
Devonshire Building | 2017-01-02 08:30 | 49710.8293 | 60.012
Devonshire Building | 2017-01-02 08:45 | 49710.8493 | 79.992
Devonshire Building | 2017-01-02 09:00 | 49710.8693 | 79.992
Devonshire Building | 2017-01-02 09:15 | 49710.8843 | 60.012
Devonshire Building | 2017-01-02 09:30 | 49710.9043 | 79.992
Devonshire Building | 2017-01-02 09:45 | 49710.9243 | 79.992
Devonshire Building | 2017-01-02 10:00 | 49710.9443 | 79.992
Devonshire Building | 2017-01-02 10:15 | 49710.9543 | 39.996
Devonshire Building | 2017-01-02 10:30 | 49710.9593 | 20.016
Devonshire Building | 2017-01-02 10:45 | 49711.2143 | 1019.988
Devonshire Building | 2017-01-02 11:00 | 49711.2243 | 39.996
Devonshire Building | 2017-01-02 11:15 | 49711.2243 | 0
Devonshire Building | 2017-01-02 11:30 | 49711.2243 | 0
Devonshire Building | 2017-01-02 11:45 | 49711.2293 | 20.016
Devonshire Building | 2017-01-02 12:00 | 49711.2293 | 0
Devonshire Building | 2017-01-02 12:15 | 49711.2343 | 20.016
Devonshire Building | 2017-01-02 12:30 | 49711.2343 | 0
Devonshire Building | 2017-01-02 12:45 | 49711.2393 | 20.016
Devonshire Building | 2017-01-02 13:00 | 49711.2393 | 0
Devonshire Building | 2017-01-02 13:15 | 49711.2443 | 20.016
Devonshire Building | 2017-01-02 13:30 | 49711.2443 | 0
Devonshire Building | 2017-01-02 13:45 | 49711.2493 | 20.016
Devonshire Building | 2017-01-02 14:00 | 49711.2543 | 20.016
Devonshire Building | 2017-01-02 14:15 | 49711.2543 | 0
Devonshire Building | 2017-01-02 14:30 | 49711.2593 | 20.016
Devonshire Building | 2017-01-02 14:45 | 49711.2593 | 0
Devonshire Building | 2017-01-02 15:00 | 49711.2643 | 20.016
Devonshire Building | 2017-01-02 15:15 | 49711.2643 | 0
Devonshire Building | 2017-01-02 15:30 | 49711.2693 | 20.016
Devonshire Building | 2017-01-02 15:45 | 49711.2693 | 0
Devonshire Building | 2017-01-02 16:00 | 49711.2693 | 0
Devonshire Building | 2017-01-02 16:15 | 49711.2743 | 20.016
Devonshire Building | 2017-01-02 16:30 | 49711.2743 | 0
Devonshire Building | 2017-01-02 16:45 | 49711.2793 | 20.016
Devonshire Building | 2017-01-02 17:00 | 49711.2793 | 0
Devonshire Building | 2017-01-02 17:15 | 49711.2843 | 20.016
Devonshire Building | 2017-01-02 17:30 | 49711.2843 | 0
Devonshire Building | 2017-01-02 17:45 | 49711.2893 | 20.016
Devonshire Building | 2017-01-02 18:00 | 49711.2893 | 0
Devonshire Building | 2017-01-02 18:15 | 49711.2943 | 20.016
Devonshire Building | 2017-01-02 18:30 | 49711.2943 | 0
Devonshire Building | 2017-01-02 18:45 | 49711.2943 | 0
Devonshire Building | 2017-01-02 19:00 | 49711.2993 | 20.016
Devonshire Building | 2017-01-02 19:15 | 49711.2993 | 0
Devonshire Building | 2017-01-02 19:30 | 49711.3043 | 20.016
Devonshire Building | 2017-01-02 19:45 | 49711.3043 | 0
Devonshire Building | 2017-01-02 20:00 | 49711.3093 | 20.016
Devonshire Building | 2017-01-02 20:15 | 49711.3093 | 0
Devonshire Building | 2017-01-02 20:30 | 49711.3143 | 20.016
Devonshire Building | 2017-01-02 20:45 | 49711.3143 | 0
Devonshire Building | 2017-01-02 21:00 | 49711.3143 | 0
Devonshire Building | 2017-01-02 21:15 | 49711.3193 | 20.016
Devonshire Building | 2017-01-02 21:30 | 49711.3193 | 0
Devonshire Building | 2017-01-02 21:45 | 49711.3243 | 20.016
Devonshire Building | 2017-01-02 22:00 | 49711.3493 | 100.008
Devonshire Building | 2017-01-02 22:15 | 49711.3493 | 0
Devonshire Building | 2017-01-02 22:30 | 49711.3543 | 20.016
Devonshire Building | 2017-01-02 22:45 | 49711.3543 | 0
Devonshire Building | 2017-01-02 23:00 | 49711.3594 | 20.016
Devonshire Building | 2017-01-02 23:15 | 49711.3594 | 0
Devonshire Building | 2017-01-02 23:30 | 49711.3594 | 0
Devonshire Building | 2017-01-02 23:45 | 49711.3644 | 20.016 | 0
Devonshire Building | 2017-01-03 | 49711.3633 | 0
Devonshire Building | 2017-01-03 00:15 | 49711.3683 | 20.016
Devonshire Building | 2017-01-03 00:30 | 49711.3683 | 0
Devonshire Building | 2017-01-03 00:45 | 49711.3733 | 20.016
Devonshire Building | 2017-01-03 01:00 | 49711.3733 | 0
Devonshire Building | 2017-01-03 01:15 | 49711.3783 | 20.016
Devonshire Building | 2017-01-03 01:30 | 49711.3783 | 0
Devonshire Building | 2017-01-03 01:45 | 49711.3833 | 20.016
Devonshire Building | 2017-01-03 02:00 | 49711.3833 | 0
Devonshire Building | 2017-01-03 02:15 | 49711.3833 | 0
Devonshire Building | 2017-01-03 02:30 | 49711.3883 | 20.016
Devonshire Building | 2017-01-03 02:45 | 49711.3883 | 0
Devonshire Building | 2017-01-03 03:00 | 49711.3933 | 20.016
Devonshire Building | 2017-01-03 03:15 | 49711.3933 | 0
Devonshire Building | 2017-01-03 03:30 | 49711.3983 | 20.016
Devonshire Building | 2017-01-03 03:45 | 49711.3983 | 0
Devonshire Building | 2017-01-03 04:00 | 49711.3983 | 0
Devonshire Building | 2017-01-03 04:15 | 49711.4033 | 20.016
Devonshire Building | 2017-01-03 04:30 | 49711.4033 | 0
Devonshire Building | 2017-01-03 04:45 | 49711.4083 | 20.016
Devonshire Building | 2017-01-03 05:00 | 49711.4083 | 0
Devonshire Building | 2017-01-03 05:15 | 49711.4133 | 20.016
Devonshire Building | 2017-01-03 05:30 | 49711.4133 | 0
Devonshire Building | 2017-01-03 05:45 | 49711.4133 | 0
Devonshire Building | 2017-01-03 06:00 | 49711.4183 | 20.016
Devonshire Building | 2017-01-03 06:15 | 49711.4183 | 0
Devonshire Building | 2017-01-03 06:30 | 49711.4233 | 20.016
Devonshire Building | 2017-01-03 06:45 | 49711.4283 | 20.016
Devonshire Building | 2017-01-03 07:00 | 49711.4333 | 20.016
Devonshire Building | 2017-01-03 07:15 | 49711.4333 | 0
Devonshire Building | 2017-01-03 07:30 | 49711.4383 | 20.016
Devonshire Building | 2017-01-03 07:45 | 49711.4633 | 100.008
Devonshire Building | 2017-01-03 08:00 | 49711.7483 | 1140.012
Devonshire Building | 2017-01-03 08:15 | 49711.7683 | 79.992
Devonshire Building | 2017-01-03 08:30 | 49711.7983 | 119.988
Devonshire Building | 2017-01-03 08:45 | 49711.8333 | 140.004
Devonshire Building | 2017-01-03 09:00 | 49711.8833 | 200.016
Devonshire Building | 2017-01-03 09:15 | 49711.9083 | 100.008
Devonshire Building | 2017-01-03 09:30 | 49711.9333 | 100.008
Devonshire Building | 2017-01-03 09:45 | 49711.9584 | 100.008
Devonshire Building | 2017-01-03 10:00 | 49711.9783 | 79.992
Devonshire Building | 2017-01-03 10:15 | 49711.9934 | 60.012
Devonshire Building | 2017-01-03 10:30 | 49712.3334 | 1360.008
Devonshire Building | 2017-01-03 10:45 | 49712.4384 | 420.012
Devonshire Building | 2017-01-03 11:00 | 49712.5484 | 439.992
Devonshire Building | 2017-01-03 11:15 | 49712.6584 | 439.992
Devonshire Building | 2017-01-03 11:30 | 49712.7684 | 439.992
Devonshire Building | 2017-01-03 11:45 | 49712.8783 | 439.992
Devonshire Building | 2017-01-03 12:00 | 49713.2434 | 1460.016
Devonshire Building | 2017-01-03 12:15 | 49713.3184 | 299.988
Devonshire Building | 2017-01-03 12:30 | 49713.3884 | 280.008
Devonshire Building | 2017-01-03 12:45 | 49713.4584 | 280.008
Devonshire Building | 2017-01-03 13:00 | 49713.5234 | 259.992
Devonshire Building | 2017-01-03 13:15 | 49713.5883 | 259.992
Devonshire Building | 2017-01-03 13:30 | 49713.6584 | 280.008
Devonshire Building | 2017-01-03 13:45 | 49713.7134 | 219.996
Devonshire Building | 2017-01-03 14:00 | 49714.0233 | 1239.984
Devonshire Building | 2017-01-03 14:15 | 49714.0583 | 140.004
Devonshire Building | 2017-01-03 14:30 | 49714.0883 | 119.988
Devonshire Building | 2017-01-03 14:45 | 49714.1233 | 140.004
Devonshire Building | 2017-01-03 15:00 | 49714.1583 | 140.004
Devonshire Building | 2017-01-03 15:15 | 49714.1983 | 159.984
Devonshire Building | 2017-01-03 15:30 | 49714.2433 | 180
Devonshire Building | 2017-01-03 15:45 | 49714.2983 | 219.996
Devonshire Building | 2017-01-03 16:00 | 49714.7483 | 1800
Devonshire Building | 2017-01-03 16:15 | 49714.8983 | 600.012
Devonshire Building | 2017-01-03 16:30 | 49714.9983 | 399.996
Devonshire Building | 2017-01-03 16:45 | 49715.0683 | 280.008
Devonshire Building | 2017-01-03 17:00 | 49715.1183 | 200.016
Devonshire Building | 2017-01-03 17:15 | 49715.1583 | 159.984
Devonshire Building | 2017-01-03 17:30 | 49715.1933 | 140.004
Devonshire Building | 2017-01-03 17:45 | 49715.2183 | 100.008
Devonshire Building | 2017-01-03 18:00 | 49715.2383 | 79.992
Devonshire Building | 2017-01-03 18:15 | 49715.2583 | 79.992
Devonshire Building | 2017-01-03 18:30 | 49715.2733 | 60.012
Devonshire Building | 2017-01-03 18:45 | 49715.2884 | 60.012
Devonshire Building | 2017-01-03 19:00 | 49715.3034 | 60.012
Devonshire Building | 2017-01-03 19:15 | 49715.3184 | 60.012
Devonshire Building | 2017-01-03 19:30 | 49715.3284 | 39.996
Devonshire Building | 2017-01-03 19:45 | 49715.3434 | 60.012
Devonshire Building | 2017-01-03 20:00 | 49715.3534 | 39.996
Devonshire Building | 2017-01-03 20:15 | 49715.3634 | 39.996
Devonshire Building | 2017-01-03 20:30 | 49715.3734 | 39.996
Devonshire Building | 2017-01-03 20:45 | 49715.3784 | 20.016
Devonshire Building | 2017-01-03 21:00 | 49715.3884 | 39.996
Devonshire Building | 2017-01-03 21:15 | 49715.3984 | 39.996
Devonshire Building | 2017-01-03 21:30 | 49715.4034 | 20.016
Devonshire Building | 2017-01-03 21:45 | 49715.4084 | 20.016
Devonshire Building | 2017-01-03 22:00 | 49715.6884 | 1119.996
Devonshire Building | 2017-01-03 22:15 | 49715.6884 | 0
Devonshire Building | 2017-01-03 22:30 | 49715.6934 | 20.016
Devonshire Building | 2017-01-03 22:45 | 49715.6934 | 0
Devonshire Building | 2017-01-03 23:00 | 49715.6984 | 20.016
Devonshire Building | 2017-01-03 23:15 | 49715.6984 | 0
Devonshire Building | 2017-01-03 23:30 | 49715.7034 | 20.016
Devonshire Building | 2017-01-03 23:45 | 49715.7034 | 0 | 0
Devonshire Building | 2017-01-04 | 49715.7109 | 20.016
Devonshire Building | 2017-01-04 00:15 | 49715.7109 | 0
Devonshire Building | 2017-01-04 00:30 | 49715.7159 | 20.016
Devonshire Building | 2017-01-04 00:45 | 49715.7159 | 0
Devonshire Building | 2017-01-04 01:00 | 49715.7209 | 20.016
Devonshire Building | 2017-01-04 01:15 | 49715.7209 | 0
Devonshire Building | 2017-01-04 01:30 | 49715.7309 | 39.996
Devonshire Building | 2017-01-04 01:45 | 49715.7509 | 79.992
Devonshire Building | 2017-01-04 02:00 | 49715.7659 | 60.012
Devonshire Building | 2017-01-04 02:15 | 49715.7859 | 79.992
Devonshire Building | 2017-01-04 02:30 | 49715.8059 | 79.992
Devonshire Building | 2017-01-04 02:45 | 49715.8209 | 60.012
Devonshire Building | 2017-01-04 03:00 | 49715.8409 | 79.992
Devonshire Building | 2017-01-04 03:15 | 49715.8609 | 79.992
Devonshire Building | 2017-01-04 03:30 | 49715.8759 | 60.012
Devonshire Building | 2017-01-04 03:45 | 49715.8959 | 79.992
Devonshire Building | 2017-01-04 04:00 | 49715.9159 | 79.992
Devonshire Building | 2017-01-04 04:15 | 49715.9209 | 20.016
Devonshire Building | 2017-01-04 04:30 | 49715.9209 | 0
Devonshire Building | 2017-01-04 04:45 | 49715.9259 | 20.016
Devonshire Building | 2017-01-04 05:00 | 49715.9259 | 0
Devonshire Building | 2017-01-04 05:15 | 49715.931 | 20.016
Devonshire Building | 2017-01-04 05:30 | 49715.931 | 0
Devonshire Building | 2017-01-04 05:45 | 49715.936 | 20.016
Devonshire Building | 2017-01-04 06:00 | 49715.936 | 0
Devonshire Building | 2017-01-04 06:15 | 49715.941 | 20.016
Devonshire Building | 2017-01-04 06:30 | 49715.946 | 20.016
Devonshire Building | 2017-01-04 06:45 | 49715.946 | 0
Devonshire Building | 2017-01-04 07:00 | 49715.951 | 20.016
Devonshire Building | 2017-01-04 07:15 | 49715.956 | 20.016
Devonshire Building | 2017-01-04 07:30 | 49715.956 | 0
Devonshire Building | 2017-01-04 07:45 | 49715.961 | 20.016
Devonshire Building | 2017-01-04 08:00 | 49715.966 | 20.016
Devonshire Building | 2017-01-04 08:15 | 49715.976 | 39.996
Devonshire Building | 2017-01-04 08:30 | 49715.981 | 20.016
Devonshire Building | 2017-01-04 08:45 | 49715.996 | 60.012
Devonshire Building | 2017-01-04 09:00 | 49716.006 | 39.996
Devonshire Building | 2017-01-04 09:15 | 49716.011 | 20.016
Devonshire Building | 2017-01-04 09:30 | 49716.011 | 0
Devonshire Building | 2017-01-04 09:45 | 49716.021 | 39.996
Devonshire Building | 2017-01-04 10:00 | 49716.181 | 640.008
Devonshire Building | 2017-01-04 10:15 | 49716.346 | 659.988
Devonshire Building | 2017-01-04 10:30 | 49716.411 | 259.992
Devonshire Building | 2017-01-04 10:45 | 49716.501 | 360
Devonshire Building | 2017-01-04 11:00 | 49716.596 | 380.016
Devonshire Building | 2017-01-04 11:15 | 49716.681 | 339.984
Devonshire Building | 2017-01-04 11:30 | 49716.751 | 280.008
Devonshire Building | 2017-01-04 11:45 | 49717.051 | 1199.988
Devonshire Building | 2017-01-04 12:00 | 49717.151 | 399.996
Devonshire Building | 2017-01-04 12:15 | 49717.191 | 159.984
Devonshire Building | 2017-01-04 12:30 | 49717.236 | 180
Devonshire Building | 2017-01-04 12:45 | 49717.286 | 200.016
Devonshire Building | 2017-01-04 13:00 | 49717.336 | 200.016
Devonshire Building | 2017-01-04 13:15 | 49717.381 | 180
Devonshire Building | 2017-01-04 13:30 | 49717.716 | 1339.992
Devonshire Building | 2017-01-04 13:45 | 49717.746 | 119.988
Devonshire Building | 2017-01-04 14:00 | 49717.776 | 119.988
Devonshire Building | 2017-01-04 14:15 | 49717.806 | 119.988
Devonshire Building | 2017-01-04 14:30 | 49717.836 | 119.988
Devonshire Building | 2017-01-04 14:45 | 49717.866 | 119.988
Devonshire Building | 2017-01-04 15:00 | 49717.896 | 119.988
Devonshire Building | 2017-01-04 15:15 | 49717.926 | 119.988
Devonshire Building | 2017-01-04 15:30 | 49718.266 | 1360.008
Devonshire Building | 2017-01-04 15:45 | 49718.291 | 100.008
Devonshire Building | 2017-01-04 16:00 | 49718.326 | 140.004
Devonshire Building | 2017-01-04 16:15 | 49718.351 | 100.008
Devonshire Building | 2017-01-04 16:30 | 49718.376 | 100.008
Devonshire Building | 2017-01-04 16:45 | 49718.406 | 119.988
Devonshire Building | 2017-01-04 17:00 | 49718.436 | 119.988
Devonshire Building | 2017-01-04 17:15 | 49718.631 | 780.012
Devonshire Building | 2017-01-04 17:30 | 49718.811 | 720
Devonshire Building | 2017-01-04 17:45 | 49718.856 | 180
Devonshire Building | 2017-01-04 18:00 | 49718.906 | 200.016
Devonshire Building | 2017-01-04 18:15 | 49718.946 | 159.984
Devonshire Building | 2017-01-04 18:30 | 49718.986 | 159.984
Devonshire Building | 2017-01-04 18:45 | 49719.021 | 140.004
Devonshire Building | 2017-01-04 19:00 | 49719.051 | 119.988
Devonshire Building | 2017-01-04 19:15 | 49719.081 | 119.988
Devonshire Building | 2017-01-04 19:30 | 49719.101 | 79.992
Devonshire Building | 2017-01-04 19:45 | 49719.136 | 140.004
Devonshire Building | 2017-01-04 20:00 | 49719.171 | 140.004
Devonshire Building | 2017-01-04 20:15 | 49719.201 | 119.988
Devonshire Building | 2017-01-04 20:30 | 49719.236 | 140.004
Devonshire Building | 2017-01-04 20:45 | 49719.266 | 119.988
Devonshire Building | 2017-01-04 21:00 | 49719.296 | 119.988
Devonshire Building | 2017-01-04 21:15 | 49719.321 | 100.008
Devonshire Building | 2017-01-04 21:30 | 49719.346 | 100.008
Devonshire Building | 2017-01-04 21:45 | 49719.376 | 119.988
Devonshire Building | 2017-01-04 22:00 | 49719.416 | 159.984
Devonshire Building | 2017-01-04 22:15 | 49719.421 | 20.016
Devonshire Building | 2017-01-04 22:30 | 49719.426 | 20.016
Devonshire Building | 2017-01-04 22:45 | 49719.431 | 20.016
Devonshire Building | 2017-01-04 23:00 | 49719.431 | 0
Devonshire Building | 2017-01-04 23:15 | 49719.436 | 20.016
Devonshire Building | 2017-01-04 23:30 | 49719.436 | 0
Devonshire Building | 2017-01-04 23:45 | 49719.441 | 20.016 | 0
Devonshire Building | 2017-01-05 | 49719.4453 | 20.016
Devonshire Building | 2017-01-05 00:15 | 49719.4453 | 0
Devonshire Building | 2017-01-05 00:30 | 49719.4503 | 20.016
Devonshire Building | 2017-01-05 00:45 | 49719.4503 | 0
Devonshire Building | 2017-01-05 01:00 | 49719.4553 | 20.016
Devonshire Building | 2017-01-05 01:15 | 49719.4553 | 0
Devonshire Building | 2017-01-05 01:30 | 49719.4603 | 20.016
Devonshire Building | 2017-01-05 01:45 | 49719.4653 | 20.016
Devonshire Building | 2017-01-05 02:00 | 49719.4653 | 0
Devonshire Building | 2017-01-05 02:15 | 49719.4703 | 20.016
Devonshire Building | 2017-01-05 02:30 | 49719.4703 | 0
Devonshire Building | 2017-01-05 02:45 | 49719.4753 | 20.016
Devonshire Building | 2017-01-05 03:00 | 49719.4753 | 0
Devonshire Building | 2017-01-05 03:15 | 49719.4803 | 20.016
Devonshire Building | 2017-01-05 03:30 | 49719.4803 | 0
Devonshire Building | 2017-01-05 03:45 | 49719.4853 | 20.016
Devonshire Building | 2017-01-05 04:00 | 49719.4853 | 0
Devonshire Building | 2017-01-05 04:15 | 49719.4903 | 20.016
Devonshire Building | 2017-01-05 04:30 | 49719.4903 | 0
Devonshire Building | 2017-01-05 04:45 | 49719.4953 | 20.016
Devonshire Building | 2017-01-05 05:00 | 49719.5004 | 20.016
Devonshire Building | 2017-01-05 05:15 | 49719.5004 | 0
Devonshire Building | 2017-01-05 05:30 | 49719.5054 | 20.016
Devonshire Building | 2017-01-05 05:45 | 49719.5054 | 0
Devonshire Building | 2017-01-05 06:00 | 49719.5104 | 20.016
Devonshire Building | 2017-01-05 06:15 | 49719.5104 | 0
Devonshire Building | 2017-01-05 06:30 | 49719.5154 | 20.016
Devonshire Building | 2017-01-05 06:45 | 49719.5204 | 20.016
Devonshire Building | 2017-01-05 07:00 | 49719.5204 | 0
Devonshire Building | 2017-01-05 07:15 | 49719.5304 | 39.996
Devonshire Building | 2017-01-05 07:30 | 49719.5354 | 20.016
Devonshire Building | 2017-01-05 07:45 | 49719.5504 | 60.012
Devonshire Building | 2017-01-05 08:00 | 49719.5554 | 20.016
Devonshire Building | 2017-01-05 08:15 | 49719.5604 | 20.016
Devonshire Building | 2017-01-05 08:30 | 49719.5654 | 20.016
Devonshire Building | 2017-01-05 08:45 | 49719.8454 | 1119.996
Devonshire Building | 2017-01-05 09:00 | 49719.8554 | 39.996
Devonshire Building | 2017-01-05 09:15 | 49719.8604 | 20.016
Devonshire Building | 2017-01-05 09:30 | 49719.8704 | 39.996
Devonshire Building | 2017-01-05 09:45 | 49719.8804 | 39.996
Devonshire Building | 2017-01-05 10:00 | 49719.8854 | 20.016
Devonshire Building | 2017-01-05 10:15 | 49719.9054 | 79.992
Devonshire Building | 2017-01-05 10:30 | 49720.2254 | 1280.016
Devonshire Building | 2017-01-05 10:45 | 49720.3304 | 420.012
Devonshire Building | 2017-01-05 11:00 | 49720.4404 | 439.992
Devonshire Building | 2017-01-05 11:15 | 49720.5504 | 439.992
Devonshire Building | 2017-01-05 11:30 | 49720.6404 | 360
Devonshire Building | 2017-01-05 11:45 | 49720.7154 | 299.988
Devonshire Building | 2017-01-05 12:00 | 49720.7704 | 219.996
Devonshire Building | 2017-01-05 12:15 | 49721.1654 | 1580.004
Devonshire Building | 2017-01-05 12:30 | 49721.2104 | 180
Devonshire Building | 2017-01-05 12:45 | 49721.2404 | 119.988
Devonshire Building | 2017-01-05 13:00 | 49721.2854 | 180
Devonshire Building | 2017-01-05 13:15 | 49721.3304 | 180
Devonshire Building | 2017-01-05 13:30 | 49721.6654 | 1339.992
Devonshire Building | 2017-01-05 13:45 | 49721.7104 | 180
Devonshire Building | 2017-01-05 14:00 | 49721.7604 | 200.016
Devonshire Building | 2017-01-05 14:15 | 49721.8104 | 200.016
Devonshire Building | 2017-01-05 14:30 | 49721.8604 | 200.016
Devonshire Building | 2017-01-05 14:45 | 49721.9154 | 219.996
Devonshire Building | 2017-01-05 15:00 | 49721.9654 | 200.016
Devonshire Building | 2017-01-05 15:15 | 49722.3054 | 1360.008
Devonshire Building | 2017-01-05 15:30 | 49722.3554 | 200.016
Devonshire Building | 2017-01-05 15:45 | 49722.4104 | 219.996
Devonshire Building | 2017-01-05 16:00 | 49722.4654 | 219.996
Devonshire Building | 2017-01-05 16:15 | 49722.5104 | 180
Devonshire Building | 2017-01-05 16:30 | 49722.5554 | 180
Devonshire Building | 2017-01-05 16:45 | 49722.6004 | 180
Devonshire Building | 2017-01-05 17:00 | 49722.9504 | 1400.004
Devonshire Building | 2017-01-05 17:15 | 49722.9804 | 119.988
Devonshire Building | 2017-01-05 17:30 | 49723.0104 | 119.988
Devonshire Building | 2017-01-05 17:45 | 49723.0454 | 140.004
Devonshire Building | 2017-01-05 18:00 | 49723.0804 | 140.004
Devonshire Building | 2017-01-05 18:15 | 49723.1104 | 119.988
Devonshire Building | 2017-01-05 18:30 | 49723.1404 | 119.988
Devonshire Building | 2017-01-05 18:45 | 49723.1754 | 140.004
Devonshire Building | 2017-01-05 19:00 | 49723.2004 | 100.008
Devonshire Building | 2017-01-05 19:15 | 49723.2304 | 119.988
Devonshire Building | 2017-01-05 19:30 | 49723.2604 | 119.988
Devonshire Building | 2017-01-05 19:45 | 49723.3004 | 159.984
Devonshire Building | 2017-01-05 20:00 | 49723.3404 | 159.984
Devonshire Building | 2017-01-05 20:15 | 49723.3704 | 119.988
Devonshire Building | 2017-01-05 20:30 | 49723.4054 | 140.004
Devonshire Building | 2017-01-05 20:45 | 49723.4354 | 119.988
Devonshire Building | 2017-01-05 21:00 | 49723.4654 | 119.988
Devonshire Building | 2017-01-05 21:15 | 49723.4954 | 119.988
Devonshire Building | 2017-01-05 21:30 | 49723.5204 | 100.008
Devonshire Building | 2017-01-05 21:45 | 49723.5504 | 119.988
Devonshire Building | 2017-01-05 22:00 | 49723.5954 | 180
Devonshire Building | 2017-01-05 22:15 | 49723.6104 | 60.012
Devonshire Building | 2017-01-05 22:30 | 49723.6254 | 60.012
Devonshire Building | 2017-01-05 22:45 | 49723.6254 | 0
Devonshire Building | 2017-01-05 23:00 | 49723.6304 | 20.016
Devonshire Building | 2017-01-05 23:15 | 49723.6354 | 20.016
Devonshire Building | 2017-01-05 23:30 | 49723.6354 | 0
Devonshire Building | 2017-01-05 23:45 | 49723.6404 | 20.016 | 0
Devonshire Building | 2017-01-06 | 49723.6445 | 20.016
Devonshire Building | 2017-01-06 00:15 | 49723.6445 | 0
Devonshire Building | 2017-01-06 00:30 | 49723.6495 | 20.016
Devonshire Building | 2017-01-06 00:45 | 49723.6545 | 20.016
Devonshire Building | 2017-01-06 01:00 | 49723.6545 | 0
Devonshire Building | 2017-01-06 01:15 | 49723.6595 | 20.016
Devonshire Building | 2017-01-06 01:30 | 49723.6595 | 0
Devonshire Building | 2017-01-06 01:45 | 49723.6645 | 20.016
Devonshire Building | 2017-01-06 02:00 | 49723.6645 | 0
Devonshire Building | 2017-01-06 02:15 | 49723.6695 | 20.016
Devonshire Building | 2017-01-06 02:30 | 49723.6746 | 20.016
Devonshire Building | 2017-01-06 02:45 | 49723.6746 | 0
Devonshire Building | 2017-01-06 03:00 | 49723.6796 | 20.016
Devonshire Building | 2017-01-06 03:15 | 49723.9496 | 1080
Devonshire Building | 2017-01-06 03:30 | 49723.9496 | 0
Devonshire Building | 2017-01-06 03:45 | 49723.9546 | 20.016
Devonshire Building | 2017-01-06 04:00 | 49723.9546 | 0
Devonshire Building | 2017-01-06 04:15 | 49723.9596 | 20.016
Devonshire Building | 2017-01-06 04:30 | 49723.9596 | 0
Devonshire Building | 2017-01-06 04:45 | 49723.9646 | 20.016
Devonshire Building | 2017-01-06 05:00 | 49723.9646 | 0
Devonshire Building | 2017-01-06 05:15 | 49723.9696 | 20.016
Devonshire Building | 2017-01-06 05:30 | 49723.9696 | 0
Devonshire Building | 2017-01-06 05:45 | 49723.9746 | 20.016
Devonshire Building | 2017-01-06 06:00 | 49723.9746 | 0
Devonshire Building | 2017-01-06 06:15 | 49723.9796 | 20.016
Devonshire Building | 2017-01-06 06:30 | 49723.9846 | 20.016
Devonshire Building | 2017-01-06 06:45 | 49723.9846 | 0
Devonshire Building | 2017-01-06 07:00 | 49723.9896 | 20.016
Devonshire Building | 2017-01-06 07:15 | 49723.9896 | 0
Devonshire Building | 2017-01-06 07:30 | 49723.9996 | 39.996
Devonshire Building | 2017-01-06 07:45 | 49724.0046 | 20.016
Devonshire Building | 2017-01-06 08:00 | 49724.0096 | 20.016
Devonshire Building | 2017-01-06 08:15 | 49724.0146 | 20.016
Devonshire Building | 2017-01-06 08:30 | 49724.0196 | 20.016
Devonshire Building | 2017-01-06 08:45 | 49724.0346 | 60.012
Devonshire Building | 2017-01-06 09:00 | 49724.0396 | 20.016
Devonshire Building | 2017-01-06 09:15 | 49724.0446 | 20.016
Devonshire Building | 2017-01-06 09:30 | 49724.0546 | 39.996
Devonshire Building | 2017-01-06 09:45 | 49724.1846 | 519.984
Devonshire Building | 2017-01-06 10:00 | 49724.3546 | 680.004
Devonshire Building | 2017-01-06 10:15 | 49724.3746 | 79.992
Devonshire Building | 2017-01-06 10:30 | 49724.3996 | 100.008
Devonshire Building | 2017-01-06 10:45 | 49724.4346 | 140.004
Devonshire Building | 2017-01-06 11:00 | 49724.7546 | 1280.016
Devonshire Building | 2017-01-06 11:15 | 49724.8396 | 339.984
Devonshire Building | 2017-01-06 11:30 | 49724.9046 | 259.992
Devonshire Building | 2017-01-06 11:45 | 49724.9646 | 240.012
Devonshire Building | 2017-01-06 12:00 | 49725.0246 | 240.012
Devonshire Building | 2017-01-06 12:15 | 49725.0796 | 219.996
Devonshire Building | 2017-01-06 12:30 | 49725.4196 | 1360.008
Devonshire Building | 2017-01-06 12:45 | 49725.4796 | 240.012
Devonshire Building | 2017-01-06 13:00 | 49725.5196 | 159.984
Devonshire Building | 2017-01-06 13:15 | 49725.5646 | 180
Devonshire Building | 2017-01-06 13:30 | 49725.6096 | 180
Devonshire Building | 2017-01-06 13:45 | 49725.6596 | 200.016
Devonshire Building | 2017-01-06 14:00 | 49725.7146 | 219.996
Devonshire Building | 2017-01-06 14:15 | 49726.0496 | 1339.992
Devonshire Building | 2017-01-06 14:30 | 49726.0996 | 200.016
Devonshire Building | 2017-01-06 14:45 | 49726.1446 | 180
Devonshire Building | 2017-01-06 15:00 | 49726.1946 | 200.016
Devonshire Building | 2017-01-06 15:15 | 49726.2396 | 180
Devonshire Building | 2017-01-06 15:30 | 49726.2896 | 200.016
Devonshire Building | 2017-01-06 15:45 | 49726.3346 | 180
Devonshire Building | 2017-01-06 16:00 | 49726.3746 | 159.984
Devonshire Building | 2017-01-06 16:15 | 49726.4196 | 180
Devonshire Building | 2017-01-06 16:30 | 49726.7496 | 1320.012
Devonshire Building | 2017-01-06 16:45 | 49726.7896 | 159.984
Devonshire Building | 2017-01-06 17:00 | 49726.8346 | 180
Devonshire Building | 2017-01-06 17:15 | 49726.8896 | 219.996
Devonshire Building | 2017-01-06 17:30 | 49726.9446 | 219.996
Devonshire Building | 2017-01-06 17:45 | 49727.0046 | 240.012
Devonshire Building | 2017-01-06 18:00 | 49727.0696 | 259.992
Devonshire Building | 2017-01-06 18:15 | 49727.1296 | 240.012
Devonshire Building | 2017-01-06 18:30 | 49727.1846 | 219.996
Devonshire Building | 2017-01-06 18:45 | 49727.2346 | 200.016
Devonshire Building | 2017-01-06 19:00 | 49727.2796 | 180
Devonshire Building | 2017-01-06 19:15 | 49727.3196 | 159.984
Devonshire Building | 2017-01-06 19:30 | 49727.3596 | 159.984
Devonshire Building | 2017-01-06 19:45 | 49727.4046 | 180
Devonshire Building | 2017-01-06 20:00 | 49727.4446 | 159.984
Devonshire Building | 2017-01-06 20:15 | 49727.4796 | 140.004
Devonshire Building | 2017-01-06 20:30 | 49727.5146 | 140.004
Devonshire Building | 2017-01-06 20:45 | 49727.5496 | 140.004
Devonshire Building | 2017-01-06 21:00 | 49727.5796 | 119.988
Devonshire Building | 2017-01-06 21:15 | 49727.6096 | 119.988
Devonshire Building | 2017-01-06 21:30 | 49727.6346 | 100.008
Devonshire Building | 2017-01-06 21:45 | 49727.6646 | 119.988
Devonshire Building | 2017-01-06 22:00 | 49727.7096 | 180
Devonshire Building | 2017-01-06 22:15 | 49727.7296 | 79.992
Devonshire Building | 2017-01-06 22:30 | 49727.7446 | 60.012
Devonshire Building | 2017-01-06 22:45 | 49727.7496 | 20.016
Devonshire Building | 2017-01-06 23:00 | 49727.7546 | 20.016
Devonshire Building | 2017-01-06 23:15 | 49727.7546 | 0
Devonshire Building | 2017-01-06 23:30 | 49727.7596 | 20.016
Devonshire Building | 2017-01-06 23:45 | 49727.7646 | 20.016 | 0
Devonshire Building | 2017-01-07 | 49727.7695 | 20.016
Devonshire Building | 2017-01-07 00:15 | 49727.7695 | 0
Devonshire Building | 2017-01-07 00:30 | 49727.7745 | 20.016
Devonshire Building | 2017-01-07 00:45 | 49727.7795 | 20.016
Devonshire Building | 2017-01-07 01:00 | 49727.7795 | 0
Devonshire Building | 2017-01-07 01:15 | 49727.7845 | 20.016
Devonshire Building | 2017-01-07 01:30 | 49727.7845 | 0
Devonshire Building | 2017-01-07 01:45 | 49727.7895 | 20.016
Devonshire Building | 2017-01-07 02:00 | 49728.0295 | 960.012
Devonshire Building | 2017-01-07 02:15 | 49728.0595 | 119.988
Devonshire Building | 2017-01-07 02:30 | 49728.0646 | 20.016
Devonshire Building | 2017-01-07 02:45 | 49728.0646 | 0
Devonshire Building | 2017-01-07 03:00 | 49728.0696 | 20.016
Devonshire Building | 2017-01-07 03:15 | 49728.0696 | 0
Devonshire Building | 2017-01-07 03:30 | 49728.0746 | 20.016
Devonshire Building | 2017-01-07 03:45 | 49728.0746 | 0
Devonshire Building | 2017-01-07 04:00 | 49728.0796 | 20.016
Devonshire Building | 2017-01-07 04:15 | 49728.0796 | 0
Devonshire Building | 2017-01-07 04:30 | 49728.0846 | 20.016
Devonshire Building | 2017-01-07 04:45 | 49728.0846 | 0
Devonshire Building | 2017-01-07 05:00 | 49728.0896 | 20.016
Devonshire Building | 2017-01-07 05:15 | 49728.0896 | 0
Devonshire Building | 2017-01-07 05:30 | 49728.0946 | 20.016
Devonshire Building | 2017-01-07 05:45 | 49728.0946 | 0
Devonshire Building | 2017-01-07 06:00 | 49728.0996 | 20.016
Devonshire Building | 2017-01-07 06:15 | 49728.0996 | 0
Devonshire Building | 2017-01-07 06:30 | 49728.1046 | 20.016
Devonshire Building | 2017-01-07 06:45 | 49728.1046 | 0
Devonshire Building | 2017-01-07 07:00 | 49728.1096 | 20.016
Devonshire Building | 2017-01-07 07:15 | 49728.1096 | 0
Devonshire Building | 2017-01-07 07:30 | 49728.1146 | 20.016
Devonshire Building | 2017-01-07 07:45 | 49728.1146 | 0
Devonshire Building | 2017-01-07 08:00 | 49728.1196 | 20.016
Devonshire Building | 2017-01-07 08:15 | 49728.1196 | 0
Devonshire Building | 2017-01-07 08:30 | 49728.1246 | 20.016
Devonshire Building | 2017-01-07 08:45 | 49728.1246 | 0
Devonshire Building | 2017-01-07 09:00 | 49728.1296 | 20.016
Devonshire Building | 2017-01-07 09:15 | 49728.1296 | 0
Devonshire Building | 2017-01-07 09:30 | 49728.1346 | 20.016
Devonshire Building | 2017-01-07 09:45 | 49728.1346 | 0
Devonshire Building | 2017-01-07 10:00 | 49728.1396 | 20.016
Devonshire Building | 2017-01-07 10:15 | 49728.1396 | 0
Devonshire Building | 2017-01-07 10:30 | 49728.1446 | 20.016
Devonshire Building | 2017-01-07 10:45 | 49728.1446 | 0
Devonshire Building | 2017-01-07 11:00 | 49728.1496 | 20.016
Devonshire Building | 2017-01-07 11:15 | 49728.1496 | 0
Devonshire Building | 2017-01-07 11:30 | 49728.1546 | 20.016
Devonshire Building | 2017-01-07 11:45 | 49728.1546 | 0
Devonshire Building | 2017-01-07 12:00 | 49728.1596 | 20.016
Devonshire Building | 2017-01-07 12:15 | 49728.1596 | 0
Devonshire Building | 2017-01-07 12:30 | 49728.1646 | 20.016
Devonshire Building | 2017-01-07 12:45 | 49728.1646 | 0
Devonshire Building | 2017-01-07 13:00 | 49728.1696 | 20.016
Devonshire Building | 2017-01-07 13:15 | 49728.1696 | 0
Devonshire Building | 2017-01-07 13:30 | 49728.1746 | 20.016
Devonshire Building | 2017-01-07 13:45 | 49728.1746 | 0
Devonshire Building | 2017-01-07 14:00 | 49728.1796 | 20.016
Devonshire Building | 2017-01-07 14:15 | 49728.1796 | 0
Devonshire Building | 2017-01-07 14:30 | 49728.1846 | 20.016
Devonshire Building | 2017-01-07 14:45 | 49728.1846 | 0
Devonshire Building | 2017-01-07 15:00 | 49728.1897 | 20.016
Devonshire Building | 2017-01-07 15:15 | 49728.1897 | 0
Devonshire Building | 2017-01-07 15:30 | 49728.1947 | 20.016
Devonshire Building | 2017-01-07 15:45 | 49728.1947 | 0
Devonshire Building | 2017-01-07 16:00 | 49728.1997 | 20.016
Devonshire Building | 2017-01-07 16:15 | 49728.1997 | 0
Devonshire Building | 2017-01-07 16:30 | 49728.2047 | 20.016
Devonshire Building | 2017-01-07 16:45 | 49728.2047 | 0
Devonshire Building | 2017-01-07 17:00 | 49728.2097 | 20.016
Devonshire Building | 2017-01-07 17:15 | 49728.2097 | 0
Devonshire Building | 2017-01-07 17:30 | 49728.2147 | 20.016
Devonshire Building | 2017-01-07 17:45 | 49728.2147 | 0
Devonshire Building | 2017-01-07 18:00 | 49728.2197 | 20.016
Devonshire Building | 2017-01-07 18:15 | 49728.2197 | 0
Devonshire Building | 2017-01-07 18:30 | 49728.2247 | 20.016
Devonshire Building | 2017-01-07 18:45 | 49728.2247 | 0
Devonshire Building | 2017-01-07 19:00 | 49728.2297 | 20.016
Devonshire Building | 2017-01-07 19:15 | 49728.2297 | 0
Devonshire Building | 2017-01-07 19:30 | 49728.2397 | 39.996
Devonshire Building | 2017-01-07 19:45 | 49728.2597 | 79.992
Devonshire Building | 2017-01-07 20:00 | 49728.2797 | 79.992
Devonshire Building | 2017-01-07 20:15 | 49728.2997 | 79.992
Devonshire Building | 2017-01-07 20:30 | 49728.3197 | 79.992
Devonshire Building | 2017-01-07 20:45 | 49728.3347 | 60.012
Devonshire Building | 2017-01-07 21:00 | 49728.3547 | 79.992
Devonshire Building | 2017-01-07 21:15 | 49728.3747 | 79.992
Devonshire Building | 2017-01-07 21:30 | 49728.3947 | 79.992
Devonshire Building | 2017-01-07 21:45 | 49728.4097 | 60.012
Devonshire Building | 2017-01-07 22:00 | 49728.4447 | 140.004
Devonshire Building | 2017-01-07 22:15 | 49728.4447 | 0
Devonshire Building | 2017-01-07 22:30 | 49728.4497 | 20.016
Devonshire Building | 2017-01-07 22:45 | 49728.4497 | 0
Devonshire Building | 2017-01-07 23:00 | 49728.4547 | 20.016
Devonshire Building | 2017-01-07 23:15 | 49728.4547 | 0
Devonshire Building | 2017-01-07 23:30 | 49728.4597 | 20.016
Devonshire Building | 2017-01-07 23:45 | 49728.4597 | 0 | 0
Devonshire Building | 2017-01-08 | 49728.4609 | 0
Devonshire Building | 2017-01-08 00:15 | 49728.4659 | 20.016
Devonshire Building | 2017-01-08 00:30 | 49728.4659 | 0
Devonshire Building | 2017-01-08 00:45 | 49728.4709 | 20.016
Devonshire Building | 2017-01-08 01:00 | 49728.4709 | 0
Devonshire Building | 2017-01-08 01:15 | 49728.476 | 20.016
Devonshire Building | 2017-01-08 01:30 | 49728.476 | 0
Devonshire Building | 2017-01-08 01:45 | 49728.481 | 20.016
Devonshire Building | 2017-01-08 02:00 | 49728.481 | 0
Devonshire Building | 2017-01-08 02:15 | 49728.746 | 1059.984
Devonshire Building | 2017-01-08 02:30 | 49728.746 | 0
Devonshire Building | 2017-01-08 02:45 | 49728.751 | 20.016
Devonshire Building | 2017-01-08 03:00 | 49728.751 | 0
Devonshire Building | 2017-01-08 03:15 | 49728.756 | 20.016
Devonshire Building | 2017-01-08 03:30 | 49728.756 | 0
Devonshire Building | 2017-01-08 03:45 | 49728.761 | 20.016
Devonshire Building | 2017-01-08 04:00 | 49728.761 | 0
Devonshire Building | 2017-01-08 04:15 | 49728.766 | 20.016
Devonshire Building | 2017-01-08 04:30 | 49728.766 | 0
Devonshire Building | 2017-01-08 04:45 | 49728.771 | 20.016
Devonshire Building | 2017-01-08 05:00 | 49728.771 | 0
Devonshire Building | 2017-01-08 05:15 | 49728.776 | 20.016
Devonshire Building | 2017-01-08 05:30 | 49728.776 | 0
Devonshire Building | 2017-01-08 05:45 | 49728.781 | 20.016
Devonshire Building | 2017-01-08 06:00 | 49728.781 | 0
Devonshire Building | 2017-01-08 06:15 | 49728.786 | 20.016
Devonshire Building | 2017-01-08 06:30 | 49728.786 | 0
Devonshire Building | 2017-01-08 06:45 | 49728.791 | 20.016
Devonshire Building | 2017-01-08 07:00 | 49728.791 | 0
Devonshire Building | 2017-01-08 07:15 | 49728.796 | 20.016
Devonshire Building | 2017-01-08 07:30 | 49728.796 | 0
Devonshire Building | 2017-01-08 07:45 | 49728.801 | 20.016
Devonshire Building | 2017-01-08 08:00 | 49728.801 | 0
Devonshire Building | 2017-01-08 08:15 | 49728.801 | 0
Devonshire Building | 2017-01-08 08:30 | 49728.806 | 20.016
Devonshire Building | 2017-01-08 08:45 | 49728.806 | 0
Devonshire Building | 2017-01-08 09:00 | 49728.811 | 20.016
Devonshire Building | 2017-01-08 09:15 | 49728.811 | 0
Devonshire Building | 2017-01-08 09:30 | 49728.816 | 20.016
Devonshire Building | 2017-01-08 09:45 | 49728.816 | 0
Devonshire Building | 2017-01-08 10:00 | 49728.821 | 20.016
Devonshire Building | 2017-01-08 10:15 | 49728.821 | 0
Devonshire Building | 2017-01-08 10:30 | 49728.826 | 20.016
Devonshire Building | 2017-01-08 10:45 | 49728.826 | 0
Devonshire Building | 2017-01-08 11:00 | 49728.831 | 20.016
Devonshire Building | 2017-01-08 11:15 | 49728.831 | 0
Devonshire Building | 2017-01-08 11:30 | 49728.836 | 20.016
Devonshire Building | 2017-01-08 11:45 | 49728.836 | 0
Devonshire Building | 2017-01-08 12:00 | 49728.841 | 20.016
Devonshire Building | 2017-01-08 12:15 | 49728.841 | 0
Devonshire Building | 2017-01-08 12:30 | 49728.846 | 20.016
Devonshire Building | 2017-01-08 12:45 | 49728.851 | 20.016
Devonshire Building | 2017-01-08 13:00 | 49728.851 | 0
Devonshire Building | 2017-01-08 13:15 | 49728.856 | 20.016
Devonshire Building | 2017-01-08 13:30 | 49728.856 | 0
Devonshire Building | 2017-01-08 13:45 | 49728.861 | 20.016
Devonshire Building | 2017-01-08 14:00 | 49728.861 | 0
Devonshire Building | 2017-01-08 14:15 | 49728.866 | 20.016
Devonshire Building | 2017-01-08 14:30 | 49728.866 | 0
Devonshire Building | 2017-01-08 14:45 | 49728.8711 | 20.016
Devonshire Building | 2017-01-08 15:00 | 49728.8711 | 0
Devonshire Building | 2017-01-08 15:15 | 49728.8761 | 20.016
Devonshire Building | 2017-01-08 15:30 | 49728.8761 | 0
Devonshire Building | 2017-01-08 15:45 | 49728.8811 | 20.016
Devonshire Building | 2017-01-08 16:00 | 49728.8811 | 0
Devonshire Building | 2017-01-08 16:15 | 49728.8861 | 20.016
Devonshire Building | 2017-01-08 16:30 | 49728.8861 | 0
Devonshire Building | 2017-01-08 16:45 | 49728.8911 | 20.016
Devonshire Building | 2017-01-08 17:00 | 49728.8911 | 0
Devonshire Building | 2017-01-08 17:15 | 49728.8961 | 20.016
Devonshire Building | 2017-01-08 17:30 | 49728.8961 | 0
Devonshire Building | 2017-01-08 17:45 | 49728.9011 | 20.016
Devonshire Building | 2017-01-08 18:00 | 49728.9011 | 0
Devonshire Building | 2017-01-08 18:15 | 49728.9061 | 20.016
Devonshire Building | 2017-01-08 18:30 | 49728.9061 | 0
Devonshire Building | 2017-01-08 18:45 | 49728.9111 | 20.016
Devonshire Building | 2017-01-08 19:00 | 49728.9111 | 0
Devonshire Building | 2017-01-08 19:15 | 49728.9311 | 79.992
Devonshire Building | 2017-01-08 19:30 | 49728.9511 | 79.992
Devonshire Building | 2017-01-08 19:45 | 49728.9661 | 60.012
Devonshire Building | 2017-01-08 20:00 | 49728.9861 | 79.992
Devonshire Building | 2017-01-08 20:15 | 49729.0061 | 79.992
Devonshire Building | 2017-01-08 20:30 | 49729.0211 | 60.012
Devonshire Building | 2017-01-08 20:45 | 49729.2911 | 1080
Devonshire Building | 2017-01-08 21:00 | 49729.3061 | 60.012
Devonshire Building | 2017-01-08 21:15 | 49729.3261 | 79.992
Devonshire Building | 2017-01-08 21:30 | 49729.3461 | 79.992
Devonshire Building | 2017-01-08 21:45 | 49729.3611 | 60.012
Devonshire Building | 2017-01-08 22:00 | 49729.3761 | 60.012
Devonshire Building | 2017-01-08 22:15 | 49729.3761 | 0
Devonshire Building | 2017-01-08 22:30 | 49729.3811 | 20.016
Devonshire Building | 2017-01-08 22:45 | 49729.3811 | 0
Devonshire Building | 2017-01-08 23:00 | 49729.3861 | 20.016
Devonshire Building | 2017-01-08 23:15 | 49729.3861 | 0
Devonshire Building | 2017-01-08 23:30 | 49729.3911 | 20.016
Devonshire Building | 2017-01-08 23:45 | 49729.3911 | 0 | 0
Devonshire Building | 2017-01-09 | 49729.3945 | 20.016
Devonshire Building | 2017-01-09 00:15 | 49729.3945 | 0
Devonshire Building | 2017-01-09 00:30 | 49729.3995 | 20.016
Devonshire Building | 2017-01-09 00:45 | 49729.3995 | 0
Devonshire Building | 2017-01-09 01:00 | 49729.4045 | 20.016
Devonshire Building | 2017-01-09 01:15 | 49729.4045 | 0
Devonshire Building | 2017-01-09 01:30 | 49729.4095 | 20.016
Devonshire Building | 2017-01-09 01:45 | 49729.4095 | 0
Devonshire Building | 2017-01-09 02:00 | 49729.4145 | 20.016
Devonshire Building | 2017-01-09 02:15 | 49729.4145 | 0
Devonshire Building | 2017-01-09 02:30 | 49729.4195 | 20.016
Devonshire Building | 2017-01-09 02:45 | 49729.4195 | 0
Devonshire Building | 2017-01-09 03:00 | 49729.4246 | 20.016
Devonshire Building | 2017-01-09 03:15 | 49729.4246 | 0
Devonshire Building | 2017-01-09 03:30 | 49729.4296 | 20.016
Devonshire Building | 2017-01-09 03:45 | 49729.4296 | 0
Devonshire Building | 2017-01-09 04:00 | 49729.4346 | 20.016
Devonshire Building | 2017-01-09 04:15 | 49729.4346 | 0
Devonshire Building | 2017-01-09 04:30 | 49729.4396 | 20.016
Devonshire Building | 2017-01-09 04:45 | 49729.4396 | 0
Devonshire Building | 2017-01-09 05:00 | 49729.4446 | 20.016
Devonshire Building | 2017-01-09 05:15 | 49729.4446 | 0
Devonshire Building | 2017-01-09 05:30 | 49729.4496 | 20.016
Devonshire Building | 2017-01-09 05:45 | 49729.4496 | 0
Devonshire Building | 2017-01-09 06:00 | 49729.4546 | 20.016
Devonshire Building | 2017-01-09 06:15 | 49729.4546 | 0
Devonshire Building | 2017-01-09 06:30 | 49729.4596 | 20.016
Devonshire Building | 2017-01-09 06:45 | 49729.4596 | 0
Devonshire Building | 2017-01-09 07:00 | 49729.4646 | 20.016
Devonshire Building | 2017-01-09 07:15 | 49729.4646 | 0
Devonshire Building | 2017-01-09 07:30 | 49729.4696 | 20.016
Devonshire Building | 2017-01-09 07:45 | 49729.4746 | 20.016
Devonshire Building | 2017-01-09 08:00 | 49729.4846 | 39.996
Devonshire Building | 2017-01-09 08:15 | 49729.4946 | 39.996
Devonshire Building | 2017-01-09 08:30 | 49729.4996 | 20.016
Devonshire Building | 2017-01-09 08:45 | 49729.5296 | 119.988
Devonshire Building | 2017-01-09 09:00 | 49729.5496 | 79.992
Devonshire Building | 2017-01-09 09:15 | 49729.9546 | 1620
Devonshire Building | 2017-01-09 09:30 | 49729.9646 | 39.996
Devonshire Building | 2017-01-09 09:45 | 49729.9746 | 39.996
Devonshire Building | 2017-01-09 10:00 | 49729.9896 | 60.012
Devonshire Building | 2017-01-09 10:15 | 49729.9996 | 39.996
Devonshire Building | 2017-01-09 10:30 | 49730.0096 | 39.996
Devonshire Building | 2017-01-09 10:45 | 49730.3096 | 1199.988
Devonshire Building | 2017-01-09 11:00 | 49730.3346 | 100.008
Devonshire Building | 2017-01-09 11:15 | 49730.3996 | 259.992
Devonshire Building | 2017-01-09 11:30 | 49730.5296 | 519.984
Devonshire Building | 2017-01-09 11:45 | 49730.9446 | 1659.996
Devonshire Building | 2017-01-09 12:00 | 49731.1096 | 659.988
Devonshire Building | 2017-01-09 12:15 | 49731.2696 | 640.008
Devonshire Building | 2017-01-09 12:30 | 49731.4146 | 579.996
Devonshire Building | 2017-01-09 12:45 | 49731.5296 | 460.008
Devonshire Building | 2017-01-09 13:00 | 49731.6346 | 420.012
Devonshire Building | 2017-01-09 13:15 | 49732.0046 | 1479.996
Devonshire Building | 2017-01-09 13:30 | 49732.0746 | 280.008
Devonshire Building | 2017-01-09 13:45 | 49732.1546 | 320.004
Devonshire Building | 2017-01-09 14:00 | 49732.2246 | 280.008
Devonshire Building | 2017-01-09 14:15 | 49732.2896 | 259.992
Devonshire Building | 2017-01-09 14:30 | 49732.3546 | 259.992
Devonshire Building | 2017-01-09 14:45 | 49732.4096 | 219.996
Devonshire Building | 2017-01-09 15:00 | 49732.7596 | 1400.004
Devonshire Building | 2017-01-09 15:15 | 49732.8146 | 219.996
Devonshire Building | 2017-01-09 15:30 | 49732.8796 | 259.992
Devonshire Building | 2017-01-09 15:45 | 49732.9446 | 259.992
Devonshire Building | 2017-01-09 16:00 | 49733.0146 | 280.008
Devonshire Building | 2017-01-09 16:15 | 49733.0796 | 259.992
Devonshire Building | 2017-01-09 16:30 | 49733.1346 | 219.996
Devonshire Building | 2017-01-09 16:45 | 49733.2096 | 299.988
Devonshire Building | 2017-01-09 17:00 | 49733.5896 | 1519.992
Devonshire Building | 2017-01-09 17:15 | 49733.6746 | 339.984
Devonshire Building | 2017-01-09 17:30 | 49733.7496 | 299.988
Devonshire Building | 2017-01-09 17:45 | 49733.8146 | 259.992
Devonshire Building | 2017-01-09 18:00 | 49733.8646 | 200.016
Devonshire Building | 2017-01-09 18:15 | 49733.9046 | 159.984
Devonshire Building | 2017-01-09 18:30 | 49733.9396 | 140.004
Devonshire Building | 2017-01-09 18:45 | 49733.9696 | 119.988
Devonshire Building | 2017-01-09 19:00 | 49733.9946 | 100.008
Devonshire Building | 2017-01-09 19:15 | 49734.0196 | 100.008
Devonshire Building | 2017-01-09 19:30 | 49734.0396 | 79.992
Devonshire Building | 2017-01-09 19:45 | 49734.0546 | 60.012
Devonshire Building | 2017-01-09 20:00 | 49734.0696 | 60.012
Devonshire Building | 2017-01-09 20:15 | 49734.0846 | 60.012
Devonshire Building | 2017-01-09 20:30 | 49734.0996 | 60.012
Devonshire Building | 2017-01-09 20:45 | 49734.1096 | 39.996
Devonshire Building | 2017-01-09 21:00 | 49734.1246 | 60.012
Devonshire Building | 2017-01-09 21:15 | 49734.1346 | 39.996
Devonshire Building | 2017-01-09 21:30 | 49734.1446 | 39.996
Devonshire Building | 2017-01-09 21:45 | 49734.1546 | 39.996
Devonshire Building | 2017-01-09 22:00 | 49734.1796 | 100.008
Devonshire Building | 2017-01-09 22:15 | 49734.1846 | 20.016
Devonshire Building | 2017-01-09 22:30 | 49734.1896 | 20.016
Devonshire Building | 2017-01-09 22:45 | 49734.1896 | 0
Devonshire Building | 2017-01-09 23:00 | 49734.1946 | 20.016
Devonshire Building | 2017-01-09 23:15 | 49734.1946 | 0
Devonshire Building | 2017-01-09 23:30 | 49734.1996 | 20.016
Devonshire Building | 2017-01-09 23:45 | 49734.1996 | 0 | 0
Devonshire Building | 2017-01-10 | 49734.2031 | 20.016
Devonshire Building | 2017-01-10 00:15 | 49734.2031 | 0
Devonshire Building | 2017-01-10 00:30 | 49734.2081 | 20.016
Devonshire Building | 2017-01-10 00:45 | 49734.2081 | 0
Devonshire Building | 2017-01-10 01:00 | 49734.2131 | 20.016
Devonshire Building | 2017-01-10 01:15 | 49734.2181 | 20.016
Devonshire Building | 2017-01-10 01:30 | 49734.2181 | 0
Devonshire Building | 2017-01-10 01:45 | 49734.2231 | 20.016
Devonshire Building | 2017-01-10 02:00 | 49734.2231 | 0
Devonshire Building | 2017-01-10 02:15 | 49734.2282 | 20.016
Devonshire Building | 2017-01-10 02:30 | 49734.2282 | 0
Devonshire Building | 2017-01-10 02:45 | 49734.2332 | 20.016
Devonshire Building | 2017-01-10 03:00 | 49734.2332 | 0
Devonshire Building | 2017-01-10 03:15 | 49734.2382 | 20.016
Devonshire Building | 2017-01-10 03:30 | 49734.2382 | 0
Devonshire Building | 2017-01-10 03:45 | 49734.2432 | 20.016
Devonshire Building | 2017-01-10 04:00 | 49734.2432 | 0
Devonshire Building | 2017-01-10 04:15 | 49734.2482 | 20.016
Devonshire Building | 2017-01-10 04:30 | 49734.2482 | 0
Devonshire Building | 2017-01-10 04:45 | 49734.2532 | 20.016
Devonshire Building | 2017-01-10 05:00 | 49734.2532 | 0
Devonshire Building | 2017-01-10 05:15 | 49734.2582 | 20.016
Devonshire Building | 2017-01-10 05:30 | 49734.2582 | 0
Devonshire Building | 2017-01-10 05:45 | 49734.2632 | 20.016
Devonshire Building | 2017-01-10 06:00 | 49734.2632 | 0
Devonshire Building | 2017-01-10 06:15 | 49734.2682 | 20.016
Devonshire Building | 2017-01-10 06:30 | 49734.2682 | 0
Devonshire Building | 2017-01-10 06:45 | 49734.2732 | 20.016
Devonshire Building | 2017-01-10 07:00 | 49734.2732 | 0
Devonshire Building | 2017-01-10 07:15 | 49734.2782 | 20.016
Devonshire Building | 2017-01-10 07:30 | 49734.2932 | 60.012
Devonshire Building | 2017-01-10 07:45 | 49734.5732 | 1119.996
Devonshire Building | 2017-01-10 08:00 | 49734.5932 | 79.992
Devonshire Building | 2017-01-10 08:15 | 49734.6132 | 79.992
Devonshire Building | 2017-01-10 08:30 | 49734.6382 | 100.008
Devonshire Building | 2017-01-10 08:45 | 49734.6582 | 79.992
Devonshire Building | 2017-01-10 09:00 | 49734.6932 | 140.004
Devonshire Building | 2017-01-10 09:15 | 49734.7182 | 100.008
Devonshire Building | 2017-01-10 09:30 | 49734.7382 | 79.992
Devonshire Building | 2017-01-10 09:45 | 49734.7582 | 79.992
Devonshire Building | 2017-01-10 10:00 | 49734.7832 | 100.008
Devonshire Building | 2017-01-10 10:15 | 49735.1132 | 1320.012
Devonshire Building | 2017-01-10 10:30 | 49735.2582 | 579.996
Devonshire Building | 2017-01-10 10:45 | 49735.4532 | 780.012
Devonshire Building | 2017-01-10 11:00 | 49735.5832 | 519.984
Devonshire Building | 2017-01-10 11:15 | 49735.6832 | 399.996
Devonshire Building | 2017-01-10 11:30 | 49736.0132 | 1320.012
Devonshire Building | 2017-01-10 11:45 | 49736.0532 | 159.984
Devonshire Building | 2017-01-10 12:00 | 49736.0932 | 159.984
Devonshire Building | 2017-01-10 12:15 | 49736.1532 | 240.012
Devonshire Building | 2017-01-10 12:30 | 49736.2482 | 380.016
Devonshire Building | 2017-01-10 12:45 | 49736.7282 | 1919.988
Devonshire Building | 2017-01-10 13:00 | 49736.9382 | 839.988
Devonshire Building | 2017-01-10 13:15 | 49737.1382 | 799.992
Devonshire Building | 2017-01-10 13:30 | 49737.2982 | 640.008
Devonshire Building | 2017-01-10 13:45 | 49737.4132 | 460.008
Devonshire Building | 2017-01-10 14:00 | 49737.5482 | 540
Devonshire Building | 2017-01-10 14:15 | 49737.9282 | 1519.992
Devonshire Building | 2017-01-10 14:30 | 49738.0232 | 380.016
Devonshire Building | 2017-01-10 14:45 | 49738.1032 | 320.004
Devonshire Building | 2017-01-10 15:00 | 49738.1682 | 259.992
Devonshire Building | 2017-01-10 15:15 | 49738.2232 | 219.996
Devonshire Building | 2017-01-10 15:30 | 49738.2782 | 219.996
Devonshire Building | 2017-01-10 15:45 | 49738.3232 | 180
Devonshire Building | 2017-01-10 16:00 | 49738.3732 | 200.016
Devonshire Building | 2017-01-10 16:15 | 49738.7132 | 1360.008
Devonshire Building | 2017-01-10 16:30 | 49738.7582 | 180
Devonshire Building | 2017-01-10 16:45 | 49738.8032 | 180
Devonshire Building | 2017-01-10 17:00 | 49738.8482 | 180
Devonshire Building | 2017-01-10 17:15 | 49738.8882 | 159.984
Devonshire Building | 2017-01-10 17:30 | 49738.9282 | 159.984
Devonshire Building | 2017-01-10 17:45 | 49738.9732 | 180
Devonshire Building | 2017-01-10 18:00 | 49739.0082 | 140.004
Devonshire Building | 2017-01-10 18:15 | 49739.2482 | 960.012
Devonshire Building | 2017-01-10 18:30 | 49739.3582 | 439.992
Devonshire Building | 2017-01-10 18:45 | 49739.3832 | 100.008
Devonshire Building | 2017-01-10 19:00 | 49739.4082 | 100.008
Devonshire Building | 2017-01-10 19:15 | 49739.4332 | 100.008
Devonshire Building | 2017-01-10 19:30 | 49739.4582 | 100.008
Devonshire Building | 2017-01-10 19:45 | 49739.4882 | 119.988
Devonshire Building | 2017-01-10 20:00 | 49739.5082 | 79.992
Devonshire Building | 2017-01-10 20:15 | 49739.5332 | 100.008
Devonshire Building | 2017-01-10 20:30 | 49739.5482 | 60.012
Devonshire Building | 2017-01-10 20:45 | 49739.5682 | 79.992
Devonshire Building | 2017-01-10 21:00 | 49739.5832 | 60.012
Devonshire Building | 2017-01-10 21:15 | 49739.5932 | 39.996
Devonshire Building | 2017-01-10 21:30 | 49739.6082 | 60.012
Devonshire Building | 2017-01-10 21:45 | 49739.6182 | 39.996
Devonshire Building | 2017-01-10 22:00 | 49739.6332 | 60.012
Devonshire Building | 2017-01-10 22:15 | 49739.6432 | 39.996
Devonshire Building | 2017-01-10 22:30 | 49739.6482 | 20.016
Devonshire Building | 2017-01-10 22:45 | 49739.6532 | 20.016
Devonshire Building | 2017-01-10 23:00 | 49739.6632 | 39.996
Devonshire Building | 2017-01-10 23:15 | 49739.6682 | 20.016
Devonshire Building | 2017-01-10 23:30 | 49739.6732 | 20.016
Devonshire Building | 2017-01-10 23:45 | 49739.6832 | 39.996 | 0
Devonshire Building | 2017-01-11 | 49739.6875 | 20.016
Devonshire Building | 2017-01-11 00:15 | 49739.6925 | 20.016
Devonshire Building | 2017-01-11 00:30 | 49739.6975 | 20.016
Devonshire Building | 2017-01-11 00:45 | 49739.7025 | 20.016
Devonshire Building | 2017-01-11 01:00 | 49739.7075 | 20.016
Devonshire Building | 2017-01-11 01:15 | 49739.7175 | 39.996
Devonshire Building | 2017-01-11 01:30 | 49739.7225 | 20.016
Devonshire Building | 2017-01-11 01:45 | 49739.7275 | 20.016
Devonshire Building | 2017-01-11 02:00 | 49739.7325 | 20.016
Devonshire Building | 2017-01-11 02:15 | 49739.7325 | 0
Devonshire Building | 2017-01-11 02:30 | 49739.7375 | 20.016
Devonshire Building | 2017-01-11 02:45 | 49739.7425 | 20.016
Devonshire Building | 2017-01-11 03:00 | 49739.7475 | 20.016
Devonshire Building | 2017-01-11 03:15 | 49739.7525 | 20.016
Devonshire Building | 2017-01-11 03:30 | 49739.7525 | 0
Devonshire Building | 2017-01-11 03:45 | 49739.7575 | 20.016
Devonshire Building | 2017-01-11 04:00 | 49739.7626 | 20.016
Devonshire Building | 2017-01-11 04:15 | 49739.7626 | 0
Devonshire Building | 2017-01-11 04:30 | 49739.7676 | 20.016
Devonshire Building | 2017-01-11 04:45 | 49739.7726 | 20.016
Devonshire Building | 2017-01-11 05:00 | 49739.7726 | 0
Devonshire Building | 2017-01-11 05:15 | 49739.7776 | 20.016
Devonshire Building | 2017-01-11 05:30 | 49739.7776 | 0
Devonshire Building | 2017-01-11 05:45 | 49739.7826 | 20.016
Devonshire Building | 2017-01-11 06:00 | 49739.7876 | 20.016
Devonshire Building | 2017-01-11 06:15 | 49739.7926 | 20.016
Devonshire Building | 2017-01-11 06:30 | 49739.7926 | 0
Devonshire Building | 2017-01-11 06:45 | 49739.7976 | 20.016
Devonshire Building | 2017-01-11 07:00 | 49739.8026 | 20.016
Devonshire Building | 2017-01-11 07:15 | 49739.8076 | 20.016
Devonshire Building | 2017-01-11 07:30 | 49739.8126 | 20.016
Devonshire Building | 2017-01-11 07:45 | 49739.8326 | 79.992
Devonshire Building | 2017-01-11 08:00 | 49739.8526 | 79.992
Devonshire Building | 2017-01-11 08:15 | 49739.8776 | 100.008
Devonshire Building | 2017-01-11 08:30 | 49739.9126 | 140.004
Devonshire Building | 2017-01-11 08:45 | 49739.9326 | 79.992
Devonshire Building | 2017-01-11 09:00 | 49740.2776 | 1379.988
Devonshire Building | 2017-01-11 09:15 | 49740.3026 | 100.008
Devonshire Building | 2017-01-11 09:30 | 49740.3276 | 100.008
Devonshire Building | 2017-01-11 09:45 | 49740.3526 | 100.008
Devonshire Building | 2017-01-11 10:00 | 49740.3776 | 100.008
Devonshire Building | 2017-01-11 10:15 | 49740.5076 | 519.984
Devonshire Building | 2017-01-11 10:30 | 49740.9126 | 1620
Devonshire Building | 2017-01-11 10:45 | 49741.0776 | 659.988
Devonshire Building | 2017-01-11 11:00 | 49741.2126 | 540
Devonshire Building | 2017-01-11 11:15 | 49741.3476 | 540
Devonshire Building | 2017-01-11 11:30 | 49741.4876 | 560.016
Devonshire Building | 2017-01-11 11:45 | 49741.9276 | 1760.004
Devonshire Building | 2017-01-11 12:00 | 49742.0326 | 420.012
Devonshire Building | 2017-01-11 12:15 | 49742.1276 | 380.016
Devonshire Building | 2017-01-11 12:30 | 49742.2326 | 420.012
Devonshire Building | 2017-01-11 12:45 | 49742.3376 | 420.012
Devonshire Building | 2017-01-11 13:00 | 49742.7476 | 1640.016
Devonshire Building | 2017-01-11 13:15 | 49742.8476 | 399.996
Devonshire Building | 2017-01-11 13:30 | 49742.9376 | 360
Devonshire Building | 2017-01-11 13:45 | 49742.9976 | 240.012
Devonshire Building | 2017-01-11 14:00 | 49743.0526 | 219.996
Devonshire Building | 2017-01-11 14:15 | 49743.0976 | 180
Devonshire Building | 2017-01-11 14:30 | 49743.4326 | 1339.992
Devonshire Building | 2017-01-11 14:45 | 49743.4576 | 100.008
Devonshire Building | 2017-01-11 15:00 | 49743.4826 | 100.008
Devonshire Building | 2017-01-11 15:15 | 49743.5076 | 100.008
Devonshire Building | 2017-01-11 15:30 | 49743.5326 | 100.008
Devonshire Building | 2017-01-11 15:45 | 49743.5576 | 100.008
Devonshire Building | 2017-01-11 16:00 | 49743.8726 | 1260
Devonshire Building | 2017-01-11 16:15 | 49743.9026 | 119.988
Devonshire Building | 2017-01-11 16:30 | 49743.9276 | 100.008
Devonshire Building | 2017-01-11 16:45 | 49743.9576 | 119.988
Devonshire Building | 2017-01-11 17:00 | 49743.9876 | 119.988
Devonshire Building | 2017-01-11 17:15 | 49744.0176 | 119.988
Devonshire Building | 2017-01-11 17:30 | 49744.3326 | 1260
Devonshire Building | 2017-01-11 17:45 | 49744.3676 | 140.004
Devonshire Building | 2017-01-11 18:00 | 49744.4076 | 159.984
Devonshire Building | 2017-01-11 18:15 | 49744.4476 | 159.984
Devonshire Building | 2017-01-11 18:30 | 49744.4826 | 140.004
Devonshire Building | 2017-01-11 18:45 | 49744.5176 | 140.004
Devonshire Building | 2017-01-11 19:00 | 49744.5476 | 119.988
Devonshire Building | 2017-01-11 19:15 | 49744.5726 | 100.008
Devonshire Building | 2017-01-11 19:30 | 49744.6026 | 119.988
Devonshire Building | 2017-01-11 19:45 | 49744.6276 | 100.008
Devonshire Building | 2017-01-11 20:00 | 49744.6476 | 79.992
Devonshire Building | 2017-01-11 20:15 | 49744.6676 | 79.992
Devonshire Building | 2017-01-11 20:30 | 49744.6876 | 79.992
Devonshire Building | 2017-01-11 20:45 | 49744.7026 | 60.012
Devonshire Building | 2017-01-11 21:00 | 49744.7176 | 60.012
Devonshire Building | 2017-01-11 21:15 | 49744.7326 | 60.012
Devonshire Building | 2017-01-11 21:30 | 49744.7426 | 39.996
Devonshire Building | 2017-01-11 21:45 | 49744.7576 | 60.012
Devonshire Building | 2017-01-11 22:00 | 49744.7726 | 60.012
Devonshire Building | 2017-01-11 22:15 | 49744.7826 | 39.996
Devonshire Building | 2017-01-11 22:30 | 49744.7876 | 20.016
Devonshire Building | 2017-01-11 22:45 | 49744.7976 | 39.996
Devonshire Building | 2017-01-11 23:00 | 49744.8026 | 20.016
Devonshire Building | 2017-01-11 23:15 | 49744.8126 | 39.996
Devonshire Building | 2017-01-11 23:30 | 49744.8176 | 20.016
Devonshire Building | 2017-01-11 23:45 | 49744.8276 | 39.996 | 0
Devonshire Building | 2017-01-12 | 49744.8359 | 20.016
Devonshire Building | 2017-01-12 00:15 | 49744.8459 | 39.996
Devonshire Building | 2017-01-12 00:30 | 49744.8509 | 20.016
Devonshire Building | 2017-01-12 00:45 | 49744.8559 | 20.016
Devonshire Building | 2017-01-12 01:00 | 49744.8659 | 39.996
Devonshire Building | 2017-01-12 01:15 | 49744.8709 | 20.016
Devonshire Building | 2017-01-12 01:30 | 49744.876 | 20.016
Devonshire Building | 2017-01-12 01:45 | 49744.881 | 20.016
Devonshire Building | 2017-01-12 02:00 | 49744.891 | 39.996
Devonshire Building | 2017-01-12 02:15 | 49744.896 | 20.016
Devonshire Building | 2017-01-12 02:30 | 49744.901 | 20.016
Devonshire Building | 2017-01-12 02:45 | 49744.906 | 20.016
Devonshire Building | 2017-01-12 03:00 | 49744.911 | 20.016
Devonshire Building | 2017-01-12 03:15 | 49744.916 | 20.016
Devonshire Building | 2017-01-12 03:30 | 49744.921 | 20.016
Devonshire Building | 2017-01-12 03:45 | 49744.926 | 20.016
Devonshire Building | 2017-01-12 04:00 | 49744.931 | 20.016
Devonshire Building | 2017-01-12 04:15 | 49744.936 | 20.016
Devonshire Building | 2017-01-12 04:30 | 49744.941 | 20.016
Devonshire Building | 2017-01-12 04:45 | 49744.946 | 20.016
Devonshire Building | 2017-01-12 05:00 | 49744.951 | 20.016
Devonshire Building | 2017-01-12 05:15 | 49744.956 | 20.016
Devonshire Building | 2017-01-12 05:30 | 49744.956 | 0
Devonshire Building | 2017-01-12 05:45 | 49744.961 | 20.016
Devonshire Building | 2017-01-12 06:00 | 49744.966 | 20.016
Devonshire Building | 2017-01-12 06:15 | 49744.971 | 20.016
Devonshire Building | 2017-01-12 06:30 | 49744.976 | 20.016
Devonshire Building | 2017-01-12 06:45 | 49744.981 | 20.016
Devonshire Building | 2017-01-12 07:00 | 49744.986 | 20.016
Devonshire Building | 2017-01-12 07:15 | 49744.986 | 0
Devonshire Building | 2017-01-12 07:30 | 49744.991 | 20.016
Devonshire Building | 2017-01-12 07:45 | 49745.006 | 60.012
Devonshire Building | 2017-01-12 08:00 | 49745.036 | 119.988
Devonshire Building | 2017-01-12 08:15 | 49745.061 | 100.008
Devonshire Building | 2017-01-12 08:30 | 49745.086 | 100.008
Devonshire Building | 2017-01-12 08:45 | 49745.386 | 1199.988
Devonshire Building | 2017-01-12 09:00 | 49745.411 | 100.008
Devonshire Building | 2017-01-12 09:15 | 49745.441 | 119.988
Devonshire Building | 2017-01-12 09:30 | 49745.471 | 119.988
Devonshire Building | 2017-01-12 09:45 | 49745.496 | 100.008
Devonshire Building | 2017-01-12 10:00 | 49745.516 | 79.992
Devonshire Building | 2017-01-12 10:15 | 49745.541 | 100.008
Devonshire Building | 2017-01-12 10:30 | 49745.571 | 119.988
Devonshire Building | 2017-01-12 10:45 | 49745.906 | 1339.992
Devonshire Building | 2017-01-12 11:00 | 49745.946 | 159.984
Devonshire Building | 2017-01-12 11:15 | 49745.981 | 140.004
Devonshire Building | 2017-01-12 11:30 | 49746.021 | 159.984
Devonshire Building | 2017-01-12 11:45 | 49746.071 | 200.016
Devonshire Building | 2017-01-12 12:00 | 49746.121 | 200.016
Devonshire Building | 2017-01-12 12:15 | 49746.531 | 1640.016
Devonshire Building | 2017-01-12 12:30 | 49746.636 | 420.012
Devonshire Building | 2017-01-12 12:45 | 49746.726 | 360
Devonshire Building | 2017-01-12 13:00 | 49746.801 | 299.988
Devonshire Building | 2017-01-12 13:15 | 49746.861 | 240.012
Devonshire Building | 2017-01-12 13:30 | 49746.921 | 240.012
Devonshire Building | 2017-01-12 13:45 | 49747.261 | 1360.008
Devonshire Building | 2017-01-12 14:00 | 49747.301 | 159.984
Devonshire Building | 2017-01-12 14:15 | 49747.346 | 180
Devonshire Building | 2017-01-12 14:30 | 49747.391 | 180
Devonshire Building | 2017-01-12 14:45 | 49747.431 | 159.984
Devonshire Building | 2017-01-12 15:00 | 49747.471 | 159.984
Devonshire Building | 2017-01-12 15:15 | 49747.516 | 180
Devonshire Building | 2017-01-12 15:30 | 49747.556 | 159.984
Devonshire Building | 2017-01-12 15:45 | 49747.876 | 1280.016
Devonshire Building | 2017-01-12 16:00 | 49747.901 | 100.008
Devonshire Building | 2017-01-12 16:15 | 49747.921 | 79.992
Devonshire Building | 2017-01-12 16:30 | 49747.941 | 79.992
Devonshire Building | 2017-01-12 16:45 | 49747.966 | 100.008
Devonshire Building | 2017-01-12 17:00 | 49748.011 | 180
Devonshire Building | 2017-01-12 17:15 | 49748.061 | 200.016
Devonshire Building | 2017-01-12 17:30 | 49748.401 | 1360.008
Devonshire Building | 2017-01-12 17:45 | 49748.456 | 219.996
Devonshire Building | 2017-01-12 18:00 | 49748.511 | 219.996
Devonshire Building | 2017-01-12 18:15 | 49748.561 | 200.016
Devonshire Building | 2017-01-12 18:30 | 49748.606 | 180
Devonshire Building | 2017-01-12 18:45 | 49748.646 | 159.984
Devonshire Building | 2017-01-12 19:00 | 49748.676 | 119.988
Devonshire Building | 2017-01-12 19:15 | 49748.706 | 119.988
Devonshire Building | 2017-01-12 19:30 | 49748.731 | 100.008
Devonshire Building | 2017-01-12 19:45 | 49748.751 | 79.992
Devonshire Building | 2017-01-12 20:00 | 49748.771 | 79.992
Devonshire Building | 2017-01-12 20:15 | 49748.791 | 79.992
Devonshire Building | 2017-01-12 20:30 | 49748.806 | 60.012
Devonshire Building | 2017-01-12 20:45 | 49748.826 | 79.992
Devonshire Building | 2017-01-12 21:00 | 49748.841 | 60.012
Devonshire Building | 2017-01-12 21:15 | 49748.851 | 39.996
Devonshire Building | 2017-01-12 21:30 | 49748.866 | 60.012
Devonshire Building | 2017-01-12 21:45 | 49748.876 | 39.996
Devonshire Building | 2017-01-12 22:00 | 49748.906 | 119.988
Devonshire Building | 2017-01-12 22:15 | 49748.906 | 0
Devonshire Building | 2017-01-12 22:30 | 49748.911 | 20.016
Devonshire Building | 2017-01-12 22:45 | 49748.916 | 20.016
Devonshire Building | 2017-01-12 23:00 | 49748.916 | 0
Devonshire Building | 2017-01-12 23:15 | 49748.921 | 20.016
Devonshire Building | 2017-01-12 23:30 | 49748.926 | 20.016
Devonshire Building | 2017-01-12 23:45 | 49748.926 | 0 | 0
Devonshire Building | 2017-01-13 | 49748.9297 | 20.016
Devonshire Building | 2017-01-13 00:15 | 49748.9347 | 20.016
Devonshire Building | 2017-01-13 00:30 | 49748.9347 | 0
Devonshire Building | 2017-01-13 00:45 | 49748.9397 | 20.016
Devonshire Building | 2017-01-13 01:00 | 49748.9397 | 0
Devonshire Building | 2017-01-13 01:15 | 49748.9447 | 20.016
Devonshire Building | 2017-01-13 01:30 | 49748.9497 | 20.016
Devonshire Building | 2017-01-13 01:45 | 49748.9497 | 0
Devonshire Building | 2017-01-13 02:00 | 49748.9547 | 20.016
Devonshire Building | 2017-01-13 02:15 | 49748.9547 | 0
Devonshire Building | 2017-01-13 02:30 | 49748.9597 | 20.016
Devonshire Building | 2017-01-13 02:45 | 49748.9647 | 20.016
Devonshire Building | 2017-01-13 03:00 | 49748.9647 | 0
Devonshire Building | 2017-01-13 03:15 | 49748.9697 | 20.016
Devonshire Building | 2017-01-13 03:30 | 49748.9697 | 0
Devonshire Building | 2017-01-13 03:45 | 49748.9747 | 20.016
Devonshire Building | 2017-01-13 04:00 | 49748.9747 | 0
Devonshire Building | 2017-01-13 04:15 | 49748.9797 | 20.016
Devonshire Building | 2017-01-13 04:30 | 49748.9797 | 0
Devonshire Building | 2017-01-13 04:45 | 49748.9847 | 20.016
Devonshire Building | 2017-01-13 05:00 | 49748.9897 | 20.016
Devonshire Building | 2017-01-13 05:15 | 49748.9897 | 0
Devonshire Building | 2017-01-13 05:30 | 49748.9947 | 20.016
Devonshire Building | 2017-01-13 05:45 | 49748.9947 | 0
Devonshire Building | 2017-01-13 06:00 | 49748.9997 | 20.016
Devonshire Building | 2017-01-13 06:15 | 49748.9997 | 0
Devonshire Building | 2017-01-13 06:30 | 49749.0048 | 20.016
Devonshire Building | 2017-01-13 06:45 | 49749.0048 | 0
Devonshire Building | 2017-01-13 07:00 | 49749.0098 | 20.016
Devonshire Building | 2017-01-13 07:15 | 49749.0098 | 0
Devonshire Building | 2017-01-13 07:30 | 49749.0148 | 20.016
Devonshire Building | 2017-01-13 07:45 | 49749.0448 | 119.988
Devonshire Building | 2017-01-13 08:00 | 49749.0948 | 200.016
Devonshire Building | 2017-01-13 08:15 | 49749.3548 | 1040.004
Devonshire Building | 2017-01-13 08:30 | 49749.3748 | 79.992
Devonshire Building | 2017-01-13 08:45 | 49749.3948 | 79.992
Devonshire Building | 2017-01-13 09:00 | 49749.4198 | 100.008
Devonshire Building | 2017-01-13 09:15 | 49749.4398 | 79.992
Devonshire Building | 2017-01-13 09:30 | 49749.4648 | 100.008
Devonshire Building | 2017-01-13 09:45 | 49749.4898 | 100.008
Devonshire Building | 2017-01-13 10:00 | 49749.5098 | 79.992
Devonshire Building | 2017-01-13 10:15 | 49749.6548 | 579.996
Devonshire Building | 2017-01-13 10:30 | 49749.8848 | 920.016
Devonshire Building | 2017-01-13 10:45 | 49749.9998 | 460.008
Devonshire Building | 2017-01-13 11:00 | 49750.1098 | 439.992
Devonshire Building | 2017-01-13 11:15 | 49750.2198 | 439.992
Devonshire Building | 2017-01-13 11:30 | 49750.4348 | 860.004
Devonshire Building | 2017-01-13 11:45 | 49750.6848 | 1000.008
Devonshire Building | 2017-01-13 12:00 | 49750.7698 | 339.984
Devonshire Building | 2017-01-13 12:15 | 49750.8498 | 320.004
Devonshire Building | 2017-01-13 12:30 | 49750.9098 | 240.012
Devonshire Building | 2017-01-13 12:45 | 49751.2848 | 1500.012
Devonshire Building | 2017-01-13 13:00 | 49751.3348 | 200.016
Devonshire Building | 2017-01-13 13:15 | 49751.3798 | 180
Devonshire Building | 2017-01-13 13:30 | 49751.4248 | 180
Devonshire Building | 2017-01-13 13:45 | 49751.4748 | 200.016
Devonshire Building | 2017-01-13 14:00 | 49751.5248 | 200.016
Devonshire Building | 2017-01-13 14:15 | 49751.8648 | 1360.008
Devonshire Building | 2017-01-13 14:30 | 49751.9048 | 159.984
Devonshire Building | 2017-01-13 14:45 | 49751.9448 | 159.984
Devonshire Building | 2017-01-13 15:00 | 49751.9898 | 180
Devonshire Building | 2017-01-13 15:15 | 49752.0348 | 180
Devonshire Building | 2017-01-13 15:30 | 49752.2548 | 879.984
Devonshire Building | 2017-01-13 15:45 | 49752.4148 | 640.008
Devonshire Building | 2017-01-13 16:00 | 49752.4548 | 159.984
Devonshire Building | 2017-01-13 16:15 | 49752.4998 | 180
Devonshire Building | 2017-01-13 16:30 | 49752.5398 | 159.984
Devonshire Building | 2017-01-13 16:45 | 49752.5748 | 140.004
Devonshire Building | 2017-01-13 17:00 | 49752.6148 | 159.984
Devonshire Building | 2017-01-13 17:15 | 49752.9448 | 1320.012
Devonshire Building | 2017-01-13 17:30 | 49752.9798 | 140.004
Devonshire Building | 2017-01-13 17:45 | 49753.0148 | 140.004
Devonshire Building | 2017-01-13 18:00 | 49753.0598 | 180
Devonshire Building | 2017-01-13 18:15 | 49753.0998 | 159.984
Devonshire Building | 2017-01-13 18:30 | 49753.1448 | 180
Devonshire Building | 2017-01-13 18:45 | 49753.1848 | 159.984
Devonshire Building | 2017-01-13 19:00 | 49753.2248 | 159.984
Devonshire Building | 2017-01-13 19:15 | 49753.2598 | 140.004
Devonshire Building | 2017-01-13 19:30 | 49753.2997 | 159.984
Devonshire Building | 2017-01-13 19:45 | 49753.3297 | 119.988
Devonshire Building | 2017-01-13 20:00 | 49753.3647 | 140.004
Devonshire Building | 2017-01-13 20:15 | 49753.3947 | 119.988
Devonshire Building | 2017-01-13 20:30 | 49753.4197 | 100.008
Devonshire Building | 2017-01-13 20:45 | 49753.4447 | 100.008
Devonshire Building | 2017-01-13 21:00 | 49753.4697 | 100.008
Devonshire Building | 2017-01-13 21:15 | 49753.4897 | 79.992
Devonshire Building | 2017-01-13 21:30 | 49753.5048 | 60.012
Devonshire Building | 2017-01-13 21:45 | 49753.5198 | 60.012
Devonshire Building | 2017-01-13 22:00 | 49753.5548 | 140.004
Devonshire Building | 2017-01-13 22:15 | 49753.5598 | 20.016
Devonshire Building | 2017-01-13 22:30 | 49753.5598 | 0
Devonshire Building | 2017-01-13 22:45 | 49753.5648 | 20.016
Devonshire Building | 2017-01-13 23:00 | 49753.5698 | 20.016
Devonshire Building | 2017-01-13 23:15 | 49753.5748 | 20.016
Devonshire Building | 2017-01-13 23:30 | 49753.5798 | 20.016
Devonshire Building | 2017-01-13 23:45 | 49753.5848 | 20.016 | 0
Devonshire Building | 2017-01-14 | 49753.5898 | 20.016
Devonshire Building | 2017-01-14 00:15 | 49753.5948 | 20.016
Devonshire Building | 2017-01-14 00:30 | 49753.5998 | 20.016
Devonshire Building | 2017-01-14 00:45 | 49753.6049 | 20.016
Devonshire Building | 2017-01-14 01:00 | 49753.6099 | 20.016
Devonshire Building | 2017-01-14 01:15 | 49753.6099 | 0
Devonshire Building | 2017-01-14 01:30 | 49753.6149 | 20.016
Devonshire Building | 2017-01-14 01:45 | 49753.6199 | 20.016
Devonshire Building | 2017-01-14 02:00 | 49753.6249 | 20.016
Devonshire Building | 2017-01-14 02:15 | 49753.6299 | 20.016
Devonshire Building | 2017-01-14 02:30 | 49753.6349 | 20.016
Devonshire Building | 2017-01-14 02:45 | 49753.6349 | 0
Devonshire Building | 2017-01-14 03:00 | 49753.6399 | 20.016
Devonshire Building | 2017-01-14 03:15 | 49753.6449 | 20.016
Devonshire Building | 2017-01-14 03:30 | 49753.6499 | 20.016
Devonshire Building | 2017-01-14 03:45 | 49753.6499 | 0
Devonshire Building | 2017-01-14 04:00 | 49753.6549 | 20.016
Devonshire Building | 2017-01-14 04:15 | 49753.6599 | 20.016
Devonshire Building | 2017-01-14 04:30 | 49753.6649 | 20.016
Devonshire Building | 2017-01-14 04:45 | 49753.6649 | 0
Devonshire Building | 2017-01-14 05:00 | 49753.6699 | 20.016
Devonshire Building | 2017-01-14 05:15 | 49753.6749 | 20.016
Devonshire Building | 2017-01-14 05:30 | 49753.6749 | 0
Devonshire Building | 2017-01-14 05:45 | 49753.6799 | 20.016
Devonshire Building | 2017-01-14 06:00 | 49753.6849 | 20.016
Devonshire Building | 2017-01-14 06:15 | 49753.6849 | 0
Devonshire Building | 2017-01-14 06:30 | 49753.6899 | 20.016
Devonshire Building | 2017-01-14 06:45 | 49753.6949 | 20.016
Devonshire Building | 2017-01-14 07:00 | 49753.6949 | 0
Devonshire Building | 2017-01-14 07:15 | 49753.6999 | 20.016
Devonshire Building | 2017-01-14 07:30 | 49753.7099 | 39.996
Devonshire Building | 2017-01-14 07:45 | 49753.7299 | 79.992
Devonshire Building | 2017-01-14 08:00 | 49753.7499 | 79.992
Devonshire Building | 2017-01-14 08:15 | 49753.7699 | 79.992
Devonshire Building | 2017-01-14 08:30 | 49753.7899 | 79.992
Devonshire Building | 2017-01-14 08:45 | 49753.8099 | 79.992
Devonshire Building | 2017-01-14 09:00 | 49753.8249 | 60.012
Devonshire Building | 2017-01-14 09:15 | 49753.8449 | 79.992
Devonshire Building | 2017-01-14 09:30 | 49753.8649 | 79.992
Devonshire Building | 2017-01-14 09:45 | 49753.8849 | 79.992
Devonshire Building | 2017-01-14 10:00 | 49753.9049 | 79.992
Devonshire Building | 2017-01-14 10:15 | 49753.9199 | 60.012
Devonshire Building | 2017-01-14 10:30 | 49753.9499 | 119.988
Devonshire Building | 2017-01-14 10:45 | 49753.9599 | 39.996
Devonshire Building | 2017-01-14 11:00 | 49753.9699 | 39.996
Devonshire Building | 2017-01-14 11:15 | 49753.9749 | 20.016
Devonshire Building | 2017-01-14 11:30 | 49753.9749 | 0
Devonshire Building | 2017-01-14 11:45 | 49754.2599 | 1140.012
Devonshire Building | 2017-01-14 12:00 | 49754.2749 | 60.012
Devonshire Building | 2017-01-14 12:15 | 49754.2799 | 20.016
Devonshire Building | 2017-01-14 12:30 | 49754.2849 | 20.016
Devonshire Building | 2017-01-14 12:45 | 49754.2949 | 39.996
Devonshire Building | 2017-01-14 13:00 | 49754.2999 | 20.016
Devonshire Building | 2017-01-14 13:15 | 49754.2999 | 0
Devonshire Building | 2017-01-14 13:30 | 49754.3049 | 20.016
Devonshire Building | 2017-01-14 13:45 | 49754.3099 | 20.016
Devonshire Building | 2017-01-14 14:00 | 49754.5799 | 1080
Devonshire Building | 2017-01-14 14:15 | 49754.5849 | 20.016
Devonshire Building | 2017-01-14 14:30 | 49754.5899 | 20.016
Devonshire Building | 2017-01-14 14:45 | 49754.595 | 20.016
Devonshire Building | 2017-01-14 15:00 | 49754.595 | 0
Devonshire Building | 2017-01-14 15:15 | 49754.6 | 20.016
Devonshire Building | 2017-01-14 15:30 | 49754.61 | 39.996
Devonshire Building | 2017-01-14 15:45 | 49754.61 | 0
Devonshire Building | 2017-01-14 16:00 | 49754.615 | 20.016
Devonshire Building | 2017-01-14 16:15 | 49754.625 | 39.996
Devonshire Building | 2017-01-14 16:30 | 49754.63 | 20.016
Devonshire Building | 2017-01-14 16:45 | 49754.94 | 1239.984
Devonshire Building | 2017-01-14 17:00 | 49754.97 | 119.988
Devonshire Building | 2017-01-14 17:15 | 49755.005 | 140.004
Devonshire Building | 2017-01-14 17:30 | 49755.04 | 140.004
Devonshire Building | 2017-01-14 17:45 | 49755.075 | 140.004
Devonshire Building | 2017-01-14 18:00 | 49755.11 | 140.004
Devonshire Building | 2017-01-14 18:15 | 49755.14 | 119.988
Devonshire Building | 2017-01-14 18:30 | 49755.165 | 100.008
Devonshire Building | 2017-01-14 18:45 | 49755.19 | 100.008
Devonshire Building | 2017-01-14 19:00 | 49755.21 | 79.992
Devonshire Building | 2017-01-14 19:15 | 49755.23 | 79.992
Devonshire Building | 2017-01-14 19:30 | 49755.25 | 79.992
Devonshire Building | 2017-01-14 19:45 | 49755.27 | 79.992
Devonshire Building | 2017-01-14 20:00 | 49755.2799 | 39.996
Devonshire Building | 2017-01-14 20:15 | 49755.295 | 60.012
Devonshire Building | 2017-01-14 20:30 | 49755.31 | 60.012
Devonshire Building | 2017-01-14 20:45 | 49755.32 | 39.996
Devonshire Building | 2017-01-14 21:00 | 49755.33 | 39.996
Devonshire Building | 2017-01-14 21:15 | 49755.34 | 39.996
Devonshire Building | 2017-01-14 21:30 | 49755.35 | 39.996
Devonshire Building | 2017-01-14 21:45 | 49755.36 | 39.996
Devonshire Building | 2017-01-14 22:00 | 49755.375 | 60.012
Devonshire Building | 2017-01-14 22:15 | 49755.38 | 20.016
Devonshire Building | 2017-01-14 22:30 | 49755.385 | 20.016
Devonshire Building | 2017-01-14 22:45 | 49755.39 | 20.016
Devonshire Building | 2017-01-14 23:00 | 49755.4 | 39.996
Devonshire Building | 2017-01-14 23:15 | 49755.405 | 20.016
Devonshire Building | 2017-01-14 23:30 | 49755.41 | 20.016
Devonshire Building | 2017-01-14 23:45 | 49755.415 | 20.016 | 0
Devonshire Building | 2017-01-15 | 49755.418 | 20.016
Devonshire Building | 2017-01-15 00:15 | 49755.423 | 20.016
Devonshire Building | 2017-01-15 00:30 | 49755.433 | 39.996
Devonshire Building | 2017-01-15 00:45 | 49755.438 | 20.016
Devonshire Building | 2017-01-15 01:00 | 49755.443 | 20.016
Devonshire Building | 2017-01-15 01:15 | 49755.448 | 20.016
Devonshire Building | 2017-01-15 01:30 | 49755.453 | 20.016
Devonshire Building | 2017-01-15 01:45 | 49755.458 | 20.016
Devonshire Building | 2017-01-15 02:00 | 49755.463 | 20.016
Devonshire Building | 2017-01-15 02:15 | 49755.463 | 0
Devonshire Building | 2017-01-15 02:30 | 49755.468 | 20.016
Devonshire Building | 2017-01-15 02:45 | 49755.473 | 20.016
Devonshire Building | 2017-01-15 03:00 | 49755.478 | 20.016
Devonshire Building | 2017-01-15 03:15 | 49755.483 | 20.016
Devonshire Building | 2017-01-15 03:30 | 49755.488 | 20.016
Devonshire Building | 2017-01-15 03:45 | 49755.493 | 20.016
Devonshire Building | 2017-01-15 04:00 | 49755.498 | 20.016
Devonshire Building | 2017-01-15 04:15 | 49755.498 | 0
Devonshire Building | 2017-01-15 04:30 | 49755.503 | 20.016
Devonshire Building | 2017-01-15 04:45 | 49755.508 | 20.016
Devonshire Building | 2017-01-15 05:00 | 49755.513 | 20.016
Devonshire Building | 2017-01-15 05:15 | 49755.513 | 0
Devonshire Building | 2017-01-15 05:30 | 49755.518 | 20.016
Devonshire Building | 2017-01-15 05:45 | 49755.523 | 20.016
Devonshire Building | 2017-01-15 06:00 | 49755.528 | 20.016
Devonshire Building | 2017-01-15 06:15 | 49755.528 | 0
Devonshire Building | 2017-01-15 06:30 | 49755.5331 | 20.016
Devonshire Building | 2017-01-15 06:45 | 49755.5381 | 20.016
Devonshire Building | 2017-01-15 07:00 | 49755.5381 | 0
Devonshire Building | 2017-01-15 07:15 | 49755.5431 | 20.016
Devonshire Building | 2017-01-15 07:30 | 49755.5481 | 20.016
Devonshire Building | 2017-01-15 07:45 | 49755.5631 | 60.012
Devonshire Building | 2017-01-15 08:00 | 49755.5781 | 60.012
Devonshire Building | 2017-01-15 08:15 | 49755.5981 | 79.992
Devonshire Building | 2017-01-15 08:30 | 49755.6181 | 79.992
Devonshire Building | 2017-01-15 08:45 | 49755.6381 | 79.992
Devonshire Building | 2017-01-15 09:00 | 49755.6581 | 79.992
Devonshire Building | 2017-01-15 09:15 | 49755.6781 | 79.992
Devonshire Building | 2017-01-15 09:30 | 49755.6931 | 60.012
Devonshire Building | 2017-01-15 09:45 | 49755.7131 | 79.992
Devonshire Building | 2017-01-15 10:00 | 49755.7331 | 79.992
Devonshire Building | 2017-01-15 10:15 | 49755.7531 | 79.992
Devonshire Building | 2017-01-15 10:30 | 49755.7581 | 20.016
Devonshire Building | 2017-01-15 10:45 | 49755.7631 | 20.016
Devonshire Building | 2017-01-15 11:00 | 49755.7631 | 0
Devonshire Building | 2017-01-15 11:15 | 49755.7681 | 20.016
Devonshire Building | 2017-01-15 11:30 | 49755.7731 | 20.016
Devonshire Building | 2017-01-15 11:45 | 49755.7731 | 0
Devonshire Building | 2017-01-15 12:00 | 49755.7781 | 20.016
Devonshire Building | 2017-01-15 12:15 | 49755.7831 | 20.016
Devonshire Building | 2017-01-15 12:30 | 49755.7831 | 0
Devonshire Building | 2017-01-15 12:45 | 49755.7881 | 20.016
Devonshire Building | 2017-01-15 13:00 | 49755.7881 | 0
Devonshire Building | 2017-01-15 13:15 | 49755.7931 | 20.016
Devonshire Building | 2017-01-15 13:30 | 49755.7931 | 0
Devonshire Building | 2017-01-15 13:45 | 49755.7981 | 20.016
Devonshire Building | 2017-01-15 14:00 | 49755.8031 | 20.016
Devonshire Building | 2017-01-15 14:15 | 49755.8031 | 0
Devonshire Building | 2017-01-15 14:30 | 49755.8081 | 20.016
Devonshire Building | 2017-01-15 14:45 | 49755.8131 | 20.016
Devonshire Building | 2017-01-15 15:00 | 49755.8181 | 20.016
Devonshire Building | 2017-01-15 15:15 | 49755.8181 | 0
Devonshire Building | 2017-01-15 15:30 | 49755.8231 | 20.016
Devonshire Building | 2017-01-15 15:45 | 49755.8281 | 20.016
Devonshire Building | 2017-01-15 16:00 | 49755.8281 | 0
Devonshire Building | 2017-01-15 16:15 | 49755.8381 | 39.996
Devonshire Building | 2017-01-15 16:30 | 49755.8381 | 0
Devonshire Building | 2017-01-15 16:45 | 49755.8431 | 20.016
Devonshire Building | 2017-01-15 17:00 | 49755.8431 | 0
Devonshire Building | 2017-01-15 17:15 | 49755.8481 | 20.016
Devonshire Building | 2017-01-15 17:30 | 49756.1181 | 1080
Devonshire Building | 2017-01-15 17:45 | 49756.1181 | 0
Devonshire Building | 2017-01-15 18:00 | 49756.1231 | 20.016
Devonshire Building | 2017-01-15 18:15 | 49756.1231 | 0
Devonshire Building | 2017-01-15 18:30 | 49756.1281 | 20.016
Devonshire Building | 2017-01-15 18:45 | 49756.1331 | 20.016
Devonshire Building | 2017-01-15 19:00 | 49756.1331 | 0
Devonshire Building | 2017-01-15 19:15 | 49756.1381 | 20.016
Devonshire Building | 2017-01-15 19:30 | 49756.1381 | 0
Devonshire Building | 2017-01-15 19:45 | 49756.1431 | 20.016
Devonshire Building | 2017-01-15 20:00 | 49756.1431 | 0
Devonshire Building | 2017-01-15 20:15 | 49756.1481 | 20.016
Devonshire Building | 2017-01-15 20:30 | 49756.1532 | 20.016
Devonshire Building | 2017-01-15 20:45 | 49756.1532 | 0
Devonshire Building | 2017-01-15 21:00 | 49756.1582 | 20.016
Devonshire Building | 2017-01-15 21:15 | 49756.1582 | 0
Devonshire Building | 2017-01-15 21:30 | 49756.1632 | 20.016
Devonshire Building | 2017-01-15 21:45 | 49756.1632 | 0
Devonshire Building | 2017-01-15 22:00 | 49756.1732 | 39.996
Devonshire Building | 2017-01-15 22:15 | 49756.1782 | 20.016
Devonshire Building | 2017-01-15 22:30 | 49756.1782 | 0
Devonshire Building | 2017-01-15 22:45 | 49756.1832 | 20.016
Devonshire Building | 2017-01-15 23:00 | 49756.1832 | 0
Devonshire Building | 2017-01-15 23:15 | 49756.1882 | 20.016
Devonshire Building | 2017-01-15 23:30 | 49756.1882 | 0
Devonshire Building | 2017-01-15 23:45 | 49756.1932 | 20.016 | 0
Devonshire Building | 2017-01-16 | 49756.1953 | 0
Devonshire Building | 2017-01-16 00:15 | 49756.2003 | 20.016
Devonshire Building | 2017-01-16 00:30 | 49756.2003 | 0
Devonshire Building | 2017-01-16 00:45 | 49756.2053 | 20.016
Devonshire Building | 2017-01-16 01:00 | 49756.2053 | 0
Devonshire Building | 2017-01-16 01:15 | 49756.2103 | 20.016
Devonshire Building | 2017-01-16 01:30 | 49756.2103 | 0
Devonshire Building | 2017-01-16 01:45 | 49756.2153 | 20.016
Devonshire Building | 2017-01-16 02:00 | 49756.2203 | 20.016
Devonshire Building | 2017-01-16 02:15 | 49756.2203 | 0
Devonshire Building | 2017-01-16 02:30 | 49756.2253 | 20.016
Devonshire Building | 2017-01-16 02:45 | 49756.2253 | 0
Devonshire Building | 2017-01-16 03:00 | 49756.2303 | 20.016
Devonshire Building | 2017-01-16 03:15 | 49756.2303 | 0
Devonshire Building | 2017-01-16 03:30 | 49756.2353 | 20.016
Devonshire Building | 2017-01-16 03:45 | 49756.2353 | 0
Devonshire Building | 2017-01-16 04:00 | 49756.2403 | 20.016
Devonshire Building | 2017-01-16 04:15 | 49756.2403 | 0
Devonshire Building | 2017-01-16 04:30 | 49756.2453 | 20.016
Devonshire Building | 2017-01-16 04:45 | 49756.2453 | 0
Devonshire Building | 2017-01-16 05:00 | 49756.2504 | 20.016
Devonshire Building | 2017-01-16 05:15 | 49756.2504 | 0
Devonshire Building | 2017-01-16 05:30 | 49756.2554 | 20.016
Devonshire Building | 2017-01-16 05:45 | 49756.2554 | 0
Devonshire Building | 2017-01-16 06:00 | 49756.2604 | 20.016
Devonshire Building | 2017-01-16 06:15 | 49756.2654 | 20.016
Devonshire Building | 2017-01-16 06:30 | 49756.2654 | 0
Devonshire Building | 2017-01-16 06:45 | 49756.2704 | 20.016
Devonshire Building | 2017-01-16 07:00 | 49756.2754 | 20.016
Devonshire Building | 2017-01-16 07:15 | 49756.2754 | 0
Devonshire Building | 2017-01-16 07:30 | 49756.2854 | 39.996
Devonshire Building | 2017-01-16 07:45 | 49756.3004 | 60.012
Devonshire Building | 2017-01-16 08:00 | 49756.3204 | 79.992
Devonshire Building | 2017-01-16 08:15 | 49756.3504 | 119.988
Devonshire Building | 2017-01-16 08:30 | 49756.3754 | 100.008
Devonshire Building | 2017-01-16 08:45 | 49756.7004 | 1299.996
Devonshire Building | 2017-01-16 09:00 | 49756.7454 | 180
Devonshire Building | 2017-01-16 09:15 | 49756.7654 | 79.992
Devonshire Building | 2017-01-16 09:30 | 49756.7954 | 119.988
Devonshire Building | 2017-01-16 09:45 | 49756.8204 | 100.008
Devonshire Building | 2017-01-16 10:00 | 49757.1504 | 1320.012
Devonshire Building | 2017-01-16 10:15 | 49757.1904 | 159.984
Devonshire Building | 2017-01-16 10:30 | 49757.2504 | 240.012
Devonshire Building | 2017-01-16 10:45 | 49757.3554 | 420.012
Devonshire Building | 2017-01-16 11:00 | 49757.4504 | 380.016
Devonshire Building | 2017-01-16 11:15 | 49757.8454 | 1580.004
Devonshire Building | 2017-01-16 11:30 | 49757.9354 | 360
Devonshire Building | 2017-01-16 11:45 | 49758.0304 | 380.016
Devonshire Building | 2017-01-16 12:00 | 49758.1254 | 380.016
Devonshire Building | 2017-01-16 12:15 | 49758.2254 | 399.996
Devonshire Building | 2017-01-16 12:30 | 49758.6304 | 1620
Devonshire Building | 2017-01-16 12:45 | 49758.7504 | 479.988
Devonshire Building | 2017-01-16 13:00 | 49758.8754 | 500.004
Devonshire Building | 2017-01-16 13:15 | 49758.9954 | 479.988
Devonshire Building | 2017-01-16 13:30 | 49759.1404 | 579.996
Devonshire Building | 2017-01-16 13:45 | 49759.6254 | 1940.004
Devonshire Building | 2017-01-16 14:00 | 49759.7854 | 640.008
Devonshire Building | 2017-01-16 14:15 | 49759.9304 | 579.996
Devonshire Building | 2017-01-16 14:30 | 49760.0504 | 479.988
Devonshire Building | 2017-01-16 14:45 | 49760.1504 | 399.996
Devonshire Building | 2017-01-16 15:00 | 49760.2504 | 399.996
Devonshire Building | 2017-01-16 15:15 | 49760.6854 | 1739.988
Devonshire Building | 2017-01-16 15:30 | 49760.8104 | 500.004
Devonshire Building | 2017-01-16 15:45 | 49760.9154 | 420.012
Devonshire Building | 2017-01-16 16:00 | 49760.9954 | 320.004
Devonshire Building | 2017-01-16 16:15 | 49761.0604 | 259.992
Devonshire Building | 2017-01-16 16:30 | 49761.1204 | 240.012
Devonshire Building | 2017-01-16 16:45 | 49761.1754 | 219.996
Devonshire Building | 2017-01-16 17:00 | 49761.5254 | 1400.004
Devonshire Building | 2017-01-16 17:15 | 49761.5604 | 140.004
Devonshire Building | 2017-01-16 17:30 | 49761.5904 | 119.988
Devonshire Building | 2017-01-16 17:45 | 49761.6304 | 159.984
Devonshire Building | 2017-01-16 18:00 | 49761.6654 | 140.004
Devonshire Building | 2017-01-16 18:15 | 49761.7004 | 140.004
Devonshire Building | 2017-01-16 18:30 | 49761.7354 | 140.004
Devonshire Building | 2017-01-16 18:45 | 49761.7654 | 119.988
Devonshire Building | 2017-01-16 19:00 | 49761.7954 | 119.988
Devonshire Building | 2017-01-16 19:15 | 49761.8254 | 119.988
Devonshire Building | 2017-01-16 19:30 | 49761.8504 | 100.008
Devonshire Building | 2017-01-16 19:45 | 49761.8804 | 119.988
Devonshire Building | 2017-01-16 20:00 | 49761.9054 | 100.008
Devonshire Building | 2017-01-16 20:15 | 49761.9304 | 100.008
Devonshire Building | 2017-01-16 20:30 | 49761.9554 | 100.008
Devonshire Building | 2017-01-16 20:45 | 49761.9804 | 100.008
Devonshire Building | 2017-01-16 21:00 | 49762.0004 | 79.992
Devonshire Building | 2017-01-16 21:15 | 49762.0154 | 60.012
Devonshire Building | 2017-01-16 21:30 | 49762.0354 | 79.992
Devonshire Building | 2017-01-16 21:45 | 49762.0504 | 60.012
Devonshire Building | 2017-01-16 22:00 | 49762.0804 | 119.988
Devonshire Building | 2017-01-16 22:15 | 49762.0854 | 20.016
Devonshire Building | 2017-01-16 22:30 | 49762.0904 | 20.016
Devonshire Building | 2017-01-16 22:45 | 49762.0904 | 0
Devonshire Building | 2017-01-16 23:00 | 49762.0954 | 20.016
Devonshire Building | 2017-01-16 23:15 | 49762.1004 | 20.016
Devonshire Building | 2017-01-16 23:30 | 49762.1054 | 20.016
Devonshire Building | 2017-01-16 23:45 | 49762.1104 | 20.016 | 0
Devonshire Building | 2017-01-17 | 49762.1094 | 0
Devonshire Building | 2017-01-17 00:15 | 49762.1144 | 20.016
Devonshire Building | 2017-01-17 00:30 | 49762.1194 | 20.016
Devonshire Building | 2017-01-17 00:45 | 49762.1244 | 20.016
Devonshire Building | 2017-01-17 01:00 | 49762.1244 | 0
Devonshire Building | 2017-01-17 01:15 | 49762.1294 | 20.016
Devonshire Building | 2017-01-17 01:30 | 49762.1344 | 20.016
Devonshire Building | 2017-01-17 01:45 | 49762.1394 | 20.016
Devonshire Building | 2017-01-17 02:00 | 49762.1394 | 0
Devonshire Building | 2017-01-17 02:15 | 49762.1444 | 20.016
Devonshire Building | 2017-01-17 02:30 | 49762.3744 | 920.016
Devonshire Building | 2017-01-17 02:45 | 49762.4144 | 159.984
Devonshire Building | 2017-01-17 03:00 | 49762.4144 | 0
Devonshire Building | 2017-01-17 03:15 | 49762.4194 | 20.016
Devonshire Building | 2017-01-17 03:30 | 49762.4194 | 0
Devonshire Building | 2017-01-17 03:45 | 49762.4244 | 20.016
Devonshire Building | 2017-01-17 04:00 | 49762.4244 | 0
Devonshire Building | 2017-01-17 04:15 | 49762.4294 | 20.016
Devonshire Building | 2017-01-17 04:30 | 49762.4294 | 0
Devonshire Building | 2017-01-17 04:45 | 49762.4344 | 20.016
Devonshire Building | 2017-01-17 05:00 | 49762.4344 | 0
Devonshire Building | 2017-01-17 05:15 | 49762.4394 | 20.016
Devonshire Building | 2017-01-17 05:30 | 49762.4394 | 0
Devonshire Building | 2017-01-17 05:45 | 49762.4444 | 20.016
Devonshire Building | 2017-01-17 06:00 | 49762.4444 | 0
Devonshire Building | 2017-01-17 06:15 | 49762.4494 | 20.016
Devonshire Building | 2017-01-17 06:30 | 49762.4544 | 20.016
Devonshire Building | 2017-01-17 06:45 | 49762.4594 | 20.016
Devonshire Building | 2017-01-17 07:00 | 49762.4594 | 0
Devonshire Building | 2017-01-17 07:15 | 49762.4644 | 20.016
Devonshire Building | 2017-01-17 07:30 | 49762.4744 | 39.996
Devonshire Building | 2017-01-17 07:45 | 49762.4844 | 39.996
Devonshire Building | 2017-01-17 08:00 | 49762.5144 | 119.988
Devonshire Building | 2017-01-17 08:15 | 49762.5444 | 119.988
Devonshire Building | 2017-01-17 08:30 | 49762.5644 | 79.992
Devonshire Building | 2017-01-17 08:45 | 49762.6044 | 159.984
Devonshire Building | 2017-01-17 09:00 | 49762.6344 | 119.988
Devonshire Building | 2017-01-17 09:15 | 49762.6644 | 119.988
Devonshire Building | 2017-01-17 09:30 | 49763.0044 | 1360.008
Devonshire Building | 2017-01-17 09:45 | 49763.0694 | 259.992
Devonshire Building | 2017-01-17 10:00 | 49763.1694 | 399.996
Devonshire Building | 2017-01-17 10:15 | 49763.2794 | 439.992
Devonshire Building | 2017-01-17 10:30 | 49763.4344 | 619.992
Devonshire Building | 2017-01-17 10:45 | 49763.7794 | 1379.988
Devonshire Building | 2017-01-17 11:00 | 49763.9094 | 519.984
Devonshire Building | 2017-01-17 11:15 | 49764.0194 | 439.992
Devonshire Building | 2017-01-17 11:30 | 49764.1244 | 420.012
Devonshire Building | 2017-01-17 11:45 | 49764.3744 | 1000.008
Devonshire Building | 2017-01-17 12:00 | 49764.5694 | 780.012
Devonshire Building | 2017-01-17 12:15 | 49764.6494 | 320.004
Devonshire Building | 2017-01-17 12:30 | 49764.7294 | 320.004
Devonshire Building | 2017-01-17 12:45 | 49764.7944 | 259.992
Devonshire Building | 2017-01-17 13:00 | 49764.8494 | 219.996
Devonshire Building | 2017-01-17 13:15 | 49765.2144 | 1460.016
Devonshire Building | 2017-01-17 13:30 | 49765.2444 | 119.988
Devonshire Building | 2017-01-17 13:45 | 49765.2844 | 159.984
Devonshire Building | 2017-01-17 14:00 | 49765.3194 | 140.004
Devonshire Building | 2017-01-17 14:15 | 49765.3694 | 200.016
Devonshire Building | 2017-01-17 14:30 | 49765.4144 | 180
Devonshire Building | 2017-01-17 14:45 | 49765.4544 | 159.984
Devonshire Building | 2017-01-17 15:00 | 49765.4944 | 159.984
Devonshire Building | 2017-01-17 15:15 | 49765.8294 | 1339.992
Devonshire Building | 2017-01-17 15:30 | 49765.8694 | 159.984
Devonshire Building | 2017-01-17 15:45 | 49765.9044 | 140.004
Devonshire Building | 2017-01-17 16:00 | 49765.9444 | 159.984
Devonshire Building | 2017-01-17 16:15 | 49765.9894 | 180
Devonshire Building | 2017-01-17 16:30 | 49766.0244 | 140.004
Devonshire Building | 2017-01-17 16:45 | 49766.0644 | 159.984
Devonshire Building | 2017-01-17 17:00 | 49766.3844 | 1280.016
Devonshire Building | 2017-01-17 17:15 | 49766.4194 | 140.004
Devonshire Building | 2017-01-17 17:30 | 49766.4594 | 159.984
Devonshire Building | 2017-01-17 17:45 | 49766.4944 | 140.004
Devonshire Building | 2017-01-17 18:00 | 49766.5344 | 159.984
Devonshire Building | 2017-01-17 18:15 | 49766.5694 | 140.004
Devonshire Building | 2017-01-17 18:30 | 49766.6044 | 140.004
Devonshire Building | 2017-01-17 18:45 | 49766.6344 | 119.988
Devonshire Building | 2017-01-17 19:00 | 49766.6644 | 119.988
Devonshire Building | 2017-01-17 19:15 | 49766.6894 | 100.008
Devonshire Building | 2017-01-17 19:30 | 49766.7144 | 100.008
Devonshire Building | 2017-01-17 19:45 | 49766.7344 | 79.992
Devonshire Building | 2017-01-17 20:00 | 49766.7594 | 100.008
Devonshire Building | 2017-01-17 20:15 | 49766.7744 | 60.012
Devonshire Building | 2017-01-17 20:30 | 49766.7944 | 79.992
Devonshire Building | 2017-01-17 20:45 | 49766.8094 | 60.012
Devonshire Building | 2017-01-17 21:00 | 49766.8194 | 39.996
Devonshire Building | 2017-01-17 21:15 | 49766.8344 | 60.012
Devonshire Building | 2017-01-17 21:30 | 49767.1194 | 1140.012
Devonshire Building | 2017-01-17 21:45 | 49767.1194 | 0
Devonshire Building | 2017-01-17 22:00 | 49767.1244 | 20.016
Devonshire Building | 2017-01-17 22:15 | 49767.1294 | 20.016
Devonshire Building | 2017-01-17 22:30 | 49767.1344 | 20.016
Devonshire Building | 2017-01-17 22:45 | 49767.1394 | 20.016
Devonshire Building | 2017-01-17 23:00 | 49767.1394 | 0
Devonshire Building | 2017-01-17 23:15 | 49767.1444 | 20.016
Devonshire Building | 2017-01-17 23:30 | 49767.1494 | 20.016
Devonshire Building | 2017-01-17 23:45 | 49767.1494 | 0 | 0
Devonshire Building | 2017-01-18 | 49767.1562 | 20.016
Devonshire Building | 2017-01-18 00:15 | 49767.1613 | 20.016
Devonshire Building | 2017-01-18 00:30 | 49767.1663 | 20.016
Devonshire Building | 2017-01-18 00:45 | 49767.1663 | 0
Devonshire Building | 2017-01-18 01:00 | 49767.1713 | 20.016
Devonshire Building | 2017-01-18 01:15 | 49767.1763 | 20.016
Devonshire Building | 2017-01-18 01:30 | 49767.1763 | 0
Devonshire Building | 2017-01-18 01:45 | 49767.1813 | 20.016
Devonshire Building | 2017-01-18 02:00 | 49767.1863 | 20.016
Devonshire Building | 2017-01-18 02:15 | 49767.1863 | 0
Devonshire Building | 2017-01-18 02:30 | 49767.1913 | 20.016
Devonshire Building | 2017-01-18 02:45 | 49767.1963 | 20.016
Devonshire Building | 2017-01-18 03:00 | 49767.1963 | 0
Devonshire Building | 2017-01-18 03:15 | 49767.2013 | 20.016
Devonshire Building | 2017-01-18 03:30 | 49767.2063 | 20.016
Devonshire Building | 2017-01-18 03:45 | 49767.2063 | 0
Devonshire Building | 2017-01-18 04:00 | 49767.2113 | 20.016
Devonshire Building | 2017-01-18 04:15 | 49767.2163 | 20.016
Devonshire Building | 2017-01-18 04:30 | 49767.2163 | 0
Devonshire Building | 2017-01-18 04:45 | 49767.2213 | 20.016
Devonshire Building | 2017-01-18 05:00 | 49767.2263 | 20.016
Devonshire Building | 2017-01-18 05:15 | 49767.2263 | 0
Devonshire Building | 2017-01-18 05:30 | 49767.2313 | 20.016
Devonshire Building | 2017-01-18 05:45 | 49767.2363 | 20.016
Devonshire Building | 2017-01-18 06:00 | 49767.2363 | 0
Devonshire Building | 2017-01-18 06:15 | 49767.2413 | 20.016
Devonshire Building | 2017-01-18 06:30 | 49767.2463 | 20.016
Devonshire Building | 2017-01-18 06:45 | 49767.2513 | 20.016
Devonshire Building | 2017-01-18 07:00 | 49767.2563 | 20.016
Devonshire Building | 2017-01-18 07:15 | 49767.2563 | 0
Devonshire Building | 2017-01-18 07:30 | 49767.2663 | 39.996
Devonshire Building | 2017-01-18 07:45 | 49767.2913 | 100.008
Devonshire Building | 2017-01-18 08:00 | 49767.3113 | 79.992
Devonshire Building | 2017-01-18 08:15 | 49767.3363 | 100.008
Devonshire Building | 2017-01-18 08:30 | 49767.3613 | 100.008
Devonshire Building | 2017-01-18 08:45 | 49767.3813 | 79.992
Devonshire Building | 2017-01-18 09:00 | 49767.4063 | 100.008
Devonshire Building | 2017-01-18 09:15 | 49767.4313 | 100.008
Devonshire Building | 2017-01-18 09:30 | 49767.5313 | 399.996
Devonshire Building | 2017-01-18 09:45 | 49767.7913 | 1040.004
Devonshire Building | 2017-01-18 10:00 | 49767.8363 | 180
Devonshire Building | 2017-01-18 10:15 | 49767.9013 | 259.992
Devonshire Building | 2017-01-18 10:30 | 49768.0013 | 399.996
Devonshire Building | 2017-01-18 10:45 | 49768.1763 | 699.984
Devonshire Building | 2017-01-18 11:00 | 49768.6313 | 1820.016
Devonshire Building | 2017-01-18 11:15 | 49768.7613 | 519.984
Devonshire Building | 2017-01-18 11:30 | 49768.8713 | 439.992
Devonshire Building | 2017-01-18 11:45 | 49768.9763 | 420.012
Devonshire Building | 2017-01-18 12:00 | 49769.0763 | 399.996
Devonshire Building | 2017-01-18 12:15 | 49769.3263 | 1000.008
Devonshire Building | 2017-01-18 12:30 | 49769.5363 | 839.988
Devonshire Building | 2017-01-18 12:45 | 49769.5963 | 240.012
Devonshire Building | 2017-01-18 13:00 | 49769.6563 | 240.012
Devonshire Building | 2017-01-18 13:15 | 49769.7213 | 259.992
Devonshire Building | 2017-01-18 13:30 | 49769.7813 | 240.012
Devonshire Building | 2017-01-18 13:45 | 49770.1063 | 1299.996
Devonshire Building | 2017-01-18 14:00 | 49770.1463 | 159.984
Devonshire Building | 2017-01-18 14:15 | 49770.1913 | 180
Devonshire Building | 2017-01-18 14:30 | 49770.2363 | 180
Devonshire Building | 2017-01-18 14:45 | 49770.2763 | 159.984
Devonshire Building | 2017-01-18 15:00 | 49770.3263 | 200.016
Devonshire Building | 2017-01-18 15:15 | 49770.3813 | 219.996
Devonshire Building | 2017-01-18 15:30 | 49770.7263 | 1379.988
Devonshire Building | 2017-01-18 15:45 | 49770.7813 | 219.996
Devonshire Building | 2017-01-18 16:00 | 49770.8313 | 200.016
Devonshire Building | 2017-01-18 16:15 | 49770.8863 | 219.996
Devonshire Building | 2017-01-18 16:30 | 49770.9313 | 180
Devonshire Building | 2017-01-18 16:45 | 49770.9763 | 180
Devonshire Building | 2017-01-18 17:00 | 49771.0163 | 159.984
Devonshire Building | 2017-01-18 17:15 | 49771.3313 | 1260
Devonshire Building | 2017-01-18 17:30 | 49771.3563 | 100.008
Devonshire Building | 2017-01-18 17:45 | 49771.3813 | 100.008
Devonshire Building | 2017-01-18 18:00 | 49771.4013 | 79.992
Devonshire Building | 2017-01-18 18:15 | 49771.4263 | 100.008
Devonshire Building | 2017-01-18 18:30 | 49771.4513 | 100.008
Devonshire Building | 2017-01-18 18:45 | 49771.4763 | 100.008
Devonshire Building | 2017-01-18 19:00 | 49771.5013 | 100.008
Devonshire Building | 2017-01-18 19:15 | 49771.5213 | 79.992
Devonshire Building | 2017-01-18 19:30 | 49771.5413 | 79.992
Devonshire Building | 2017-01-18 19:45 | 49771.5663 | 100.008
Devonshire Building | 2017-01-18 20:00 | 49771.5813 | 60.012
Devonshire Building | 2017-01-18 20:15 | 49771.5963 | 60.012
Devonshire Building | 2017-01-18 20:30 | 49771.6113 | 60.012
Devonshire Building | 2017-01-18 20:45 | 49771.6263 | 60.012
Devonshire Building | 2017-01-18 21:00 | 49771.6413 | 60.012
Devonshire Building | 2017-01-18 21:15 | 49771.6513 | 39.996
Devonshire Building | 2017-01-18 21:30 | 49771.6613 | 39.996
Devonshire Building | 2017-01-18 21:45 | 49771.6713 | 39.996
Devonshire Building | 2017-01-18 22:00 | 49771.7013 | 119.988
Devonshire Building | 2017-01-18 22:15 | 49771.7063 | 20.016
Devonshire Building | 2017-01-18 22:30 | 49771.7063 | 0
Devonshire Building | 2017-01-18 22:45 | 49771.7113 | 20.016
Devonshire Building | 2017-01-18 23:00 | 49771.7113 | 0
Devonshire Building | 2017-01-18 23:15 | 49771.7164 | 20.016
Devonshire Building | 2017-01-18 23:30 | 49771.7214 | 20.016
Devonshire Building | 2017-01-18 23:45 | 49771.7214 | 0 | 0
Devonshire Building | 2017-01-19 | 49771.7266 | 20.016
Devonshire Building | 2017-01-19 00:15 | 49771.7316 | 20.016
Devonshire Building | 2017-01-19 00:30 | 49771.7316 | 0
Devonshire Building | 2017-01-19 00:45 | 49771.7366 | 20.016
Devonshire Building | 2017-01-19 01:00 | 49771.7366 | 0
Devonshire Building | 2017-01-19 01:15 | 49771.7416 | 20.016
Devonshire Building | 2017-01-19 01:30 | 49771.7416 | 0
Devonshire Building | 2017-01-19 01:45 | 49771.7466 | 20.016
Devonshire Building | 2017-01-19 02:00 | 49771.7516 | 20.016
Devonshire Building | 2017-01-19 02:15 | 49771.7516 | 0
Devonshire Building | 2017-01-19 02:30 | 49771.7566 | 20.016
Devonshire Building | 2017-01-19 02:45 | 49771.7566 | 0
Devonshire Building | 2017-01-19 03:00 | 49771.7616 | 20.016
Devonshire Building | 2017-01-19 03:15 | 49771.7616 | 0
Devonshire Building | 2017-01-19 03:30 | 49771.7666 | 20.016
Devonshire Building | 2017-01-19 03:45 | 49771.7716 | 20.016
Devonshire Building | 2017-01-19 04:00 | 49771.7716 | 0
Devonshire Building | 2017-01-19 04:15 | 49771.7766 | 20.016
Devonshire Building | 2017-01-19 04:30 | 49771.7766 | 0
Devonshire Building | 2017-01-19 04:45 | 49771.7816 | 20.016
Devonshire Building | 2017-01-19 05:00 | 49771.7816 | 0
Devonshire Building | 2017-01-19 05:15 | 49771.7866 | 20.016
Devonshire Building | 2017-01-19 05:30 | 49771.7866 | 0
Devonshire Building | 2017-01-19 05:45 | 49771.7916 | 20.016
Devonshire Building | 2017-01-19 06:00 | 49772.0516 | 1040.004
Devonshire Building | 2017-01-19 06:15 | 49772.0516 | 0
Devonshire Building | 2017-01-19 06:30 | 49772.0566 | 20.016
Devonshire Building | 2017-01-19 06:45 | 49772.0616 | 20.016
Devonshire Building | 2017-01-19 07:00 | 49772.0766 | 60.012
Devonshire Building | 2017-01-19 07:15 | 49772.0816 | 20.016
Devonshire Building | 2017-01-19 07:30 | 49772.0866 | 20.016
Devonshire Building | 2017-01-19 07:45 | 49772.1066 | 79.992
Devonshire Building | 2017-01-19 08:00 | 49772.1316 | 100.008
Devonshire Building | 2017-01-19 08:15 | 49772.1516 | 79.992
Devonshire Building | 2017-01-19 08:30 | 49772.1716 | 79.992
Devonshire Building | 2017-01-19 08:45 | 49772.2066 | 140.004
Devonshire Building | 2017-01-19 09:00 | 49772.2316 | 100.008
Devonshire Building | 2017-01-19 09:15 | 49772.2616 | 119.988
Devonshire Building | 2017-01-19 09:30 | 49772.2866 | 100.008
Devonshire Building | 2017-01-19 09:45 | 49772.3166 | 119.988
Devonshire Building | 2017-01-19 10:00 | 49772.5516 | 939.996
Devonshire Building | 2017-01-19 10:15 | 49772.7366 | 740.016
Devonshire Building | 2017-01-19 10:30 | 49772.8916 | 619.992
Devonshire Building | 2017-01-19 10:45 | 49773.0366 | 579.996
Devonshire Building | 2017-01-19 11:00 | 49773.1666 | 519.984
Devonshire Building | 2017-01-19 11:15 | 49773.3016 | 540
Devonshire Building | 2017-01-19 11:30 | 49773.7216 | 1680.012
Devonshire Building | 2017-01-19 11:45 | 49773.8166 | 380.016
Devonshire Building | 2017-01-19 12:00 | 49773.8916 | 299.988
Devonshire Building | 2017-01-19 12:15 | 49773.9666 | 299.988
Devonshire Building | 2017-01-19 12:30 | 49774.0166 | 200.016
Devonshire Building | 2017-01-19 12:45 | 49774.3766 | 1440
Devonshire Building | 2017-01-19 13:00 | 49774.4466 | 280.008
Devonshire Building | 2017-01-19 13:15 | 49774.4966 | 200.016
Devonshire Building | 2017-01-19 13:30 | 49774.5616 | 259.992
Devonshire Building | 2017-01-19 13:45 | 49774.6266 | 259.992
Devonshire Building | 2017-01-19 14:00 | 49774.6766 | 200.016
Devonshire Building | 2017-01-19 14:15 | 49774.7316 | 219.996
Devonshire Building | 2017-01-19 14:30 | 49775.0866 | 1419.984
Devonshire Building | 2017-01-19 14:45 | 49775.1416 | 219.996
Devonshire Building | 2017-01-19 15:00 | 49775.2066 | 259.992
Devonshire Building | 2017-01-19 15:15 | 49775.3016 | 380.016
Devonshire Building | 2017-01-19 15:30 | 49775.4016 | 399.996
Devonshire Building | 2017-01-19 15:45 | 49775.4916 | 360
Devonshire Building | 2017-01-19 16:00 | 49775.5766 | 339.984
Devonshire Building | 2017-01-19 16:15 | 49775.9716 | 1580.004
Devonshire Building | 2017-01-19 16:30 | 49776.0366 | 259.992
Devonshire Building | 2017-01-19 16:45 | 49776.0966 | 240.012
Devonshire Building | 2017-01-19 17:00 | 49776.1516 | 219.996
Devonshire Building | 2017-01-19 17:15 | 49776.2016 | 200.016
Devonshire Building | 2017-01-19 17:30 | 49776.2466 | 180
Devonshire Building | 2017-01-19 17:45 | 49776.2866 | 159.984
Devonshire Building | 2017-01-19 18:00 | 49776.5866 | 1199.988
Devonshire Building | 2017-01-19 18:15 | 49776.6016 | 60.012
Devonshire Building | 2017-01-19 18:30 | 49776.6166 | 60.012
Devonshire Building | 2017-01-19 18:45 | 49776.6316 | 60.012
Devonshire Building | 2017-01-19 19:00 | 49776.6416 | 39.996
Devonshire Building | 2017-01-19 19:15 | 49776.6566 | 60.012
Devonshire Building | 2017-01-19 19:30 | 49776.6716 | 60.012
Devonshire Building | 2017-01-19 19:45 | 49776.6816 | 39.996
Devonshire Building | 2017-01-19 20:00 | 49776.6966 | 60.012
Devonshire Building | 2017-01-19 20:15 | 49776.7116 | 60.012
Devonshire Building | 2017-01-19 20:30 | 49776.7216 | 39.996
Devonshire Building | 2017-01-19 20:45 | 49776.7366 | 60.012
Devonshire Building | 2017-01-19 21:00 | 49776.7466 | 39.996
Devonshire Building | 2017-01-19 21:15 | 49776.7566 | 39.996
Devonshire Building | 2017-01-19 21:30 | 49776.7716 | 60.012
Devonshire Building | 2017-01-19 21:45 | 49776.7816 | 39.996
Devonshire Building | 2017-01-19 22:00 | 49776.7966 | 60.012
Devonshire Building | 2017-01-19 22:15 | 49776.8066 | 39.996
Devonshire Building | 2017-01-19 22:30 | 49776.8117 | 20.016
Devonshire Building | 2017-01-19 22:45 | 49776.8216 | 39.996
Devonshire Building | 2017-01-19 23:00 | 49776.8316 | 39.996
Devonshire Building | 2017-01-19 23:15 | 49776.8367 | 20.016
Devonshire Building | 2017-01-19 23:30 | 49776.8467 | 39.996
Devonshire Building | 2017-01-19 23:45 | 49776.8517 | 20.016 | 0
Devonshire Building | 2017-01-20 | 49776.8594 | 39.996
Devonshire Building | 2017-01-20 00:15 | 49776.8644 | 20.016
Devonshire Building | 2017-01-20 00:30 | 49776.8694 | 20.016
Devonshire Building | 2017-01-20 00:45 | 49776.8794 | 39.996
Devonshire Building | 2017-01-20 01:00 | 49776.8844 | 20.016
Devonshire Building | 2017-01-20 01:15 | 49776.8894 | 20.016
Devonshire Building | 2017-01-20 01:30 | 49776.8994 | 39.996
Devonshire Building | 2017-01-20 01:45 | 49776.9044 | 20.016
Devonshire Building | 2017-01-20 02:00 | 49776.9094 | 20.016
Devonshire Building | 2017-01-20 02:15 | 49776.9144 | 20.016
Devonshire Building | 2017-01-20 02:30 | 49776.9194 | 20.016
Devonshire Building | 2017-01-20 02:45 | 49776.9244 | 20.016
Devonshire Building | 2017-01-20 03:00 | 49776.9294 | 20.016
Devonshire Building | 2017-01-20 03:15 | 49776.9344 | 20.016
Devonshire Building | 2017-01-20 03:30 | 49776.9394 | 20.016
Devonshire Building | 2017-01-20 03:45 | 49776.9444 | 20.016
Devonshire Building | 2017-01-20 04:00 | 49776.9494 | 20.016
Devonshire Building | 2017-01-20 04:15 | 49776.9544 | 20.016
Devonshire Building | 2017-01-20 04:30 | 49776.9594 | 20.016
Devonshire Building | 2017-01-20 04:45 | 49776.9644 | 20.016
Devonshire Building | 2017-01-20 05:00 | 49776.9694 | 20.016
Devonshire Building | 2017-01-20 05:15 | 49776.9694 | 0
Devonshire Building | 2017-01-20 05:30 | 49776.9745 | 20.016
Devonshire Building | 2017-01-20 05:45 | 49776.9795 | 20.016
Devonshire Building | 2017-01-20 06:00 | 49776.9845 | 20.016
Devonshire Building | 2017-01-20 06:15 | 49776.9895 | 20.016
Devonshire Building | 2017-01-20 06:30 | 49776.9945 | 20.016
Devonshire Building | 2017-01-20 06:45 | 49776.9945 | 0
Devonshire Building | 2017-01-20 07:00 | 49776.9995 | 20.016
Devonshire Building | 2017-01-20 07:15 | 49777.0045 | 20.016
Devonshire Building | 2017-01-20 07:30 | 49777.0095 | 20.016
Devonshire Building | 2017-01-20 07:45 | 49777.0295 | 79.992
Devonshire Building | 2017-01-20 08:00 | 49777.0545 | 100.008
Devonshire Building | 2017-01-20 08:15 | 49777.1045 | 200.016
Devonshire Building | 2017-01-20 08:30 | 49777.1345 | 119.988
Devonshire Building | 2017-01-20 08:45 | 49777.1695 | 140.004
Devonshire Building | 2017-01-20 09:00 | 49777.5245 | 1419.984
Devonshire Building | 2017-01-20 09:15 | 49777.6395 | 460.008
Devonshire Building | 2017-01-20 09:30 | 49777.7695 | 519.984
Devonshire Building | 2017-01-20 09:45 | 49777.8745 | 420.012
Devonshire Building | 2017-01-20 10:00 | 49777.9595 | 339.984
Devonshire Building | 2017-01-20 10:15 | 49778.0345 | 299.988
Devonshire Building | 2017-01-20 10:30 | 49778.1095 | 299.988
Devonshire Building | 2017-01-20 10:45 | 49778.4795 | 1479.996
Devonshire Building | 2017-01-20 11:00 | 49778.5545 | 299.988
Devonshire Building | 2017-01-20 11:15 | 49778.6295 | 299.988
Devonshire Building | 2017-01-20 11:30 | 49778.7045 | 299.988
Devonshire Building | 2017-01-20 11:45 | 49778.7645 | 240.012
Devonshire Building | 2017-01-20 12:00 | 49778.8195 | 219.996
Devonshire Building | 2017-01-20 12:15 | 49778.8695 | 200.016
Devonshire Building | 2017-01-20 12:30 | 49779.0795 | 839.988
Devonshire Building | 2017-01-20 12:45 | 49779.2545 | 699.984
Devonshire Building | 2017-01-20 13:00 | 49779.2895 | 140.004
Devonshire Building | 2017-01-20 13:15 | 49779.3245 | 140.004
Devonshire Building | 2017-01-20 13:30 | 49779.3645 | 159.984
Devonshire Building | 2017-01-20 13:45 | 49779.4145 | 200.016
Devonshire Building | 2017-01-20 14:00 | 49779.4545 | 159.984
Devonshire Building | 2017-01-20 14:15 | 49779.4995 | 180
Devonshire Building | 2017-01-20 14:30 | 49779.8295 | 1320.012
Devonshire Building | 2017-01-20 14:45 | 49779.8695 | 159.984
Devonshire Building | 2017-01-20 15:00 | 49779.9145 | 180
Devonshire Building | 2017-01-20 15:15 | 49779.9595 | 180
Devonshire Building | 2017-01-20 15:30 | 49780.0045 | 180
Devonshire Building | 2017-01-20 15:45 | 49780.0495 | 180
Devonshire Building | 2017-01-20 16:00 | 49780.0895 | 159.984
Devonshire Building | 2017-01-20 16:15 | 49780.4295 | 1360.008
Devonshire Building | 2017-01-20 16:30 | 49780.4645 | 140.004
Devonshire Building | 2017-01-20 16:45 | 49780.5095 | 180
Devonshire Building | 2017-01-20 17:00 | 49780.5545 | 180
Devonshire Building | 2017-01-20 17:15 | 49780.5945 | 159.984
Devonshire Building | 2017-01-20 17:30 | 49780.6545 | 240.012
Devonshire Building | 2017-01-20 17:45 | 49780.7195 | 259.992
Devonshire Building | 2017-01-20 18:00 | 49780.7795 | 240.012
Devonshire Building | 2017-01-20 18:15 | 49781.1345 | 1419.984
Devonshire Building | 2017-01-20 18:30 | 49781.1895 | 219.996
Devonshire Building | 2017-01-20 18:45 | 49781.2495 | 240.012
Devonshire Building | 2017-01-20 19:00 | 49781.3045 | 219.996
Devonshire Building | 2017-01-20 19:15 | 49781.3595 | 219.996
Devonshire Building | 2017-01-20 19:30 | 49781.4095 | 200.016
Devonshire Building | 2017-01-20 19:45 | 49781.4495 | 159.984
Devonshire Building | 2017-01-20 20:00 | 49781.4894 | 159.984
Devonshire Building | 2017-01-20 20:15 | 49781.5194 | 119.988
Devonshire Building | 2017-01-20 20:30 | 49781.5494 | 119.988
Devonshire Building | 2017-01-20 20:45 | 49781.5694 | 79.992
Devonshire Building | 2017-01-20 21:00 | 49781.5894 | 79.992
Devonshire Building | 2017-01-20 21:15 | 49781.6094 | 79.992
Devonshire Building | 2017-01-20 21:30 | 49781.6244 | 60.012
Devonshire Building | 2017-01-20 21:45 | 49781.6394 | 60.012
Devonshire Building | 2017-01-20 22:00 | 49781.6544 | 60.012
Devonshire Building | 2017-01-20 22:15 | 49781.6644 | 39.996
Devonshire Building | 2017-01-20 22:30 | 49781.6744 | 39.996
Devonshire Building | 2017-01-20 22:45 | 49781.6844 | 39.996
Devonshire Building | 2017-01-20 23:00 | 49781.6894 | 20.016
Devonshire Building | 2017-01-20 23:15 | 49781.6994 | 39.996
Devonshire Building | 2017-01-20 23:30 | 49781.7094 | 39.996
Devonshire Building | 2017-01-20 23:45 | 49781.7144 | 20.016 | 0
Devonshire Building | 2017-01-21 | 49781.7266 | 39.996
Devonshire Building | 2017-01-21 00:15 | 49781.7366 | 39.996
Devonshire Building | 2017-01-21 00:30 | 49781.7416 | 20.016
Devonshire Building | 2017-01-21 00:45 | 49781.7466 | 20.016
Devonshire Building | 2017-01-21 01:00 | 49781.7566 | 39.996
Devonshire Building | 2017-01-21 01:15 | 49781.7616 | 20.016
Devonshire Building | 2017-01-21 01:30 | 49781.7666 | 20.016
Devonshire Building | 2017-01-21 01:45 | 49781.7766 | 39.996
Devonshire Building | 2017-01-21 02:00 | 49781.7816 | 20.016
Devonshire Building | 2017-01-21 02:15 | 49781.7866 | 20.016
Devonshire Building | 2017-01-21 02:30 | 49781.7916 | 20.016
Devonshire Building | 2017-01-21 02:45 | 49781.7966 | 20.016
Devonshire Building | 2017-01-21 03:00 | 49781.8016 | 20.016
Devonshire Building | 2017-01-21 03:15 | 49781.8066 | 20.016
Devonshire Building | 2017-01-21 03:30 | 49781.8116 | 20.016
Devonshire Building | 2017-01-21 03:45 | 49781.8166 | 20.016
Devonshire Building | 2017-01-21 04:00 | 49781.8216 | 20.016
Devonshire Building | 2017-01-21 04:15 | 49781.8266 | 20.016
Devonshire Building | 2017-01-21 04:30 | 49781.8316 | 20.016
Devonshire Building | 2017-01-21 04:45 | 49781.8366 | 20.016
Devonshire Building | 2017-01-21 05:00 | 49781.8416 | 20.016
Devonshire Building | 2017-01-21 05:15 | 49781.8466 | 20.016
Devonshire Building | 2017-01-21 05:30 | 49781.8516 | 20.016
Devonshire Building | 2017-01-21 05:45 | 49781.8566 | 20.016
Devonshire Building | 2017-01-21 06:00 | 49781.8566 | 0
Devonshire Building | 2017-01-21 06:15 | 49781.8616 | 20.016
Devonshire Building | 2017-01-21 06:30 | 49781.8666 | 20.016
Devonshire Building | 2017-01-21 06:45 | 49781.8716 | 20.016
Devonshire Building | 2017-01-21 07:00 | 49781.8716 | 0
Devonshire Building | 2017-01-21 07:15 | 49781.8767 | 20.016
Devonshire Building | 2017-01-21 07:30 | 49781.8817 | 20.016
Devonshire Building | 2017-01-21 07:45 | 49781.9017 | 79.992
Devonshire Building | 2017-01-21 08:00 | 49781.9217 | 79.992
Devonshire Building | 2017-01-21 08:15 | 49781.9417 | 79.992
Devonshire Building | 2017-01-21 08:30 | 49781.9616 | 79.992
Devonshire Building | 2017-01-21 08:45 | 49781.9816 | 79.992
Devonshire Building | 2017-01-21 09:00 | 49782.0016 | 79.992
Devonshire Building | 2017-01-21 09:15 | 49782.0216 | 79.992
Devonshire Building | 2017-01-21 09:30 | 49782.0416 | 79.992
Devonshire Building | 2017-01-21 09:45 | 49782.0566 | 60.012
Devonshire Building | 2017-01-21 10:00 | 49782.0766 | 79.992
Devonshire Building | 2017-01-21 10:15 | 49782.0966 | 79.992
Devonshire Building | 2017-01-21 10:30 | 49782.1116 | 60.012
Devonshire Building | 2017-01-21 10:45 | 49782.1116 | 0
Devonshire Building | 2017-01-21 11:00 | 49782.1166 | 20.016
Devonshire Building | 2017-01-21 11:15 | 49782.1217 | 20.016
Devonshire Building | 2017-01-21 11:30 | 49782.1217 | 0
Devonshire Building | 2017-01-21 11:45 | 49782.1267 | 20.016
Devonshire Building | 2017-01-21 12:00 | 49782.1317 | 20.016
Devonshire Building | 2017-01-21 12:15 | 49782.1317 | 0
Devonshire Building | 2017-01-21 12:30 | 49782.1367 | 20.016
Devonshire Building | 2017-01-21 12:45 | 49782.1417 | 20.016
Devonshire Building | 2017-01-21 13:00 | 49782.1417 | 0
Devonshire Building | 2017-01-21 13:15 | 49782.1467 | 20.016
Devonshire Building | 2017-01-21 13:30 | 49782.1467 | 0
Devonshire Building | 2017-01-21 13:45 | 49782.1517 | 20.016
Devonshire Building | 2017-01-21 14:00 | 49782.1567 | 20.016
Devonshire Building | 2017-01-21 14:15 | 49782.1567 | 0
Devonshire Building | 2017-01-21 14:30 | 49782.1617 | 20.016
Devonshire Building | 2017-01-21 14:45 | 49782.1667 | 20.016
Devonshire Building | 2017-01-21 15:00 | 49782.1667 | 0
Devonshire Building | 2017-01-21 15:15 | 49782.1717 | 20.016
Devonshire Building | 2017-01-21 15:30 | 49782.1767 | 20.016
Devonshire Building | 2017-01-21 15:45 | 49782.1767 | 0
Devonshire Building | 2017-01-21 16:00 | 49782.1817 | 20.016
Devonshire Building | 2017-01-21 16:15 | 49782.1817 | 0
Devonshire Building | 2017-01-21 16:30 | 49782.1867 | 20.016
Devonshire Building | 2017-01-21 16:45 | 49782.1917 | 20.016
Devonshire Building | 2017-01-21 17:00 | 49782.1917 | 0
Devonshire Building | 2017-01-21 17:15 | 49782.1967 | 20.016
Devonshire Building | 2017-01-21 17:30 | 49782.4667 | 1080
Devonshire Building | 2017-01-21 17:45 | 49782.4717 | 20.016
Devonshire Building | 2017-01-21 18:00 | 49782.4717 | 0
Devonshire Building | 2017-01-21 18:15 | 49782.4767 | 20.016
Devonshire Building | 2017-01-21 18:30 | 49782.4767 | 0
Devonshire Building | 2017-01-21 18:45 | 49782.4817 | 20.016
Devonshire Building | 2017-01-21 19:00 | 49782.4817 | 0
Devonshire Building | 2017-01-21 19:15 | 49782.4867 | 20.016
Devonshire Building | 2017-01-21 19:30 | 49782.4917 | 20.016
Devonshire Building | 2017-01-21 19:45 | 49782.4917 | 0
Devonshire Building | 2017-01-21 20:00 | 49782.4967 | 20.016
Devonshire Building | 2017-01-21 20:15 | 49782.4967 | 0
Devonshire Building | 2017-01-21 20:30 | 49782.5017 | 20.016
Devonshire Building | 2017-01-21 20:45 | 49782.5017 | 0
Devonshire Building | 2017-01-21 21:00 | 49782.5067 | 20.016
Devonshire Building | 2017-01-21 21:15 | 49782.5067 | 0
Devonshire Building | 2017-01-21 21:30 | 49782.5117 | 20.016
Devonshire Building | 2017-01-21 21:45 | 49782.5117 | 0
Devonshire Building | 2017-01-21 22:00 | 49782.5217 | 39.996
Devonshire Building | 2017-01-21 22:15 | 49782.5267 | 20.016
Devonshire Building | 2017-01-21 22:30 | 49782.5267 | 0
Devonshire Building | 2017-01-21 22:45 | 49782.5318 | 20.016
Devonshire Building | 2017-01-21 23:00 | 49782.5318 | 0
Devonshire Building | 2017-01-21 23:15 | 49782.5368 | 20.016
Devonshire Building | 2017-01-21 23:30 | 49782.5368 | 0
Devonshire Building | 2017-01-21 23:45 | 49782.5418 | 20.016 | 0
Devonshire Building | 2017-01-22 | 49782.5391 | 0
Devonshire Building | 2017-01-22 00:15 | 49782.5441 | 20.016
Devonshire Building | 2017-01-22 00:30 | 49782.5491 | 20.016
Devonshire Building | 2017-01-22 00:45 | 49782.5491 | 0
Devonshire Building | 2017-01-22 01:00 | 49782.5541 | 20.016
Devonshire Building | 2017-01-22 01:15 | 49782.5541 | 0
Devonshire Building | 2017-01-22 01:30 | 49782.5591 | 20.016
Devonshire Building | 2017-01-22 01:45 | 49782.5591 | 0
Devonshire Building | 2017-01-22 02:00 | 49782.5641 | 20.016
Devonshire Building | 2017-01-22 02:15 | 49782.5641 | 0
Devonshire Building | 2017-01-22 02:30 | 49782.5691 | 20.016
Devonshire Building | 2017-01-22 02:45 | 49782.5691 | 0
Devonshire Building | 2017-01-22 03:00 | 49782.5741 | 20.016
Devonshire Building | 2017-01-22 03:15 | 49782.5741 | 0
Devonshire Building | 2017-01-22 03:30 | 49782.5791 | 20.016
Devonshire Building | 2017-01-22 03:45 | 49782.5841 | 20.016
Devonshire Building | 2017-01-22 04:00 | 49782.5841 | 0
Devonshire Building | 2017-01-22 04:15 | 49782.5891 | 20.016
Devonshire Building | 2017-01-22 04:30 | 49782.5891 | 0
Devonshire Building | 2017-01-22 04:45 | 49782.5941 | 20.016
Devonshire Building | 2017-01-22 05:00 | 49782.5941 | 0
Devonshire Building | 2017-01-22 05:15 | 49782.5991 | 20.016
Devonshire Building | 2017-01-22 05:30 | 49782.5991 | 0
Devonshire Building | 2017-01-22 05:45 | 49782.6041 | 20.016
Devonshire Building | 2017-01-22 06:00 | 49782.6041 | 0
Devonshire Building | 2017-01-22 06:15 | 49782.6091 | 20.016
Devonshire Building | 2017-01-22 06:30 | 49782.6091 | 0
Devonshire Building | 2017-01-22 06:45 | 49782.6141 | 20.016
Devonshire Building | 2017-01-22 07:00 | 49782.6191 | 20.016
Devonshire Building | 2017-01-22 07:15 | 49782.6191 | 0
Devonshire Building | 2017-01-22 07:30 | 49782.6241 | 20.016
Devonshire Building | 2017-01-22 07:45 | 49782.6341 | 39.996
Devonshire Building | 2017-01-22 08:00 | 49782.6541 | 79.992
Devonshire Building | 2017-01-22 08:15 | 49782.6741 | 79.992
Devonshire Building | 2017-01-22 08:30 | 49782.6941 | 79.992
Devonshire Building | 2017-01-22 08:45 | 49782.7141 | 79.992
Devonshire Building | 2017-01-22 09:00 | 49782.7291 | 60.012
Devonshire Building | 2017-01-22 09:15 | 49782.7491 | 79.992
Devonshire Building | 2017-01-22 09:30 | 49782.7691 | 79.992
Devonshire Building | 2017-01-22 09:45 | 49782.7891 | 79.992
Devonshire Building | 2017-01-22 10:00 | 49782.8091 | 79.992
Devonshire Building | 2017-01-22 10:15 | 49782.8241 | 60.012
Devonshire Building | 2017-01-22 10:30 | 49782.8241 | 0
Devonshire Building | 2017-01-22 10:45 | 49782.8291 | 20.016
Devonshire Building | 2017-01-22 11:00 | 49782.8291 | 0
Devonshire Building | 2017-01-22 11:15 | 49782.8341 | 20.016
Devonshire Building | 2017-01-22 11:30 | 49782.8391 | 20.016
Devonshire Building | 2017-01-22 11:45 | 49782.8391 | 0
Devonshire Building | 2017-01-22 12:00 | 49782.8441 | 20.016
Devonshire Building | 2017-01-22 12:15 | 49782.8441 | 0
Devonshire Building | 2017-01-22 12:30 | 49782.8491 | 20.016
Devonshire Building | 2017-01-22 12:45 | 49782.8491 | 0
Devonshire Building | 2017-01-22 13:00 | 49782.8541 | 20.016
Devonshire Building | 2017-01-22 13:15 | 49782.8591 | 20.016
Devonshire Building | 2017-01-22 13:30 | 49782.8591 | 0
Devonshire Building | 2017-01-22 13:45 | 49782.8641 | 20.016
Devonshire Building | 2017-01-22 14:00 | 49782.8692 | 20.016
Devonshire Building | 2017-01-22 14:15 | 49782.8692 | 0
Devonshire Building | 2017-01-22 14:30 | 49782.8742 | 20.016
Devonshire Building | 2017-01-22 14:45 | 49782.8742 | 0
Devonshire Building | 2017-01-22 15:00 | 49782.8792 | 20.016
Devonshire Building | 2017-01-22 15:15 | 49782.8792 | 0
Devonshire Building | 2017-01-22 15:30 | 49782.8842 | 20.016
Devonshire Building | 2017-01-22 15:45 | 49782.8892 | 20.016
Devonshire Building | 2017-01-22 16:00 | 49782.8892 | 0
Devonshire Building | 2017-01-22 16:15 | 49782.8942 | 20.016
Devonshire Building | 2017-01-22 16:30 | 49782.8942 | 0
Devonshire Building | 2017-01-22 16:45 | 49782.8992 | 20.016
Devonshire Building | 2017-01-22 17:00 | 49782.9042 | 20.016
Devonshire Building | 2017-01-22 17:15 | 49782.9092 | 20.016
Devonshire Building | 2017-01-22 17:30 | 49782.9092 | 0
Devonshire Building | 2017-01-22 17:45 | 49782.9142 | 20.016
Devonshire Building | 2017-01-22 18:00 | 49782.9192 | 20.016
Devonshire Building | 2017-01-22 18:15 | 49782.9192 | 0
Devonshire Building | 2017-01-22 18:30 | 49782.9242 | 20.016
Devonshire Building | 2017-01-22 18:45 | 49782.9292 | 20.016
Devonshire Building | 2017-01-22 19:00 | 49782.9342 | 20.016
Devonshire Building | 2017-01-22 19:15 | 49782.9342 | 0
Devonshire Building | 2017-01-22 19:30 | 49782.9392 | 20.016
Devonshire Building | 2017-01-22 19:45 | 49782.9442 | 20.016
Devonshire Building | 2017-01-22 20:00 | 49782.9492 | 20.016
Devonshire Building | 2017-01-22 20:15 | 49782.9492 | 0
Devonshire Building | 2017-01-22 20:30 | 49782.9542 | 20.016
Devonshire Building | 2017-01-22 20:45 | 49782.9592 | 20.016
Devonshire Building | 2017-01-22 21:00 | 49782.9592 | 0
Devonshire Building | 2017-01-22 21:15 | 49782.9642 | 20.016
Devonshire Building | 2017-01-22 21:30 | 49783.0292 | 259.992
Devonshire Building | 2017-01-22 21:45 | 49783.2292 | 799.992
Devonshire Building | 2017-01-22 22:00 | 49783.2392 | 39.996
Devonshire Building | 2017-01-22 22:15 | 49783.2442 | 20.016
Devonshire Building | 2017-01-22 22:30 | 49783.2492 | 20.016
Devonshire Building | 2017-01-22 22:45 | 49783.2492 | 0
Devonshire Building | 2017-01-22 23:00 | 49783.2542 | 20.016
Devonshire Building | 2017-01-22 23:15 | 49783.2542 | 0
Devonshire Building | 2017-01-22 23:30 | 49783.2592 | 20.016
Devonshire Building | 2017-01-22 23:45 | 49783.2592 | 0 | 0
Devonshire Building | 2017-01-23 | 49783.2656 | 20.016
Devonshire Building | 2017-01-23 00:15 | 49783.2706 | 20.016
Devonshire Building | 2017-01-23 00:30 | 49783.2706 | 0
Devonshire Building | 2017-01-23 00:45 | 49783.2756 | 20.016
Devonshire Building | 2017-01-23 01:00 | 49783.2756 | 0
Devonshire Building | 2017-01-23 01:15 | 49783.2806 | 20.016
Devonshire Building | 2017-01-23 01:30 | 49783.2806 | 0
Devonshire Building | 2017-01-23 01:45 | 49783.2856 | 20.016
Devonshire Building | 2017-01-23 02:00 | 49783.2856 | 0
Devonshire Building | 2017-01-23 02:15 | 49783.2907 | 20.016
Devonshire Building | 2017-01-23 02:30 | 49783.2957 | 20.016
Devonshire Building | 2017-01-23 02:45 | 49783.2957 | 0
Devonshire Building | 2017-01-23 03:00 | 49783.3007 | 20.016
Devonshire Building | 2017-01-23 03:15 | 49783.3007 | 0
Devonshire Building | 2017-01-23 03:30 | 49783.3057 | 20.016
Devonshire Building | 2017-01-23 03:45 | 49783.3057 | 0
Devonshire Building | 2017-01-23 04:00 | 49783.3107 | 20.016
Devonshire Building | 2017-01-23 04:15 | 49783.3107 | 0
Devonshire Building | 2017-01-23 04:30 | 49783.3157 | 20.016
Devonshire Building | 2017-01-23 04:45 | 49783.3207 | 20.016
Devonshire Building | 2017-01-23 05:00 | 49783.3207 | 0
Devonshire Building | 2017-01-23 05:15 | 49783.3257 | 20.016
Devonshire Building | 2017-01-23 05:30 | 49783.3257 | 0
Devonshire Building | 2017-01-23 05:45 | 49783.3307 | 20.016
Devonshire Building | 2017-01-23 06:00 | 49783.3307 | 0
Devonshire Building | 2017-01-23 06:15 | 49783.3357 | 20.016
Devonshire Building | 2017-01-23 06:30 | 49783.3407 | 20.016
Devonshire Building | 2017-01-23 06:45 | 49783.3457 | 20.016
Devonshire Building | 2017-01-23 07:00 | 49783.3457 | 0
Devonshire Building | 2017-01-23 07:15 | 49783.3507 | 20.016
Devonshire Building | 2017-01-23 07:30 | 49783.3607 | 39.996
Devonshire Building | 2017-01-23 07:45 | 49783.3807 | 79.992
Devonshire Building | 2017-01-23 08:00 | 49783.4007 | 79.992
Devonshire Building | 2017-01-23 08:15 | 49783.4357 | 140.004
Devonshire Building | 2017-01-23 08:30 | 49783.4607 | 100.008
Devonshire Building | 2017-01-23 08:45 | 49783.4857 | 100.008
Devonshire Building | 2017-01-23 09:00 | 49783.5107 | 100.008
Devonshire Building | 2017-01-23 09:15 | 49783.5407 | 119.988
Devonshire Building | 2017-01-23 09:30 | 49783.8707 | 1320.012
Devonshire Building | 2017-01-23 09:45 | 49783.8957 | 100.008
Devonshire Building | 2017-01-23 10:00 | 49783.9157 | 79.992
Devonshire Building | 2017-01-23 10:15 | 49783.9407 | 100.008
Devonshire Building | 2017-01-23 10:30 | 49783.9657 | 100.008
Devonshire Building | 2017-01-23 10:45 | 49784.2857 | 1280.016
Devonshire Building | 2017-01-23 11:00 | 49784.2907 | 20.016
Devonshire Building | 2017-01-23 11:15 | 49784.3107 | 79.992
Devonshire Building | 2017-01-23 11:30 | 49784.3257 | 60.012
Devonshire Building | 2017-01-23 11:45 | 49784.3757 | 200.016
Devonshire Building | 2017-01-23 12:00 | 49784.7757 | 1599.984
Devonshire Building | 2017-01-23 12:15 | 49784.8557 | 320.004
Devonshire Building | 2017-01-23 12:30 | 49784.9407 | 339.984
Devonshire Building | 2017-01-23 12:45 | 49785.0207 | 320.004
Devonshire Building | 2017-01-23 13:00 | 49785.0957 | 299.988
Devonshire Building | 2017-01-23 13:15 | 49785.1657 | 280.008
Devonshire Building | 2017-01-23 13:30 | 49785.5057 | 1360.008
Devonshire Building | 2017-01-23 13:45 | 49785.5757 | 280.008
Devonshire Building | 2017-01-23 14:00 | 49785.6557 | 320.004
Devonshire Building | 2017-01-23 14:15 | 49785.7307 | 299.988
Devonshire Building | 2017-01-23 14:30 | 49785.8007 | 280.008
Devonshire Building | 2017-01-23 14:45 | 49785.8657 | 259.992
Devonshire Building | 2017-01-23 15:00 | 49786.2307 | 1460.016
Devonshire Building | 2017-01-23 15:15 | 49786.2907 | 240.012
Devonshire Building | 2017-01-23 15:30 | 49786.3507 | 240.012
Devonshire Building | 2017-01-23 15:45 | 49786.4057 | 219.996
Devonshire Building | 2017-01-23 16:00 | 49786.4607 | 219.996
Devonshire Building | 2017-01-23 16:15 | 49786.5007 | 159.984
Devonshire Building | 2017-01-23 16:30 | 49786.8407 | 1360.008
Devonshire Building | 2017-01-23 16:45 | 49786.8607 | 79.992
Devonshire Building | 2017-01-23 17:00 | 49786.8857 | 100.008
Devonshire Building | 2017-01-23 17:15 | 49786.9057 | 79.992
Devonshire Building | 2017-01-23 17:30 | 49786.9257 | 79.992
Devonshire Building | 2017-01-23 17:45 | 49786.9507 | 100.008
Devonshire Building | 2017-01-23 18:00 | 49786.9707 | 79.992
Devonshire Building | 2017-01-23 18:15 | 49786.9957 | 100.008
Devonshire Building | 2017-01-23 18:30 | 49787.0157 | 79.992
Devonshire Building | 2017-01-23 18:45 | 49787.1257 | 439.992
Devonshire Building | 2017-01-23 19:00 | 49787.3257 | 799.992
Devonshire Building | 2017-01-23 19:15 | 49787.3407 | 60.012
Devonshire Building | 2017-01-23 19:30 | 49787.3557 | 60.012
Devonshire Building | 2017-01-23 19:45 | 49787.3707 | 60.012
Devonshire Building | 2017-01-23 20:00 | 49787.3907 | 79.992
Devonshire Building | 2017-01-23 20:15 | 49787.4057 | 60.012
Devonshire Building | 2017-01-23 20:30 | 49787.4257 | 79.992
Devonshire Building | 2017-01-23 20:45 | 49787.4407 | 60.012
Devonshire Building | 2017-01-23 21:00 | 49787.4557 | 60.012
Devonshire Building | 2017-01-23 21:15 | 49787.4707 | 60.012
Devonshire Building | 2017-01-23 21:30 | 49787.4857 | 60.012
Devonshire Building | 2017-01-23 21:45 | 49787.5007 | 60.012
Devonshire Building | 2017-01-23 22:00 | 49787.5157 | 60.012
Devonshire Building | 2017-01-23 22:15 | 49787.5257 | 39.996
Devonshire Building | 2017-01-23 22:30 | 49787.5357 | 39.996
Devonshire Building | 2017-01-23 22:45 | 49787.5457 | 39.996
Devonshire Building | 2017-01-23 23:00 | 49787.5557 | 39.996
Devonshire Building | 2017-01-23 23:15 | 49787.5607 | 20.016
Devonshire Building | 2017-01-23 23:30 | 49787.5707 | 39.996
Devonshire Building | 2017-01-23 23:45 | 49787.5807 | 39.996 | 0
Devonshire Building | 2017-01-24 | 49787.5859 | 20.016
Devonshire Building | 2017-01-24 00:15 | 49787.5959 | 39.996
Devonshire Building | 2017-01-24 00:30 | 49787.6009 | 20.016
Devonshire Building | 2017-01-24 00:45 | 49787.6059 | 20.016
Devonshire Building | 2017-01-24 01:00 | 49787.6159 | 39.996
Devonshire Building | 2017-01-24 01:15 | 49787.6209 | 20.016
Devonshire Building | 2017-01-24 01:30 | 49787.626 | 20.016
Devonshire Building | 2017-01-24 01:45 | 49787.631 | 20.016
Devonshire Building | 2017-01-24 02:00 | 49787.636 | 20.016
Devonshire Building | 2017-01-24 02:15 | 49787.646 | 39.996
Devonshire Building | 2017-01-24 02:30 | 49787.651 | 20.016
Devonshire Building | 2017-01-24 02:45 | 49787.656 | 20.016
Devonshire Building | 2017-01-24 03:00 | 49787.661 | 20.016
Devonshire Building | 2017-01-24 03:15 | 49787.666 | 20.016
Devonshire Building | 2017-01-24 03:30 | 49787.671 | 20.016
Devonshire Building | 2017-01-24 03:45 | 49787.676 | 20.016
Devonshire Building | 2017-01-24 04:00 | 49787.681 | 20.016
Devonshire Building | 2017-01-24 04:15 | 49787.686 | 20.016
Devonshire Building | 2017-01-24 04:30 | 49787.686 | 0
Devonshire Building | 2017-01-24 04:45 | 49787.691 | 20.016
Devonshire Building | 2017-01-24 05:00 | 49787.696 | 20.016
Devonshire Building | 2017-01-24 05:15 | 49787.701 | 20.016
Devonshire Building | 2017-01-24 05:30 | 49787.706 | 20.016
Devonshire Building | 2017-01-24 05:45 | 49787.706 | 0
Devonshire Building | 2017-01-24 06:00 | 49787.711 | 20.016
Devonshire Building | 2017-01-24 06:15 | 49787.716 | 20.016
Devonshire Building | 2017-01-24 06:30 | 49787.721 | 20.016
Devonshire Building | 2017-01-24 06:45 | 49787.726 | 20.016
Devonshire Building | 2017-01-24 07:00 | 49787.731 | 20.016
Devonshire Building | 2017-01-24 07:15 | 49787.736 | 20.016
Devonshire Building | 2017-01-24 07:30 | 49787.736 | 0
Devonshire Building | 2017-01-24 07:45 | 49787.746 | 39.996
Devonshire Building | 2017-01-24 08:00 | 49787.766 | 79.992
Devonshire Building | 2017-01-24 08:15 | 49787.786 | 79.992
Devonshire Building | 2017-01-24 08:30 | 49787.806 | 79.992
Devonshire Building | 2017-01-24 08:45 | 49787.826 | 79.992
Devonshire Building | 2017-01-24 09:00 | 49788.146 | 1280.016
Devonshire Building | 2017-01-24 09:15 | 49788.171 | 100.008
Devonshire Building | 2017-01-24 09:30 | 49788.196 | 100.008
Devonshire Building | 2017-01-24 09:45 | 49788.221 | 100.008
Devonshire Building | 2017-01-24 10:00 | 49788.246 | 100.008
Devonshire Building | 2017-01-24 10:15 | 49788.286 | 159.984
Devonshire Building | 2017-01-24 10:30 | 49788.651 | 1460.016
Devonshire Building | 2017-01-24 10:45 | 49788.751 | 399.996
Devonshire Building | 2017-01-24 11:00 | 49788.846 | 380.016
Devonshire Building | 2017-01-24 11:15 | 49788.926 | 320.004
Devonshire Building | 2017-01-24 11:30 | 49789.006 | 320.004
Devonshire Building | 2017-01-24 11:45 | 49789.116 | 439.992
Devonshire Building | 2017-01-24 12:00 | 49789.476 | 1440
Devonshire Building | 2017-01-24 12:15 | 49789.536 | 240.012
Devonshire Building | 2017-01-24 12:30 | 49789.601 | 259.992
Devonshire Building | 2017-01-24 12:45 | 49789.671 | 280.008
Devonshire Building | 2017-01-24 13:00 | 49789.731 | 240.012
Devonshire Building | 2017-01-24 13:15 | 49790.091 | 1440
Devonshire Building | 2017-01-24 13:30 | 49790.166 | 299.988
Devonshire Building | 2017-01-24 13:45 | 49790.246 | 320.004
Devonshire Building | 2017-01-24 14:00 | 49790.321 | 299.988
Devonshire Building | 2017-01-24 14:15 | 49790.391 | 280.008
Devonshire Building | 2017-01-24 14:30 | 49790.456 | 259.992
Devonshire Building | 2017-01-24 14:45 | 49790.851 | 1580.004
Devonshire Building | 2017-01-24 15:00 | 49790.901 | 200.016
Devonshire Building | 2017-01-24 15:15 | 49790.956 | 219.996
Devonshire Building | 2017-01-24 15:30 | 49791.021 | 259.992
Devonshire Building | 2017-01-24 15:45 | 49791.086 | 259.992
Devonshire Building | 2017-01-24 16:00 | 49791.141 | 219.996
Devonshire Building | 2017-01-24 16:15 | 49791.201 | 240.012
Devonshire Building | 2017-01-24 16:30 | 49791.796 | 2379.996
Devonshire Building | 2017-01-24 16:45 | 49791.841 | 180
Devonshire Building | 2017-01-24 17:00 | 49791.896 | 219.996
Devonshire Building | 2017-01-24 17:15 | 49791.951 | 219.996
Devonshire Building | 2017-01-24 17:30 | 49792.001 | 200.016
Devonshire Building | 2017-01-24 17:45 | 49792.036 | 140.004
Devonshire Building | 2017-01-24 18:00 | 49792.071 | 140.004
Devonshire Building | 2017-01-24 18:15 | 49792.576 | 2019.996
Devonshire Building | 2017-01-24 18:30 | 49792.691 | 460.008
Devonshire Building | 2017-01-24 18:45 | 49792.706 | 60.012
Devonshire Building | 2017-01-24 19:00 | 49792.716 | 39.996
Devonshire Building | 2017-01-24 19:15 | 49792.726 | 39.996
Devonshire Building | 2017-01-24 19:30 | 49792.741 | 60.012
Devonshire Building | 2017-01-24 19:45 | 49792.751 | 39.996
Devonshire Building | 2017-01-24 20:00 | 49792.7661 | 60.012
Devonshire Building | 2017-01-24 20:15 | 49792.7761 | 39.996
Devonshire Building | 2017-01-24 20:30 | 49792.7911 | 60.012
Devonshire Building | 2017-01-24 20:45 | 49792.8011 | 39.996
Devonshire Building | 2017-01-24 21:00 | 49792.8161 | 60.012
Devonshire Building | 2017-01-24 21:15 | 49792.8261 | 39.996
Devonshire Building | 2017-01-24 21:30 | 49792.8361 | 39.996
Devonshire Building | 2017-01-24 21:45 | 49792.8461 | 39.996
Devonshire Building | 2017-01-24 22:00 | 49792.8611 | 60.012
Devonshire Building | 2017-01-24 22:15 | 49792.8661 | 20.016
Devonshire Building | 2017-01-24 22:30 | 49792.8761 | 39.996
Devonshire Building | 2017-01-24 22:45 | 49792.8811 | 20.016
Devonshire Building | 2017-01-24 23:00 | 49792.8911 | 39.996
Devonshire Building | 2017-01-24 23:15 | 49792.8961 | 20.016
Devonshire Building | 2017-01-24 23:30 | 49792.9061 | 39.996
Devonshire Building | 2017-01-24 23:45 | 49792.9111 | 20.016 | 0
Devonshire Building | 2017-01-25 | 49792.9141 | 20.016
Devonshire Building | 2017-01-25 00:15 | 49792.9241 | 39.996
Devonshire Building | 2017-01-25 00:30 | 49792.9291 | 20.016
Devonshire Building | 2017-01-25 00:45 | 49792.9341 | 20.016
Devonshire Building | 2017-01-25 01:00 | 49792.9391 | 20.016
Devonshire Building | 2017-01-25 01:15 | 49792.9491 | 39.996
Devonshire Building | 2017-01-25 01:30 | 49792.9541 | 20.016
Devonshire Building | 2017-01-25 01:45 | 49792.9591 | 20.016
Devonshire Building | 2017-01-25 02:00 | 49792.9641 | 20.016
Devonshire Building | 2017-01-25 02:15 | 49792.9691 | 20.016
Devonshire Building | 2017-01-25 02:30 | 49792.9741 | 20.016
Devonshire Building | 2017-01-25 02:45 | 49792.9791 | 20.016
Devonshire Building | 2017-01-25 03:00 | 49792.9841 | 20.016
Devonshire Building | 2017-01-25 03:15 | 49792.9891 | 20.016
Devonshire Building | 2017-01-25 03:30 | 49792.9941 | 20.016
Devonshire Building | 2017-01-25 03:45 | 49792.9941 | 0
Devonshire Building | 2017-01-25 04:00 | 49792.9991 | 20.016
Devonshire Building | 2017-01-25 04:15 | 49793.0041 | 20.016
Devonshire Building | 2017-01-25 04:30 | 49793.0091 | 20.016
Devonshire Building | 2017-01-25 04:45 | 49793.0141 | 20.016
Devonshire Building | 2017-01-25 05:00 | 49793.0141 | 0
Devonshire Building | 2017-01-25 05:15 | 49793.0191 | 20.016
Devonshire Building | 2017-01-25 05:30 | 49793.0241 | 20.016
Devonshire Building | 2017-01-25 05:45 | 49793.0291 | 20.016
Devonshire Building | 2017-01-25 06:00 | 49793.0291 | 0
Devonshire Building | 2017-01-25 06:15 | 49793.0391 | 39.996
Devonshire Building | 2017-01-25 06:30 | 49793.0391 | 0
Devonshire Building | 2017-01-25 06:45 | 49793.0491 | 39.996
Devonshire Building | 2017-01-25 07:00 | 49793.0541 | 20.016
Devonshire Building | 2017-01-25 07:15 | 49793.0541 | 0
Devonshire Building | 2017-01-25 07:30 | 49793.0591 | 20.016
Devonshire Building | 2017-01-25 07:45 | 49793.0741 | 60.012
Devonshire Building | 2017-01-25 08:00 | 49793.0941 | 79.992
Devonshire Building | 2017-01-25 08:15 | 49793.1291 | 140.004
Devonshire Building | 2017-01-25 08:30 | 49793.1541 | 100.008
Devonshire Building | 2017-01-25 08:45 | 49793.1841 | 119.988
Devonshire Building | 2017-01-25 09:00 | 49793.7541 | 2279.988
Devonshire Building | 2017-01-25 09:15 | 49793.7841 | 119.988
Devonshire Building | 2017-01-25 09:30 | 49793.8091 | 100.008
Devonshire Building | 2017-01-25 09:45 | 49793.8641 | 219.996
Devonshire Building | 2017-01-25 10:00 | 49793.9491 | 339.984
Devonshire Building | 2017-01-25 10:15 | 49794.0641 | 460.008
Devonshire Building | 2017-01-25 10:30 | 49794.8891 | 3300.012
Devonshire Building | 2017-01-25 10:45 | 49795.0891 | 799.992
Devonshire Building | 2017-01-25 11:00 | 49795.2141 | 500.004
Devonshire Building | 2017-01-25 11:15 | 49795.3041 | 360
Devonshire Building | 2017-01-25 11:30 | 49795.3641 | 240.012
Devonshire Building | 2017-01-25 11:45 | 49795.4141 | 200.016
Devonshire Building | 2017-01-25 12:00 | 49796.0141 | 2400.012
Devonshire Building | 2017-01-25 12:15 | 49796.0291 | 60.012
Devonshire Building | 2017-01-25 12:30 | 49796.0491 | 79.992
Devonshire Building | 2017-01-25 12:45 | 49796.0691 | 79.992
Devonshire Building | 2017-01-25 13:00 | 49796.0891 | 79.992
Devonshire Building | 2017-01-25 13:15 | 49796.4891 | 1599.984
Devonshire Building | 2017-01-25 13:30 | 49796.6991 | 839.988
Devonshire Building | 2017-01-25 13:45 | 49796.7391 | 159.984
Devonshire Building | 2017-01-25 14:00 | 49796.7841 | 180
Devonshire Building | 2017-01-25 14:15 | 49796.8391 | 219.996
Devonshire Building | 2017-01-25 14:30 | 49796.8891 | 200.016
Devonshire Building | 2017-01-25 14:45 | 49797.2441 | 1419.984
Devonshire Building | 2017-01-25 15:00 | 49797.5641 | 1280.016
Devonshire Building | 2017-01-25 15:15 | 49797.6141 | 200.016
Devonshire Building | 2017-01-25 15:30 | 49797.6691 | 219.996
Devonshire Building | 2017-01-25 15:45 | 49797.7241 | 219.996
Devonshire Building | 2017-01-25 16:00 | 49798.2991 | 2300.004
Devonshire Building | 2017-01-25 16:15 | 49798.5391 | 960.012
Devonshire Building | 2017-01-25 16:30 | 49798.6691 | 519.984
Devonshire Building | 2017-01-25 16:45 | 49798.7691 | 399.996
Devonshire Building | 2017-01-25 17:00 | 49798.8491 | 320.004
Devonshire Building | 2017-01-25 17:15 | 49798.9191 | 280.008
Devonshire Building | 2017-01-25 17:30 | 49799.4341 | 2059.992
Devonshire Building | 2017-01-25 17:45 | 49799.6191 | 740.016
Devonshire Building | 2017-01-25 18:00 | 49799.6741 | 219.996
Devonshire Building | 2017-01-25 18:15 | 49799.7291 | 219.996
Devonshire Building | 2017-01-25 18:30 | 49799.7741 | 180
Devonshire Building | 2017-01-25 18:45 | 49799.8091 | 140.004
Devonshire Building | 2017-01-25 19:00 | 49799.8441 | 140.004
Devonshire Building | 2017-01-25 19:15 | 49799.8691 | 100.008
Devonshire Building | 2017-01-25 19:30 | 49799.8941 | 100.008
Devonshire Building | 2017-01-25 19:45 | 49799.9141 | 79.992
Devonshire Building | 2017-01-25 20:00 | 49799.9291 | 60.012
Devonshire Building | 2017-01-25 20:15 | 49799.9441 | 60.012
Devonshire Building | 2017-01-25 20:30 | 49799.9592 | 60.012
Devonshire Building | 2017-01-25 20:45 | 49799.9742 | 60.012
Devonshire Building | 2017-01-25 21:00 | 49799.9892 | 60.012
Devonshire Building | 2017-01-25 21:15 | 49799.9992 | 39.996
Devonshire Building | 2017-01-25 21:30 | 49800.0092 | 39.996
Devonshire Building | 2017-01-25 21:45 | 49800.0192 | 39.996
Devonshire Building | 2017-01-25 22:00 | 49800.0442 | 100.008
Devonshire Building | 2017-01-25 22:15 | 49800.0492 | 20.016
Devonshire Building | 2017-01-25 22:30 | 49800.0542 | 20.016
Devonshire Building | 2017-01-25 22:45 | 49800.0542 | 0
Devonshire Building | 2017-01-25 23:00 | 49800.0592 | 20.016
Devonshire Building | 2017-01-25 23:15 | 49800.0642 | 20.016
Devonshire Building | 2017-01-25 23:30 | 49800.0642 | 0
Devonshire Building | 2017-01-25 23:45 | 49800.0692 | 20.016 | 0
Devonshire Building | 2017-01-26 | 49800.0703 | 0
Devonshire Building | 2017-01-26 00:15 | 49800.0753 | 20.016
Devonshire Building | 2017-01-26 00:30 | 49800.0803 | 20.016
Devonshire Building | 2017-01-26 00:45 | 49800.0803 | 0
Devonshire Building | 2017-01-26 01:00 | 49800.0853 | 20.016
Devonshire Building | 2017-01-26 01:15 | 49800.0853 | 0
Devonshire Building | 2017-01-26 01:30 | 49800.0903 | 20.016
Devonshire Building | 2017-01-26 01:45 | 49800.0953 | 20.016
Devonshire Building | 2017-01-26 02:00 | 49800.0953 | 0
Devonshire Building | 2017-01-26 02:15 | 49800.1003 | 20.016
Devonshire Building | 2017-01-26 02:30 | 49800.1003 | 0
Devonshire Building | 2017-01-26 02:45 | 49800.1053 | 20.016
Devonshire Building | 2017-01-26 03:00 | 49800.1103 | 20.016
Devonshire Building | 2017-01-26 03:15 | 49800.1103 | 0
Devonshire Building | 2017-01-26 03:30 | 49800.1153 | 20.016
Devonshire Building | 2017-01-26 03:45 | 49800.1153 | 0
Devonshire Building | 2017-01-26 04:00 | 49800.1203 | 20.016
Devonshire Building | 2017-01-26 04:15 | 49800.1254 | 20.016
Devonshire Building | 2017-01-26 04:30 | 49800.1254 | 0
Devonshire Building | 2017-01-26 04:45 | 49800.1304 | 20.016
Devonshire Building | 2017-01-26 05:00 | 49800.1304 | 0
Devonshire Building | 2017-01-26 05:15 | 49800.1354 | 20.016
Devonshire Building | 2017-01-26 05:30 | 49800.1354 | 0
Devonshire Building | 2017-01-26 05:45 | 49800.1404 | 20.016
Devonshire Building | 2017-01-26 06:00 | 49800.1404 | 0
Devonshire Building | 2017-01-26 06:15 | 49800.1454 | 20.016
Devonshire Building | 2017-01-26 06:30 | 49800.1504 | 20.016
Devonshire Building | 2017-01-26 06:45 | 49800.1504 | 0
Devonshire Building | 2017-01-26 07:00 | 49800.1554 | 20.016
Devonshire Building | 2017-01-26 07:15 | 49800.1604 | 20.016
Devonshire Building | 2017-01-26 07:30 | 49800.4054 | 979.992
Devonshire Building | 2017-01-26 07:45 | 49800.7104 | 1220.004
Devonshire Building | 2017-01-26 08:00 | 49800.7304 | 79.992
Devonshire Building | 2017-01-26 08:15 | 49800.7554 | 100.008
Devonshire Building | 2017-01-26 08:30 | 49800.7804 | 100.008
Devonshire Building | 2017-01-26 08:45 | 49800.8054 | 100.008
Devonshire Building | 2017-01-26 09:00 | 49800.8304 | 100.008
Devonshire Building | 2017-01-26 09:15 | 49800.8554 | 100.008
Devonshire Building | 2017-01-26 09:30 | 49800.8804 | 100.008
Devonshire Building | 2017-01-26 09:45 | 49800.9054 | 100.008
Devonshire Building | 2017-01-26 10:00 | 49801.4904 | 2340
Devonshire Building | 2017-01-26 10:15 | 49801.5104 | 79.992
Devonshire Building | 2017-01-26 10:30 | 49801.5354 | 100.008
Devonshire Building | 2017-01-26 10:45 | 49801.5604 | 100.008
Devonshire Building | 2017-01-26 11:00 | 49802.0304 | 1879.992
Devonshire Building | 2017-01-26 11:15 | 49802.1754 | 579.996
Devonshire Building | 2017-01-26 11:30 | 49802.1954 | 79.992
Devonshire Building | 2017-01-26 11:45 | 49802.2254 | 119.988
Devonshire Building | 2017-01-26 12:00 | 49802.2604 | 140.004
Devonshire Building | 2017-01-26 12:15 | 49802.4854 | 900
Devonshire Building | 2017-01-26 12:30 | 49802.8904 | 1620
Devonshire Building | 2017-01-26 12:45 | 49802.9554 | 259.992
Devonshire Building | 2017-01-26 13:00 | 49803.0204 | 259.992
Devonshire Building | 2017-01-26 13:15 | 49803.0804 | 240.012
Devonshire Building | 2017-01-26 13:30 | 49803.1504 | 280.008
Devonshire Building | 2017-01-26 13:45 | 49803.2154 | 259.992
Devonshire Building | 2017-01-26 14:00 | 49803.8604 | 2580.012
Devonshire Building | 2017-01-26 14:15 | 49803.9354 | 299.988
Devonshire Building | 2017-01-26 14:30 | 49804.0204 | 339.984
Devonshire Building | 2017-01-26 14:45 | 49804.0854 | 259.992
Devonshire Building | 2017-01-26 15:00 | 49804.1554 | 280.008
Devonshire Building | 2017-01-26 15:15 | 49804.2154 | 240.012
Devonshire Building | 2017-01-26 15:30 | 49804.8704 | 2620.008
Devonshire Building | 2017-01-26 15:45 | 49804.9154 | 180
Devonshire Building | 2017-01-26 16:00 | 49804.9704 | 219.996
Devonshire Building | 2017-01-26 16:15 | 49805.0254 | 219.996
Devonshire Building | 2017-01-26 16:30 | 49805.0954 | 280.008
Devonshire Building | 2017-01-26 16:45 | 49805.1804 | 339.984
Devonshire Building | 2017-01-26 17:00 | 49805.8704 | 2760.012
Devonshire Building | 2017-01-26 17:15 | 49806.1204 | 1000.008
Devonshire Building | 2017-01-26 17:30 | 49806.2604 | 560.016
Devonshire Building | 2017-01-26 17:45 | 49806.3454 | 339.984
Devonshire Building | 2017-01-26 18:00 | 49806.4004 | 219.996
Devonshire Building | 2017-01-26 18:15 | 49806.4404 | 159.984
Devonshire Building | 2017-01-26 18:30 | 49806.4754 | 140.004
Devonshire Building | 2017-01-26 18:45 | 49806.5054 | 119.988
Devonshire Building | 2017-01-26 19:00 | 49806.5304 | 100.008
Devonshire Building | 2017-01-26 19:15 | 49806.5454 | 60.012
Devonshire Building | 2017-01-26 19:30 | 49806.5654 | 79.992
Devonshire Building | 2017-01-26 19:45 | 49806.5804 | 60.012
Devonshire Building | 2017-01-26 20:00 | 49806.5954 | 60.012
Devonshire Building | 2017-01-26 20:15 | 49806.6104 | 60.012
Devonshire Building | 2017-01-26 20:30 | 49806.6204 | 39.996
Devonshire Building | 2017-01-26 20:45 | 49806.6354 | 60.012
Devonshire Building | 2017-01-26 21:00 | 49806.6454 | 39.996
Devonshire Building | 2017-01-26 21:15 | 49806.6554 | 39.996
Devonshire Building | 2017-01-26 21:30 | 49806.6654 | 39.996
Devonshire Building | 2017-01-26 21:45 | 49806.6804 | 60.012
Devonshire Building | 2017-01-26 22:00 | 49806.7054 | 100.008
Devonshire Building | 2017-01-26 22:15 | 49806.7104 | 20.016
Devonshire Building | 2017-01-26 22:30 | 49806.7154 | 20.016
Devonshire Building | 2017-01-26 22:45 | 49806.7154 | 0
Devonshire Building | 2017-01-26 23:00 | 49806.7204 | 20.016
Devonshire Building | 2017-01-26 23:15 | 49806.7254 | 20.016
Devonshire Building | 2017-01-26 23:30 | 49806.7254 | 0
Devonshire Building | 2017-01-26 23:45 | 49806.7304 | 20.016 | 0
Devonshire Building | 2017-01-27 | 49806.7344 | 20.016
Devonshire Building | 2017-01-27 00:15 | 49806.7344 | 0
Devonshire Building | 2017-01-27 00:30 | 49806.7394 | 20.016
Devonshire Building | 2017-01-27 00:45 | 49806.7394 | 0
Devonshire Building | 2017-01-27 01:00 | 49806.7444 | 20.016
Devonshire Building | 2017-01-27 01:15 | 49806.7494 | 20.016
Devonshire Building | 2017-01-27 01:30 | 49806.7494 | 0
Devonshire Building | 2017-01-27 01:45 | 49806.7544 | 20.016
Devonshire Building | 2017-01-27 02:00 | 49806.7594 | 20.016
Devonshire Building | 2017-01-27 02:15 | 49806.7594 | 0
Devonshire Building | 2017-01-27 02:30 | 49806.7644 | 20.016
Devonshire Building | 2017-01-27 02:45 | 49806.7644 | 0
Devonshire Building | 2017-01-27 03:00 | 49806.7694 | 20.016
Devonshire Building | 2017-01-27 03:15 | 49806.7744 | 20.016
Devonshire Building | 2017-01-27 03:30 | 49806.7744 | 0
Devonshire Building | 2017-01-27 03:45 | 49806.7794 | 20.016
Devonshire Building | 2017-01-27 04:00 | 49806.7844 | 20.016
Devonshire Building | 2017-01-27 04:15 | 49806.7844 | 0
Devonshire Building | 2017-01-27 04:30 | 49806.7894 | 20.016
Devonshire Building | 2017-01-27 04:45 | 49806.7894 | 0
Devonshire Building | 2017-01-27 05:00 | 49806.7944 | 20.016
Devonshire Building | 2017-01-27 05:15 | 49806.7994 | 20.016
Devonshire Building | 2017-01-27 05:30 | 49806.7994 | 0
Devonshire Building | 2017-01-27 05:45 | 49806.8044 | 20.016
Devonshire Building | 2017-01-27 06:00 | 49806.8044 | 0
Devonshire Building | 2017-01-27 06:15 | 49806.8094 | 20.016
Devonshire Building | 2017-01-27 06:30 | 49806.8144 | 20.016
Devonshire Building | 2017-01-27 06:45 | 49806.8194 | 20.016
Devonshire Building | 2017-01-27 07:00 | 49806.8245 | 20.016
Devonshire Building | 2017-01-27 07:15 | 49806.8695 | 180
Devonshire Building | 2017-01-27 07:30 | 49807.3944 | 2099.988
Devonshire Building | 2017-01-27 07:45 | 49807.4195 | 100.008
Devonshire Building | 2017-01-27 08:00 | 49807.4394 | 79.992
Devonshire Building | 2017-01-27 08:15 | 49807.4645 | 100.008
Devonshire Building | 2017-01-27 08:30 | 49807.4944 | 119.988
Devonshire Building | 2017-01-27 08:45 | 49807.5194 | 100.008
Devonshire Building | 2017-01-27 09:00 | 49807.5594 | 159.984
Devonshire Building | 2017-01-27 09:15 | 49807.5844 | 100.008
Devonshire Building | 2017-01-27 09:30 | 49807.6044 | 79.992
Devonshire Building | 2017-01-27 09:45 | 49807.6244 | 79.992
Devonshire Building | 2017-01-27 10:00 | 49807.6494 | 100.008
Devonshire Building | 2017-01-27 10:15 | 49808.2744 | 2499.984
Devonshire Building | 2017-01-27 10:30 | 49808.3144 | 159.984
Devonshire Building | 2017-01-27 10:45 | 49808.3994 | 339.984
Devonshire Building | 2017-01-27 11:00 | 49808.5244 | 500.004
Devonshire Building | 2017-01-27 11:15 | 49808.6394 | 460.008
Devonshire Building | 2017-01-27 11:30 | 49809.1194 | 1919.988
Devonshire Building | 2017-01-27 11:45 | 49809.3644 | 979.992
Devonshire Building | 2017-01-27 12:00 | 49809.4344 | 280.008
Devonshire Building | 2017-01-27 12:15 | 49809.4994 | 259.992
Devonshire Building | 2017-01-27 12:30 | 49809.5594 | 240.012
Devonshire Building | 2017-01-27 12:45 | 49809.6194 | 240.012
Devonshire Building | 2017-01-27 13:00 | 49809.6694 | 200.016
Devonshire Building | 2017-01-27 13:15 | 49810.1394 | 1879.992
Devonshire Building | 2017-01-27 13:30 | 49810.3044 | 659.988
Devonshire Building | 2017-01-27 13:45 | 49810.3294 | 100.008
Devonshire Building | 2017-01-27 14:00 | 49810.3494 | 79.992
Devonshire Building | 2017-01-27 14:15 | 49810.3794 | 119.988
Devonshire Building | 2017-01-27 14:30 | 49810.4044 | 100.008
Devonshire Building | 2017-01-27 14:45 | 49810.4494 | 180
Devonshire Building | 2017-01-27 15:00 | 49810.5344 | 339.984
Devonshire Building | 2017-01-27 15:15 | 49810.8044 | 1080
Devonshire Building | 2017-01-27 15:30 | 49811.2744 | 1879.992
Devonshire Building | 2017-01-27 15:45 | 49811.3894 | 460.008
Devonshire Building | 2017-01-27 16:00 | 49811.5044 | 460.008
Devonshire Building | 2017-01-27 16:15 | 49811.6344 | 519.984
Devonshire Building | 2017-01-27 16:30 | 49811.7644 | 519.984
Devonshire Building | 2017-01-27 16:45 | 49811.8894 | 500.004
Devonshire Building | 2017-01-27 17:00 | 49812.0494 | 640.008
Devonshire Building | 2017-01-27 17:15 | 49812.6794 | 2520
Devonshire Building | 2017-01-27 17:30 | 49812.7444 | 259.992
Devonshire Building | 2017-01-27 17:45 | 49812.8094 | 259.992
Devonshire Building | 2017-01-27 18:00 | 49812.8694 | 240.012
Devonshire Building | 2017-01-27 18:15 | 49812.9194 | 200.016
Devonshire Building | 2017-01-27 18:30 | 49812.9644 | 180
Devonshire Building | 2017-01-27 18:45 | 49813.0044 | 159.984
Devonshire Building | 2017-01-27 19:00 | 49813.0344 | 119.988
Devonshire Building | 2017-01-27 19:15 | 49813.0644 | 119.988
Devonshire Building | 2017-01-27 19:30 | 49813.0844 | 79.992
Devonshire Building | 2017-01-27 19:45 | 49813.1094 | 100.008
Devonshire Building | 2017-01-27 20:00 | 49813.1294 | 79.992
Devonshire Building | 2017-01-27 20:15 | 49813.1494 | 79.992
Devonshire Building | 2017-01-27 20:30 | 49813.1644 | 60.012
Devonshire Building | 2017-01-27 20:45 | 49813.1794 | 60.012
Devonshire Building | 2017-01-27 21:00 | 49813.1944 | 60.012
Devonshire Building | 2017-01-27 21:15 | 49813.2094 | 60.012
Devonshire Building | 2017-01-27 21:30 | 49813.2244 | 60.012
Devonshire Building | 2017-01-27 21:45 | 49813.2394 | 60.012
Devonshire Building | 2017-01-27 22:00 | 49813.2544 | 60.012
Devonshire Building | 2017-01-27 22:15 | 49813.2594 | 20.016
Devonshire Building | 2017-01-27 22:30 | 49813.2694 | 39.996
Devonshire Building | 2017-01-27 22:45 | 49813.2794 | 39.996
Devonshire Building | 2017-01-27 23:00 | 49813.2894 | 39.996
Devonshire Building | 2017-01-27 23:15 | 49813.2944 | 20.016
Devonshire Building | 2017-01-27 23:30 | 49813.3044 | 39.996
Devonshire Building | 2017-01-27 23:45 | 49813.3144 | 39.996 | 0
Devonshire Building | 2017-01-28 | 49813.3203 | 20.016
Devonshire Building | 2017-01-28 00:15 | 49813.3303 | 39.996
Devonshire Building | 2017-01-28 00:30 | 49813.3403 | 39.996
Devonshire Building | 2017-01-28 00:45 | 49813.3453 | 20.016
Devonshire Building | 2017-01-28 01:00 | 49813.3553 | 39.996
Devonshire Building | 2017-01-28 01:15 | 49813.3603 | 20.016
Devonshire Building | 2017-01-28 01:30 | 49813.3703 | 39.996
Devonshire Building | 2017-01-28 01:45 | 49813.3753 | 20.016
Devonshire Building | 2017-01-28 02:00 | 49813.3853 | 39.996
Devonshire Building | 2017-01-28 02:15 | 49813.3903 | 20.016
Devonshire Building | 2017-01-28 02:30 | 49813.3953 | 20.016
Devonshire Building | 2017-01-28 02:45 | 49813.4053 | 39.996
Devonshire Building | 2017-01-28 03:00 | 49813.4103 | 20.016
Devonshire Building | 2017-01-28 03:15 | 49813.4153 | 20.016
Devonshire Building | 2017-01-28 03:30 | 49813.4203 | 20.016
Devonshire Building | 2017-01-28 03:45 | 49813.4303 | 39.996
Devonshire Building | 2017-01-28 04:00 | 49813.4353 | 20.016
Devonshire Building | 2017-01-28 04:15 | 49813.4403 | 20.016
Devonshire Building | 2017-01-28 04:30 | 49813.4453 | 20.016
Devonshire Building | 2017-01-28 04:45 | 49813.4504 | 20.016
Devonshire Building | 2017-01-28 05:00 | 49813.4554 | 20.016
Devonshire Building | 2017-01-28 05:15 | 49813.4604 | 20.016
Devonshire Building | 2017-01-28 05:30 | 49813.4654 | 20.016
Devonshire Building | 2017-01-28 05:45 | 49813.4704 | 20.016
Devonshire Building | 2017-01-28 06:00 | 49813.4754 | 20.016
Devonshire Building | 2017-01-28 06:15 | 49813.4804 | 20.016
Devonshire Building | 2017-01-28 06:30 | 49813.4854 | 20.016
Devonshire Building | 2017-01-28 06:45 | 49813.4904 | 20.016
Devonshire Building | 2017-01-28 07:00 | 49813.4954 | 20.016
Devonshire Building | 2017-01-28 07:15 | 49813.5004 | 20.016
Devonshire Building | 2017-01-28 07:30 | 49813.5054 | 20.016
Devonshire Building | 2017-01-28 07:45 | 49813.5254 | 79.992
Devonshire Building | 2017-01-28 08:00 | 49813.5454 | 79.992
Devonshire Building | 2017-01-28 08:15 | 49813.5704 | 100.008
Devonshire Building | 2017-01-28 08:30 | 49813.5904 | 79.992
Devonshire Building | 2017-01-28 08:45 | 49813.6104 | 79.992
Devonshire Building | 2017-01-28 09:00 | 49813.6304 | 79.992
Devonshire Building | 2017-01-28 09:15 | 49813.6504 | 79.992
Devonshire Building | 2017-01-28 09:30 | 49813.6704 | 79.992
Devonshire Building | 2017-01-28 09:45 | 49813.6904 | 79.992
Devonshire Building | 2017-01-28 10:00 | 49813.7054 | 60.012
Devonshire Building | 2017-01-28 10:15 | 49813.7254 | 79.992
Devonshire Building | 2017-01-28 10:30 | 49813.7454 | 79.992
Devonshire Building | 2017-01-28 10:45 | 49813.7554 | 39.996
Devonshire Building | 2017-01-28 11:00 | 49813.7654 | 39.996
Devonshire Building | 2017-01-28 11:15 | 49813.7754 | 39.996
Devonshire Building | 2017-01-28 11:30 | 49813.7854 | 39.996
Devonshire Building | 2017-01-28 11:45 | 49813.7904 | 20.016
Devonshire Building | 2017-01-28 12:00 | 49813.8004 | 39.996
Devonshire Building | 2017-01-28 12:15 | 49814.3504 | 2199.996
Devonshire Building | 2017-01-28 12:30 | 49814.3554 | 20.016
Devonshire Building | 2017-01-28 12:45 | 49814.3654 | 39.996
Devonshire Building | 2017-01-28 13:00 | 49814.3704 | 20.016
Devonshire Building | 2017-01-28 13:15 | 49814.3754 | 20.016
Devonshire Building | 2017-01-28 13:30 | 49814.3804 | 20.016
Devonshire Building | 2017-01-28 13:45 | 49814.3854 | 20.016
Devonshire Building | 2017-01-28 14:00 | 49814.3954 | 39.996
Devonshire Building | 2017-01-28 14:15 | 49814.4004 | 20.016
Devonshire Building | 2017-01-28 14:30 | 49814.4054 | 20.016
Devonshire Building | 2017-01-28 14:45 | 49814.4054 | 0
Devonshire Building | 2017-01-28 15:00 | 49814.4154 | 39.996
Devonshire Building | 2017-01-28 15:15 | 49814.4254 | 39.996
Devonshire Building | 2017-01-28 15:30 | 49814.4254 | 0
Devonshire Building | 2017-01-28 15:45 | 49814.4304 | 20.016
Devonshire Building | 2017-01-28 16:00 | 49814.4354 | 20.016
Devonshire Building | 2017-01-28 16:15 | 49815.0154 | 2319.984
Devonshire Building | 2017-01-28 16:30 | 49815.0154 | 0
Devonshire Building | 2017-01-28 16:45 | 49815.0254 | 39.996
Devonshire Building | 2017-01-28 17:00 | 49815.0254 | 0
Devonshire Building | 2017-01-28 17:15 | 49815.0304 | 20.016
Devonshire Building | 2017-01-28 17:30 | 49815.0304 | 0
Devonshire Building | 2017-01-28 17:45 | 49815.0354 | 20.016
Devonshire Building | 2017-01-28 18:00 | 49815.0404 | 20.016
Devonshire Building | 2017-01-28 18:15 | 49815.0404 | 0
Devonshire Building | 2017-01-28 18:30 | 49815.0454 | 20.016
Devonshire Building | 2017-01-28 18:45 | 49815.0454 | 0
Devonshire Building | 2017-01-28 19:00 | 49815.0504 | 20.016
Devonshire Building | 2017-01-28 19:15 | 49815.0504 | 0
Devonshire Building | 2017-01-28 19:30 | 49815.0554 | 20.016
Devonshire Building | 2017-01-28 19:45 | 49815.0604 | 20.016
Devonshire Building | 2017-01-28 20:00 | 49815.0604 | 0
Devonshire Building | 2017-01-28 20:15 | 49815.0654 | 20.016
Devonshire Building | 2017-01-28 20:30 | 49815.0654 | 0
Devonshire Building | 2017-01-28 20:45 | 49815.0704 | 20.016
Devonshire Building | 2017-01-28 21:00 | 49815.0754 | 20.016
Devonshire Building | 2017-01-28 21:15 | 49815.0754 | 0
Devonshire Building | 2017-01-28 21:30 | 49815.0804 | 20.016
Devonshire Building | 2017-01-28 21:45 | 49815.0804 | 0
Devonshire Building | 2017-01-28 22:00 | 49815.1055 | 100.008
Devonshire Building | 2017-01-28 22:15 | 49815.1105 | 20.016
Devonshire Building | 2017-01-28 22:30 | 49815.1105 | 0
Devonshire Building | 2017-01-28 22:45 | 49815.1155 | 20.016
Devonshire Building | 2017-01-28 23:00 | 49815.1205 | 20.016
Devonshire Building | 2017-01-28 23:15 | 49815.1205 | 0
Devonshire Building | 2017-01-28 23:30 | 49815.1255 | 20.016
Devonshire Building | 2017-01-28 23:45 | 49815.1255 | 0 | 0
Devonshire Building | 2017-01-29 | 49815.1289 | 20.016
Devonshire Building | 2017-01-29 00:15 | 49815.1339 | 20.016
Devonshire Building | 2017-01-29 00:30 | 49815.1339 | 0
Devonshire Building | 2017-01-29 00:45 | 49815.1389 | 20.016
Devonshire Building | 2017-01-29 01:00 | 49815.1389 | 0
Devonshire Building | 2017-01-29 01:15 | 49815.1439 | 20.016
Devonshire Building | 2017-01-29 01:30 | 49815.1489 | 20.016
Devonshire Building | 2017-01-29 01:45 | 49815.1489 | 0
Devonshire Building | 2017-01-29 02:00 | 49815.1539 | 20.016
Devonshire Building | 2017-01-29 02:15 | 49815.1539 | 0
Devonshire Building | 2017-01-29 02:30 | 49815.1589 | 20.016
Devonshire Building | 2017-01-29 02:45 | 49815.1589 | 0
Devonshire Building | 2017-01-29 03:00 | 49815.1639 | 20.016
Devonshire Building | 2017-01-29 03:15 | 49815.1689 | 20.016
Devonshire Building | 2017-01-29 03:30 | 49815.1689 | 0
Devonshire Building | 2017-01-29 03:45 | 49815.1739 | 20.016
Devonshire Building | 2017-01-29 04:00 | 49815.1739 | 0
Devonshire Building | 2017-01-29 04:15 | 49815.179 | 20.016
Devonshire Building | 2017-01-29 04:30 | 49815.184 | 20.016
Devonshire Building | 2017-01-29 04:45 | 49815.184 | 0
Devonshire Building | 2017-01-29 05:00 | 49815.189 | 20.016
Devonshire Building | 2017-01-29 05:15 | 49815.189 | 0
Devonshire Building | 2017-01-29 05:30 | 49815.194 | 20.016
Devonshire Building | 2017-01-29 05:45 | 49815.194 | 0
Devonshire Building | 2017-01-29 06:00 | 49815.199 | 20.016
Devonshire Building | 2017-01-29 06:15 | 49815.199 | 0
Devonshire Building | 2017-01-29 06:30 | 49815.204 | 20.016
Devonshire Building | 2017-01-29 06:45 | 49815.209 | 20.016
Devonshire Building | 2017-01-29 07:00 | 49815.209 | 0
Devonshire Building | 2017-01-29 07:15 | 49815.214 | 20.016
Devonshire Building | 2017-01-29 07:30 | 49815.214 | 0
Devonshire Building | 2017-01-29 07:45 | 49815.229 | 60.012
Devonshire Building | 2017-01-29 08:00 | 49815.249 | 79.992
Devonshire Building | 2017-01-29 08:15 | 49815.269 | 79.992
Devonshire Building | 2017-01-29 08:30 | 49815.289 | 79.992
Devonshire Building | 2017-01-29 08:45 | 49815.304 | 60.012
Devonshire Building | 2017-01-29 09:00 | 49815.324 | 79.992
Devonshire Building | 2017-01-29 09:15 | 49815.344 | 79.992
Devonshire Building | 2017-01-29 09:30 | 49815.364 | 79.992
Devonshire Building | 2017-01-29 09:45 | 49815.379 | 60.012
Devonshire Building | 2017-01-29 10:00 | 49815.399 | 79.992
Devonshire Building | 2017-01-29 10:15 | 49815.419 | 79.992
Devonshire Building | 2017-01-29 10:30 | 49815.424 | 20.016
Devonshire Building | 2017-01-29 10:45 | 49815.424 | 0
Devonshire Building | 2017-01-29 11:00 | 49815.429 | 20.016
Devonshire Building | 2017-01-29 11:15 | 49815.434 | 20.016
Devonshire Building | 2017-01-29 11:30 | 49815.434 | 0
Devonshire Building | 2017-01-29 11:45 | 49815.439 | 20.016
Devonshire Building | 2017-01-29 12:00 | 49815.439 | 0
Devonshire Building | 2017-01-29 12:15 | 49815.444 | 20.016
Devonshire Building | 2017-01-29 12:30 | 49815.449 | 20.016
Devonshire Building | 2017-01-29 12:45 | 49815.449 | 0
Devonshire Building | 2017-01-29 13:00 | 49815.454 | 20.016
Devonshire Building | 2017-01-29 13:15 | 49815.454 | 0
Devonshire Building | 2017-01-29 13:30 | 49815.459 | 20.016
Devonshire Building | 2017-01-29 13:45 | 49815.464 | 20.016
Devonshire Building | 2017-01-29 14:00 | 49815.824 | 1440
Devonshire Building | 2017-01-29 14:15 | 49816.004 | 720
Devonshire Building | 2017-01-29 14:30 | 49816.004 | 0
Devonshire Building | 2017-01-29 14:45 | 49816.009 | 20.016
Devonshire Building | 2017-01-29 15:00 | 49816.014 | 20.016
Devonshire Building | 2017-01-29 15:15 | 49816.019 | 20.016
Devonshire Building | 2017-01-29 15:30 | 49816.019 | 0
Devonshire Building | 2017-01-29 15:45 | 49816.024 | 20.016
Devonshire Building | 2017-01-29 16:00 | 49816.024 | 0
Devonshire Building | 2017-01-29 16:15 | 49816.029 | 20.016
Devonshire Building | 2017-01-29 16:30 | 49816.034 | 20.016
Devonshire Building | 2017-01-29 16:45 | 49816.034 | 0
Devonshire Building | 2017-01-29 17:00 | 49816.039 | 20.016
Devonshire Building | 2017-01-29 17:15 | 49816.044 | 20.016
Devonshire Building | 2017-01-29 17:30 | 49816.044 | 0
Devonshire Building | 2017-01-29 17:45 | 49816.049 | 20.016
Devonshire Building | 2017-01-29 18:00 | 49816.049 | 0
Devonshire Building | 2017-01-29 18:15 | 49816.054 | 20.016
Devonshire Building | 2017-01-29 18:30 | 49816.054 | 0
Devonshire Building | 2017-01-29 18:45 | 49816.0591 | 20.016
Devonshire Building | 2017-01-29 19:00 | 49816.0591 | 0
Devonshire Building | 2017-01-29 19:15 | 49816.0641 | 20.016
Devonshire Building | 2017-01-29 19:30 | 49816.0641 | 0
Devonshire Building | 2017-01-29 19:45 | 49816.0691 | 20.016
Devonshire Building | 2017-01-29 20:00 | 49816.0741 | 20.016
Devonshire Building | 2017-01-29 20:15 | 49816.0741 | 0
Devonshire Building | 2017-01-29 20:30 | 49816.0791 | 20.016
Devonshire Building | 2017-01-29 20:45 | 49816.0791 | 0
Devonshire Building | 2017-01-29 21:00 | 49816.0841 | 20.016
Devonshire Building | 2017-01-29 21:15 | 49816.0841 | 0
Devonshire Building | 2017-01-29 21:30 | 49816.0891 | 20.016
Devonshire Building | 2017-01-29 21:45 | 49816.0941 | 20.016
Devonshire Building | 2017-01-29 22:00 | 49816.0991 | 20.016
Devonshire Building | 2017-01-29 22:15 | 49816.0991 | 0
Devonshire Building | 2017-01-29 22:30 | 49816.1041 | 20.016
Devonshire Building | 2017-01-29 22:45 | 49816.1091 | 20.016
Devonshire Building | 2017-01-29 23:00 | 49816.1091 | 0
Devonshire Building | 2017-01-29 23:15 | 49816.1141 | 20.016
Devonshire Building | 2017-01-29 23:30 | 49816.1141 | 0
Devonshire Building | 2017-01-29 23:45 | 49816.1191 | 20.016 | 0
Devonshire Building | 2017-01-30 | 49816.1211 | 0
Devonshire Building | 2017-01-30 00:15 | 49816.1261 | 20.016
Devonshire Building | 2017-01-30 00:30 | 49816.1311 | 20.016
Devonshire Building | 2017-01-30 00:45 | 49816.1311 | 0
Devonshire Building | 2017-01-30 01:00 | 49816.1361 | 20.016
Devonshire Building | 2017-01-30 01:15 | 49816.1361 | 0
Devonshire Building | 2017-01-30 01:30 | 49816.1411 | 20.016
Devonshire Building | 2017-01-30 01:45 | 49816.1461 | 20.016
Devonshire Building | 2017-01-30 02:00 | 49816.1461 | 0
Devonshire Building | 2017-01-30 02:15 | 49816.1511 | 20.016
Devonshire Building | 2017-01-30 02:30 | 49816.1511 | 0
Devonshire Building | 2017-01-30 02:45 | 49816.1561 | 20.016
Devonshire Building | 2017-01-30 03:00 | 49816.1561 | 0
Devonshire Building | 2017-01-30 03:15 | 49816.1611 | 20.016
Devonshire Building | 2017-01-30 03:30 | 49816.1661 | 20.016
Devonshire Building | 2017-01-30 03:45 | 49816.1661 | 0
Devonshire Building | 2017-01-30 04:00 | 49816.1711 | 20.016
Devonshire Building | 2017-01-30 04:15 | 49816.1761 | 20.016
Devonshire Building | 2017-01-30 04:30 | 49816.1761 | 0
Devonshire Building | 2017-01-30 04:45 | 49816.1811 | 20.016
Devonshire Building | 2017-01-30 05:00 | 49816.1861 | 20.016
Devonshire Building | 2017-01-30 05:15 | 49816.1911 | 20.016
Devonshire Building | 2017-01-30 05:30 | 49816.1911 | 0
Devonshire Building | 2017-01-30 05:45 | 49816.1962 | 20.016
Devonshire Building | 2017-01-30 06:00 | 49816.2012 | 20.016
Devonshire Building | 2017-01-30 06:15 | 49816.2062 | 20.016
Devonshire Building | 2017-01-30 06:30 | 49816.2112 | 20.016
Devonshire Building | 2017-01-30 06:45 | 49816.2162 | 20.016
Devonshire Building | 2017-01-30 07:00 | 49816.2262 | 39.996
Devonshire Building | 2017-01-30 07:15 | 49816.2262 | 0
Devonshire Building | 2017-01-30 07:30 | 49816.2312 | 20.016
Devonshire Building | 2017-01-30 07:45 | 49816.2512 | 79.992
Devonshire Building | 2017-01-30 08:00 | 49816.2762 | 100.008
Devonshire Building | 2017-01-30 08:15 | 49816.3012 | 100.008
Devonshire Building | 2017-01-30 08:30 | 49816.4362 | 540
Devonshire Building | 2017-01-30 08:45 | 49816.4812 | 180
Devonshire Building | 2017-01-30 09:00 | 49816.8862 | 1620
Devonshire Building | 2017-01-30 09:15 | 49817.1112 | 900
Devonshire Building | 2017-01-30 09:30 | 49817.1412 | 119.988
Devonshire Building | 2017-01-30 09:45 | 49817.1662 | 100.008
Devonshire Building | 2017-01-30 10:00 | 49817.1962 | 119.988
Devonshire Building | 2017-01-30 10:15 | 49817.2212 | 100.008
Devonshire Building | 2017-01-30 10:30 | 49817.3012 | 320.004
Devonshire Building | 2017-01-30 10:45 | 49817.9062 | 2419.992
Devonshire Building | 2017-01-30 11:00 | 49818.0562 | 600.012
Devonshire Building | 2017-01-30 11:15 | 49818.1712 | 460.008
Devonshire Building | 2017-01-30 11:30 | 49818.2662 | 380.016
Devonshire Building | 2017-01-30 11:45 | 49818.9312 | 2660.004
Devonshire Building | 2017-01-30 12:00 | 49818.9962 | 259.992
Devonshire Building | 2017-01-30 12:15 | 49819.0612 | 259.992
Devonshire Building | 2017-01-30 12:30 | 49819.1262 | 259.992
Devonshire Building | 2017-01-30 12:45 | 49819.1962 | 280.008
Devonshire Building | 2017-01-30 13:00 | 49819.2562 | 240.012
Devonshire Building | 2017-01-30 13:15 | 49819.3212 | 259.992
Devonshire Building | 2017-01-30 13:30 | 49819.9612 | 2559.996
Devonshire Building | 2017-01-30 13:45 | 49820.0362 | 299.988
Devonshire Building | 2017-01-30 14:00 | 49820.1112 | 299.988
Devonshire Building | 2017-01-30 14:15 | 49820.1812 | 280.008
Devonshire Building | 2017-01-30 14:30 | 49820.2412 | 240.012
Devonshire Building | 2017-01-30 14:45 | 49820.3012 | 240.012
Devonshire Building | 2017-01-30 15:00 | 49820.8912 | 2360.016
Devonshire Building | 2017-01-30 15:15 | 49820.9262 | 140.004
Devonshire Building | 2017-01-30 15:30 | 49820.9762 | 200.016
Devonshire Building | 2017-01-30 15:45 | 49821.0512 | 299.988
Devonshire Building | 2017-01-30 16:00 | 49821.1262 | 299.988
Devonshire Building | 2017-01-30 16:15 | 49821.1962 | 280.008
Devonshire Building | 2017-01-30 16:30 | 49821.8162 | 2480.004
Devonshire Building | 2017-01-30 16:45 | 49821.8762 | 240.012
Devonshire Building | 2017-01-30 17:00 | 49821.9412 | 259.992
Devonshire Building | 2017-01-30 17:15 | 49822.0012 | 240.012
Devonshire Building | 2017-01-30 17:30 | 49822.0562 | 219.996
Devonshire Building | 2017-01-30 17:45 | 49822.1062 | 200.016
Devonshire Building | 2017-01-30 18:00 | 49822.1462 | 159.984
Devonshire Building | 2017-01-30 18:15 | 49822.1962 | 200.016
Devonshire Building | 2017-01-30 18:30 | 49822.2262 | 119.988
Devonshire Building | 2017-01-30 18:45 | 49822.2512 | 100.008
Devonshire Building | 2017-01-30 19:00 | 49822.2712 | 79.992
Devonshire Building | 2017-01-30 19:15 | 49822.2962 | 100.008
Devonshire Building | 2017-01-30 19:30 | 49822.3162 | 79.992
Devonshire Building | 2017-01-30 19:45 | 49822.3412 | 100.008
Devonshire Building | 2017-01-30 20:00 | 49822.3612 | 79.992
Devonshire Building | 2017-01-30 20:15 | 49822.3812 | 79.992
Devonshire Building | 2017-01-30 20:30 | 49822.4062 | 100.008
Devonshire Building | 2017-01-30 20:45 | 49822.4262 | 79.992
Devonshire Building | 2017-01-30 21:00 | 49822.4462 | 79.992
Devonshire Building | 2017-01-30 21:15 | 49822.4662 | 79.992
Devonshire Building | 2017-01-30 21:30 | 49823.0212 | 2220.012
Devonshire Building | 2017-01-30 21:45 | 49823.0362 | 60.012
Devonshire Building | 2017-01-30 22:00 | 49823.0512 | 60.012
Devonshire Building | 2017-01-30 22:15 | 49823.0662 | 60.012
Devonshire Building | 2017-01-30 22:30 | 49823.0812 | 60.012
Devonshire Building | 2017-01-30 22:45 | 49823.1012 | 79.992
Devonshire Building | 2017-01-30 23:00 | 49823.1162 | 60.012
Devonshire Building | 2017-01-30 23:15 | 49823.1362 | 79.992
Devonshire Building | 2017-01-30 23:30 | 49823.1562 | 79.992
Devonshire Building | 2017-01-30 23:45 | 49823.1712 | 60.012 | 0
Devonshire Building | 2017-01-31 | 49823.1836 | 60.012
Devonshire Building | 2017-01-31 00:15 | 49823.1986 | 60.012
Devonshire Building | 2017-01-31 00:30 | 49823.2086 | 39.996
Devonshire Building | 2017-01-31 00:45 | 49823.2186 | 39.996
Devonshire Building | 2017-01-31 01:00 | 49823.2286 | 39.996
Devonshire Building | 2017-01-31 01:15 | 49823.2436 | 60.012
Devonshire Building | 2017-01-31 01:30 | 49823.2486 | 20.016
Devonshire Building | 2017-01-31 01:45 | 49823.2586 | 39.996
Devonshire Building | 2017-01-31 02:00 | 49823.2686 | 39.996
Devonshire Building | 2017-01-31 02:15 | 49823.2786 | 39.996
Devonshire Building | 2017-01-31 02:30 | 49823.2836 | 20.016
Devonshire Building | 2017-01-31 02:45 | 49823.2936 | 39.996
Devonshire Building | 2017-01-31 03:00 | 49823.2986 | 20.016
Devonshire Building | 2017-01-31 03:15 | 49823.3036 | 20.016
Devonshire Building | 2017-01-31 03:30 | 49823.3136 | 39.996
Devonshire Building | 2017-01-31 03:45 | 49823.3186 | 20.016
Devonshire Building | 2017-01-31 04:00 | 49823.3236 | 20.016
Devonshire Building | 2017-01-31 04:15 | 49823.3286 | 20.016
Devonshire Building | 2017-01-31 04:30 | 49823.3336 | 20.016
Devonshire Building | 2017-01-31 04:45 | 49823.3386 | 20.016
Devonshire Building | 2017-01-31 05:00 | 49823.3436 | 20.016
Devonshire Building | 2017-01-31 05:15 | 49823.3486 | 20.016
Devonshire Building | 2017-01-31 05:30 | 49823.3586 | 39.996
Devonshire Building | 2017-01-31 05:45 | 49823.3636 | 20.016
Devonshire Building | 2017-01-31 06:00 | 49823.3686 | 20.016
Devonshire Building | 2017-01-31 06:15 | 49823.3736 | 20.016
Devonshire Building | 2017-01-31 06:30 | 49823.3786 | 20.016
Devonshire Building | 2017-01-31 06:45 | 49823.3837 | 20.016
Devonshire Building | 2017-01-31 07:00 | 49823.3887 | 20.016
Devonshire Building | 2017-01-31 07:15 | 49823.3987 | 39.996
Devonshire Building | 2017-01-31 07:30 | 49823.4137 | 60.012
Devonshire Building | 2017-01-31 07:45 | 49823.4337 | 79.992
Devonshire Building | 2017-01-31 08:00 | 49823.4587 | 100.008
Devonshire Building | 2017-01-31 08:15 | 49823.4787 | 79.992
Devonshire Building | 2017-01-31 08:30 | 49823.5087 | 119.988
Devonshire Building | 2017-01-31 08:45 | 49823.5386 | 119.988
Devonshire Building | 2017-01-31 09:00 | 49823.5686 | 119.988
Devonshire Building | 2017-01-31 09:15 | 49823.5986 | 119.988
Devonshire Building | 2017-01-31 09:30 | 49823.6236 | 100.008
Devonshire Building | 2017-01-31 09:45 | 49823.7236 | 399.996
Devonshire Building | 2017-01-31 10:00 | 49824.2486 | 2099.988
Devonshire Building | 2017-01-31 10:15 | 49824.2786 | 119.988
Devonshire Building | 2017-01-31 10:30 | 49824.3286 | 200.016
Devonshire Building | 2017-01-31 10:45 | 49824.7336 | 1620
Devonshire Building | 2017-01-31 11:00 | 49825.1086 | 1500.012
Devonshire Building | 2017-01-31 11:15 | 49825.2436 | 540
Devonshire Building | 2017-01-31 11:30 | 49825.3636 | 479.988
Devonshire Building | 2017-01-31 11:45 | 49825.4636 | 399.996
Devonshire Building | 2017-01-31 12:00 | 49825.5486 | 339.984
Devonshire Building | 2017-01-31 12:15 | 49825.6286 | 320.004
Devonshire Building | 2017-01-31 12:30 | 49826.2536 | 2499.984
Devonshire Building | 2017-01-31 12:45 | 49826.3486 | 380.016
Devonshire Building | 2017-01-31 13:00 | 49826.4486 | 399.996
Devonshire Building | 2017-01-31 13:15 | 49826.5336 | 339.984
Devonshire Building | 2017-01-31 13:30 | 49826.6186 | 339.984
Devonshire Building | 2017-01-31 13:45 | 49827.2436 | 2499.984
Devonshire Building | 2017-01-31 14:00 | 49827.3186 | 299.988
Devonshire Building | 2017-01-31 14:15 | 49827.4036 | 339.984
Devonshire Building | 2017-01-31 14:30 | 49827.4786 | 299.988
Devonshire Building | 2017-01-31 14:45 | 49827.5486 | 280.008
Devonshire Building | 2017-01-31 15:00 | 49827.6036 | 219.996
Devonshire Building | 2017-01-31 15:15 | 49827.6486 | 180
Devonshire Building | 2017-01-31 15:30 | 49828.2536 | 2419.992
Devonshire Building | 2017-01-31 15:45 | 49828.2736 | 79.992
Devonshire Building | 2017-01-31 16:00 | 49828.2936 | 79.992
Devonshire Building | 2017-01-31 16:15 | 49828.3186 | 100.008
Devonshire Building | 2017-01-31 16:30 | 49828.3436 | 100.008
Devonshire Building | 2017-01-31 16:45 | 49828.3686 | 100.008
Devonshire Building | 2017-01-31 17:00 | 49828.3986 | 119.988
Devonshire Building | 2017-01-31 17:15 | 49828.9886 | 2360.016
Devonshire Building | 2017-01-31 17:30 | 49829.0386 | 200.016
Devonshire Building | 2017-01-31 17:45 | 49829.0936 | 219.996
Devonshire Building | 2017-01-31 18:00 | 49829.1436 | 200.016
Devonshire Building | 2017-01-31 18:15 | 49829.1986 | 219.996
Devonshire Building | 2017-01-31 18:30 | 49829.2436 | 180
Devonshire Building | 2017-01-31 18:45 | 49829.2936 | 200.016
Devonshire Building | 2017-01-31 19:00 | 49829.3386 | 180
Devonshire Building | 2017-01-31 19:15 | 49829.3786 | 159.984
Devonshire Building | 2017-01-31 19:30 | 49829.4186 | 159.984
Devonshire Building | 2017-01-31 19:45 | 49829.4486 | 119.988
Devonshire Building | 2017-01-31 20:00 | 49829.4786 | 119.988
Devonshire Building | 2017-01-31 20:15 | 49829.5086 | 119.988
Devonshire Building | 2017-01-31 20:30 | 49829.5336 | 100.008
Devonshire Building | 2017-01-31 20:45 | 49829.5536 | 79.992
Devonshire Building | 2017-01-31 21:00 | 49829.5736 | 79.992
Devonshire Building | 2017-01-31 21:15 | 49829.5886 | 60.012
Devonshire Building | 2017-01-31 21:30 | 49829.6036 | 60.012
Devonshire Building | 2017-01-31 21:45 | 49829.6186 | 60.012
Devonshire Building | 2017-01-31 22:00 | 49829.6436 | 100.008
Devonshire Building | 2017-01-31 22:15 | 49829.6486 | 20.016
Devonshire Building | 2017-01-31 22:30 | 49829.6536 | 20.016
Devonshire Building | 2017-01-31 22:45 | 49829.6586 | 20.016
Devonshire Building | 2017-01-31 23:00 | 49829.6636 | 20.016
Devonshire Building | 2017-01-31 23:15 | 49829.6686 | 20.016
Devonshire Building | 2017-01-31 23:30 | 49829.6736 | 20.016
Devonshire Building | 2017-01-31 23:45 | 49829.6786 | 20.016 | 20.016
Devonshire Building | 2017-02-01 | 49829.6797 | 0
Devonshire Building | 2017-02-01 00:15 | 49829.6847 | 20.016
Devonshire Building | 2017-02-01 00:30 | 49829.6897 | 20.016
Devonshire Building | 2017-02-01 00:45 | 49829.6947 | 20.016
Devonshire Building | 2017-02-01 01:00 | 49829.6997 | 20.016
Devonshire Building | 2017-02-01 01:15 | 49829.6997 | 0
Devonshire Building | 2017-02-01 01:30 | 49829.7047 | 20.016
Devonshire Building | 2017-02-01 01:45 | 49829.7247 | 79.992
Devonshire Building | 2017-02-01 02:00 | 49829.7447 | 79.992
Devonshire Building | 2017-02-01 02:15 | 49829.7647 | 79.992
Devonshire Building | 2017-02-01 02:30 | 49829.7847 | 79.992
Devonshire Building | 2017-02-01 02:45 | 49829.8047 | 79.992
Devonshire Building | 2017-02-01 03:00 | 49829.8247 | 79.992
Devonshire Building | 2017-02-01 03:15 | 49829.8447 | 79.992
Devonshire Building | 2017-02-01 03:30 | 49829.8647 | 79.992
Devonshire Building | 2017-02-01 03:45 | 49829.8847 | 79.992
Devonshire Building | 2017-02-01 04:00 | 49829.8997 | 60.012
Devonshire Building | 2017-02-01 04:15 | 49829.8997 | 0
Devonshire Building | 2017-02-01 04:30 | 49829.9047 | 20.016
Devonshire Building | 2017-02-01 04:45 | 49829.9097 | 20.016
Devonshire Building | 2017-02-01 05:00 | 49829.9147 | 20.016
Devonshire Building | 2017-02-01 05:15 | 49829.9147 | 0
Devonshire Building | 2017-02-01 05:30 | 49829.9197 | 20.016
Devonshire Building | 2017-02-01 05:45 | 49829.9247 | 20.016
Devonshire Building | 2017-02-01 06:00 | 49829.9247 | 0
Devonshire Building | 2017-02-01 06:15 | 49829.9297 | 20.016
Devonshire Building | 2017-02-01 06:30 | 49829.9347 | 20.016
Devonshire Building | 2017-02-01 06:45 | 49829.9397 | 20.016
Devonshire Building | 2017-02-01 07:00 | 49829.9397 | 0
Devonshire Building | 2017-02-01 07:15 | 49829.9447 | 20.016
Devonshire Building | 2017-02-01 07:30 | 49829.9497 | 20.016
Devonshire Building | 2017-02-01 07:45 | 49829.9597 | 39.996
Devonshire Building | 2017-02-01 08:00 | 49829.9697 | 39.996
Devonshire Building | 2017-02-01 08:15 | 49829.9797 | 39.996
Devonshire Building | 2017-02-01 08:30 | 49829.9797 | 0
Devonshire Building | 2017-02-01 08:45 | 49830.2697 | 1159.992
Devonshire Building | 2017-02-01 09:00 | 49830.2797 | 39.996
Devonshire Building | 2017-02-01 09:15 | 49830.2897 | 39.996
Devonshire Building | 2017-02-01 09:30 | 49830.2997 | 39.996
Devonshire Building | 2017-02-01 09:45 | 49830.3047 | 20.016
Devonshire Building | 2017-02-01 10:00 | 49830.3147 | 39.996
Devonshire Building | 2017-02-01 10:15 | 49830.3297 | 60.012
Devonshire Building | 2017-02-01 10:30 | 49830.6497 | 1280.016
Devonshire Building | 2017-02-01 10:45 | 49830.6697 | 79.992
Devonshire Building | 2017-02-01 11:00 | 49830.6947 | 100.008
Devonshire Building | 2017-02-01 11:15 | 49830.7647 | 280.008
Devonshire Building | 2017-02-01 11:30 | 49830.8597 | 380.016
Devonshire Building | 2017-02-01 11:45 | 49830.9397 | 320.004
Devonshire Building | 2017-02-01 12:00 | 49831.2647 | 1299.996
Devonshire Building | 2017-02-01 12:15 | 49831.3547 | 360
Devonshire Building | 2017-02-01 12:30 | 49831.4097 | 219.996
Devonshire Building | 2017-02-01 12:45 | 49831.4597 | 200.016
Devonshire Building | 2017-02-01 13:00 | 49831.5197 | 240.012
Devonshire Building | 2017-02-01 13:15 | 49831.5698 | 200.016
Devonshire Building | 2017-02-01 13:30 | 49831.6248 | 219.996
Devonshire Building | 2017-02-01 13:45 | 49831.9898 | 1460.016
Devonshire Building | 2017-02-01 14:00 | 49832.0398 | 200.016
Devonshire Building | 2017-02-01 14:15 | 49832.0848 | 180
Devonshire Building | 2017-02-01 14:30 | 49832.1398 | 219.996
Devonshire Building | 2017-02-01 14:45 | 49832.1898 | 200.016
Devonshire Building | 2017-02-01 15:00 | 49832.2398 | 200.016
Devonshire Building | 2017-02-01 15:15 | 49832.5848 | 1379.988
Devonshire Building | 2017-02-01 15:30 | 49832.6348 | 200.016
Devonshire Building | 2017-02-01 15:45 | 49832.6998 | 259.992
Devonshire Building | 2017-02-01 16:00 | 49832.7698 | 280.008
Devonshire Building | 2017-02-01 16:15 | 49832.8248 | 219.996
Devonshire Building | 2017-02-01 16:30 | 49832.8848 | 240.012
Devonshire Building | 2017-02-01 16:45 | 49832.9448 | 240.012
Devonshire Building | 2017-02-01 17:00 | 49833.2948 | 1400.004
Devonshire Building | 2017-02-01 17:15 | 49833.3348 | 159.984
Devonshire Building | 2017-02-01 17:30 | 49833.3748 | 159.984
Devonshire Building | 2017-02-01 17:45 | 49833.4248 | 200.016
Devonshire Building | 2017-02-01 18:00 | 49833.4698 | 180
Devonshire Building | 2017-02-01 18:15 | 49833.5048 | 140.004
Devonshire Building | 2017-02-01 18:30 | 49833.5398 | 140.004
Devonshire Building | 2017-02-01 18:45 | 49833.5748 | 140.004
Devonshire Building | 2017-02-01 19:00 | 49833.5998 | 100.008
Devonshire Building | 2017-02-01 19:15 | 49833.6298 | 119.988
Devonshire Building | 2017-02-01 19:30 | 49833.6598 | 119.988
Devonshire Building | 2017-02-01 19:45 | 49833.6948 | 140.004
Devonshire Building | 2017-02-01 20:00 | 49833.7298 | 140.004
Devonshire Building | 2017-02-01 20:15 | 49833.7648 | 140.004
Devonshire Building | 2017-02-01 20:30 | 49833.7948 | 119.988
Devonshire Building | 2017-02-01 20:45 | 49833.8248 | 119.988
Devonshire Building | 2017-02-01 21:00 | 49833.8548 | 119.988
Devonshire Building | 2017-02-01 21:15 | 49833.8798 | 100.008
Devonshire Building | 2017-02-01 21:30 | 49833.9098 | 119.988
Devonshire Building | 2017-02-01 21:45 | 49833.9348 | 100.008
Devonshire Building | 2017-02-01 22:00 | 49833.9798 | 180
Devonshire Building | 2017-02-01 22:15 | 49833.9998 | 79.992
Devonshire Building | 2017-02-01 22:30 | 49834.0148 | 60.012
Devonshire Building | 2017-02-01 22:45 | 49834.0198 | 20.016
Devonshire Building | 2017-02-01 23:00 | 49834.0248 | 20.016
Devonshire Building | 2017-02-01 23:15 | 49834.0298 | 20.016
Devonshire Building | 2017-02-01 23:30 | 49834.0348 | 20.016
Devonshire Building | 2017-02-01 23:45 | 49834.0348 | 0 | 0
Devonshire Building | 2017-02-02 | 49834.0391 | 20.016
Devonshire Building | 2017-02-02 00:15 | 49834.0441 | 20.016
Devonshire Building | 2017-02-02 00:30 | 49834.0441 | 0
Devonshire Building | 2017-02-02 00:45 | 49834.0491 | 20.016
Devonshire Building | 2017-02-02 01:00 | 49834.0541 | 20.016
Devonshire Building | 2017-02-02 01:15 | 49834.0541 | 0
Devonshire Building | 2017-02-02 01:30 | 49834.0591 | 20.016
Devonshire Building | 2017-02-02 01:45 | 49834.0641 | 20.016
Devonshire Building | 2017-02-02 02:00 | 49834.0641 | 0
Devonshire Building | 2017-02-02 02:15 | 49834.0691 | 20.016
Devonshire Building | 2017-02-02 02:30 | 49834.0741 | 20.016
Devonshire Building | 2017-02-02 02:45 | 49834.0741 | 0
Devonshire Building | 2017-02-02 03:00 | 49834.0791 | 20.016
Devonshire Building | 2017-02-02 03:15 | 49834.0841 | 20.016
Devonshire Building | 2017-02-02 03:30 | 49834.0841 | 0
Devonshire Building | 2017-02-02 03:45 | 49834.0891 | 20.016
Devonshire Building | 2017-02-02 04:00 | 49834.0941 | 20.016
Devonshire Building | 2017-02-02 04:15 | 49834.0941 | 0
Devonshire Building | 2017-02-02 04:30 | 49834.0991 | 20.016
Devonshire Building | 2017-02-02 04:45 | 49834.0991 | 0
Devonshire Building | 2017-02-02 05:00 | 49834.1041 | 20.016
Devonshire Building | 2017-02-02 05:15 | 49834.1091 | 20.016
Devonshire Building | 2017-02-02 05:30 | 49834.1091 | 0
Devonshire Building | 2017-02-02 05:45 | 49834.1141 | 20.016
Devonshire Building | 2017-02-02 06:00 | 49834.3891 | 1100.016
Devonshire Building | 2017-02-02 06:15 | 49834.3891 | 0
Devonshire Building | 2017-02-02 06:30 | 49834.3941 | 20.016
Devonshire Building | 2017-02-02 06:45 | 49834.3941 | 0
Devonshire Building | 2017-02-02 07:00 | 49834.3991 | 20.016
Devonshire Building | 2017-02-02 07:15 | 49834.4041 | 20.016
Devonshire Building | 2017-02-02 07:30 | 49834.4041 | 0
Devonshire Building | 2017-02-02 07:45 | 49834.4091 | 20.016
Devonshire Building | 2017-02-02 08:00 | 49834.4141 | 20.016
Devonshire Building | 2017-02-02 08:15 | 49834.4241 | 39.996
Devonshire Building | 2017-02-02 08:30 | 49834.4291 | 20.016
Devonshire Building | 2017-02-02 08:45 | 49834.4541 | 100.008
Devonshire Building | 2017-02-02 09:00 | 49834.4741 | 79.992
Devonshire Building | 2017-02-02 09:15 | 49834.4792 | 20.016
Devonshire Building | 2017-02-02 09:30 | 49834.4892 | 39.996
Devonshire Building | 2017-02-02 09:45 | 49834.4991 | 39.996
Devonshire Building | 2017-02-02 10:00 | 49834.6341 | 540
Devonshire Building | 2017-02-02 10:15 | 49834.8541 | 879.984
Devonshire Building | 2017-02-02 10:30 | 49834.8841 | 119.988
Devonshire Building | 2017-02-02 10:45 | 49834.9391 | 219.996
Devonshire Building | 2017-02-02 11:00 | 49835.0391 | 399.996
Devonshire Building | 2017-02-02 11:15 | 49835.1391 | 399.996
Devonshire Building | 2017-02-02 11:30 | 49835.2241 | 339.984
Devonshire Building | 2017-02-02 11:45 | 49835.5841 | 1440
Devonshire Building | 2017-02-02 12:00 | 49835.6441 | 240.012
Devonshire Building | 2017-02-02 12:15 | 49835.7041 | 240.012
Devonshire Building | 2017-02-02 12:30 | 49835.7541 | 200.016
Devonshire Building | 2017-02-02 12:45 | 49835.8041 | 200.016
Devonshire Building | 2017-02-02 13:00 | 49836.1542 | 1400.004
Devonshire Building | 2017-02-02 13:15 | 49836.1892 | 140.004
Devonshire Building | 2017-02-02 13:30 | 49836.2242 | 140.004
Devonshire Building | 2017-02-02 13:45 | 49836.2641 | 159.984
Devonshire Building | 2017-02-02 14:00 | 49836.3291 | 259.992
Devonshire Building | 2017-02-02 14:15 | 49836.3741 | 180
Devonshire Building | 2017-02-02 14:30 | 49836.7591 | 1540.008
Devonshire Building | 2017-02-02 14:45 | 49836.8891 | 519.984
Devonshire Building | 2017-02-02 15:00 | 49836.9341 | 180
Devonshire Building | 2017-02-02 15:15 | 49836.9791 | 180
Devonshire Building | 2017-02-02 15:30 | 49837.0341 | 219.996
Devonshire Building | 2017-02-02 15:45 | 49837.0841 | 200.016
Devonshire Building | 2017-02-02 16:00 | 49837.1342 | 200.016
Devonshire Building | 2017-02-02 16:15 | 49837.1792 | 180
Devonshire Building | 2017-02-02 16:30 | 49837.7591 | 2319.984
Devonshire Building | 2017-02-02 16:45 | 49837.7941 | 140.004
Devonshire Building | 2017-02-02 17:00 | 49837.8241 | 119.988
Devonshire Building | 2017-02-02 17:15 | 49837.8591 | 140.004
Devonshire Building | 2017-02-02 17:30 | 49837.8891 | 119.988
Devonshire Building | 2017-02-02 17:45 | 49837.9341 | 180
Devonshire Building | 2017-02-02 18:00 | 49837.9741 | 159.984
Devonshire Building | 2017-02-02 18:15 | 49838.0141 | 159.984
Devonshire Building | 2017-02-02 18:30 | 49838.0491 | 140.004
Devonshire Building | 2017-02-02 18:45 | 49838.0741 | 100.008
Devonshire Building | 2017-02-02 19:00 | 49838.1391 | 259.992
Devonshire Building | 2017-02-02 19:15 | 49838.2441 | 420.012
Devonshire Building | 2017-02-02 19:30 | 49838.3441 | 399.996
Devonshire Building | 2017-02-02 19:45 | 49838.4241 | 320.004
Devonshire Building | 2017-02-02 20:00 | 49838.4891 | 259.992
Devonshire Building | 2017-02-02 20:15 | 49838.5391 | 200.016
Devonshire Building | 2017-02-02 20:30 | 49838.5791 | 159.984
Devonshire Building | 2017-02-02 20:45 | 49838.6091 | 119.988
Devonshire Building | 2017-02-02 21:00 | 49838.6341 | 100.008
Devonshire Building | 2017-02-02 21:15 | 49838.6541 | 79.992
Devonshire Building | 2017-02-02 21:30 | 49838.6741 | 79.992
Devonshire Building | 2017-02-02 21:45 | 49839.2141 | 2160
Devonshire Building | 2017-02-02 22:00 | 49839.2241 | 39.996
Devonshire Building | 2017-02-02 22:15 | 49839.2291 | 20.016
Devonshire Building | 2017-02-02 22:30 | 49839.2341 | 20.016
Devonshire Building | 2017-02-02 22:45 | 49839.2391 | 20.016
Devonshire Building | 2017-02-02 23:00 | 49839.2441 | 20.016
Devonshire Building | 2017-02-02 23:15 | 49839.2441 | 0
Devonshire Building | 2017-02-02 23:30 | 49839.2492 | 20.016
Devonshire Building | 2017-02-02 23:45 | 49839.2542 | 20.016 | 0
Devonshire Building | 2017-02-03 | 49839.2578 | 20.016
Devonshire Building | 2017-02-03 00:15 | 49839.2628 | 20.016
Devonshire Building | 2017-02-03 00:30 | 49839.2678 | 20.016
Devonshire Building | 2017-02-03 00:45 | 49839.2728 | 20.016
Devonshire Building | 2017-02-03 01:00 | 49839.2778 | 20.016
Devonshire Building | 2017-02-03 01:15 | 49839.2778 | 0
Devonshire Building | 2017-02-03 01:30 | 49839.2828 | 20.016
Devonshire Building | 2017-02-03 01:45 | 49839.2878 | 20.016
Devonshire Building | 2017-02-03 02:00 | 49839.2928 | 20.016
Devonshire Building | 2017-02-03 02:15 | 49839.2978 | 20.016
Devonshire Building | 2017-02-03 02:30 | 49839.3028 | 20.016
Devonshire Building | 2017-02-03 02:45 | 49839.3078 | 20.016
Devonshire Building | 2017-02-03 03:00 | 49839.3078 | 0
Devonshire Building | 2017-02-03 03:15 | 49839.3129 | 20.016
Devonshire Building | 2017-02-03 03:30 | 49839.3179 | 20.016
Devonshire Building | 2017-02-03 03:45 | 49839.3229 | 20.016
Devonshire Building | 2017-02-03 04:00 | 49839.3279 | 20.016
Devonshire Building | 2017-02-03 04:15 | 49839.3329 | 20.016
Devonshire Building | 2017-02-03 04:30 | 49839.3329 | 0
Devonshire Building | 2017-02-03 04:45 | 49839.3379 | 20.016
Devonshire Building | 2017-02-03 05:00 | 49839.3429 | 20.016
Devonshire Building | 2017-02-03 05:15 | 49839.3479 | 20.016
Devonshire Building | 2017-02-03 05:30 | 49839.3479 | 0
Devonshire Building | 2017-02-03 05:45 | 49839.3529 | 20.016
Devonshire Building | 2017-02-03 06:00 | 49839.3579 | 20.016
Devonshire Building | 2017-02-03 06:15 | 49839.3579 | 0
Devonshire Building | 2017-02-03 06:30 | 49839.3629 | 20.016
Devonshire Building | 2017-02-03 06:45 | 49839.3679 | 20.016
Devonshire Building | 2017-02-03 07:00 | 49839.3679 | 0
Devonshire Building | 2017-02-03 07:15 | 49839.3729 | 20.016
Devonshire Building | 2017-02-03 07:30 | 49839.3779 | 20.016
Devonshire Building | 2017-02-03 07:45 | 49839.3829 | 20.016
Devonshire Building | 2017-02-03 08:00 | 49839.3929 | 39.996
Devonshire Building | 2017-02-03 08:15 | 49839.4029 | 39.996
Devonshire Building | 2017-02-03 08:30 | 49839.4129 | 39.996
Devonshire Building | 2017-02-03 08:45 | 49839.4279 | 60.012
Devonshire Building | 2017-02-03 09:00 | 49839.4429 | 60.012
Devonshire Building | 2017-02-03 09:15 | 49839.6179 | 699.984
Devonshire Building | 2017-02-03 09:30 | 49839.9729 | 1419.984
Devonshire Building | 2017-02-03 09:45 | 49839.9779 | 20.016
Devonshire Building | 2017-02-03 10:00 | 49839.9929 | 60.012
Devonshire Building | 2017-02-03 10:15 | 49840.0279 | 140.004
Devonshire Building | 2017-02-03 10:30 | 49840.0779 | 200.016
Devonshire Building | 2017-02-03 10:45 | 49840.1579 | 320.004
Devonshire Building | 2017-02-03 11:00 | 49840.8029 | 2580.012
Devonshire Building | 2017-02-03 11:15 | 49840.9029 | 399.996
Devonshire Building | 2017-02-03 11:30 | 49841.0079 | 420.012
Devonshire Building | 2017-02-03 11:45 | 49841.0879 | 320.004
Devonshire Building | 2017-02-03 12:00 | 49841.1729 | 339.984
Devonshire Building | 2017-02-03 12:15 | 49841.2379 | 259.992
Devonshire Building | 2017-02-03 12:30 | 49841.3979 | 640.008
Devonshire Building | 2017-02-03 12:45 | 49841.9379 | 2160
Devonshire Building | 2017-02-03 13:00 | 49841.9729 | 140.004
Devonshire Building | 2017-02-03 13:15 | 49842.0179 | 180
Devonshire Building | 2017-02-03 13:30 | 49842.0629 | 180
Devonshire Building | 2017-02-03 13:45 | 49842.1229 | 240.012
Devonshire Building | 2017-02-03 14:00 | 49842.1879 | 259.992
Devonshire Building | 2017-02-03 14:15 | 49842.8229 | 2540.016
Devonshire Building | 2017-02-03 14:30 | 49842.9479 | 500.004
Devonshire Building | 2017-02-03 14:45 | 49843.0479 | 399.996
Devonshire Building | 2017-02-03 15:00 | 49843.1429 | 380.016
Devonshire Building | 2017-02-03 15:15 | 49843.2279 | 339.984
Devonshire Building | 2017-02-03 15:30 | 49843.3079 | 320.004
Devonshire Building | 2017-02-03 15:45 | 49843.3879 | 320.004
Devonshire Building | 2017-02-03 16:00 | 49843.4629 | 299.988
Devonshire Building | 2017-02-03 16:15 | 49844.1029 | 2559.996
Devonshire Building | 2017-02-03 16:30 | 49844.1729 | 280.008
Devonshire Building | 2017-02-03 16:45 | 49844.2479 | 299.988
Devonshire Building | 2017-02-03 17:00 | 49844.3179 | 280.008
Devonshire Building | 2017-02-03 17:15 | 49844.3829 | 259.992
Devonshire Building | 2017-02-03 17:30 | 49844.4429 | 240.012
Devonshire Building | 2017-02-03 17:45 | 49844.5029 | 240.012
Devonshire Building | 2017-02-03 18:00 | 49844.5679 | 259.992
Devonshire Building | 2017-02-03 18:15 | 49844.6179 | 200.016
Devonshire Building | 2017-02-03 18:30 | 49844.6579 | 159.984
Devonshire Building | 2017-02-03 18:45 | 49844.7479 | 360
Devonshire Building | 2017-02-03 19:00 | 49845.2529 | 2019.996
Devonshire Building | 2017-02-03 19:15 | 49845.2679 | 60.012
Devonshire Building | 2017-02-03 19:30 | 49845.2829 | 60.012
Devonshire Building | 2017-02-03 19:45 | 49845.3029 | 79.992
Devonshire Building | 2017-02-03 20:00 | 49845.3229 | 79.992
Devonshire Building | 2017-02-03 20:15 | 49845.3379 | 60.012
Devonshire Building | 2017-02-03 20:30 | 49845.3529 | 60.012
Devonshire Building | 2017-02-03 20:45 | 49845.3729 | 79.992
Devonshire Building | 2017-02-03 21:00 | 49845.3879 | 60.012
Devonshire Building | 2017-02-03 21:15 | 49845.4029 | 60.012
Devonshire Building | 2017-02-03 21:30 | 49845.4179 | 60.012
Devonshire Building | 2017-02-03 21:45 | 49845.4329 | 60.012
Devonshire Building | 2017-02-03 22:00 | 49845.4479 | 60.012
Devonshire Building | 2017-02-03 22:15 | 49845.463 | 60.012
Devonshire Building | 2017-02-03 22:30 | 49845.4729 | 39.996
Devonshire Building | 2017-02-03 22:45 | 49845.488 | 60.012
Devonshire Building | 2017-02-03 23:00 | 49845.503 | 60.012
Devonshire Building | 2017-02-03 23:15 | 49845.513 | 39.996
Devonshire Building | 2017-02-03 23:30 | 49845.523 | 39.996
Devonshire Building | 2017-02-03 23:45 | 49845.538 | 60.012 | 0
Devonshire Building | 2017-02-04 | 49845.5508 | 39.996
Devonshire Building | 2017-02-04 00:15 | 49845.5608 | 39.996
Devonshire Building | 2017-02-04 00:30 | 49845.5708 | 39.996
Devonshire Building | 2017-02-04 00:45 | 49845.5808 | 39.996
Devonshire Building | 2017-02-04 01:00 | 49845.5908 | 39.996
Devonshire Building | 2017-02-04 01:15 | 49845.6008 | 39.996
Devonshire Building | 2017-02-04 01:30 | 49845.6108 | 39.996
Devonshire Building | 2017-02-04 01:45 | 49845.6208 | 39.996
Devonshire Building | 2017-02-04 02:00 | 49845.6308 | 39.996
Devonshire Building | 2017-02-04 02:15 | 49845.6408 | 39.996
Devonshire Building | 2017-02-04 02:30 | 49845.6508 | 39.996
Devonshire Building | 2017-02-04 02:45 | 49845.6558 | 20.016
Devonshire Building | 2017-02-04 03:00 | 49845.6658 | 39.996
Devonshire Building | 2017-02-04 03:15 | 49845.6758 | 39.996
Devonshire Building | 2017-02-04 03:30 | 49845.6858 | 39.996
Devonshire Building | 2017-02-04 03:45 | 49845.6908 | 20.016
Devonshire Building | 2017-02-04 04:00 | 49845.7008 | 39.996
Devonshire Building | 2017-02-04 04:15 | 49845.7108 | 39.996
Devonshire Building | 2017-02-04 04:30 | 49845.7158 | 20.016
Devonshire Building | 2017-02-04 04:45 | 49845.7258 | 39.996
Devonshire Building | 2017-02-04 05:00 | 49845.7308 | 20.016
Devonshire Building | 2017-02-04 05:15 | 49845.7408 | 39.996
Devonshire Building | 2017-02-04 05:30 | 49845.7508 | 39.996
Devonshire Building | 2017-02-04 05:45 | 49845.7558 | 20.016
Devonshire Building | 2017-02-04 06:00 | 49845.7658 | 39.996
Devonshire Building | 2017-02-04 06:15 | 49845.7708 | 20.016
Devonshire Building | 2017-02-04 06:30 | 49845.7808 | 39.996
Devonshire Building | 2017-02-04 06:45 | 49845.7858 | 20.016
Devonshire Building | 2017-02-04 07:00 | 49845.7958 | 39.996
Devonshire Building | 2017-02-04 07:15 | 49845.8008 | 20.016
Devonshire Building | 2017-02-04 07:30 | 49845.8108 | 39.996
Devonshire Building | 2017-02-04 07:45 | 49845.8158 | 20.016
Devonshire Building | 2017-02-04 08:00 | 49845.8358 | 79.992
Devonshire Building | 2017-02-04 08:15 | 49845.8608 | 100.008
Devonshire Building | 2017-02-04 08:30 | 49845.8808 | 79.992
Devonshire Building | 2017-02-04 08:45 | 49845.9058 | 100.008
Devonshire Building | 2017-02-04 09:00 | 49845.9258 | 79.992
Devonshire Building | 2017-02-04 09:15 | 49845.9508 | 100.008
Devonshire Building | 2017-02-04 09:30 | 49845.9708 | 79.992
Devonshire Building | 2017-02-04 09:45 | 49845.9958 | 100.008
Devonshire Building | 2017-02-04 10:00 | 49846.0158 | 79.992
Devonshire Building | 2017-02-04 10:15 | 49846.0358 | 79.992
Devonshire Building | 2017-02-04 10:30 | 49846.0408 | 20.016
Devonshire Building | 2017-02-04 10:45 | 49846.0508 | 39.996
Devonshire Building | 2017-02-04 11:00 | 49846.0558 | 20.016
Devonshire Building | 2017-02-04 11:15 | 49846.0608 | 20.016
Devonshire Building | 2017-02-04 11:30 | 49846.0658 | 20.016
Devonshire Building | 2017-02-04 11:45 | 49846.0758 | 39.996
Devonshire Building | 2017-02-04 12:00 | 49846.0808 | 20.016
Devonshire Building | 2017-02-04 12:15 | 49846.0908 | 39.996
Devonshire Building | 2017-02-04 12:30 | 49846.0958 | 20.016
Devonshire Building | 2017-02-04 12:45 | 49846.1058 | 39.996
Devonshire Building | 2017-02-04 13:00 | 49846.1158 | 39.996
Devonshire Building | 2017-02-04 13:15 | 49846.1208 | 20.016
Devonshire Building | 2017-02-04 13:30 | 49846.1308 | 39.996
Devonshire Building | 2017-02-04 13:45 | 49846.1358 | 20.016
Devonshire Building | 2017-02-04 14:00 | 49846.1458 | 39.996
Devonshire Building | 2017-02-04 14:15 | 49846.1558 | 39.996
Devonshire Building | 2017-02-04 14:30 | 49846.1658 | 39.996
Devonshire Building | 2017-02-04 14:45 | 49846.1708 | 20.016
Devonshire Building | 2017-02-04 15:00 | 49846.1808 | 39.996
Devonshire Building | 2017-02-04 15:15 | 49846.1958 | 60.012
Devonshire Building | 2017-02-04 15:30 | 49846.2008 | 20.016
Devonshire Building | 2017-02-04 15:45 | 49846.2108 | 39.996
Devonshire Building | 2017-02-04 16:00 | 49846.2158 | 20.016
Devonshire Building | 2017-02-04 16:15 | 49846.2208 | 20.016
Devonshire Building | 2017-02-04 16:30 | 49846.2308 | 39.996
Devonshire Building | 2017-02-04 16:45 | 49846.2358 | 20.016
Devonshire Building | 2017-02-04 17:00 | 49846.5108 | 1100.016
Devonshire Building | 2017-02-04 17:15 | 49846.5208 | 39.996
Devonshire Building | 2017-02-04 17:30 | 49846.5308 | 39.996
Devonshire Building | 2017-02-04 17:45 | 49846.5408 | 39.996
Devonshire Building | 2017-02-04 18:00 | 49846.5458 | 20.016
Devonshire Building | 2017-02-04 18:15 | 49846.5608 | 60.012
Devonshire Building | 2017-02-04 18:30 | 49846.5708 | 39.996
Devonshire Building | 2017-02-04 18:45 | 49846.5808 | 39.996
Devonshire Building | 2017-02-04 19:00 | 49846.5958 | 60.012
Devonshire Building | 2017-02-04 19:15 | 49846.6108 | 60.012
Devonshire Building | 2017-02-04 19:30 | 49846.6258 | 60.012
Devonshire Building | 2017-02-04 19:45 | 49846.6458 | 79.992
Devonshire Building | 2017-02-04 20:00 | 49846.6608 | 60.012
Devonshire Building | 2017-02-04 20:15 | 49846.6808 | 79.992
Devonshire Building | 2017-02-04 20:30 | 49846.6958 | 60.012
Devonshire Building | 2017-02-04 20:45 | 49846.7158 | 79.992
Devonshire Building | 2017-02-04 21:00 | 49846.7309 | 60.012
Devonshire Building | 2017-02-04 21:15 | 49846.7459 | 60.012
Devonshire Building | 2017-02-04 21:30 | 49846.7609 | 60.012
Devonshire Building | 2017-02-04 21:45 | 49846.7759 | 60.012
Devonshire Building | 2017-02-04 22:00 | 49846.7959 | 79.992
Devonshire Building | 2017-02-04 22:15 | 49846.8109 | 60.012
Devonshire Building | 2017-02-04 22:30 | 49846.8259 | 60.012
Devonshire Building | 2017-02-04 22:45 | 49846.8359 | 39.996
Devonshire Building | 2017-02-04 23:00 | 49846.8509 | 60.012
Devonshire Building | 2017-02-04 23:15 | 49846.8609 | 39.996
Devonshire Building | 2017-02-04 23:30 | 49846.8709 | 39.996
Devonshire Building | 2017-02-04 23:45 | 49846.8859 | 60.012 | 20.016
Devonshire Building | 2017-02-05 | 49846.8945 | 39.996
Devonshire Building | 2017-02-05 00:15 | 49846.9045 | 39.996
Devonshire Building | 2017-02-05 00:30 | 49846.9195 | 60.012
Devonshire Building | 2017-02-05 00:45 | 49846.9295 | 39.996
Devonshire Building | 2017-02-05 01:00 | 49846.9395 | 39.996
Devonshire Building | 2017-02-05 01:15 | 49846.9495 | 39.996
Devonshire Building | 2017-02-05 01:30 | 49846.9595 | 39.996
Devonshire Building | 2017-02-05 01:45 | 49846.9695 | 39.996
Devonshire Building | 2017-02-05 02:00 | 49846.9795 | 39.996
Devonshire Building | 2017-02-05 02:15 | 49846.9945 | 60.012
Devonshire Building | 2017-02-05 02:30 | 49847.0045 | 39.996
Devonshire Building | 2017-02-05 02:45 | 49847.0145 | 39.996
Devonshire Building | 2017-02-05 03:00 | 49847.0245 | 39.996
Devonshire Building | 2017-02-05 03:15 | 49847.0345 | 39.996
Devonshire Building | 2017-02-05 03:30 | 49847.0395 | 20.016
Devonshire Building | 2017-02-05 03:45 | 49847.0495 | 39.996
Devonshire Building | 2017-02-05 04:00 | 49847.0595 | 39.996
Devonshire Building | 2017-02-05 04:15 | 49847.0695 | 39.996
Devonshire Building | 2017-02-05 04:30 | 49847.0795 | 39.996
Devonshire Building | 2017-02-05 04:45 | 49847.0895 | 39.996
Devonshire Building | 2017-02-05 05:00 | 49847.0995 | 39.996
Devonshire Building | 2017-02-05 05:15 | 49847.1045 | 20.016
Devonshire Building | 2017-02-05 05:30 | 49847.1145 | 39.996
Devonshire Building | 2017-02-05 05:45 | 49847.1245 | 39.996
Devonshire Building | 2017-02-05 06:00 | 49847.1295 | 20.016
Devonshire Building | 2017-02-05 06:15 | 49847.1395 | 39.996
Devonshire Building | 2017-02-05 06:30 | 49847.1445 | 20.016
Devonshire Building | 2017-02-05 06:45 | 49847.1545 | 39.996
Devonshire Building | 2017-02-05 07:00 | 49847.1645 | 39.996
Devonshire Building | 2017-02-05 07:15 | 49847.1695 | 20.016
Devonshire Building | 2017-02-05 07:30 | 49847.1795 | 39.996
Devonshire Building | 2017-02-05 07:45 | 49847.2045 | 100.008
Devonshire Building | 2017-02-05 08:00 | 49847.2245 | 79.992
Devonshire Building | 2017-02-05 08:15 | 49847.2495 | 100.008
Devonshire Building | 2017-02-05 08:30 | 49847.2695 | 79.992
Devonshire Building | 2017-02-05 08:45 | 49847.2945 | 100.008
Devonshire Building | 2017-02-05 09:00 | 49847.3145 | 79.992
Devonshire Building | 2017-02-05 09:15 | 49847.3345 | 79.992
Devonshire Building | 2017-02-05 09:30 | 49847.3595 | 100.008
Devonshire Building | 2017-02-05 09:45 | 49847.3795 | 79.992
Devonshire Building | 2017-02-05 10:00 | 49847.3995 | 79.992
Devonshire Building | 2017-02-05 10:15 | 49847.4245 | 100.008
Devonshire Building | 2017-02-05 10:30 | 49847.4445 | 79.992
Devonshire Building | 2017-02-05 10:45 | 49847.4595 | 60.012
Devonshire Building | 2017-02-05 11:00 | 49847.4645 | 20.016
Devonshire Building | 2017-02-05 11:15 | 49847.4695 | 20.016
Devonshire Building | 2017-02-05 11:30 | 49847.4745 | 20.016
Devonshire Building | 2017-02-05 11:45 | 49847.4795 | 20.016
Devonshire Building | 2017-02-05 12:00 | 49847.4846 | 20.016
Devonshire Building | 2017-02-05 12:15 | 49847.4896 | 20.016
Devonshire Building | 2017-02-05 12:30 | 49847.4946 | 20.016
Devonshire Building | 2017-02-05 12:45 | 49847.5046 | 39.996
Devonshire Building | 2017-02-05 13:00 | 49847.5096 | 20.016
Devonshire Building | 2017-02-05 13:15 | 49847.5146 | 20.016
Devonshire Building | 2017-02-05 13:30 | 49847.5196 | 20.016
Devonshire Building | 2017-02-05 13:45 | 49847.5246 | 20.016
Devonshire Building | 2017-02-05 14:00 | 49847.5296 | 20.016
Devonshire Building | 2017-02-05 14:15 | 49847.5346 | 20.016
Devonshire Building | 2017-02-05 14:30 | 49847.5396 | 20.016
Devonshire Building | 2017-02-05 14:45 | 49847.5446 | 20.016
Devonshire Building | 2017-02-05 15:00 | 49847.5496 | 20.016
Devonshire Building | 2017-02-05 15:15 | 49847.5546 | 20.016
Devonshire Building | 2017-02-05 15:30 | 49847.5596 | 20.016
Devonshire Building | 2017-02-05 15:45 | 49847.5696 | 39.996
Devonshire Building | 2017-02-05 16:00 | 49847.5746 | 20.016
Devonshire Building | 2017-02-05 16:15 | 49847.5796 | 20.016
Devonshire Building | 2017-02-05 16:30 | 49847.5846 | 20.016
Devonshire Building | 2017-02-05 16:45 | 49847.5896 | 20.016
Devonshire Building | 2017-02-05 17:00 | 49847.8696 | 1119.996
Devonshire Building | 2017-02-05 17:15 | 49847.8746 | 20.016
Devonshire Building | 2017-02-05 17:30 | 49847.8846 | 39.996
Devonshire Building | 2017-02-05 17:45 | 49847.8846 | 0
Devonshire Building | 2017-02-05 18:00 | 49847.8896 | 20.016
Devonshire Building | 2017-02-05 18:15 | 49847.8946 | 20.016
Devonshire Building | 2017-02-05 18:30 | 49847.8996 | 20.016
Devonshire Building | 2017-02-05 18:45 | 49847.8996 | 0
Devonshire Building | 2017-02-05 19:00 | 49847.9046 | 20.016
Devonshire Building | 2017-02-05 19:15 | 49847.9096 | 20.016
Devonshire Building | 2017-02-05 19:30 | 49847.9146 | 20.016
Devonshire Building | 2017-02-05 19:45 | 49847.9146 | 0
Devonshire Building | 2017-02-05 20:00 | 49847.9196 | 20.016
Devonshire Building | 2017-02-05 20:15 | 49847.9247 | 20.016
Devonshire Building | 2017-02-05 20:30 | 49847.9247 | 0
Devonshire Building | 2017-02-05 20:45 | 49847.9297 | 20.016
Devonshire Building | 2017-02-05 21:00 | 49847.9347 | 20.016
Devonshire Building | 2017-02-05 21:15 | 49847.9397 | 20.016
Devonshire Building | 2017-02-05 21:30 | 49847.9397 | 0
Devonshire Building | 2017-02-05 21:45 | 49847.9447 | 20.016
Devonshire Building | 2017-02-05 22:00 | 49847.9497 | 20.016
Devonshire Building | 2017-02-05 22:15 | 49847.9547 | 20.016
Devonshire Building | 2017-02-05 22:30 | 49847.9597 | 20.016
Devonshire Building | 2017-02-05 22:45 | 49847.9647 | 20.016
Devonshire Building | 2017-02-05 23:00 | 49847.9697 | 20.016
Devonshire Building | 2017-02-05 23:15 | 49847.9697 | 0
Devonshire Building | 2017-02-05 23:30 | 49847.9747 | 20.016
Devonshire Building | 2017-02-05 23:45 | 49847.9797 | 20.016 | 0
Devonshire Building | 2017-02-06 | 49847.9844 | 20.016
Devonshire Building | 2017-02-06 00:15 | 49847.9894 | 20.016
Devonshire Building | 2017-02-06 00:30 | 49847.9944 | 20.016
Devonshire Building | 2017-02-06 00:45 | 49847.9994 | 20.016
Devonshire Building | 2017-02-06 01:00 | 49847.9994 | 0
Devonshire Building | 2017-02-06 01:15 | 49848.0044 | 20.016
Devonshire Building | 2017-02-06 01:30 | 49848.0094 | 20.016
Devonshire Building | 2017-02-06 01:45 | 49848.0144 | 20.016
Devonshire Building | 2017-02-06 02:00 | 49848.0194 | 20.016
Devonshire Building | 2017-02-06 02:15 | 49848.0194 | 0
Devonshire Building | 2017-02-06 02:30 | 49848.0244 | 20.016
Devonshire Building | 2017-02-06 02:45 | 49848.0294 | 20.016
Devonshire Building | 2017-02-06 03:00 | 49848.0344 | 20.016
Devonshire Building | 2017-02-06 03:15 | 49848.0344 | 0
Devonshire Building | 2017-02-06 03:30 | 49848.0394 | 20.016
Devonshire Building | 2017-02-06 03:45 | 49848.0444 | 20.016
Devonshire Building | 2017-02-06 04:00 | 49848.0494 | 20.016
Devonshire Building | 2017-02-06 04:15 | 49848.0494 | 0
Devonshire Building | 2017-02-06 04:30 | 49848.0544 | 20.016
Devonshire Building | 2017-02-06 04:45 | 49848.0594 | 20.016
Devonshire Building | 2017-02-06 05:00 | 49848.0644 | 20.016
Devonshire Building | 2017-02-06 05:15 | 49848.0644 | 0
Devonshire Building | 2017-02-06 05:30 | 49848.0694 | 20.016
Devonshire Building | 2017-02-06 05:45 | 49848.0745 | 20.016
Devonshire Building | 2017-02-06 06:00 | 49848.0745 | 0
Devonshire Building | 2017-02-06 06:15 | 49848.0795 | 20.016
Devonshire Building | 2017-02-06 06:30 | 49848.0845 | 20.016
Devonshire Building | 2017-02-06 06:45 | 49848.0895 | 20.016
Devonshire Building | 2017-02-06 07:00 | 49848.0945 | 20.016
Devonshire Building | 2017-02-06 07:15 | 49848.0995 | 20.016
Devonshire Building | 2017-02-06 07:30 | 49848.1045 | 20.016
Devonshire Building | 2017-02-06 07:45 | 49848.1295 | 100.008
Devonshire Building | 2017-02-06 08:00 | 49848.1545 | 100.008
Devonshire Building | 2017-02-06 08:15 | 49848.1795 | 100.008
Devonshire Building | 2017-02-06 08:30 | 49848.2095 | 119.988
Devonshire Building | 2017-02-06 08:45 | 49848.5345 | 1299.996
Devonshire Building | 2017-02-06 09:00 | 49848.7245 | 759.996
Devonshire Building | 2017-02-06 09:15 | 49848.9195 | 780.012
Devonshire Building | 2017-02-06 09:30 | 49849.0495 | 519.984
Devonshire Building | 2017-02-06 09:45 | 49849.1445 | 380.016
Devonshire Building | 2017-02-06 10:00 | 49849.2195 | 299.988
Devonshire Building | 2017-02-06 10:15 | 49849.2795 | 240.012
Devonshire Building | 2017-02-06 10:30 | 49849.6495 | 1479.996
Devonshire Building | 2017-02-06 10:45 | 49849.6845 | 140.004
Devonshire Building | 2017-02-06 11:00 | 49849.7795 | 380.016
Devonshire Building | 2017-02-06 11:15 | 49849.8945 | 460.008
Devonshire Building | 2017-02-06 11:30 | 49850.0245 | 519.984
Devonshire Building | 2017-02-06 11:45 | 49850.4595 | 1739.988
Devonshire Building | 2017-02-06 12:00 | 49850.5895 | 519.984
Devonshire Building | 2017-02-06 12:15 | 49850.7095 | 479.988
Devonshire Building | 2017-02-06 12:30 | 49850.8045 | 380.016
Devonshire Building | 2017-02-06 12:45 | 49850.8895 | 339.984
Devonshire Building | 2017-02-06 13:00 | 49851.1345 | 979.992
Devonshire Building | 2017-02-06 13:15 | 49851.3745 | 960.012
Devonshire Building | 2017-02-06 13:30 | 49851.4645 | 360
Devonshire Building | 2017-02-06 13:45 | 49851.5545 | 360
Devonshire Building | 2017-02-06 14:00 | 49851.6395 | 339.984
Devonshire Building | 2017-02-06 14:15 | 49851.7145 | 299.988
Devonshire Building | 2017-02-06 14:30 | 49851.7945 | 320.004
Devonshire Building | 2017-02-06 14:45 | 49852.1645 | 1479.996
Devonshire Building | 2017-02-06 15:00 | 49852.2495 | 339.984
Devonshire Building | 2017-02-06 15:15 | 49852.3295 | 320.004
Devonshire Building | 2017-02-06 15:30 | 49852.4095 | 320.004
Devonshire Building | 2017-02-06 15:45 | 49852.4895 | 320.004
Devonshire Building | 2017-02-06 16:00 | 49852.5695 | 320.004
Devonshire Building | 2017-02-06 16:15 | 49852.9445 | 1500.012
Devonshire Building | 2017-02-06 16:30 | 49853.0145 | 280.008
Devonshire Building | 2017-02-06 16:45 | 49853.0895 | 299.988
Devonshire Building | 2017-02-06 17:00 | 49853.1545 | 259.992
Devonshire Building | 2017-02-06 17:15 | 49853.2195 | 259.992
Devonshire Building | 2017-02-06 17:30 | 49853.2795 | 240.012
Devonshire Building | 2017-02-06 17:45 | 49853.3395 | 240.012
Devonshire Building | 2017-02-06 18:00 | 49853.3945 | 219.996
Devonshire Building | 2017-02-06 18:15 | 49853.7245 | 1320.012
Devonshire Building | 2017-02-06 18:30 | 49853.7645 | 159.984
Devonshire Building | 2017-02-06 18:45 | 49853.7845 | 79.992
Devonshire Building | 2017-02-06 19:00 | 49853.8095 | 100.008
Devonshire Building | 2017-02-06 19:15 | 49853.8345 | 100.008
Devonshire Building | 2017-02-06 19:30 | 49853.8595 | 100.008
Devonshire Building | 2017-02-06 19:45 | 49853.8845 | 100.008
Devonshire Building | 2017-02-06 20:00 | 49853.9045 | 79.992
Devonshire Building | 2017-02-06 20:15 | 49853.9295 | 100.008
Devonshire Building | 2017-02-06 20:30 | 49853.9495 | 79.992
Devonshire Building | 2017-02-06 20:45 | 49853.9695 | 79.992
Devonshire Building | 2017-02-06 21:00 | 49853.9845 | 60.012
Devonshire Building | 2017-02-06 21:15 | 49853.9945 | 39.996
Devonshire Building | 2017-02-06 21:30 | 49854.0095 | 60.012
Devonshire Building | 2017-02-06 21:45 | 49854.0195 | 39.996
Devonshire Building | 2017-02-06 22:00 | 49854.0345 | 60.012
Devonshire Building | 2017-02-06 22:15 | 49854.0445 | 39.996
Devonshire Building | 2017-02-06 22:30 | 49854.0545 | 39.996
Devonshire Building | 2017-02-06 22:45 | 49854.0645 | 39.996
Devonshire Building | 2017-02-06 23:00 | 49854.0695 | 20.016
Devonshire Building | 2017-02-06 23:15 | 49854.0795 | 39.996
Devonshire Building | 2017-02-06 23:30 | 49854.0895 | 39.996
Devonshire Building | 2017-02-06 23:45 | 49854.0945 | 20.016 | 0
Devonshire Building | 2017-02-07 | 49854.1055 | 39.996
Devonshire Building | 2017-02-07 00:15 | 49854.1155 | 39.996
Devonshire Building | 2017-02-07 00:30 | 49854.1205 | 20.016
Devonshire Building | 2017-02-07 00:45 | 49854.1305 | 39.996
Devonshire Building | 2017-02-07 01:00 | 49854.1355 | 20.016
Devonshire Building | 2017-02-07 01:15 | 49854.1455 | 39.996
Devonshire Building | 2017-02-07 01:30 | 49854.1505 | 20.016
Devonshire Building | 2017-02-07 01:45 | 49854.1555 | 20.016
Devonshire Building | 2017-02-07 02:00 | 49854.1655 | 39.996
Devonshire Building | 2017-02-07 02:15 | 49854.1705 | 20.016
Devonshire Building | 2017-02-07 02:30 | 49854.1755 | 20.016
Devonshire Building | 2017-02-07 02:45 | 49854.1805 | 20.016
Devonshire Building | 2017-02-07 03:00 | 49854.1855 | 20.016
Devonshire Building | 2017-02-07 03:15 | 49854.1955 | 39.996
Devonshire Building | 2017-02-07 03:30 | 49854.2005 | 20.016
Devonshire Building | 2017-02-07 03:45 | 49854.2055 | 20.016
Devonshire Building | 2017-02-07 04:00 | 49854.2105 | 20.016
Devonshire Building | 2017-02-07 04:15 | 49854.2155 | 20.016
Devonshire Building | 2017-02-07 04:30 | 49854.2205 | 20.016
Devonshire Building | 2017-02-07 04:45 | 49854.2255 | 20.016
Devonshire Building | 2017-02-07 05:00 | 49854.2305 | 20.016
Devonshire Building | 2017-02-07 05:15 | 49854.2355 | 20.016
Devonshire Building | 2017-02-07 05:30 | 49854.2405 | 20.016
Devonshire Building | 2017-02-07 05:45 | 49854.2455 | 20.016
Devonshire Building | 2017-02-07 06:00 | 49854.2505 | 20.016
Devonshire Building | 2017-02-07 06:15 | 49854.2555 | 20.016
Devonshire Building | 2017-02-07 06:30 | 49854.2605 | 20.016
Devonshire Building | 2017-02-07 06:45 | 49854.2656 | 20.016
Devonshire Building | 2017-02-07 07:00 | 49854.2706 | 20.016
Devonshire Building | 2017-02-07 07:15 | 49854.2756 | 20.016
Devonshire Building | 2017-02-07 07:30 | 49854.2856 | 39.996
Devonshire Building | 2017-02-07 07:45 | 49854.3106 | 100.008
Devonshire Building | 2017-02-07 08:00 | 49854.3306 | 79.992
Devonshire Building | 2017-02-07 08:15 | 49854.3656 | 140.004
Devonshire Building | 2017-02-07 08:30 | 49854.3906 | 100.008
Devonshire Building | 2017-02-07 08:45 | 49854.4156 | 100.008
Devonshire Building | 2017-02-07 09:00 | 49854.7556 | 1360.008
Devonshire Building | 2017-02-07 09:15 | 49854.7956 | 159.984
Devonshire Building | 2017-02-07 09:30 | 49854.8406 | 180
Devonshire Building | 2017-02-07 09:45 | 49854.9106 | 280.008
Devonshire Building | 2017-02-07 10:00 | 49855.0706 | 640.008
Devonshire Building | 2017-02-07 10:15 | 49855.2106 | 560.016
Devonshire Building | 2017-02-07 10:30 | 49855.5456 | 1339.992
Devonshire Building | 2017-02-07 10:45 | 49855.7106 | 659.988
Devonshire Building | 2017-02-07 11:00 | 49855.8156 | 420.012
Devonshire Building | 2017-02-07 11:15 | 49855.9256 | 439.992
Devonshire Building | 2017-02-07 11:30 | 49856.0006 | 299.988
Devonshire Building | 2017-02-07 11:45 | 49856.0806 | 320.004
Devonshire Building | 2017-02-07 12:00 | 49856.4406 | 1440
Devonshire Building | 2017-02-07 12:15 | 49856.5006 | 240.012
Devonshire Building | 2017-02-07 12:30 | 49856.5706 | 280.008
Devonshire Building | 2017-02-07 12:45 | 49856.6406 | 280.008
Devonshire Building | 2017-02-07 13:00 | 49856.8706 | 920.016
Devonshire Building | 2017-02-07 13:15 | 49857.0606 | 759.996
Devonshire Building | 2017-02-07 13:30 | 49857.1156 | 219.996
Devonshire Building | 2017-02-07 13:45 | 49857.1656 | 200.016
Devonshire Building | 2017-02-07 14:00 | 49857.2156 | 200.016
Devonshire Building | 2017-02-07 14:15 | 49857.2606 | 180
Devonshire Building | 2017-02-07 14:30 | 49857.3006 | 159.984
Devonshire Building | 2017-02-07 14:45 | 49857.6756 | 1500.012
Devonshire Building | 2017-02-07 15:00 | 49857.7256 | 200.016
Devonshire Building | 2017-02-07 15:15 | 49857.7856 | 240.012
Devonshire Building | 2017-02-07 15:30 | 49857.8556 | 280.008
Devonshire Building | 2017-02-07 15:45 | 49857.9156 | 240.012
Devonshire Building | 2017-02-07 16:00 | 49857.9756 | 240.012
Devonshire Building | 2017-02-07 16:15 | 49858.0306 | 219.996
Devonshire Building | 2017-02-07 16:30 | 49858.3706 | 1360.008
Devonshire Building | 2017-02-07 16:45 | 49858.4156 | 180
Devonshire Building | 2017-02-07 17:00 | 49858.4656 | 200.016
Devonshire Building | 2017-02-07 17:15 | 49858.5206 | 219.996
Devonshire Building | 2017-02-07 17:30 | 49858.5706 | 200.016
Devonshire Building | 2017-02-07 17:45 | 49858.6206 | 200.016
Devonshire Building | 2017-02-07 18:00 | 49858.6656 | 180
Devonshire Building | 2017-02-07 18:15 | 49858.9906 | 1299.996
Devonshire Building | 2017-02-07 18:30 | 49859.0306 | 159.984
Devonshire Building | 2017-02-07 18:45 | 49859.0756 | 180
Devonshire Building | 2017-02-07 19:00 | 49859.1156 | 159.984
Devonshire Building | 2017-02-07 19:15 | 49859.1556 | 159.984
Devonshire Building | 2017-02-07 19:30 | 49859.1906 | 140.004
Devonshire Building | 2017-02-07 19:45 | 49859.2206 | 119.988
Devonshire Building | 2017-02-07 20:00 | 49859.2456 | 100.008
Devonshire Building | 2017-02-07 20:15 | 49859.2706 | 100.008
Devonshire Building | 2017-02-07 20:30 | 49859.2906 | 79.992
Devonshire Building | 2017-02-07 20:45 | 49859.3106 | 79.992
Devonshire Building | 2017-02-07 21:00 | 49859.3256 | 60.012
Devonshire Building | 2017-02-07 21:15 | 49859.3406 | 60.012
Devonshire Building | 2017-02-07 21:30 | 49859.3556 | 60.012
Devonshire Building | 2017-02-07 21:45 | 49859.3706 | 60.012
Devonshire Building | 2017-02-07 22:00 | 49859.3856 | 60.012
Devonshire Building | 2017-02-07 22:15 | 49859.3956 | 39.996
Devonshire Building | 2017-02-07 22:30 | 49859.4056 | 39.996
Devonshire Building | 2017-02-07 22:45 | 49859.4156 | 39.996
Devonshire Building | 2017-02-07 23:00 | 49859.4256 | 39.996
Devonshire Building | 2017-02-07 23:15 | 49859.4356 | 39.996
Devonshire Building | 2017-02-07 23:30 | 49859.4456 | 39.996
Devonshire Building | 2017-02-07 23:45 | 49859.4556 | 39.996 | 20.016
Devonshire Building | 2017-02-08 | 49859.4609 | 20.016
Devonshire Building | 2017-02-08 00:15 | 49859.4709 | 39.996
Devonshire Building | 2017-02-08 00:30 | 49859.4809 | 39.996
Devonshire Building | 2017-02-08 00:45 | 49859.4909 | 39.996
Devonshire Building | 2017-02-08 01:00 | 49859.4959 | 20.016
Devonshire Building | 2017-02-08 01:15 | 49859.5059 | 39.996
Devonshire Building | 2017-02-08 01:30 | 49859.5209 | 60.012
Devonshire Building | 2017-02-08 01:45 | 49859.5459 | 100.008
Devonshire Building | 2017-02-08 02:00 | 49859.5709 | 100.008
Devonshire Building | 2017-02-08 02:15 | 49859.5909 | 79.992
Devonshire Building | 2017-02-08 02:30 | 49859.6159 | 100.008
Devonshire Building | 2017-02-08 02:45 | 49859.6409 | 100.008
Devonshire Building | 2017-02-08 03:00 | 49859.6609 | 79.992
Devonshire Building | 2017-02-08 03:15 | 49859.6859 | 100.008
Devonshire Building | 2017-02-08 03:30 | 49859.7059 | 79.992
Devonshire Building | 2017-02-08 03:45 | 49859.7309 | 100.008
Devonshire Building | 2017-02-08 04:00 | 49859.7509 | 79.992
Devonshire Building | 2017-02-08 04:15 | 49859.7709 | 79.992
Devonshire Building | 2017-02-08 04:30 | 49859.7759 | 20.016
Devonshire Building | 2017-02-08 04:45 | 49859.7859 | 39.996
Devonshire Building | 2017-02-08 05:00 | 49859.791 | 20.016
Devonshire Building | 2017-02-08 05:15 | 49859.796 | 20.016
Devonshire Building | 2017-02-08 05:30 | 49859.801 | 20.016
Devonshire Building | 2017-02-08 05:45 | 49859.811 | 39.996
Devonshire Building | 2017-02-08 06:00 | 49859.816 | 20.016
Devonshire Building | 2017-02-08 06:15 | 49859.821 | 20.016
Devonshire Building | 2017-02-08 06:30 | 49859.831 | 39.996
Devonshire Building | 2017-02-08 06:45 | 49859.836 | 20.016
Devonshire Building | 2017-02-08 07:00 | 49859.841 | 20.016
Devonshire Building | 2017-02-08 07:15 | 49859.846 | 20.016
Devonshire Building | 2017-02-08 07:30 | 49859.856 | 39.996
Devonshire Building | 2017-02-08 07:45 | 49859.861 | 20.016
Devonshire Building | 2017-02-08 08:00 | 49859.866 | 20.016
Devonshire Building | 2017-02-08 08:15 | 49859.876 | 39.996
Devonshire Building | 2017-02-08 08:30 | 49859.881 | 20.016
Devonshire Building | 2017-02-08 08:45 | 49859.906 | 100.008
Devonshire Building | 2017-02-08 09:00 | 49860.206 | 1199.988
Devonshire Building | 2017-02-08 09:15 | 49860.221 | 60.012
Devonshire Building | 2017-02-08 09:30 | 49860.231 | 39.996
Devonshire Building | 2017-02-08 09:45 | 49860.241 | 39.996
Devonshire Building | 2017-02-08 10:00 | 49860.261 | 79.992
Devonshire Building | 2017-02-08 10:15 | 49860.291 | 119.988
Devonshire Building | 2017-02-08 10:30 | 49860.341 | 200.016
Devonshire Building | 2017-02-08 10:45 | 49860.751 | 1640.016
Devonshire Building | 2017-02-08 11:00 | 49860.861 | 439.992
Devonshire Building | 2017-02-08 11:15 | 49860.956 | 380.016
Devonshire Building | 2017-02-08 11:30 | 49861.036 | 320.004
Devonshire Building | 2017-02-08 11:45 | 49861.106 | 280.008
Devonshire Building | 2017-02-08 12:00 | 49861.461 | 1419.984
Devonshire Building | 2017-02-08 12:15 | 49861.576 | 460.008
Devonshire Building | 2017-02-08 12:30 | 49861.736 | 640.008
Devonshire Building | 2017-02-08 12:45 | 49862.006 | 1080
Devonshire Building | 2017-02-08 13:00 | 49862.161 | 619.992
Devonshire Building | 2017-02-08 13:15 | 49862.571 | 1640.016
Devonshire Building | 2017-02-08 13:30 | 49862.661 | 360
Devonshire Building | 2017-02-08 13:45 | 49862.756 | 380.016
Devonshire Building | 2017-02-08 14:00 | 49862.836 | 320.004
Devonshire Building | 2017-02-08 14:15 | 49862.911 | 299.988
Devonshire Building | 2017-02-08 14:30 | 49862.986 | 299.988
Devonshire Building | 2017-02-08 14:45 | 49863.056 | 280.008
Devonshire Building | 2017-02-08 15:00 | 49863.171 | 460.008
Devonshire Building | 2017-02-08 15:15 | 49863.441 | 1080
Devonshire Building | 2017-02-08 15:30 | 49863.476 | 140.004
Devonshire Building | 2017-02-08 15:45 | 49863.511 | 140.004
Devonshire Building | 2017-02-08 16:00 | 49863.546 | 140.004
Devonshire Building | 2017-02-08 16:15 | 49863.586 | 159.984
Devonshire Building | 2017-02-08 16:30 | 49863.616 | 119.988
Devonshire Building | 2017-02-08 16:45 | 49863.746 | 519.984
Devonshire Building | 2017-02-08 17:00 | 49863.996 | 1000.008
Devonshire Building | 2017-02-08 17:15 | 49864.026 | 119.988
Devonshire Building | 2017-02-08 17:30 | 49864.066 | 159.984
Devonshire Building | 2017-02-08 17:45 | 49864.106 | 159.984
Devonshire Building | 2017-02-08 18:00 | 49864.141 | 140.004
Devonshire Building | 2017-02-08 18:15 | 49864.171 | 119.988
Devonshire Building | 2017-02-08 18:30 | 49864.206 | 140.004
Devonshire Building | 2017-02-08 18:45 | 49864.236 | 119.988
Devonshire Building | 2017-02-08 19:00 | 49864.261 | 100.008
Devonshire Building | 2017-02-08 19:15 | 49864.291 | 119.988
Devonshire Building | 2017-02-08 19:30 | 49864.316 | 100.008
Devonshire Building | 2017-02-08 19:45 | 49864.361 | 180
Devonshire Building | 2017-02-08 20:00 | 49864.396 | 140.004
Devonshire Building | 2017-02-08 20:15 | 49864.436 | 159.984
Devonshire Building | 2017-02-08 20:30 | 49864.471 | 140.004
Devonshire Building | 2017-02-08 20:45 | 49864.506 | 140.004
Devonshire Building | 2017-02-08 21:00 | 49864.541 | 140.004
Devonshire Building | 2017-02-08 21:15 | 49864.571 | 119.988
Devonshire Building | 2017-02-08 21:30 | 49864.606 | 140.004
Devonshire Building | 2017-02-08 21:45 | 49864.631 | 100.008
Devonshire Building | 2017-02-08 22:00 | 49864.676 | 180
Devonshire Building | 2017-02-08 22:15 | 49864.696 | 79.992
Devonshire Building | 2017-02-08 22:30 | 49864.706 | 39.996
Devonshire Building | 2017-02-08 22:45 | 49864.711 | 20.016
Devonshire Building | 2017-02-08 23:00 | 49864.716 | 20.016
Devonshire Building | 2017-02-08 23:15 | 49864.716 | 0
Devonshire Building | 2017-02-08 23:30 | 49864.721 | 20.016
Devonshire Building | 2017-02-08 23:45 | 49864.726 | 20.016 | 0
Devonshire Building | 2017-02-09 | 49864.7305 | 20.016
Devonshire Building | 2017-02-09 00:15 | 49864.7305 | 0
Devonshire Building | 2017-02-09 00:30 | 49864.7355 | 20.016
Devonshire Building | 2017-02-09 00:45 | 49864.7405 | 20.016
Devonshire Building | 2017-02-09 01:00 | 49864.7455 | 20.016
Devonshire Building | 2017-02-09 01:15 | 49864.7455 | 0
Devonshire Building | 2017-02-09 01:30 | 49864.7505 | 20.016
Devonshire Building | 2017-02-09 01:45 | 49864.7555 | 20.016
Devonshire Building | 2017-02-09 02:00 | 49864.7555 | 0
Devonshire Building | 2017-02-09 02:15 | 49864.7605 | 20.016
Devonshire Building | 2017-02-09 02:30 | 49864.7655 | 20.016
Devonshire Building | 2017-02-09 02:45 | 49864.7705 | 20.016
Devonshire Building | 2017-02-09 03:00 | 49864.7705 | 0
Devonshire Building | 2017-02-09 03:15 | 49864.7755 | 20.016
Devonshire Building | 2017-02-09 03:30 | 49864.7805 | 20.016
Devonshire Building | 2017-02-09 03:45 | 49864.7805 | 0
Devonshire Building | 2017-02-09 04:00 | 49864.7855 | 20.016
Devonshire Building | 2017-02-09 04:15 | 49865.0655 | 1119.996
Devonshire Building | 2017-02-09 04:30 | 49865.0655 | 0
Devonshire Building | 2017-02-09 04:45 | 49865.0705 | 20.016
Devonshire Building | 2017-02-09 05:00 | 49865.0705 | 0
Devonshire Building | 2017-02-09 05:15 | 49865.0755 | 20.016
Devonshire Building | 2017-02-09 05:30 | 49865.0805 | 20.016
Devonshire Building | 2017-02-09 05:45 | 49865.0805 | 0
Devonshire Building | 2017-02-09 06:00 | 49865.0855 | 20.016
Devonshire Building | 2017-02-09 06:15 | 49865.0855 | 0
Devonshire Building | 2017-02-09 06:30 | 49865.0905 | 20.016
Devonshire Building | 2017-02-09 06:45 | 49865.0955 | 20.016
Devonshire Building | 2017-02-09 07:00 | 49865.1005 | 20.016
Devonshire Building | 2017-02-09 07:15 | 49865.1005 | 0
Devonshire Building | 2017-02-09 07:30 | 49865.1205 | 79.992
Devonshire Building | 2017-02-09 07:45 | 49865.1205 | 0
Devonshire Building | 2017-02-09 08:00 | 49865.1305 | 39.996
Devonshire Building | 2017-02-09 08:15 | 49865.1355 | 20.016
Devonshire Building | 2017-02-09 08:30 | 49865.1405 | 20.016
Devonshire Building | 2017-02-09 08:45 | 49865.1505 | 39.996
Devonshire Building | 2017-02-09 09:00 | 49865.1705 | 79.992
Devonshire Building | 2017-02-09 09:15 | 49865.1805 | 39.996
Devonshire Building | 2017-02-09 09:30 | 49865.1855 | 20.016
Devonshire Building | 2017-02-09 09:45 | 49865.1905 | 20.016
Devonshire Building | 2017-02-09 10:00 | 49865.5455 | 1419.984
Devonshire Building | 2017-02-09 10:15 | 49865.5555 | 39.996
Devonshire Building | 2017-02-09 10:30 | 49865.5655 | 39.996
Devonshire Building | 2017-02-09 10:45 | 49865.5805 | 60.012
Devonshire Building | 2017-02-09 11:00 | 49865.6055 | 100.008
Devonshire Building | 2017-02-09 11:15 | 49865.6355 | 119.988
Devonshire Building | 2017-02-09 11:30 | 49865.9955 | 1440
Devonshire Building | 2017-02-09 11:45 | 49866.0456 | 200.016
Devonshire Building | 2017-02-09 12:00 | 49866.1105 | 259.992
Devonshire Building | 2017-02-09 12:15 | 49866.1706 | 240.012
Devonshire Building | 2017-02-09 12:30 | 49866.2256 | 219.996
Devonshire Building | 2017-02-09 12:45 | 49866.2805 | 219.996
Devonshire Building | 2017-02-09 13:00 | 49866.3306 | 200.016
Devonshire Building | 2017-02-09 13:15 | 49866.6806 | 1400.004
Devonshire Building | 2017-02-09 13:30 | 49866.7406 | 240.012
Devonshire Building | 2017-02-09 13:45 | 49866.8006 | 240.012
Devonshire Building | 2017-02-09 14:00 | 49866.8656 | 259.992
Devonshire Building | 2017-02-09 14:15 | 49866.9356 | 280.008
Devonshire Building | 2017-02-09 14:30 | 49867.0056 | 280.008
Devonshire Building | 2017-02-09 14:45 | 49867.0706 | 259.992
Devonshire Building | 2017-02-09 15:00 | 49867.4506 | 1519.992
Devonshire Building | 2017-02-09 15:15 | 49867.5206 | 280.008
Devonshire Building | 2017-02-09 15:30 | 49867.5956 | 299.988
Devonshire Building | 2017-02-09 15:45 | 49867.6706 | 299.988
Devonshire Building | 2017-02-09 16:00 | 49867.7406 | 280.008
Devonshire Building | 2017-02-09 16:15 | 49867.8106 | 280.008
Devonshire Building | 2017-02-09 16:30 | 49867.8756 | 259.992
Devonshire Building | 2017-02-09 16:45 | 49868.2656 | 1559.988
Devonshire Building | 2017-02-09 17:00 | 49868.3456 | 320.004
Devonshire Building | 2017-02-09 17:15 | 49868.4556 | 439.992
Devonshire Building | 2017-02-09 17:30 | 49868.5655 | 439.992
Devonshire Building | 2017-02-09 17:45 | 49868.6606 | 380.016
Devonshire Building | 2017-02-09 18:00 | 49868.7506 | 360
Devonshire Building | 2017-02-09 18:15 | 49868.8206 | 280.008
Devonshire Building | 2017-02-09 18:30 | 49868.8856 | 259.992
Devonshire Building | 2017-02-09 18:45 | 49868.9356 | 200.016
Devonshire Building | 2017-02-09 19:00 | 49868.9756 | 159.984
Devonshire Building | 2017-02-09 19:15 | 49869.0106 | 140.004
Devonshire Building | 2017-02-09 19:30 | 49869.0406 | 119.988
Devonshire Building | 2017-02-09 19:45 | 49869.0705 | 119.988
Devonshire Building | 2017-02-09 20:00 | 49869.0956 | 100.008
Devonshire Building | 2017-02-09 20:15 | 49869.1155 | 79.992
Devonshire Building | 2017-02-09 20:30 | 49869.1355 | 79.992
Devonshire Building | 2017-02-09 20:45 | 49869.1505 | 60.012
Devonshire Building | 2017-02-09 21:00 | 49869.2805 | 519.984
Devonshire Building | 2017-02-09 21:15 | 49869.4405 | 640.008
Devonshire Building | 2017-02-09 21:30 | 49869.4456 | 20.016
Devonshire Building | 2017-02-09 21:45 | 49869.4506 | 20.016
Devonshire Building | 2017-02-09 22:00 | 49869.4556 | 20.016
Devonshire Building | 2017-02-09 22:15 | 49869.4606 | 20.016
Devonshire Building | 2017-02-09 22:30 | 49869.4656 | 20.016
Devonshire Building | 2017-02-09 22:45 | 49869.4656 | 0
Devonshire Building | 2017-02-09 23:00 | 49869.4706 | 20.016
Devonshire Building | 2017-02-09 23:15 | 49869.4756 | 20.016
Devonshire Building | 2017-02-09 23:30 | 49869.4806 | 20.016
Devonshire Building | 2017-02-09 23:45 | 49869.4856 | 20.016 | 0
Devonshire Building | 2017-02-10 | 49869.4844 | 0
Devonshire Building | 2017-02-10 00:15 | 49869.4894 | 20.016
Devonshire Building | 2017-02-10 00:30 | 49869.4944 | 20.016
Devonshire Building | 2017-02-10 00:45 | 49869.4994 | 20.016
Devonshire Building | 2017-02-10 01:00 | 49869.5044 | 20.016
Devonshire Building | 2017-02-10 01:15 | 49869.5044 | 0
Devonshire Building | 2017-02-10 01:30 | 49869.5094 | 20.016
Devonshire Building | 2017-02-10 01:45 | 49869.5144 | 20.016
Devonshire Building | 2017-02-10 02:00 | 49869.5194 | 20.016
Devonshire Building | 2017-02-10 02:15 | 49869.5244 | 20.016
Devonshire Building | 2017-02-10 02:30 | 49869.5244 | 0
Devonshire Building | 2017-02-10 02:45 | 49869.5294 | 20.016
Devonshire Building | 2017-02-10 03:00 | 49869.5344 | 20.016
Devonshire Building | 2017-02-10 03:15 | 49869.5394 | 20.016
Devonshire Building | 2017-02-10 03:30 | 49869.5444 | 20.016
Devonshire Building | 2017-02-10 03:45 | 49869.5444 | 0
Devonshire Building | 2017-02-10 04:00 | 49869.5494 | 20.016
Devonshire Building | 2017-02-10 04:15 | 49869.5544 | 20.016
Devonshire Building | 2017-02-10 04:30 | 49869.5594 | 20.016
Devonshire Building | 2017-02-10 04:45 | 49869.5594 | 0
Devonshire Building | 2017-02-10 05:00 | 49869.5644 | 20.016
Devonshire Building | 2017-02-10 05:15 | 49869.5694 | 20.016
Devonshire Building | 2017-02-10 05:30 | 49869.5694 | 0
Devonshire Building | 2017-02-10 05:45 | 49869.5745 | 20.016
Devonshire Building | 2017-02-10 06:00 | 49869.5745 | 0
Devonshire Building | 2017-02-10 06:15 | 49869.5795 | 20.016
Devonshire Building | 2017-02-10 06:30 | 49869.5845 | 20.016
Devonshire Building | 2017-02-10 06:45 | 49869.5895 | 20.016
Devonshire Building | 2017-02-10 07:00 | 49869.5945 | 20.016
Devonshire Building | 2017-02-10 07:15 | 49869.5995 | 20.016
Devonshire Building | 2017-02-10 07:30 | 49869.6045 | 20.016
Devonshire Building | 2017-02-10 07:45 | 49869.6095 | 20.016
Devonshire Building | 2017-02-10 08:00 | 49869.6145 | 20.016
Devonshire Building | 2017-02-10 08:15 | 49869.6195 | 20.016
Devonshire Building | 2017-02-10 08:30 | 49869.6245 | 20.016
Devonshire Building | 2017-02-10 08:45 | 49869.6295 | 20.016
Devonshire Building | 2017-02-10 09:00 | 49869.6445 | 60.012
Devonshire Building | 2017-02-10 09:15 | 49869.6545 | 39.996
Devonshire Building | 2017-02-10 09:30 | 49869.9395 | 1140.012
Devonshire Building | 2017-02-10 09:45 | 49869.9645 | 100.008
Devonshire Building | 2017-02-10 10:00 | 49869.9895 | 100.008
Devonshire Building | 2017-02-10 10:15 | 49870.0345 | 180
Devonshire Building | 2017-02-10 10:30 | 49870.2095 | 699.984
Devonshire Building | 2017-02-10 10:45 | 49870.4595 | 1000.008
Devonshire Building | 2017-02-10 11:00 | 49870.9395 | 1919.988
Devonshire Building | 2017-02-10 11:15 | 49871.0945 | 619.992
Devonshire Building | 2017-02-10 11:30 | 49871.2045 | 439.992
Devonshire Building | 2017-02-10 11:45 | 49871.3145 | 439.992
Devonshire Building | 2017-02-10 12:00 | 49871.4245 | 439.992
Devonshire Building | 2017-02-10 12:15 | 49871.5295 | 420.012
Devonshire Building | 2017-02-10 12:30 | 49871.8845 | 1419.984
Devonshire Building | 2017-02-10 12:45 | 49871.9345 | 200.016
Devonshire Building | 2017-02-10 13:00 | 49871.9945 | 240.012
Devonshire Building | 2017-02-10 13:15 | 49872.0495 | 219.996
Devonshire Building | 2017-02-10 13:30 | 49872.1095 | 240.012
Devonshire Building | 2017-02-10 13:45 | 49872.1645 | 219.996
Devonshire Building | 2017-02-10 14:00 | 49872.2145 | 200.016
Devonshire Building | 2017-02-10 14:15 | 49872.4045 | 759.996
Devonshire Building | 2017-02-10 14:30 | 49872.5795 | 699.984
Devonshire Building | 2017-02-10 14:45 | 49872.6045 | 100.008
Devonshire Building | 2017-02-10 15:00 | 49872.6395 | 140.004
Devonshire Building | 2017-02-10 15:15 | 49872.6645 | 100.008
Devonshire Building | 2017-02-10 15:30 | 49872.6945 | 119.988
Devonshire Building | 2017-02-10 15:45 | 49872.7295 | 140.004
Devonshire Building | 2017-02-10 16:00 | 49872.7795 | 200.016
Devonshire Building | 2017-02-10 16:15 | 49873.1195 | 1360.008
Devonshire Building | 2017-02-10 16:30 | 49873.1945 | 299.988
Devonshire Building | 2017-02-10 16:45 | 49873.2695 | 299.988
Devonshire Building | 2017-02-10 17:00 | 49873.3395 | 280.008
Devonshire Building | 2017-02-10 17:15 | 49873.3945 | 219.996
Devonshire Building | 2017-02-10 17:30 | 49873.4595 | 259.992
Devonshire Building | 2017-02-10 17:45 | 49873.5245 | 259.992
Devonshire Building | 2017-02-10 18:00 | 49873.5845 | 240.012
Devonshire Building | 2017-02-10 18:15 | 49873.6545 | 280.008
Devonshire Building | 2017-02-10 18:30 | 49873.7145 | 240.012
Devonshire Building | 2017-02-10 18:45 | 49873.7795 | 259.992
Devonshire Building | 2017-02-10 19:00 | 49873.8395 | 240.012
Devonshire Building | 2017-02-10 19:15 | 49873.8995 | 240.012
Devonshire Building | 2017-02-10 19:30 | 49873.9545 | 219.996
Devonshire Building | 2017-02-10 19:45 | 49873.9995 | 180
Devonshire Building | 2017-02-10 20:00 | 49874.0395 | 159.984
Devonshire Building | 2017-02-10 20:15 | 49874.0745 | 140.004
Devonshire Building | 2017-02-10 20:30 | 49874.3495 | 1100.016
Devonshire Building | 2017-02-10 20:45 | 49874.3645 | 60.012
Devonshire Building | 2017-02-10 21:00 | 49874.3745 | 39.996
Devonshire Building | 2017-02-10 21:15 | 49874.3895 | 60.012
Devonshire Building | 2017-02-10 21:30 | 49874.3995 | 39.996
Devonshire Building | 2017-02-10 21:45 | 49874.4195 | 79.992
Devonshire Building | 2017-02-10 22:00 | 49874.4345 | 60.012
Devonshire Building | 2017-02-10 22:15 | 49874.4495 | 60.012
Devonshire Building | 2017-02-10 22:30 | 49874.4645 | 60.012
Devonshire Building | 2017-02-10 22:45 | 49874.4745 | 39.996
Devonshire Building | 2017-02-10 23:00 | 49874.4845 | 39.996
Devonshire Building | 2017-02-10 23:15 | 49874.4945 | 39.996
Devonshire Building | 2017-02-10 23:30 | 49874.5045 | 39.996
Devonshire Building | 2017-02-10 23:45 | 49874.5145 | 39.996 | 0
Devonshire Building | 2017-02-11 | 49874.5234 | 39.996
Devonshire Building | 2017-02-11 00:15 | 49874.5334 | 39.996
Devonshire Building | 2017-02-11 00:30 | 49874.5434 | 39.996
Devonshire Building | 2017-02-11 00:45 | 49874.5484 | 20.016
Devonshire Building | 2017-02-11 01:00 | 49874.5584 | 39.996
Devonshire Building | 2017-02-11 01:15 | 49874.5634 | 20.016
Devonshire Building | 2017-02-11 01:30 | 49874.5734 | 39.996
Devonshire Building | 2017-02-11 01:45 | 49874.5784 | 20.016
Devonshire Building | 2017-02-11 02:00 | 49874.5835 | 20.016
Devonshire Building | 2017-02-11 02:15 | 49874.5885 | 20.016
Devonshire Building | 2017-02-11 02:30 | 49874.5985 | 39.996
Devonshire Building | 2017-02-11 02:45 | 49874.6035 | 20.016
Devonshire Building | 2017-02-11 03:00 | 49874.6085 | 20.016
Devonshire Building | 2017-02-11 03:15 | 49874.6135 | 20.016
Devonshire Building | 2017-02-11 03:30 | 49874.6185 | 20.016
Devonshire Building | 2017-02-11 03:45 | 49874.6235 | 20.016
Devonshire Building | 2017-02-11 04:00 | 49874.6285 | 20.016
Devonshire Building | 2017-02-11 04:15 | 49874.6335 | 20.016
Devonshire Building | 2017-02-11 04:30 | 49874.6385 | 20.016
Devonshire Building | 2017-02-11 04:45 | 49874.6435 | 20.016
Devonshire Building | 2017-02-11 05:00 | 49874.6485 | 20.016
Devonshire Building | 2017-02-11 05:15 | 49874.6535 | 20.016
Devonshire Building | 2017-02-11 05:30 | 49874.6585 | 20.016
Devonshire Building | 2017-02-11 05:45 | 49874.6635 | 20.016
Devonshire Building | 2017-02-11 06:00 | 49874.6685 | 20.016
Devonshire Building | 2017-02-11 06:15 | 49874.6735 | 20.016
Devonshire Building | 2017-02-11 06:30 | 49874.6785 | 20.016
Devonshire Building | 2017-02-11 06:45 | 49874.6835 | 20.016
Devonshire Building | 2017-02-11 07:00 | 49874.6835 | 0
Devonshire Building | 2017-02-11 07:15 | 49874.6885 | 20.016
Devonshire Building | 2017-02-11 07:30 | 49874.6935 | 20.016
Devonshire Building | 2017-02-11 07:45 | 49874.6985 | 20.016
Devonshire Building | 2017-02-11 08:00 | 49874.7035 | 20.016
Devonshire Building | 2017-02-11 08:15 | 49874.7035 | 0
Devonshire Building | 2017-02-11 08:30 | 49874.7085 | 20.016
Devonshire Building | 2017-02-11 08:45 | 49874.7135 | 20.016
Devonshire Building | 2017-02-11 09:00 | 49874.7186 | 20.016
Devonshire Building | 2017-02-11 09:15 | 49874.7186 | 0
Devonshire Building | 2017-02-11 09:30 | 49874.7236 | 20.016
Devonshire Building | 2017-02-11 09:45 | 49874.7286 | 20.016
Devonshire Building | 2017-02-11 10:00 | 49874.7386 | 39.996
Devonshire Building | 2017-02-11 10:15 | 49874.7386 | 0
Devonshire Building | 2017-02-11 10:30 | 49874.7436 | 20.016
Devonshire Building | 2017-02-11 10:45 | 49874.7486 | 20.016
Devonshire Building | 2017-02-11 11:00 | 49874.7536 | 20.016
Devonshire Building | 2017-02-11 11:15 | 49874.7586 | 20.016
Devonshire Building | 2017-02-11 11:30 | 49874.7686 | 39.996
Devonshire Building | 2017-02-11 11:45 | 49874.7736 | 20.016
Devonshire Building | 2017-02-11 12:00 | 49874.7836 | 39.996
Devonshire Building | 2017-02-11 12:15 | 49874.8036 | 79.992
Devonshire Building | 2017-02-11 12:30 | 49874.8086 | 20.016
Devonshire Building | 2017-02-11 12:45 | 49874.9436 | 540
Devonshire Building | 2017-02-11 13:00 | 49875.1086 | 659.988
Devonshire Building | 2017-02-11 13:15 | 49875.1136 | 20.016
Devonshire Building | 2017-02-11 13:30 | 49875.1286 | 60.012
Devonshire Building | 2017-02-11 13:45 | 49875.1436 | 60.012
Devonshire Building | 2017-02-11 14:00 | 49875.1736 | 119.988
Devonshire Building | 2017-02-11 14:15 | 49875.1936 | 79.992
Devonshire Building | 2017-02-11 14:30 | 49875.2086 | 60.012
Devonshire Building | 2017-02-11 14:45 | 49875.2286 | 79.992
Devonshire Building | 2017-02-11 15:00 | 49875.2486 | 79.992
Devonshire Building | 2017-02-11 15:15 | 49875.2686 | 79.992
Devonshire Building | 2017-02-11 15:30 | 49875.2886 | 79.992
Devonshire Building | 2017-02-11 15:45 | 49875.3086 | 79.992
Devonshire Building | 2017-02-11 16:00 | 49875.3286 | 79.992
Devonshire Building | 2017-02-11 16:15 | 49875.3486 | 79.992
Devonshire Building | 2017-02-11 16:30 | 49875.3886 | 159.984
Devonshire Building | 2017-02-11 16:45 | 49875.6686 | 1119.996
Devonshire Building | 2017-02-11 17:00 | 49875.6736 | 20.016
Devonshire Building | 2017-02-11 17:15 | 49875.6736 | 0
Devonshire Building | 2017-02-11 17:30 | 49875.6786 | 20.016
Devonshire Building | 2017-02-11 17:45 | 49875.6836 | 20.016
Devonshire Building | 2017-02-11 18:00 | 49875.6836 | 0
Devonshire Building | 2017-02-11 18:15 | 49875.6886 | 20.016
Devonshire Building | 2017-02-11 18:30 | 49875.6886 | 0
Devonshire Building | 2017-02-11 18:45 | 49875.6936 | 20.016
Devonshire Building | 2017-02-11 19:00 | 49875.6936 | 0
Devonshire Building | 2017-02-11 19:15 | 49875.6986 | 20.016
Devonshire Building | 2017-02-11 19:30 | 49875.7036 | 20.016
Devonshire Building | 2017-02-11 19:45 | 49875.7036 | 0
Devonshire Building | 2017-02-11 20:00 | 49875.7086 | 20.016
Devonshire Building | 2017-02-11 20:15 | 49875.7086 | 0
Devonshire Building | 2017-02-11 20:30 | 49875.7136 | 20.016
Devonshire Building | 2017-02-11 20:45 | 49875.7186 | 20.016
Devonshire Building | 2017-02-11 21:00 | 49875.7186 | 0
Devonshire Building | 2017-02-11 21:15 | 49875.7236 | 20.016
Devonshire Building | 2017-02-11 21:30 | 49875.7236 | 0
Devonshire Building | 2017-02-11 21:45 | 49875.7286 | 20.016
Devonshire Building | 2017-02-11 22:00 | 49875.7436 | 60.012
Devonshire Building | 2017-02-11 22:15 | 49875.7436 | 0
Devonshire Building | 2017-02-11 22:30 | 49875.7486 | 20.016
Devonshire Building | 2017-02-11 22:45 | 49875.7536 | 20.016
Devonshire Building | 2017-02-11 23:00 | 49875.7586 | 20.016
Devonshire Building | 2017-02-11 23:15 | 49875.7586 | 0
Devonshire Building | 2017-02-11 23:30 | 49875.7636 | 20.016
Devonshire Building | 2017-02-11 23:45 | 49875.7686 | 20.016 | 0
Devonshire Building | 2017-02-12 | 49875.7734 | 20.016
Devonshire Building | 2017-02-12 00:15 | 49875.7784 | 20.016
Devonshire Building | 2017-02-12 00:30 | 49875.7784 | 0
Devonshire Building | 2017-02-12 00:45 | 49875.7834 | 20.016
Devonshire Building | 2017-02-12 01:00 | 49875.7885 | 20.016
Devonshire Building | 2017-02-12 01:15 | 49875.7935 | 20.016
Devonshire Building | 2017-02-12 01:30 | 49875.7935 | 0
Devonshire Building | 2017-02-12 01:45 | 49875.7985 | 20.016
Devonshire Building | 2017-02-12 02:00 | 49875.8035 | 20.016
Devonshire Building | 2017-02-12 02:15 | 49875.8035 | 0
Devonshire Building | 2017-02-12 02:30 | 49875.8085 | 20.016
Devonshire Building | 2017-02-12 02:45 | 49875.8135 | 20.016
Devonshire Building | 2017-02-12 03:00 | 49875.8135 | 0
Devonshire Building | 2017-02-12 03:15 | 49875.8185 | 20.016
Devonshire Building | 2017-02-12 03:30 | 49875.8235 | 20.016
Devonshire Building | 2017-02-12 03:45 | 49875.8235 | 0
Devonshire Building | 2017-02-12 04:00 | 49875.8285 | 20.016
Devonshire Building | 2017-02-12 04:15 | 49875.8335 | 20.016
Devonshire Building | 2017-02-12 04:30 | 49875.8335 | 0
Devonshire Building | 2017-02-12 04:45 | 49875.8385 | 20.016
Devonshire Building | 2017-02-12 05:00 | 49875.8385 | 0
Devonshire Building | 2017-02-12 05:15 | 49875.8435 | 20.016
Devonshire Building | 2017-02-12 05:30 | 49875.8485 | 20.016
Devonshire Building | 2017-02-12 05:45 | 49875.8485 | 0
Devonshire Building | 2017-02-12 06:00 | 49875.8535 | 20.016
Devonshire Building | 2017-02-12 06:15 | 49875.8535 | 0
Devonshire Building | 2017-02-12 06:30 | 49875.8585 | 20.016
Devonshire Building | 2017-02-12 06:45 | 49875.8635 | 20.016
Devonshire Building | 2017-02-12 07:00 | 49875.8635 | 0
Devonshire Building | 2017-02-12 07:15 | 49875.8685 | 20.016
Devonshire Building | 2017-02-12 07:30 | 49875.8685 | 0
Devonshire Building | 2017-02-12 07:45 | 49875.8735 | 20.016
Devonshire Building | 2017-02-12 08:00 | 49875.8785 | 20.016
Devonshire Building | 2017-02-12 08:15 | 49875.8785 | 0
Devonshire Building | 2017-02-12 08:30 | 49875.8835 | 20.016
Devonshire Building | 2017-02-12 08:45 | 49875.8885 | 20.016
Devonshire Building | 2017-02-12 09:00 | 49875.8885 | 0
Devonshire Building | 2017-02-12 09:15 | 49875.8935 | 20.016
Devonshire Building | 2017-02-12 09:30 | 49875.8935 | 0
Devonshire Building | 2017-02-12 09:45 | 49875.8985 | 20.016
Devonshire Building | 2017-02-12 10:00 | 49875.8985 | 0
Devonshire Building | 2017-02-12 10:15 | 49875.9035 | 20.016
Devonshire Building | 2017-02-12 10:30 | 49875.9085 | 20.016
Devonshire Building | 2017-02-12 10:45 | 49875.9085 | 0
Devonshire Building | 2017-02-12 11:00 | 49875.9136 | 20.016
Devonshire Building | 2017-02-12 11:15 | 49875.9186 | 20.016
Devonshire Building | 2017-02-12 11:30 | 49875.9236 | 20.016
Devonshire Building | 2017-02-12 11:45 | 49875.9236 | 0
Devonshire Building | 2017-02-12 12:00 | 49875.9286 | 20.016
Devonshire Building | 2017-02-12 12:15 | 49875.9286 | 0
Devonshire Building | 2017-02-12 12:30 | 49875.9336 | 20.016
Devonshire Building | 2017-02-12 12:45 | 49875.9336 | 0
Devonshire Building | 2017-02-12 13:00 | 49875.9386 | 20.016
Devonshire Building | 2017-02-12 13:15 | 49875.9436 | 20.016
Devonshire Building | 2017-02-12 13:30 | 49875.9486 | 20.016
Devonshire Building | 2017-02-12 13:45 | 49875.9686 | 79.992
Devonshire Building | 2017-02-12 14:00 | 49875.9886 | 79.992
Devonshire Building | 2017-02-12 14:15 | 49876.0036 | 60.012
Devonshire Building | 2017-02-12 14:30 | 49876.0236 | 79.992
Devonshire Building | 2017-02-12 14:45 | 49876.0436 | 79.992
Devonshire Building | 2017-02-12 15:00 | 49876.0636 | 79.992
Devonshire Building | 2017-02-12 15:15 | 49876.0786 | 60.012
Devonshire Building | 2017-02-12 15:30 | 49876.0986 | 79.992
Devonshire Building | 2017-02-12 15:45 | 49876.1186 | 79.992
Devonshire Building | 2017-02-12 16:00 | 49876.1386 | 79.992
Devonshire Building | 2017-02-12 16:15 | 49876.1436 | 20.016
Devonshire Building | 2017-02-12 16:30 | 49876.1436 | 0
Devonshire Building | 2017-02-12 16:45 | 49876.1486 | 20.016
Devonshire Building | 2017-02-12 17:00 | 49876.4236 | 1100.016
Devonshire Building | 2017-02-12 17:15 | 49876.4236 | 0
Devonshire Building | 2017-02-12 17:30 | 49876.4286 | 20.016
Devonshire Building | 2017-02-12 17:45 | 49876.4286 | 0
Devonshire Building | 2017-02-12 18:00 | 49876.4336 | 20.016
Devonshire Building | 2017-02-12 18:15 | 49876.4386 | 20.016
Devonshire Building | 2017-02-12 18:30 | 49876.4386 | 0
Devonshire Building | 2017-02-12 18:45 | 49876.4436 | 20.016
Devonshire Building | 2017-02-12 19:00 | 49876.4486 | 20.016
Devonshire Building | 2017-02-12 19:15 | 49876.4486 | 0
Devonshire Building | 2017-02-12 19:30 | 49876.4536 | 20.016
Devonshire Building | 2017-02-12 19:45 | 49876.4536 | 0
Devonshire Building | 2017-02-12 20:00 | 49876.4586 | 20.016
Devonshire Building | 2017-02-12 20:15 | 49876.4586 | 0
Devonshire Building | 2017-02-12 20:30 | 49876.4636 | 20.016
Devonshire Building | 2017-02-12 20:45 | 49876.4686 | 20.016
Devonshire Building | 2017-02-12 21:00 | 49876.4686 | 0
Devonshire Building | 2017-02-12 21:15 | 49876.4736 | 20.016
Devonshire Building | 2017-02-12 21:30 | 49876.4736 | 0
Devonshire Building | 2017-02-12 21:45 | 49876.4786 | 20.016
Devonshire Building | 2017-02-12 22:00 | 49876.4886 | 39.996
Devonshire Building | 2017-02-12 22:15 | 49876.4886 | 0
Devonshire Building | 2017-02-12 22:30 | 49876.4936 | 20.016
Devonshire Building | 2017-02-12 22:45 | 49876.4986 | 20.016
Devonshire Building | 2017-02-12 23:00 | 49876.4986 | 0
Devonshire Building | 2017-02-12 23:15 | 49876.5036 | 20.016
Devonshire Building | 2017-02-12 23:30 | 49876.5086 | 20.016
Devonshire Building | 2017-02-12 23:45 | 49876.5136 | 20.016 | 0
Devonshire Building | 2017-02-13 | 49876.5156 | 0
Devonshire Building | 2017-02-13 00:15 | 49876.5206 | 20.016
Devonshire Building | 2017-02-13 00:30 | 49876.5256 | 20.016
Devonshire Building | 2017-02-13 00:45 | 49876.5306 | 20.016
Devonshire Building | 2017-02-13 01:00 | 49876.5356 | 20.016
Devonshire Building | 2017-02-13 01:15 | 49876.5356 | 0
Devonshire Building | 2017-02-13 01:30 | 49876.5407 | 20.016
Devonshire Building | 2017-02-13 01:45 | 49876.5457 | 20.016
Devonshire Building | 2017-02-13 02:00 | 49876.5507 | 20.016
Devonshire Building | 2017-02-13 02:15 | 49876.5507 | 0
Devonshire Building | 2017-02-13 02:30 | 49876.5557 | 20.016
Devonshire Building | 2017-02-13 02:45 | 49876.5607 | 20.016
Devonshire Building | 2017-02-13 03:00 | 49876.5657 | 20.016
Devonshire Building | 2017-02-13 03:15 | 49876.5657 | 0
Devonshire Building | 2017-02-13 03:30 | 49876.5707 | 20.016
Devonshire Building | 2017-02-13 03:45 | 49876.5757 | 20.016
Devonshire Building | 2017-02-13 04:00 | 49876.5757 | 0
Devonshire Building | 2017-02-13 04:15 | 49876.5807 | 20.016
Devonshire Building | 2017-02-13 04:30 | 49876.5857 | 20.016
Devonshire Building | 2017-02-13 04:45 | 49876.5857 | 0
Devonshire Building | 2017-02-13 05:00 | 49876.5907 | 20.016
Devonshire Building | 2017-02-13 05:15 | 49876.5957 | 20.016
Devonshire Building | 2017-02-13 05:30 | 49876.5957 | 0
Devonshire Building | 2017-02-13 05:45 | 49876.6007 | 20.016
Devonshire Building | 2017-02-13 06:00 | 49876.6057 | 20.016
Devonshire Building | 2017-02-13 06:15 | 49876.6057 | 0
Devonshire Building | 2017-02-13 06:30 | 49876.6107 | 20.016
Devonshire Building | 2017-02-13 06:45 | 49876.6157 | 20.016
Devonshire Building | 2017-02-13 07:00 | 49876.6207 | 20.016
Devonshire Building | 2017-02-13 07:15 | 49876.6257 | 20.016
Devonshire Building | 2017-02-13 07:30 | 49876.6307 | 20.016
Devonshire Building | 2017-02-13 07:45 | 49876.6457 | 60.012
Devonshire Building | 2017-02-13 08:00 | 49876.6557 | 39.996
Devonshire Building | 2017-02-13 08:15 | 49876.6707 | 60.012
Devonshire Building | 2017-02-13 08:30 | 49876.6757 | 20.016
Devonshire Building | 2017-02-13 08:45 | 49876.6807 | 20.016
Devonshire Building | 2017-02-13 09:00 | 49876.9907 | 1239.984
Devonshire Building | 2017-02-13 09:15 | 49877.0057 | 60.012
Devonshire Building | 2017-02-13 09:30 | 49877.0357 | 119.988
Devonshire Building | 2017-02-13 09:45 | 49877.0857 | 200.016
Devonshire Building | 2017-02-13 10:00 | 49877.1607 | 299.988
Devonshire Building | 2017-02-13 10:15 | 49877.2557 | 380.016
Devonshire Building | 2017-02-13 10:30 | 49877.7057 | 1800
Devonshire Building | 2017-02-13 10:45 | 49877.8757 | 680.004
Devonshire Building | 2017-02-13 11:00 | 49878.0357 | 640.008
Devonshire Building | 2017-02-13 11:15 | 49878.1857 | 600.012
Devonshire Building | 2017-02-13 11:30 | 49878.3207 | 540
Devonshire Building | 2017-02-13 11:45 | 49878.4457 | 500.004
Devonshire Building | 2017-02-13 12:00 | 49878.8307 | 1540.008
Devonshire Building | 2017-02-13 12:15 | 49878.9407 | 439.992
Devonshire Building | 2017-02-13 12:30 | 49879.0507 | 439.992
Devonshire Building | 2017-02-13 12:45 | 49879.1607 | 439.992
Devonshire Building | 2017-02-13 13:00 | 49879.2657 | 420.012
Devonshire Building | 2017-02-13 13:15 | 49879.6857 | 1680.012
Devonshire Building | 2017-02-13 13:30 | 49879.7957 | 439.992
Devonshire Building | 2017-02-13 13:45 | 49879.8957 | 399.996
Devonshire Building | 2017-02-13 14:00 | 49879.9857 | 360
Devonshire Building | 2017-02-13 14:15 | 49880.0607 | 299.988
Devonshire Building | 2017-02-13 14:30 | 49880.1257 | 259.992
Devonshire Building | 2017-02-13 14:45 | 49880.4707 | 1379.988
Devonshire Building | 2017-02-13 15:00 | 49880.5107 | 159.984
Devonshire Building | 2017-02-13 15:15 | 49880.5507 | 159.984
Devonshire Building | 2017-02-13 15:30 | 49880.6007 | 200.016
Devonshire Building | 2017-02-13 15:45 | 49880.6607 | 240.012
Devonshire Building | 2017-02-13 16:00 | 49880.7307 | 280.008
Devonshire Building | 2017-02-13 16:15 | 49881.1057 | 1500.012
Devonshire Building | 2017-02-13 16:30 | 49881.1607 | 219.996
Devonshire Building | 2017-02-13 16:45 | 49881.2257 | 259.992
Devonshire Building | 2017-02-13 17:00 | 49881.2857 | 240.012
Devonshire Building | 2017-02-13 17:15 | 49881.3357 | 200.016
Devonshire Building | 2017-02-13 17:30 | 49881.3807 | 180
Devonshire Building | 2017-02-13 17:45 | 49881.4257 | 180
Devonshire Building | 2017-02-13 18:00 | 49881.4607 | 140.004
Devonshire Building | 2017-02-13 18:15 | 49881.5057 | 180
Devonshire Building | 2017-02-13 18:30 | 49881.5357 | 119.988
Devonshire Building | 2017-02-13 18:45 | 49881.7907 | 1019.988
Devonshire Building | 2017-02-13 19:00 | 49881.8457 | 219.996
Devonshire Building | 2017-02-13 19:15 | 49881.8557 | 39.996
Devonshire Building | 2017-02-13 19:30 | 49881.8657 | 39.996
Devonshire Building | 2017-02-13 19:45 | 49881.8757 | 39.996
Devonshire Building | 2017-02-13 20:00 | 49881.8857 | 39.996
Devonshire Building | 2017-02-13 20:15 | 49881.9007 | 60.012
Devonshire Building | 2017-02-13 20:30 | 49881.9107 | 39.996
Devonshire Building | 2017-02-13 20:45 | 49881.9207 | 39.996
Devonshire Building | 2017-02-13 21:00 | 49881.9307 | 39.996
Devonshire Building | 2017-02-13 21:15 | 49881.9457 | 60.012
Devonshire Building | 2017-02-13 21:30 | 49881.9557 | 39.996
Devonshire Building | 2017-02-13 21:45 | 49881.9657 | 39.996
Devonshire Building | 2017-02-13 22:00 | 49881.9807 | 60.012
Devonshire Building | 2017-02-13 22:15 | 49881.9907 | 39.996
Devonshire Building | 2017-02-13 22:30 | 49881.9957 | 20.016
Devonshire Building | 2017-02-13 22:45 | 49882.0057 | 39.996
Devonshire Building | 2017-02-13 23:00 | 49882.0157 | 39.996
Devonshire Building | 2017-02-13 23:15 | 49882.0207 | 20.016
Devonshire Building | 2017-02-13 23:30 | 49882.0307 | 39.996
Devonshire Building | 2017-02-13 23:45 | 49882.0357 | 20.016 | 0
Devonshire Building | 2017-02-14 | 49882.0391 | 20.016
Devonshire Building | 2017-02-14 00:15 | 49882.0491 | 39.996
Devonshire Building | 2017-02-14 00:30 | 49882.0541 | 20.016
Devonshire Building | 2017-02-14 00:45 | 49882.0641 | 39.996
Devonshire Building | 2017-02-14 01:00 | 49882.0691 | 20.016
Devonshire Building | 2017-02-14 01:15 | 49882.0741 | 20.016
Devonshire Building | 2017-02-14 01:30 | 49882.0841 | 39.996
Devonshire Building | 2017-02-14 01:45 | 49882.0891 | 20.016
Devonshire Building | 2017-02-14 02:00 | 49882.0941 | 20.016
Devonshire Building | 2017-02-14 02:15 | 49882.0991 | 20.016
Devonshire Building | 2017-02-14 02:30 | 49882.1041 | 20.016
Devonshire Building | 2017-02-14 02:45 | 49882.1091 | 20.016
Devonshire Building | 2017-02-14 03:00 | 49882.1141 | 20.016
Devonshire Building | 2017-02-14 03:15 | 49882.1191 | 20.016
Devonshire Building | 2017-02-14 03:30 | 49882.1241 | 20.016
Devonshire Building | 2017-02-14 03:45 | 49882.1291 | 20.016
Devonshire Building | 2017-02-14 04:00 | 49882.1341 | 20.016
Devonshire Building | 2017-02-14 04:15 | 49882.1391 | 20.016
Devonshire Building | 2017-02-14 04:30 | 49882.1441 | 20.016
Devonshire Building | 2017-02-14 04:45 | 49882.1491 | 20.016
Devonshire Building | 2017-02-14 05:00 | 49882.1541 | 20.016
Devonshire Building | 2017-02-14 05:15 | 49882.1591 | 20.016
Devonshire Building | 2017-02-14 05:30 | 49882.1641 | 20.016
Devonshire Building | 2017-02-14 05:45 | 49882.1691 | 20.016
Devonshire Building | 2017-02-14 06:00 | 49882.1741 | 20.016
Devonshire Building | 2017-02-14 06:15 | 49882.1791 | 20.016
Devonshire Building | 2017-02-14 06:30 | 49882.1841 | 20.016
Devonshire Building | 2017-02-14 06:45 | 49882.1892 | 20.016
Devonshire Building | 2017-02-14 07:00 | 49882.1942 | 20.016
Devonshire Building | 2017-02-14 07:15 | 49882.1992 | 20.016
Devonshire Building | 2017-02-14 07:30 | 49882.2042 | 20.016
Devonshire Building | 2017-02-14 07:45 | 49882.2092 | 20.016
Devonshire Building | 2017-02-14 08:00 | 49882.2142 | 20.016
Devonshire Building | 2017-02-14 08:15 | 49882.2242 | 39.996
Devonshire Building | 2017-02-14 08:30 | 49882.2342 | 39.996
Devonshire Building | 2017-02-14 08:45 | 49882.2492 | 60.012
Devonshire Building | 2017-02-14 09:00 | 49882.5692 | 1280.016
Devonshire Building | 2017-02-14 09:15 | 49882.5842 | 60.012
Devonshire Building | 2017-02-14 09:30 | 49882.5892 | 20.016
Devonshire Building | 2017-02-14 09:45 | 49882.6192 | 119.988
Devonshire Building | 2017-02-14 10:00 | 49882.6392 | 79.992
Devonshire Building | 2017-02-14 10:15 | 49882.6792 | 159.984
Devonshire Building | 2017-02-14 10:30 | 49882.7642 | 339.984
Devonshire Building | 2017-02-14 10:45 | 49883.1842 | 1680.012
Devonshire Building | 2017-02-14 11:00 | 49883.5042 | 1280.016
Devonshire Building | 2017-02-14 11:15 | 49883.7192 | 860.004
Devonshire Building | 2017-02-14 11:30 | 49883.8392 | 479.988
Devonshire Building | 2017-02-14 11:45 | 49883.9192 | 320.004
Devonshire Building | 2017-02-14 12:00 | 49883.9942 | 299.988
Devonshire Building | 2017-02-14 12:15 | 49884.2992 | 1220.004
Devonshire Building | 2017-02-14 12:30 | 49884.3292 | 119.988
Devonshire Building | 2017-02-14 12:45 | 49884.3492 | 79.992
Devonshire Building | 2017-02-14 13:00 | 49884.3742 | 100.008
Devonshire Building | 2017-02-14 13:15 | 49884.3942 | 79.992
Devonshire Building | 2017-02-14 13:30 | 49884.4142 | 79.992
Devonshire Building | 2017-02-14 13:45 | 49884.4392 | 100.008
Devonshire Building | 2017-02-14 14:00 | 49884.6742 | 939.996
Devonshire Building | 2017-02-14 14:15 | 49884.7892 | 460.008
Devonshire Building | 2017-02-14 14:30 | 49884.8142 | 100.008
Devonshire Building | 2017-02-14 14:45 | 49884.8392 | 100.008
Devonshire Building | 2017-02-14 15:00 | 49884.8692 | 119.988
Devonshire Building | 2017-02-14 15:15 | 49884.9442 | 299.988
Devonshire Building | 2017-02-14 15:30 | 49885.0792 | 540
Devonshire Building | 2017-02-14 15:45 | 49885.5142 | 1739.988
Devonshire Building | 2017-02-14 16:00 | 49885.7042 | 759.996
Devonshire Building | 2017-02-14 16:15 | 49885.8892 | 740.016
Devonshire Building | 2017-02-14 16:30 | 49886.0742 | 740.016
Devonshire Building | 2017-02-14 16:45 | 49886.2592 | 740.016
Devonshire Building | 2017-02-14 17:00 | 49886.4392 | 720
Devonshire Building | 2017-02-14 17:15 | 49886.6192 | 720
Devonshire Building | 2017-02-14 17:30 | 49887.0592 | 1760.004
Devonshire Building | 2017-02-14 17:45 | 49887.2092 | 600.012
Devonshire Building | 2017-02-14 18:00 | 49887.3242 | 460.008
Devonshire Building | 2017-02-14 18:15 | 49887.4142 | 360
Devonshire Building | 2017-02-14 18:30 | 49887.4942 | 320.004
Devonshire Building | 2017-02-14 18:45 | 49887.5642 | 280.008
Devonshire Building | 2017-02-14 19:00 | 49887.6342 | 280.008
Devonshire Building | 2017-02-14 19:15 | 49887.6992 | 259.992
Devonshire Building | 2017-02-14 19:30 | 49887.7542 | 219.996
Devonshire Building | 2017-02-14 19:45 | 49887.8142 | 240.012
Devonshire Building | 2017-02-14 20:00 | 49887.8692 | 219.996
Devonshire Building | 2017-02-14 20:15 | 49887.9242 | 219.996
Devonshire Building | 2017-02-14 20:30 | 49887.9792 | 219.996
Devonshire Building | 2017-02-14 20:45 | 49888.0342 | 219.996
Devonshire Building | 2017-02-14 21:00 | 49888.0842 | 200.016
Devonshire Building | 2017-02-14 21:15 | 49888.1392 | 219.996
Devonshire Building | 2017-02-14 21:30 | 49888.1892 | 200.016
Devonshire Building | 2017-02-14 21:45 | 49888.2442 | 219.996
Devonshire Building | 2017-02-14 22:00 | 49888.2992 | 219.996
Devonshire Building | 2017-02-14 22:15 | 49888.3342 | 140.004
Devonshire Building | 2017-02-14 22:30 | 49888.3692 | 140.004
Devonshire Building | 2017-02-14 22:45 | 49888.4042 | 140.004
Devonshire Building | 2017-02-14 23:00 | 49888.4342 | 119.988
Devonshire Building | 2017-02-14 23:15 | 49888.4692 | 140.004
Devonshire Building | 2017-02-14 23:30 | 49888.5092 | 159.984
Devonshire Building | 2017-02-14 23:45 | 49888.5492 | 159.984 | 20.016
Devonshire Building | 2017-02-15 | 49888.5938 | 180
Devonshire Building | 2017-02-15 00:15 | 49888.6438 | 200.016
Devonshire Building | 2017-02-15 00:30 | 49888.6988 | 219.996
Devonshire Building | 2017-02-15 00:45 | 49888.7488 | 200.016
Devonshire Building | 2017-02-15 01:00 | 49888.8038 | 219.996
Devonshire Building | 2017-02-15 01:15 | 49888.8588 | 219.996
Devonshire Building | 2017-02-15 01:30 | 49888.9188 | 240.012
Devonshire Building | 2017-02-15 01:45 | 49888.9738 | 219.996
Devonshire Building | 2017-02-15 02:00 | 49889.0338 | 240.012
Devonshire Building | 2017-02-15 02:15 | 49889.0888 | 219.996
Devonshire Building | 2017-02-15 02:30 | 49889.1488 | 240.012
Devonshire Building | 2017-02-15 02:45 | 49889.2038 | 219.996
Devonshire Building | 2017-02-15 03:00 | 49889.2638 | 240.012
Devonshire Building | 2017-02-15 03:15 | 49889.3188 | 219.996
Devonshire Building | 2017-02-15 03:30 | 49889.3788 | 240.012
Devonshire Building | 2017-02-15 03:45 | 49889.4338 | 219.996
Devonshire Building | 2017-02-15 04:00 | 49889.4938 | 240.012
Devonshire Building | 2017-02-15 04:15 | 49889.5488 | 219.996
Devonshire Building | 2017-02-15 04:30 | 49889.6088 | 240.012
Devonshire Building | 2017-02-15 04:45 | 49889.6638 | 219.996
Devonshire Building | 2017-02-15 05:00 | 49889.7188 | 219.996
Devonshire Building | 2017-02-15 05:15 | 49889.7788 | 240.012
Devonshire Building | 2017-02-15 05:30 | 49889.8338 | 219.996
Devonshire Building | 2017-02-15 05:45 | 49889.8888 | 219.996
Devonshire Building | 2017-02-15 06:00 | 49889.9488 | 240.012
Devonshire Building | 2017-02-15 06:15 | 49890.0038 | 219.996
Devonshire Building | 2017-02-15 06:30 | 49890.0638 | 240.012
Devonshire Building | 2017-02-15 06:45 | 49890.1188 | 219.996
Devonshire Building | 2017-02-15 07:00 | 49890.1738 | 219.996
Devonshire Building | 2017-02-15 07:15 | 49890.2338 | 240.012
Devonshire Building | 2017-02-15 07:30 | 49890.3088 | 299.988
Devonshire Building | 2017-02-15 07:45 | 49890.4088 | 399.996
Devonshire Building | 2017-02-15 08:00 | 49890.5188 | 439.992
Devonshire Building | 2017-02-15 08:15 | 49890.6288 | 439.992
Devonshire Building | 2017-02-15 08:30 | 49891.0088 | 1519.992
Devonshire Building | 2017-02-15 08:45 | 49891.1288 | 479.988
Devonshire Building | 2017-02-15 09:00 | 49891.2488 | 479.988
Devonshire Building | 2017-02-15 09:15 | 49891.3538 | 420.012
Devonshire Building | 2017-02-15 09:30 | 49891.4588 | 420.012
Devonshire Building | 2017-02-15 09:45 | 49891.5438 | 339.984
Devonshire Building | 2017-02-15 10:00 | 49891.6188 | 299.988
Devonshire Building | 2017-02-15 10:15 | 49892.0638 | 1779.984
Devonshire Building | 2017-02-15 10:30 | 49892.2138 | 600.012
Devonshire Building | 2017-02-15 10:45 | 49892.3088 | 380.016
Devonshire Building | 2017-02-15 11:00 | 49892.4088 | 399.996
Devonshire Building | 2017-02-15 11:15 | 49892.4888 | 320.004
Devonshire Building | 2017-02-15 11:30 | 49892.7388 | 1000.008
Devonshire Building | 2017-02-15 11:45 | 49892.7888 | 200.016
Devonshire Building | 2017-02-15 12:00 | 49892.8388 | 200.016
Devonshire Building | 2017-02-15 12:15 | 49892.8938 | 219.996
Devonshire Building | 2017-02-15 12:30 | 49892.9388 | 180
Devonshire Building | 2017-02-15 12:45 | 49893.3238 | 1540.008
Devonshire Building | 2017-02-15 13:00 | 49893.3688 | 180
Devonshire Building | 2017-02-15 13:15 | 49893.3988 | 119.988
Devonshire Building | 2017-02-15 13:30 | 49893.4588 | 240.012
Devonshire Building | 2017-02-15 13:45 | 49893.5288 | 280.008
Devonshire Building | 2017-02-15 14:00 | 49893.6188 | 360
Devonshire Building | 2017-02-15 14:15 | 49893.7088 | 360
Devonshire Building | 2017-02-15 14:30 | 49894.1438 | 1739.988
Devonshire Building | 2017-02-15 14:45 | 49894.2088 | 259.992
Devonshire Building | 2017-02-15 15:00 | 49894.2888 | 320.004
Devonshire Building | 2017-02-15 15:15 | 49894.3588 | 280.008
Devonshire Building | 2017-02-15 15:30 | 49894.4288 | 280.008
Devonshire Building | 2017-02-15 15:45 | 49894.4938 | 259.992
Devonshire Building | 2017-02-15 16:00 | 49894.7388 | 979.992
Devonshire Building | 2017-02-15 16:15 | 49894.9888 | 1000.008
Devonshire Building | 2017-02-15 16:30 | 49895.0488 | 240.012
Devonshire Building | 2017-02-15 16:45 | 49895.1088 | 240.012
Devonshire Building | 2017-02-15 17:00 | 49895.1838 | 299.988
Devonshire Building | 2017-02-15 17:15 | 49895.2688 | 339.984
Devonshire Building | 2017-02-15 17:30 | 49895.3438 | 299.988
Devonshire Building | 2017-02-15 17:45 | 49895.4138 | 280.008
Devonshire Building | 2017-02-15 18:00 | 49895.7938 | 1519.992
Devonshire Building | 2017-02-15 18:15 | 49895.8438 | 200.016
Devonshire Building | 2017-02-15 18:30 | 49895.8938 | 200.016
Devonshire Building | 2017-02-15 18:45 | 49895.9388 | 180
Devonshire Building | 2017-02-15 19:00 | 49895.9788 | 159.984
Devonshire Building | 2017-02-15 19:15 | 49896.0088 | 119.988
Devonshire Building | 2017-02-15 19:30 | 49896.0388 | 119.988
Devonshire Building | 2017-02-15 19:45 | 49896.0638 | 100.008
Devonshire Building | 2017-02-15 20:00 | 49896.0838 | 79.992
Devonshire Building | 2017-02-15 20:15 | 49896.0988 | 60.012
Devonshire Building | 2017-02-15 20:30 | 49896.1188 | 79.992
Devonshire Building | 2017-02-15 20:45 | 49896.1288 | 39.996
Devonshire Building | 2017-02-15 21:00 | 49896.1438 | 60.012
Devonshire Building | 2017-02-15 21:15 | 49896.1538 | 39.996
Devonshire Building | 2017-02-15 21:30 | 49896.1688 | 60.012
Devonshire Building | 2017-02-15 21:45 | 49896.1788 | 39.996
Devonshire Building | 2017-02-15 22:00 | 49896.1888 | 39.996
Devonshire Building | 2017-02-15 22:15 | 49896.1988 | 39.996
Devonshire Building | 2017-02-15 22:30 | 49896.2038 | 20.016
Devonshire Building | 2017-02-15 22:45 | 49896.2088 | 20.016
Devonshire Building | 2017-02-15 23:00 | 49896.2188 | 39.996
Devonshire Building | 2017-02-15 23:15 | 49896.2238 | 20.016
Devonshire Building | 2017-02-15 23:30 | 49896.2288 | 20.016
Devonshire Building | 2017-02-15 23:45 | 49896.2388 | 39.996 | 20.016
Devonshire Building | 2017-02-16 | 49896.2461 | 20.016
Devonshire Building | 2017-02-16 00:15 | 49896.2511 | 20.016
Devonshire Building | 2017-02-16 00:30 | 49896.2561 | 20.016
Devonshire Building | 2017-02-16 00:45 | 49896.2611 | 20.016
Devonshire Building | 2017-02-16 01:00 | 49896.2711 | 39.996
Devonshire Building | 2017-02-16 01:15 | 49896.2761 | 20.016
Devonshire Building | 2017-02-16 01:30 | 49896.2811 | 20.016
Devonshire Building | 2017-02-16 01:45 | 49896.2861 | 20.016
Devonshire Building | 2017-02-16 02:00 | 49896.2911 | 20.016
Devonshire Building | 2017-02-16 02:15 | 49896.2961 | 20.016
Devonshire Building | 2017-02-16 02:30 | 49896.3011 | 20.016
Devonshire Building | 2017-02-16 02:45 | 49896.3061 | 20.016
Devonshire Building | 2017-02-16 03:00 | 49896.3111 | 20.016
Devonshire Building | 2017-02-16 03:15 | 49896.3161 | 20.016
Devonshire Building | 2017-02-16 03:30 | 49896.3211 | 20.016
Devonshire Building | 2017-02-16 03:45 | 49896.3261 | 20.016
Devonshire Building | 2017-02-16 04:00 | 49896.3311 | 20.016
Devonshire Building | 2017-02-16 04:15 | 49896.3362 | 20.016
Devonshire Building | 2017-02-16 04:30 | 49896.3412 | 20.016
Devonshire Building | 2017-02-16 04:45 | 49896.3462 | 20.016
Devonshire Building | 2017-02-16 05:00 | 49896.3512 | 20.016
Devonshire Building | 2017-02-16 05:15 | 49896.3562 | 20.016
Devonshire Building | 2017-02-16 05:30 | 49896.3612 | 20.016
Devonshire Building | 2017-02-16 05:45 | 49896.3612 | 0
Devonshire Building | 2017-02-16 06:00 | 49896.3662 | 20.016
Devonshire Building | 2017-02-16 06:15 | 49896.3712 | 20.016
Devonshire Building | 2017-02-16 06:30 | 49896.3762 | 20.016
Devonshire Building | 2017-02-16 06:45 | 49896.3812 | 20.016
Devonshire Building | 2017-02-16 07:00 | 49896.3862 | 20.016
Devonshire Building | 2017-02-16 07:15 | 49896.3912 | 20.016
Devonshire Building | 2017-02-16 07:30 | 49896.4062 | 60.012
Devonshire Building | 2017-02-16 07:45 | 49896.4162 | 39.996
Devonshire Building | 2017-02-16 08:00 | 49896.4412 | 100.008
Devonshire Building | 2017-02-16 08:15 | 49896.4662 | 100.008
Devonshire Building | 2017-02-16 08:30 | 49896.7612 | 1180.008
Devonshire Building | 2017-02-16 08:45 | 49896.7962 | 140.004
Devonshire Building | 2017-02-16 09:00 | 49896.8212 | 100.008
Devonshire Building | 2017-02-16 09:15 | 49896.8512 | 119.988
Devonshire Building | 2017-02-16 09:30 | 49896.8762 | 100.008
Devonshire Building | 2017-02-16 09:45 | 49896.9012 | 100.008
Devonshire Building | 2017-02-16 10:00 | 49896.9212 | 79.992
Devonshire Building | 2017-02-16 10:15 | 49897.2612 | 1360.008
Devonshire Building | 2017-02-16 10:30 | 49897.2912 | 119.988
Devonshire Building | 2017-02-16 10:45 | 49897.3262 | 140.004
Devonshire Building | 2017-02-16 11:00 | 49897.4362 | 439.992
Devonshire Building | 2017-02-16 11:15 | 49897.5612 | 500.004
Devonshire Building | 2017-02-16 11:30 | 49897.6812 | 479.988
Devonshire Building | 2017-02-16 11:45 | 49898.0862 | 1620
Devonshire Building | 2017-02-16 12:00 | 49898.1962 | 439.992
Devonshire Building | 2017-02-16 12:15 | 49898.2962 | 399.996
Devonshire Building | 2017-02-16 12:30 | 49898.3812 | 339.984
Devonshire Building | 2017-02-16 12:45 | 49898.4562 | 299.988
Devonshire Building | 2017-02-16 13:00 | 49898.5262 | 280.008
Devonshire Building | 2017-02-16 13:15 | 49898.9012 | 1500.012
Devonshire Building | 2017-02-16 13:30 | 49898.9512 | 200.016
Devonshire Building | 2017-02-16 13:45 | 49899.0112 | 240.012
Devonshire Building | 2017-02-16 14:00 | 49899.0662 | 219.996
Devonshire Building | 2017-02-16 14:15 | 49899.1212 | 219.996
Devonshire Building | 2017-02-16 14:30 | 49899.1762 | 219.996
Devonshire Building | 2017-02-16 14:45 | 49899.2312 | 219.996
Devonshire Building | 2017-02-16 15:00 | 49899.6062 | 1500.012
Devonshire Building | 2017-02-16 15:15 | 49899.6762 | 280.008
Devonshire Building | 2017-02-16 15:30 | 49899.7412 | 259.992
Devonshire Building | 2017-02-16 15:45 | 49899.8112 | 280.008
Devonshire Building | 2017-02-16 16:00 | 49899.8712 | 240.012
Devonshire Building | 2017-02-16 16:15 | 49899.9362 | 259.992
Devonshire Building | 2017-02-16 16:30 | 49900.2912 | 1419.984
Devonshire Building | 2017-02-16 16:45 | 49900.3662 | 299.988
Devonshire Building | 2017-02-16 17:00 | 49900.4362 | 280.008
Devonshire Building | 2017-02-16 17:15 | 49900.5062 | 280.008
Devonshire Building | 2017-02-16 17:30 | 49900.5662 | 240.012
Devonshire Building | 2017-02-16 17:45 | 49900.6212 | 219.996
Devonshire Building | 2017-02-16 18:00 | 49900.6662 | 180
Devonshire Building | 2017-02-16 18:15 | 49900.7062 | 159.984
Devonshire Building | 2017-02-16 18:30 | 49900.7412 | 140.004
Devonshire Building | 2017-02-16 18:45 | 49900.7662 | 100.008
Devonshire Building | 2017-02-16 19:00 | 49900.7912 | 100.008
Devonshire Building | 2017-02-16 19:15 | 49900.8162 | 100.008
Devonshire Building | 2017-02-16 19:30 | 49900.8312 | 60.012
Devonshire Building | 2017-02-16 19:45 | 49900.8512 | 79.992
Devonshire Building | 2017-02-16 20:00 | 49900.8662 | 60.012
Devonshire Building | 2017-02-16 20:15 | 49900.8812 | 60.012
Devonshire Building | 2017-02-16 20:30 | 49900.8912 | 39.996
Devonshire Building | 2017-02-16 20:45 | 49901.1812 | 1159.992
Devonshire Building | 2017-02-16 21:00 | 49901.1862 | 20.016
Devonshire Building | 2017-02-16 21:15 | 49901.1912 | 20.016
Devonshire Building | 2017-02-16 21:30 | 49901.1912 | 0
Devonshire Building | 2017-02-16 21:45 | 49901.1962 | 20.016
Devonshire Building | 2017-02-16 22:00 | 49901.2012 | 20.016
Devonshire Building | 2017-02-16 22:15 | 49901.2062 | 20.016
Devonshire Building | 2017-02-16 22:30 | 49901.2112 | 20.016
Devonshire Building | 2017-02-16 22:45 | 49901.2112 | 0
Devonshire Building | 2017-02-16 23:00 | 49901.2162 | 20.016
Devonshire Building | 2017-02-16 23:15 | 49901.2212 | 20.016
Devonshire Building | 2017-02-16 23:30 | 49901.2212 | 0
Devonshire Building | 2017-02-16 23:45 | 49901.2262 | 20.016 | 0
Devonshire Building | 2017-02-17 | 49901.2266 | 0
Devonshire Building | 2017-02-17 00:15 | 49901.2316 | 20.016
Devonshire Building | 2017-02-17 00:30 | 49901.2366 | 20.016
Devonshire Building | 2017-02-17 00:45 | 49901.2366 | 0
Devonshire Building | 2017-02-17 01:00 | 49901.2416 | 20.016
Devonshire Building | 2017-02-17 01:15 | 49901.2416 | 0
Devonshire Building | 2017-02-17 01:30 | 49901.2466 | 20.016
Devonshire Building | 2017-02-17 01:45 | 49901.2466 | 0
Devonshire Building | 2017-02-17 02:00 | 49901.2516 | 20.016
Devonshire Building | 2017-02-17 02:15 | 49901.2566 | 20.016
Devonshire Building | 2017-02-17 02:30 | 49901.2566 | 0
Devonshire Building | 2017-02-17 02:45 | 49901.2616 | 20.016
Devonshire Building | 2017-02-17 03:00 | 49901.2616 | 0
Devonshire Building | 2017-02-17 03:15 | 49901.2666 | 20.016
Devonshire Building | 2017-02-17 03:30 | 49901.2666 | 0
Devonshire Building | 2017-02-17 03:45 | 49901.2716 | 20.016
Devonshire Building | 2017-02-17 04:00 | 49901.2766 | 20.016
Devonshire Building | 2017-02-17 04:15 | 49901.2766 | 0
Devonshire Building | 2017-02-17 04:30 | 49901.2816 | 20.016
Devonshire Building | 2017-02-17 04:45 | 49901.2816 | 0
Devonshire Building | 2017-02-17 05:00 | 49901.2866 | 20.016
Devonshire Building | 2017-02-17 05:15 | 49901.2866 | 0
Devonshire Building | 2017-02-17 05:30 | 49901.2916 | 20.016
Devonshire Building | 2017-02-17 05:45 | 49901.2916 | 0
Devonshire Building | 2017-02-17 06:00 | 49901.2966 | 20.016
Devonshire Building | 2017-02-17 06:15 | 49901.3016 | 20.016
Devonshire Building | 2017-02-17 06:30 | 49901.3016 | 0
Devonshire Building | 2017-02-17 06:45 | 49901.3066 | 20.016
Devonshire Building | 2017-02-17 07:00 | 49901.3116 | 20.016
Devonshire Building | 2017-02-17 07:15 | 49901.3166 | 20.016
Devonshire Building | 2017-02-17 07:30 | 49901.3166 | 0
Devonshire Building | 2017-02-17 07:45 | 49901.3416 | 100.008
Devonshire Building | 2017-02-17 08:00 | 49901.3716 | 119.988
Devonshire Building | 2017-02-17 08:15 | 49901.3916 | 79.992
Devonshire Building | 2017-02-17 08:30 | 49901.4166 | 100.008
Devonshire Building | 2017-02-17 08:45 | 49901.4466 | 119.988
Devonshire Building | 2017-02-17 09:00 | 49901.4666 | 79.992
Devonshire Building | 2017-02-17 09:15 | 49901.4916 | 100.008
Devonshire Building | 2017-02-17 09:30 | 49901.5516 | 240.012
Devonshire Building | 2017-02-17 09:45 | 49901.8416 | 1159.992
Devonshire Building | 2017-02-17 10:00 | 49901.8816 | 159.984
Devonshire Building | 2017-02-17 10:15 | 49901.9316 | 200.016
Devonshire Building | 2017-02-17 10:30 | 49901.9966 | 259.992
Devonshire Building | 2017-02-17 10:45 | 49902.0766 | 320.004
Devonshire Building | 2017-02-17 11:00 | 49902.1466 | 280.008
Devonshire Building | 2017-02-17 11:15 | 49902.4916 | 1379.988
Devonshire Building | 2017-02-17 11:30 | 49902.5516 | 240.012
Devonshire Building | 2017-02-17 11:45 | 49902.6166 | 259.992
Devonshire Building | 2017-02-17 12:00 | 49902.6766 | 240.012
Devonshire Building | 2017-02-17 12:15 | 49902.7416 | 259.992
Devonshire Building | 2017-02-17 12:30 | 49902.8016 | 240.012
Devonshire Building | 2017-02-17 12:45 | 49902.8616 | 240.012
Devonshire Building | 2017-02-17 13:00 | 49903.2166 | 1419.984
Devonshire Building | 2017-02-17 13:15 | 49903.2716 | 219.996
Devonshire Building | 2017-02-17 13:30 | 49903.3316 | 240.012
Devonshire Building | 2017-02-17 13:45 | 49903.3866 | 219.996
Devonshire Building | 2017-02-17 14:00 | 49903.4466 | 240.012
Devonshire Building | 2017-02-17 14:15 | 49903.5016 | 219.996
Devonshire Building | 2017-02-17 14:30 | 49903.5616 | 240.012
Devonshire Building | 2017-02-17 14:45 | 49903.6166 | 219.996
Devonshire Building | 2017-02-17 15:00 | 49903.9466 | 1320.012
Devonshire Building | 2017-02-17 15:15 | 49903.9966 | 200.016
Devonshire Building | 2017-02-17 15:30 | 49904.0616 | 259.992
Devonshire Building | 2017-02-17 15:45 | 49904.1166 | 219.996
Devonshire Building | 2017-02-17 16:00 | 49904.1666 | 200.016
Devonshire Building | 2017-02-17 16:15 | 49904.2166 | 200.016
Devonshire Building | 2017-02-17 16:30 | 49904.2667 | 200.016
Devonshire Building | 2017-02-17 16:45 | 49904.3217 | 219.996
Devonshire Building | 2017-02-17 17:00 | 49904.6517 | 1320.012
Devonshire Building | 2017-02-17 17:15 | 49904.6917 | 159.984
Devonshire Building | 2017-02-17 17:30 | 49904.7216 | 119.988
Devonshire Building | 2017-02-17 17:45 | 49904.7516 | 119.988
Devonshire Building | 2017-02-17 18:00 | 49904.7716 | 79.992
Devonshire Building | 2017-02-17 18:15 | 49904.8016 | 119.988
Devonshire Building | 2017-02-17 18:30 | 49904.8266 | 100.008
Devonshire Building | 2017-02-17 18:45 | 49904.8516 | 100.008
Devonshire Building | 2017-02-17 19:00 | 49904.8966 | 180
Devonshire Building | 2017-02-17 19:15 | 49904.9416 | 180
Devonshire Building | 2017-02-17 19:30 | 49904.9866 | 180
Devonshire Building | 2017-02-17 19:45 | 49905.0316 | 180
Devonshire Building | 2017-02-17 20:00 | 49905.0716 | 159.984
Devonshire Building | 2017-02-17 20:15 | 49905.1116 | 159.984
Devonshire Building | 2017-02-17 20:30 | 49905.1516 | 159.984
Devonshire Building | 2017-02-17 20:45 | 49905.1866 | 140.004
Devonshire Building | 2017-02-17 21:00 | 49905.2166 | 119.988
Devonshire Building | 2017-02-17 21:15 | 49905.2466 | 119.988
Devonshire Building | 2017-02-17 21:30 | 49905.2716 | 100.008
Devonshire Building | 2017-02-17 21:45 | 49905.2916 | 79.992
Devonshire Building | 2017-02-17 22:00 | 49905.3266 | 140.004
Devonshire Building | 2017-02-17 22:15 | 49905.3366 | 39.996
Devonshire Building | 2017-02-17 22:30 | 49905.3466 | 39.996
Devonshire Building | 2017-02-17 22:45 | 49905.3566 | 39.996
Devonshire Building | 2017-02-17 23:00 | 49905.3666 | 39.996
Devonshire Building | 2017-02-17 23:15 | 49905.3716 | 20.016
Devonshire Building | 2017-02-17 23:30 | 49905.3816 | 39.996
Devonshire Building | 2017-02-17 23:45 | 49905.3916 | 39.996 | 0
Devonshire Building | 2017-02-18 | 49905.3984 | 39.996
Devonshire Building | 2017-02-18 00:15 | 49905.4034 | 20.016
Devonshire Building | 2017-02-18 00:30 | 49905.4134 | 39.996
Devonshire Building | 2017-02-18 00:45 | 49905.4234 | 39.996
Devonshire Building | 2017-02-18 01:00 | 49905.4284 | 20.016
Devonshire Building | 2017-02-18 01:15 | 49905.4384 | 39.996
Devonshire Building | 2017-02-18 01:30 | 49905.4434 | 20.016
Devonshire Building | 2017-02-18 01:45 | 49905.4485 | 20.016
Devonshire Building | 2017-02-18 02:00 | 49905.4585 | 39.996
Devonshire Building | 2017-02-18 02:15 | 49905.4635 | 20.016
Devonshire Building | 2017-02-18 02:30 | 49905.4685 | 20.016
Devonshire Building | 2017-02-18 02:45 | 49905.4735 | 20.016
Devonshire Building | 2017-02-18 03:00 | 49905.4785 | 20.016
Devonshire Building | 2017-02-18 03:15 | 49905.4835 | 20.016
Devonshire Building | 2017-02-18 03:30 | 49905.4885 | 20.016
Devonshire Building | 2017-02-18 03:45 | 49905.4935 | 20.016
Devonshire Building | 2017-02-18 04:00 | 49905.4985 | 20.016
Devonshire Building | 2017-02-18 04:15 | 49905.5035 | 20.016
Devonshire Building | 2017-02-18 04:30 | 49905.5085 | 20.016
Devonshire Building | 2017-02-18 04:45 | 49905.5135 | 20.016
Devonshire Building | 2017-02-18 05:00 | 49905.5185 | 20.016
Devonshire Building | 2017-02-18 05:15 | 49905.7835 | 1059.984
Devonshire Building | 2017-02-18 05:30 | 49905.7885 | 20.016
Devonshire Building | 2017-02-18 05:45 | 49905.7885 | 0
Devonshire Building | 2017-02-18 06:00 | 49905.7935 | 20.016
Devonshire Building | 2017-02-18 06:15 | 49905.7935 | 0
Devonshire Building | 2017-02-18 06:30 | 49905.7985 | 20.016
Devonshire Building | 2017-02-18 06:45 | 49905.7985 | 0
Devonshire Building | 2017-02-18 07:00 | 49905.8035 | 20.016
Devonshire Building | 2017-02-18 07:15 | 49905.8035 | 0
Devonshire Building | 2017-02-18 07:30 | 49905.8085 | 20.016
Devonshire Building | 2017-02-18 07:45 | 49905.8085 | 0
Devonshire Building | 2017-02-18 08:00 | 49905.8135 | 20.016
Devonshire Building | 2017-02-18 08:15 | 49905.8135 | 0
Devonshire Building | 2017-02-18 08:30 | 49905.8185 | 20.016
Devonshire Building | 2017-02-18 08:45 | 49905.8185 | 0
Devonshire Building | 2017-02-18 09:00 | 49905.8235 | 20.016
Devonshire Building | 2017-02-18 09:15 | 49905.8235 | 0
Devonshire Building | 2017-02-18 09:30 | 49905.8285 | 20.016
Devonshire Building | 2017-02-18 09:45 | 49905.8285 | 0
Devonshire Building | 2017-02-18 10:00 | 49905.8435 | 60.012
Devonshire Building | 2017-02-18 10:15 | 49905.8435 | 0
Devonshire Building | 2017-02-18 10:30 | 49905.8485 | 20.016
Devonshire Building | 2017-02-18 10:45 | 49905.8485 | 0
Devonshire Building | 2017-02-18 11:00 | 49905.8535 | 20.016
Devonshire Building | 2017-02-18 11:15 | 49905.8535 | 0
Devonshire Building | 2017-02-18 11:30 | 49905.8585 | 20.016
Devonshire Building | 2017-02-18 11:45 | 49905.8636 | 20.016
Devonshire Building | 2017-02-18 12:00 | 49905.8636 | 0
Devonshire Building | 2017-02-18 12:15 | 49905.8686 | 20.016
Devonshire Building | 2017-02-18 12:30 | 49905.8686 | 0
Devonshire Building | 2017-02-18 12:45 | 49905.8736 | 20.016
Devonshire Building | 2017-02-18 13:00 | 49905.8786 | 20.016
Devonshire Building | 2017-02-18 13:15 | 49905.8986 | 79.992
Devonshire Building | 2017-02-18 13:30 | 49905.9136 | 60.012
Devonshire Building | 2017-02-18 13:45 | 49905.9386 | 100.008
Devonshire Building | 2017-02-18 14:00 | 49905.9536 | 60.012
Devonshire Building | 2017-02-18 14:15 | 49905.9736 | 79.992
Devonshire Building | 2017-02-18 14:30 | 49905.9936 | 79.992
Devonshire Building | 2017-02-18 14:45 | 49906.0136 | 79.992
Devonshire Building | 2017-02-18 15:00 | 49906.0336 | 79.992
Devonshire Building | 2017-02-18 15:15 | 49906.0536 | 79.992
Devonshire Building | 2017-02-18 15:30 | 49906.0686 | 60.012
Devonshire Building | 2017-02-18 15:45 | 49906.0836 | 60.012
Devonshire Building | 2017-02-18 16:00 | 49906.0886 | 20.016
Devonshire Building | 2017-02-18 16:15 | 49906.0936 | 20.016
Devonshire Building | 2017-02-18 16:30 | 49906.0936 | 0
Devonshire Building | 2017-02-18 16:45 | 49906.1036 | 39.996
Devonshire Building | 2017-02-18 17:00 | 49906.1036 | 0
Devonshire Building | 2017-02-18 17:15 | 49906.1086 | 20.016
Devonshire Building | 2017-02-18 17:30 | 49906.1086 | 0
Devonshire Building | 2017-02-18 17:45 | 49906.1136 | 20.016
Devonshire Building | 2017-02-18 18:00 | 49906.1136 | 0
Devonshire Building | 2017-02-18 18:15 | 49906.1186 | 20.016
Devonshire Building | 2017-02-18 18:30 | 49906.1186 | 0
Devonshire Building | 2017-02-18 18:45 | 49906.1236 | 20.016
Devonshire Building | 2017-02-18 19:00 | 49906.1236 | 0
Devonshire Building | 2017-02-18 19:15 | 49906.1286 | 20.016
Devonshire Building | 2017-02-18 19:30 | 49906.1286 | 0
Devonshire Building | 2017-02-18 19:45 | 49906.1336 | 20.016
Devonshire Building | 2017-02-18 20:00 | 49906.1336 | 0
Devonshire Building | 2017-02-18 20:15 | 49906.1386 | 20.016
Devonshire Building | 2017-02-18 20:30 | 49906.1386 | 0
Devonshire Building | 2017-02-18 20:45 | 49906.1436 | 20.016
Devonshire Building | 2017-02-18 21:00 | 49906.1436 | 0
Devonshire Building | 2017-02-18 21:15 | 49906.1486 | 20.016
Devonshire Building | 2017-02-18 21:30 | 49906.1486 | 0
Devonshire Building | 2017-02-18 21:45 | 49906.1536 | 20.016
Devonshire Building | 2017-02-18 22:00 | 49906.1786 | 100.008
Devonshire Building | 2017-02-18 22:15 | 49906.1786 | 0
Devonshire Building | 2017-02-18 22:30 | 49906.1836 | 20.016
Devonshire Building | 2017-02-18 22:45 | 49906.1836 | 0
Devonshire Building | 2017-02-18 23:00 | 49906.1886 | 20.016
Devonshire Building | 2017-02-18 23:15 | 49906.1886 | 0
Devonshire Building | 2017-02-18 23:30 | 49906.1936 | 20.016
Devonshire Building | 2017-02-18 23:45 | 49906.1936 | 0 | 0
Devonshire Building | 2017-02-19 | 49906.1992 | 20.016
Devonshire Building | 2017-02-19 00:15 | 49906.1992 | 0
Devonshire Building | 2017-02-19 00:30 | 49906.2042 | 20.016
Devonshire Building | 2017-02-19 00:45 | 49906.2042 | 0
Devonshire Building | 2017-02-19 01:00 | 49906.2092 | 20.016
Devonshire Building | 2017-02-19 01:15 | 49906.2092 | 0
Devonshire Building | 2017-02-19 01:30 | 49906.2142 | 20.016
Devonshire Building | 2017-02-19 01:45 | 49906.2142 | 0
Devonshire Building | 2017-02-19 02:00 | 49906.2192 | 20.016
Devonshire Building | 2017-02-19 02:15 | 49906.2192 | 0
Devonshire Building | 2017-02-19 02:30 | 49906.2192 | 0
Devonshire Building | 2017-02-19 02:45 | 49906.2242 | 20.016
Devonshire Building | 2017-02-19 03:00 | 49906.4892 | 1059.984
Devonshire Building | 2017-02-19 03:15 | 49906.4892 | 0
Devonshire Building | 2017-02-19 03:30 | 49906.4942 | 20.016
Devonshire Building | 2017-02-19 03:45 | 49906.4942 | 0
Devonshire Building | 2017-02-19 04:00 | 49906.4992 | 20.016
Devonshire Building | 2017-02-19 04:15 | 49906.4992 | 0
Devonshire Building | 2017-02-19 04:30 | 49906.5042 | 20.016
Devonshire Building | 2017-02-19 04:45 | 49906.5042 | 0
Devonshire Building | 2017-02-19 05:00 | 49906.5093 | 20.016
Devonshire Building | 2017-02-19 05:15 | 49906.5093 | 0
Devonshire Building | 2017-02-19 05:30 | 49906.5143 | 20.016
Devonshire Building | 2017-02-19 05:45 | 49906.5143 | 0
Devonshire Building | 2017-02-19 06:00 | 49906.5193 | 20.016
Devonshire Building | 2017-02-19 06:15 | 49906.5193 | 0
Devonshire Building | 2017-02-19 06:30 | 49906.5193 | 0
Devonshire Building | 2017-02-19 06:45 | 49906.5243 | 20.016
Devonshire Building | 2017-02-19 07:00 | 49906.5243 | 0
Devonshire Building | 2017-02-19 07:15 | 49906.5293 | 20.016
Devonshire Building | 2017-02-19 07:30 | 49906.5293 | 0
Devonshire Building | 2017-02-19 07:45 | 49906.5343 | 20.016
Devonshire Building | 2017-02-19 08:00 | 49906.5343 | 0
Devonshire Building | 2017-02-19 08:15 | 49906.5393 | 20.016
Devonshire Building | 2017-02-19 08:30 | 49906.5393 | 0
Devonshire Building | 2017-02-19 08:45 | 49906.5443 | 20.016
Devonshire Building | 2017-02-19 09:00 | 49906.5443 | 0
Devonshire Building | 2017-02-19 09:15 | 49906.5493 | 20.016
Devonshire Building | 2017-02-19 09:30 | 49906.5493 | 0
Devonshire Building | 2017-02-19 09:45 | 49906.5543 | 20.016
Devonshire Building | 2017-02-19 10:00 | 49906.5543 | 0
Devonshire Building | 2017-02-19 10:15 | 49906.5593 | 20.016
Devonshire Building | 2017-02-19 10:30 | 49906.5593 | 0
Devonshire Building | 2017-02-19 10:45 | 49906.5593 | 0
Devonshire Building | 2017-02-19 11:00 | 49906.5643 | 20.016
Devonshire Building | 2017-02-19 11:15 | 49906.5643 | 0
Devonshire Building | 2017-02-19 11:30 | 49906.5693 | 20.016
Devonshire Building | 2017-02-19 11:45 | 49906.5743 | 20.016
Devonshire Building | 2017-02-19 12:00 | 49906.5743 | 0
Devonshire Building | 2017-02-19 12:15 | 49906.5793 | 20.016
Devonshire Building | 2017-02-19 12:30 | 49906.5793 | 0
Devonshire Building | 2017-02-19 12:45 | 49906.5893 | 39.996
Devonshire Building | 2017-02-19 13:00 | 49906.5893 | 0
Devonshire Building | 2017-02-19 13:15 | 49906.5943 | 20.016
Devonshire Building | 2017-02-19 13:30 | 49906.6043 | 39.996
Devonshire Building | 2017-02-19 13:45 | 49906.6243 | 79.992
Devonshire Building | 2017-02-19 14:00 | 49906.6443 | 79.992
Devonshire Building | 2017-02-19 14:15 | 49906.6593 | 60.012
Devonshire Building | 2017-02-19 14:30 | 49906.6793 | 79.992
Devonshire Building | 2017-02-19 14:45 | 49906.6993 | 79.992
Devonshire Building | 2017-02-19 15:00 | 49906.7193 | 79.992
Devonshire Building | 2017-02-19 15:15 | 49906.7343 | 60.012
Devonshire Building | 2017-02-19 15:30 | 49906.7543 | 79.992
Devonshire Building | 2017-02-19 15:45 | 49906.7743 | 79.992
Devonshire Building | 2017-02-19 16:00 | 49906.7943 | 79.992
Devonshire Building | 2017-02-19 16:15 | 49906.7993 | 20.016
Devonshire Building | 2017-02-19 16:30 | 49906.7993 | 0
Devonshire Building | 2017-02-19 16:45 | 49906.8043 | 20.016
Devonshire Building | 2017-02-19 17:00 | 49906.8093 | 20.016
Devonshire Building | 2017-02-19 17:15 | 49906.8093 | 0
Devonshire Building | 2017-02-19 17:30 | 49906.8143 | 20.016
Devonshire Building | 2017-02-19 17:45 | 49906.8143 | 0
Devonshire Building | 2017-02-19 18:00 | 49906.8193 | 20.016
Devonshire Building | 2017-02-19 18:15 | 49906.8193 | 0
Devonshire Building | 2017-02-19 18:30 | 49906.8243 | 20.016
Devonshire Building | 2017-02-19 18:45 | 49906.8293 | 20.016
Devonshire Building | 2017-02-19 19:00 | 49906.8293 | 0
Devonshire Building | 2017-02-19 19:15 | 49906.8343 | 20.016
Devonshire Building | 2017-02-19 19:30 | 49906.8343 | 0
Devonshire Building | 2017-02-19 19:45 | 49906.8393 | 20.016
Devonshire Building | 2017-02-19 20:00 | 49906.8393 | 0
Devonshire Building | 2017-02-19 20:15 | 49906.8443 | 20.016
Devonshire Building | 2017-02-19 20:30 | 49906.8443 | 0
Devonshire Building | 2017-02-19 20:45 | 49906.8493 | 20.016
Devonshire Building | 2017-02-19 21:00 | 49906.8543 | 20.016
Devonshire Building | 2017-02-19 21:15 | 49906.8543 | 0
Devonshire Building | 2017-02-19 21:30 | 49906.8594 | 20.016
Devonshire Building | 2017-02-19 21:45 | 49906.8594 | 0
Devonshire Building | 2017-02-19 22:00 | 49906.8844 | 100.008
Devonshire Building | 2017-02-19 22:15 | 49906.8894 | 20.016
Devonshire Building | 2017-02-19 22:30 | 49906.8894 | 0
Devonshire Building | 2017-02-19 22:45 | 49906.8894 | 0
Devonshire Building | 2017-02-19 23:00 | 49906.8944 | 20.016
Devonshire Building | 2017-02-19 23:15 | 49906.8944 | 0
Devonshire Building | 2017-02-19 23:30 | 49906.8994 | 20.016
Devonshire Building | 2017-02-19 23:45 | 49906.8994 | 0 | 0
Devonshire Building | 2017-02-20 | 49906.9062 | 20.016
Devonshire Building | 2017-02-20 00:15 | 49906.9062 | 0
Devonshire Building | 2017-02-20 00:30 | 49906.9113 | 20.016
Devonshire Building | 2017-02-20 00:45 | 49906.9113 | 0
Devonshire Building | 2017-02-20 01:00 | 49906.9163 | 20.016
Devonshire Building | 2017-02-20 01:15 | 49906.9163 | 0
Devonshire Building | 2017-02-20 01:30 | 49906.9213 | 20.016
Devonshire Building | 2017-02-20 01:45 | 49906.9213 | 0
Devonshire Building | 2017-02-20 02:00 | 49906.9263 | 20.016
Devonshire Building | 2017-02-20 02:15 | 49906.9263 | 0
Devonshire Building | 2017-02-20 02:30 | 49906.9313 | 20.016
Devonshire Building | 2017-02-20 02:45 | 49906.9313 | 0
Devonshire Building | 2017-02-20 03:00 | 49906.9363 | 20.016
Devonshire Building | 2017-02-20 03:15 | 49906.9363 | 0
Devonshire Building | 2017-02-20 03:30 | 49906.9413 | 20.016
Devonshire Building | 2017-02-20 03:45 | 49906.9413 | 0
Devonshire Building | 2017-02-20 04:00 | 49906.9463 | 20.016
Devonshire Building | 2017-02-20 04:15 | 49906.9463 | 0
Devonshire Building | 2017-02-20 04:30 | 49906.9513 | 20.016
Devonshire Building | 2017-02-20 04:45 | 49906.9513 | 0
Devonshire Building | 2017-02-20 05:00 | 49906.9563 | 20.016
Devonshire Building | 2017-02-20 05:15 | 49906.9563 | 0
Devonshire Building | 2017-02-20 05:30 | 49906.9613 | 20.016
Devonshire Building | 2017-02-20 05:45 | 49906.9613 | 0
Devonshire Building | 2017-02-20 06:00 | 49906.9663 | 20.016
Devonshire Building | 2017-02-20 06:15 | 49906.9663 | 0
Devonshire Building | 2017-02-20 06:30 | 49906.9713 | 20.016
Devonshire Building | 2017-02-20 06:45 | 49906.9763 | 20.016
Devonshire Building | 2017-02-20 07:00 | 49906.9813 | 20.016
Devonshire Building | 2017-02-20 07:15 | 49906.9863 | 20.016
Devonshire Building | 2017-02-20 07:30 | 49907.2513 | 1059.984
Devonshire Building | 2017-02-20 07:45 | 49907.2563 | 20.016
Devonshire Building | 2017-02-20 08:00 | 49907.2613 | 20.016
Devonshire Building | 2017-02-20 08:15 | 49907.2713 | 39.996
Devonshire Building | 2017-02-20 08:30 | 49907.2763 | 20.016
Devonshire Building | 2017-02-20 08:45 | 49907.2863 | 39.996
Devonshire Building | 2017-02-20 09:00 | 49907.3013 | 60.012
Devonshire Building | 2017-02-20 09:15 | 49907.3213 | 79.992
Devonshire Building | 2017-02-20 09:30 | 49907.3363 | 60.012
Devonshire Building | 2017-02-20 09:45 | 49907.4363 | 399.996
Devonshire Building | 2017-02-20 10:00 | 49907.6263 | 759.996
Devonshire Building | 2017-02-20 10:15 | 49907.6363 | 39.996
Devonshire Building | 2017-02-20 10:30 | 49907.6463 | 39.996
Devonshire Building | 2017-02-20 10:45 | 49907.6513 | 20.016
Devonshire Building | 2017-02-20 11:00 | 49907.6663 | 60.012
Devonshire Building | 2017-02-20 11:15 | 49907.6763 | 39.996
Devonshire Building | 2017-02-20 11:30 | 49908.0163 | 1360.008
Devonshire Building | 2017-02-20 11:45 | 49908.0463 | 119.988
Devonshire Building | 2017-02-20 12:00 | 49908.0963 | 200.016
Devonshire Building | 2017-02-20 12:15 | 49908.1863 | 360
Devonshire Building | 2017-02-20 12:30 | 49908.2763 | 360
Devonshire Building | 2017-02-20 12:45 | 49908.3563 | 320.004
Devonshire Building | 2017-02-20 13:00 | 49908.7313 | 1500.012
Devonshire Building | 2017-02-20 13:15 | 49908.7963 | 259.992
Devonshire Building | 2017-02-20 13:30 | 49908.8663 | 280.008
Devonshire Building | 2017-02-20 13:45 | 49908.9363 | 280.008
Devonshire Building | 2017-02-20 14:00 | 49909.0163 | 320.004
Devonshire Building | 2017-02-20 14:15 | 49909.0763 | 240.012
Devonshire Building | 2017-02-20 14:30 | 49909.1413 | 259.992
Devonshire Building | 2017-02-20 14:45 | 49909.2963 | 619.992
Devonshire Building | 2017-02-20 15:00 | 49909.5413 | 979.992
Devonshire Building | 2017-02-20 15:15 | 49909.5663 | 100.008
Devonshire Building | 2017-02-20 15:30 | 49909.5913 | 100.008
Devonshire Building | 2017-02-20 15:45 | 49909.6163 | 100.008
Devonshire Building | 2017-02-20 16:00 | 49909.6463 | 119.988
Devonshire Building | 2017-02-20 16:15 | 49909.6813 | 140.004
Devonshire Building | 2017-02-20 16:30 | 49909.9313 | 1000.008
Devonshire Building | 2017-02-20 16:45 | 49910.0613 | 519.984
Devonshire Building | 2017-02-20 17:00 | 49910.1063 | 180
Devonshire Building | 2017-02-20 17:15 | 49910.1563 | 200.016
Devonshire Building | 2017-02-20 17:30 | 49910.2013 | 180
Devonshire Building | 2017-02-20 17:45 | 49910.2463 | 180
Devonshire Building | 2017-02-20 18:00 | 49910.2913 | 180
Devonshire Building | 2017-02-20 18:15 | 49910.3363 | 180
Devonshire Building | 2017-02-20 18:30 | 49910.3713 | 140.004
Devonshire Building | 2017-02-20 18:45 | 49910.4063 | 140.004
Devonshire Building | 2017-02-20 19:00 | 49910.4413 | 140.004
Devonshire Building | 2017-02-20 19:15 | 49910.4713 | 119.988
Devonshire Building | 2017-02-20 19:30 | 49910.5013 | 119.988
Devonshire Building | 2017-02-20 19:45 | 49910.5263 | 100.008
Devonshire Building | 2017-02-20 20:00 | 49910.5463 | 79.992
Devonshire Building | 2017-02-20 20:15 | 49910.5713 | 100.008
Devonshire Building | 2017-02-20 20:30 | 49910.5863 | 60.012
Devonshire Building | 2017-02-20 20:45 | 49910.6063 | 79.992
Devonshire Building | 2017-02-20 21:00 | 49910.6213 | 60.012
Devonshire Building | 2017-02-20 21:15 | 49910.6363 | 60.012
Devonshire Building | 2017-02-20 21:30 | 49910.6463 | 39.996
Devonshire Building | 2017-02-20 21:45 | 49910.6613 | 60.012
Devonshire Building | 2017-02-20 22:00 | 49910.9263 | 1059.984
Devonshire Building | 2017-02-20 22:15 | 49910.9313 | 20.016
Devonshire Building | 2017-02-20 22:30 | 49910.9364 | 20.016
Devonshire Building | 2017-02-20 22:45 | 49910.9364 | 0
Devonshire Building | 2017-02-20 23:00 | 49910.9414 | 20.016
Devonshire Building | 2017-02-20 23:15 | 49910.9414 | 0
Devonshire Building | 2017-02-20 23:30 | 49910.9464 | 20.016
Devonshire Building | 2017-02-20 23:45 | 49910.9514 | 20.016 | 0
Devonshire Building | 2017-02-21 | 49910.9492 | 0
Devonshire Building | 2017-02-21 00:15 | 49910.9542 | 20.016
Devonshire Building | 2017-02-21 00:30 | 49910.9542 | 0
Devonshire Building | 2017-02-21 00:45 | 49910.9592 | 20.016
Devonshire Building | 2017-02-21 01:00 | 49910.9592 | 0
Devonshire Building | 2017-02-21 01:15 | 49910.9642 | 20.016
Devonshire Building | 2017-02-21 01:30 | 49910.9642 | 0
Devonshire Building | 2017-02-21 01:45 | 49910.9692 | 20.016
Devonshire Building | 2017-02-21 02:00 | 49910.9692 | 0
Devonshire Building | 2017-02-21 02:15 | 49910.9742 | 20.016
Devonshire Building | 2017-02-21 02:30 | 49910.9742 | 0
Devonshire Building | 2017-02-21 02:45 | 49910.9792 | 20.016
Devonshire Building | 2017-02-21 03:00 | 49910.9792 | 0
Devonshire Building | 2017-02-21 03:15 | 49910.9842 | 20.016
Devonshire Building | 2017-02-21 03:30 | 49910.9893 | 20.016
Devonshire Building | 2017-02-21 03:45 | 49910.9893 | 0
Devonshire Building | 2017-02-21 04:00 | 49910.9943 | 20.016
Devonshire Building | 2017-02-21 04:15 | 49910.9943 | 0
Devonshire Building | 2017-02-21 04:30 | 49910.9993 | 20.016
Devonshire Building | 2017-02-21 04:45 | 49910.9993 | 0
Devonshire Building | 2017-02-21 05:00 | 49911.0043 | 20.016
Devonshire Building | 2017-02-21 05:15 | 49911.0043 | 0
Devonshire Building | 2017-02-21 05:30 | 49911.0093 | 20.016
Devonshire Building | 2017-02-21 05:45 | 49911.0093 | 0
Devonshire Building | 2017-02-21 06:00 | 49911.0143 | 20.016
Devonshire Building | 2017-02-21 06:15 | 49911.0143 | 0
Devonshire Building | 2017-02-21 06:30 | 49911.0193 | 20.016
Devonshire Building | 2017-02-21 06:45 | 49911.0243 | 20.016
Devonshire Building | 2017-02-21 07:00 | 49911.0293 | 20.016
Devonshire Building | 2017-02-21 07:15 | 49911.0343 | 20.016
Devonshire Building | 2017-02-21 07:30 | 49911.0393 | 20.016
Devonshire Building | 2017-02-21 07:45 | 49911.0493 | 39.996
Devonshire Building | 2017-02-21 08:00 | 49911.0543 | 20.016
Devonshire Building | 2017-02-21 08:15 | 49911.0643 | 39.996
Devonshire Building | 2017-02-21 08:30 | 49911.0693 | 20.016
Devonshire Building | 2017-02-21 08:45 | 49911.0843 | 60.012
Devonshire Building | 2017-02-21 09:00 | 49911.0893 | 20.016
Devonshire Building | 2017-02-21 09:15 | 49911.0993 | 39.996
Devonshire Building | 2017-02-21 09:30 | 49911.3793 | 1119.996
Devonshire Building | 2017-02-21 09:45 | 49911.3993 | 79.992
Devonshire Building | 2017-02-21 10:00 | 49911.4243 | 100.008
Devonshire Building | 2017-02-21 10:15 | 49911.4493 | 100.008
Devonshire Building | 2017-02-21 10:30 | 49911.7493 | 1199.988
Devonshire Building | 2017-02-21 10:45 | 49911.8843 | 540
Devonshire Building | 2017-02-21 11:00 | 49911.9893 | 420.012
Devonshire Building | 2017-02-21 11:15 | 49912.0843 | 380.016
Devonshire Building | 2017-02-21 11:30 | 49912.1693 | 339.984
Devonshire Building | 2017-02-21 11:45 | 49912.2543 | 339.984
Devonshire Building | 2017-02-21 12:00 | 49912.6193 | 1460.016
Devonshire Building | 2017-02-21 12:15 | 49912.7193 | 399.996
Devonshire Building | 2017-02-21 12:30 | 49912.8143 | 380.016
Devonshire Building | 2017-02-21 12:45 | 49912.9043 | 360
Devonshire Building | 2017-02-21 13:00 | 49912.9943 | 360
Devonshire Building | 2017-02-21 13:15 | 49913.0693 | 299.988
Devonshire Building | 2017-02-21 13:30 | 49913.1543 | 339.984
Devonshire Building | 2017-02-21 13:45 | 49913.4643 | 1239.984
Devonshire Building | 2017-02-21 14:00 | 49913.5093 | 180
Devonshire Building | 2017-02-21 14:15 | 49913.5593 | 200.016
Devonshire Building | 2017-02-21 14:30 | 49913.5993 | 159.984
Devonshire Building | 2017-02-21 14:45 | 49913.6393 | 159.984
Devonshire Building | 2017-02-21 15:00 | 49913.6793 | 159.984
Devonshire Building | 2017-02-21 15:15 | 49913.7143 | 140.004
Devonshire Building | 2017-02-21 15:30 | 49913.7493 | 140.004
Devonshire Building | 2017-02-21 15:45 | 49914.0743 | 1299.996
Devonshire Building | 2017-02-21 16:00 | 49914.0893 | 60.012
Devonshire Building | 2017-02-21 16:15 | 49914.1093 | 79.992
Devonshire Building | 2017-02-21 16:30 | 49914.1293 | 79.992
Devonshire Building | 2017-02-21 16:45 | 49914.1593 | 119.988
Devonshire Building | 2017-02-21 17:00 | 49914.2193 | 240.012
Devonshire Building | 2017-02-21 17:15 | 49914.3393 | 479.988
Devonshire Building | 2017-02-21 17:30 | 49914.8093 | 1879.992
Devonshire Building | 2017-02-21 17:45 | 49914.9543 | 579.996
Devonshire Building | 2017-02-21 18:00 | 49915.0643 | 439.992
Devonshire Building | 2017-02-21 18:15 | 49915.1293 | 259.992
Devonshire Building | 2017-02-21 18:30 | 49915.1843 | 219.996
Devonshire Building | 2017-02-21 18:45 | 49915.2243 | 159.984
Devonshire Building | 2017-02-21 19:00 | 49915.2543 | 119.988
Devonshire Building | 2017-02-21 19:15 | 49915.2793 | 100.008
Devonshire Building | 2017-02-21 19:30 | 49915.2993 | 79.992
Devonshire Building | 2017-02-21 19:45 | 49915.3343 | 140.004
Devonshire Building | 2017-02-21 20:00 | 49915.3693 | 140.004
Devonshire Building | 2017-02-21 20:15 | 49915.3993 | 119.988
Devonshire Building | 2017-02-21 20:30 | 49915.4293 | 119.988
Devonshire Building | 2017-02-21 20:45 | 49915.4593 | 119.988
Devonshire Building | 2017-02-21 21:00 | 49915.4843 | 100.008
Devonshire Building | 2017-02-21 21:15 | 49915.5093 | 100.008
Devonshire Building | 2017-02-21 21:30 | 49915.5343 | 100.008
Devonshire Building | 2017-02-21 21:45 | 49915.5593 | 100.008
Devonshire Building | 2017-02-21 22:00 | 49915.5893 | 119.988
Devonshire Building | 2017-02-21 22:15 | 49915.6093 | 79.992
Devonshire Building | 2017-02-21 22:30 | 49915.6143 | 20.016
Devonshire Building | 2017-02-21 22:45 | 49915.6193 | 20.016
Devonshire Building | 2017-02-21 23:00 | 49915.6243 | 20.016
Devonshire Building | 2017-02-21 23:15 | 49915.6293 | 20.016
Devonshire Building | 2017-02-21 23:30 | 49915.6343 | 20.016
Devonshire Building | 2017-02-21 23:45 | 49915.6393 | 20.016 | 0
Devonshire Building | 2017-02-22 | 49915.6406 | 0
Devonshire Building | 2017-02-22 00:15 | 49915.6456 | 20.016
Devonshire Building | 2017-02-22 00:30 | 49915.6506 | 20.016
Devonshire Building | 2017-02-22 00:45 | 49915.6556 | 20.016
Devonshire Building | 2017-02-22 01:00 | 49915.6606 | 20.016
Devonshire Building | 2017-02-22 01:15 | 49915.6657 | 20.016
Devonshire Building | 2017-02-22 01:30 | 49915.6707 | 20.016
Devonshire Building | 2017-02-22 01:45 | 49915.6757 | 20.016
Devonshire Building | 2017-02-22 02:00 | 49915.6757 | 0
Devonshire Building | 2017-02-22 02:15 | 49915.6807 | 20.016
Devonshire Building | 2017-02-22 02:30 | 49915.6857 | 20.016
Devonshire Building | 2017-02-22 02:45 | 49915.6907 | 20.016
Devonshire Building | 2017-02-22 03:00 | 49915.6957 | 20.016
Devonshire Building | 2017-02-22 03:15 | 49915.6957 | 0
Devonshire Building | 2017-02-22 03:30 | 49915.7007 | 20.016
Devonshire Building | 2017-02-22 03:45 | 49915.7057 | 20.016
Devonshire Building | 2017-02-22 04:00 | 49915.7107 | 20.016
Devonshire Building | 2017-02-22 04:15 | 49915.7107 | 0
Devonshire Building | 2017-02-22 04:30 | 49915.7157 | 20.016
Devonshire Building | 2017-02-22 04:45 | 49915.7207 | 20.016
Devonshire Building | 2017-02-22 05:00 | 49915.7207 | 0
Devonshire Building | 2017-02-22 05:15 | 49915.7257 | 20.016
Devonshire Building | 2017-02-22 05:30 | 49915.7307 | 20.016
Devonshire Building | 2017-02-22 05:45 | 49915.7307 | 0
Devonshire Building | 2017-02-22 06:00 | 49915.7357 | 20.016
Devonshire Building | 2017-02-22 06:15 | 49915.7407 | 20.016
Devonshire Building | 2017-02-22 06:30 | 49915.7457 | 20.016
Devonshire Building | 2017-02-22 06:45 | 49915.7507 | 20.016
Devonshire Building | 2017-02-22 07:00 | 49915.7557 | 20.016
Devonshire Building | 2017-02-22 07:15 | 49915.7607 | 20.016
Devonshire Building | 2017-02-22 07:30 | 49915.7657 | 20.016
Devonshire Building | 2017-02-22 07:45 | 49915.7707 | 20.016
Devonshire Building | 2017-02-22 08:00 | 49915.7757 | 20.016
Devonshire Building | 2017-02-22 08:15 | 49916.0557 | 1119.996
Devonshire Building | 2017-02-22 08:30 | 49916.0657 | 39.996
Devonshire Building | 2017-02-22 08:45 | 49916.0757 | 39.996
Devonshire Building | 2017-02-22 09:00 | 49916.0857 | 39.996
Devonshire Building | 2017-02-22 09:15 | 49916.0957 | 39.996
Devonshire Building | 2017-02-22 09:30 | 49916.1057 | 39.996
Devonshire Building | 2017-02-22 09:45 | 49916.1107 | 20.016
Devonshire Building | 2017-02-22 10:00 | 49916.1207 | 39.996
Devonshire Building | 2017-02-22 10:15 | 49916.4757 | 1419.984
Devonshire Building | 2017-02-22 10:30 | 49916.6457 | 680.004
Devonshire Building | 2017-02-22 10:45 | 49916.7707 | 500.004
Devonshire Building | 2017-02-22 11:00 | 49916.8707 | 399.996
Devonshire Building | 2017-02-22 11:15 | 49916.9607 | 360
Devonshire Building | 2017-02-22 11:30 | 49917.0457 | 339.984
Devonshire Building | 2017-02-22 11:45 | 49917.3857 | 1360.008
Devonshire Building | 2017-02-22 12:00 | 49917.6607 | 1100.016
Devonshire Building | 2017-02-22 12:15 | 49917.7407 | 320.004
Devonshire Building | 2017-02-22 12:30 | 49917.8007 | 240.012
Devonshire Building | 2017-02-22 12:45 | 49917.8457 | 180
Devonshire Building | 2017-02-22 13:00 | 49917.8957 | 200.016
Devonshire Building | 2017-02-22 13:15 | 49917.9357 | 159.984
Devonshire Building | 2017-02-22 13:30 | 49918.5507 | 2459.988
Devonshire Building | 2017-02-22 13:45 | 49918.6057 | 219.996
Devonshire Building | 2017-02-22 14:00 | 49918.6657 | 240.012
Devonshire Building | 2017-02-22 14:15 | 49918.7207 | 219.996
Devonshire Building | 2017-02-22 14:30 | 49918.7807 | 240.012
Devonshire Building | 2017-02-22 14:45 | 49918.8357 | 219.996
Devonshire Building | 2017-02-22 15:00 | 49918.8957 | 240.012
Devonshire Building | 2017-02-22 15:15 | 49919.4957 | 2400.012
Devonshire Building | 2017-02-22 15:30 | 49919.5657 | 280.008
Devonshire Building | 2017-02-22 15:45 | 49919.6357 | 280.008
Devonshire Building | 2017-02-22 16:00 | 49919.7058 | 280.008
Devonshire Building | 2017-02-22 16:15 | 49919.7758 | 280.008
Devonshire Building | 2017-02-22 16:30 | 49919.8507 | 299.988
Devonshire Building | 2017-02-22 16:45 | 49920.2507 | 1599.984
Devonshire Building | 2017-02-22 17:00 | 49920.5457 | 1180.008
Devonshire Building | 2017-02-22 17:15 | 49920.5958 | 200.016
Devonshire Building | 2017-02-22 17:30 | 49920.6508 | 219.996
Devonshire Building | 2017-02-22 17:45 | 49920.6957 | 180
Devonshire Building | 2017-02-22 18:00 | 49920.7407 | 180
Devonshire Building | 2017-02-22 18:15 | 49920.7758 | 140.004
Devonshire Building | 2017-02-22 18:30 | 49920.8108 | 140.004
Devonshire Building | 2017-02-22 18:45 | 49920.8458 | 140.004
Devonshire Building | 2017-02-22 19:00 | 49920.8757 | 119.988
Devonshire Building | 2017-02-22 19:15 | 49920.9008 | 100.008
Devonshire Building | 2017-02-22 19:30 | 49920.9207 | 79.992
Devonshire Building | 2017-02-22 19:45 | 49920.9407 | 79.992
Devonshire Building | 2017-02-22 20:00 | 49920.9558 | 60.012
Devonshire Building | 2017-02-22 20:15 | 49920.9757 | 79.992
Devonshire Building | 2017-02-22 20:30 | 49920.9857 | 39.996
Devonshire Building | 2017-02-22 20:45 | 49921.0008 | 60.012
Devonshire Building | 2017-02-22 21:00 | 49921.0108 | 39.996
Devonshire Building | 2017-02-22 21:15 | 49921.0258 | 60.012
Devonshire Building | 2017-02-22 21:30 | 49921.0358 | 39.996
Devonshire Building | 2017-02-22 21:45 | 49921.0458 | 39.996
Devonshire Building | 2017-02-22 22:00 | 49921.5707 | 2099.988
Devonshire Building | 2017-02-22 22:15 | 49921.5707 | 0
Devonshire Building | 2017-02-22 22:30 | 49921.5758 | 20.016
Devonshire Building | 2017-02-22 22:45 | 49921.5808 | 20.016
Devonshire Building | 2017-02-22 23:00 | 49921.5808 | 0
Devonshire Building | 2017-02-22 23:15 | 49921.5858 | 20.016
Devonshire Building | 2017-02-22 23:30 | 49921.5858 | 0
Devonshire Building | 2017-02-22 23:45 | 49921.5908 | 20.016 | 0
Devonshire Building | 2017-02-23 | 49921.5898 | 0
Devonshire Building | 2017-02-23 00:15 | 49921.5948 | 20.016
Devonshire Building | 2017-02-23 00:30 | 49921.5948 | 0
Devonshire Building | 2017-02-23 00:45 | 49921.5998 | 20.016
Devonshire Building | 2017-02-23 01:00 | 49921.5998 | 0
Devonshire Building | 2017-02-23 01:15 | 49921.6049 | 20.016
Devonshire Building | 2017-02-23 01:30 | 49921.6049 | 0
Devonshire Building | 2017-02-23 01:45 | 49921.6099 | 20.016
Devonshire Building | 2017-02-23 02:00 | 49921.6099 | 0
Devonshire Building | 2017-02-23 02:15 | 49921.6149 | 20.016
Devonshire Building | 2017-02-23 02:30 | 49921.6149 | 0
Devonshire Building | 2017-02-23 02:45 | 49921.6199 | 20.016
Devonshire Building | 2017-02-23 03:00 | 49921.6199 | 0
Devonshire Building | 2017-02-23 03:15 | 49921.6249 | 20.016
Devonshire Building | 2017-02-23 03:30 | 49921.6299 | 20.016
Devonshire Building | 2017-02-23 03:45 | 49921.6299 | 0
Devonshire Building | 2017-02-23 04:00 | 49921.6349 | 20.016
Devonshire Building | 2017-02-23 04:15 | 49921.6349 | 0
Devonshire Building | 2017-02-23 04:30 | 49921.6399 | 20.016
Devonshire Building | 2017-02-23 04:45 | 49921.6399 | 0
Devonshire Building | 2017-02-23 05:00 | 49921.6449 | 20.016
Devonshire Building | 2017-02-23 05:15 | 49921.6449 | 0
Devonshire Building | 2017-02-23 05:30 | 49921.6499 | 20.016
Devonshire Building | 2017-02-23 05:45 | 49921.6499 | 0
Devonshire Building | 2017-02-23 06:00 | 49921.6549 | 20.016
Devonshire Building | 2017-02-23 06:15 | 49921.6549 | 0
Devonshire Building | 2017-02-23 06:30 | 49921.6599 | 20.016
Devonshire Building | 2017-02-23 06:45 | 49921.6649 | 20.016
Devonshire Building | 2017-02-23 07:00 | 49921.6699 | 20.016
Devonshire Building | 2017-02-23 07:15 | 49921.6699 | 0
Devonshire Building | 2017-02-23 07:30 | 49921.6749 | 20.016
Devonshire Building | 2017-02-23 07:45 | 49921.6799 | 20.016
Devonshire Building | 2017-02-23 08:00 | 49921.6849 | 20.016
Devonshire Building | 2017-02-23 08:15 | 49921.6899 | 20.016
Devonshire Building | 2017-02-23 08:30 | 49921.6899 | 0
Devonshire Building | 2017-02-23 08:45 | 49921.6999 | 39.996
Devonshire Building | 2017-02-23 09:00 | 49921.7099 | 39.996
Devonshire Building | 2017-02-23 09:15 | 49921.9949 | 1140.012
Devonshire Building | 2017-02-23 09:30 | 49922.0299 | 140.004
Devonshire Building | 2017-02-23 09:45 | 49922.0399 | 39.996
Devonshire Building | 2017-02-23 10:00 | 49922.0499 | 39.996
Devonshire Building | 2017-02-23 10:15 | 49922.0849 | 140.004
Devonshire Building | 2017-02-23 10:30 | 49922.1299 | 180
Devonshire Building | 2017-02-23 10:45 | 49922.1449 | 60.012
Devonshire Building | 2017-02-23 11:00 | 49922.4649 | 1280.016
Devonshire Building | 2017-02-23 11:15 | 49922.4749 | 39.996
Devonshire Building | 2017-02-23 11:30 | 49922.4899 | 60.012
Devonshire Building | 2017-02-23 11:45 | 49922.5099 | 79.992
Devonshire Building | 2017-02-23 12:00 | 49922.5299 | 79.992
Devonshire Building | 2017-02-23 12:15 | 49922.8299 | 1199.988
Devonshire Building | 2017-02-23 12:30 | 49922.9349 | 420.012
Devonshire Building | 2017-02-23 12:45 | 49923.0049 | 280.008
Devonshire Building | 2017-02-23 13:00 | 49923.1049 | 399.996
Devonshire Building | 2017-02-23 13:15 | 49923.2099 | 420.012
Devonshire Building | 2017-02-23 13:30 | 49923.3299 | 479.988
Devonshire Building | 2017-02-23 13:45 | 49923.5099 | 720
Devonshire Building | 2017-02-23 14:00 | 49923.9399 | 1720.008
Devonshire Building | 2017-02-23 14:15 | 49924.0499 | 439.992
Devonshire Building | 2017-02-23 14:30 | 49924.1449 | 380.016
Devonshire Building | 2017-02-23 14:45 | 49924.2299 | 339.984
Devonshire Building | 2017-02-23 15:00 | 49924.3099 | 320.004
Devonshire Building | 2017-02-23 15:15 | 49924.3999 | 360
Devonshire Building | 2017-02-23 15:30 | 49924.4799 | 320.004
Devonshire Building | 2017-02-23 15:45 | 49924.8349 | 1419.984
Devonshire Building | 2017-02-23 16:00 | 49924.8899 | 219.996
Devonshire Building | 2017-02-23 16:15 | 49924.9849 | 380.016
Devonshire Building | 2017-02-23 16:30 | 49925.0949 | 439.992
Devonshire Building | 2017-02-23 16:45 | 49925.1849 | 360
Devonshire Building | 2017-02-23 17:00 | 49925.2699 | 339.984
Devonshire Building | 2017-02-23 17:15 | 49925.3499 | 320.004
Devonshire Building | 2017-02-23 17:30 | 49925.7149 | 1460.016
Devonshire Building | 2017-02-23 17:45 | 49925.7849 | 280.008
Devonshire Building | 2017-02-23 18:00 | 49925.8499 | 259.992
Devonshire Building | 2017-02-23 18:15 | 49925.8999 | 200.016
Devonshire Building | 2017-02-23 18:30 | 49925.9449 | 180
Devonshire Building | 2017-02-23 18:45 | 49925.9799 | 140.004
Devonshire Building | 2017-02-23 19:00 | 49926.0149 | 140.004
Devonshire Building | 2017-02-23 19:15 | 49926.0399 | 100.008
Devonshire Building | 2017-02-23 19:30 | 49926.0699 | 119.988
Devonshire Building | 2017-02-23 19:45 | 49926.0899 | 79.992
Devonshire Building | 2017-02-23 20:00 | 49926.1099 | 79.992
Devonshire Building | 2017-02-23 20:15 | 49926.1299 | 79.992
Devonshire Building | 2017-02-23 20:30 | 49926.1449 | 60.012
Devonshire Building | 2017-02-23 20:45 | 49926.1599 | 60.012
Devonshire Building | 2017-02-23 21:00 | 49926.1749 | 60.012
Devonshire Building | 2017-02-23 21:15 | 49926.1899 | 60.012
Devonshire Building | 2017-02-23 21:30 | 49926.2049 | 60.012
Devonshire Building | 2017-02-23 21:45 | 49926.2199 | 60.012
Devonshire Building | 2017-02-23 22:00 | 49926.2449 | 100.008
Devonshire Building | 2017-02-23 22:15 | 49926.2499 | 20.016
Devonshire Building | 2017-02-23 22:30 | 49926.255 | 20.016
Devonshire Building | 2017-02-23 22:45 | 49926.255 | 0
Devonshire Building | 2017-02-23 23:00 | 49926.26 | 20.016
Devonshire Building | 2017-02-23 23:15 | 49926.265 | 20.016
Devonshire Building | 2017-02-23 23:30 | 49926.265 | 0
Devonshire Building | 2017-02-23 23:45 | 49926.27 | 20.016 | 0
Devonshire Building | 2017-02-24 | 49926.2695 | 0
Devonshire Building | 2017-02-24 00:15 | 49926.2745 | 20.016
Devonshire Building | 2017-02-24 00:30 | 49926.2795 | 20.016
Devonshire Building | 2017-02-24 00:45 | 49926.2795 | 0
Devonshire Building | 2017-02-24 01:00 | 49926.2845 | 20.016
Devonshire Building | 2017-02-24 01:15 | 49926.2845 | 0
Devonshire Building | 2017-02-24 01:30 | 49926.2895 | 20.016
Devonshire Building | 2017-02-24 01:45 | 49926.2945 | 20.016
Devonshire Building | 2017-02-24 02:00 | 49926.2945 | 0
Devonshire Building | 2017-02-24 02:15 | 49926.2996 | 20.016
Devonshire Building | 2017-02-24 02:30 | 49926.2996 | 0
Devonshire Building | 2017-02-24 02:45 | 49926.3046 | 20.016
Devonshire Building | 2017-02-24 03:00 | 49926.3046 | 0
Devonshire Building | 2017-02-24 03:15 | 49926.3096 | 20.016
Devonshire Building | 2017-02-24 03:30 | 49926.3096 | 0
Devonshire Building | 2017-02-24 03:45 | 49926.3146 | 20.016
Devonshire Building | 2017-02-24 04:00 | 49926.3196 | 20.016
Devonshire Building | 2017-02-24 04:15 | 49926.3196 | 0
Devonshire Building | 2017-02-24 04:30 | 49926.3246 | 20.016
Devonshire Building | 2017-02-24 04:45 | 49926.3246 | 0
Devonshire Building | 2017-02-24 05:00 | 49926.3296 | 20.016
Devonshire Building | 2017-02-24 05:15 | 49926.3296 | 0
Devonshire Building | 2017-02-24 05:30 | 49926.3346 | 20.016
Devonshire Building | 2017-02-24 05:45 | 49926.3346 | 0
Devonshire Building | 2017-02-24 06:00 | 49926.3396 | 20.016
Devonshire Building | 2017-02-24 06:15 | 49926.3446 | 20.016
Devonshire Building | 2017-02-24 06:30 | 49926.3446 | 0
Devonshire Building | 2017-02-24 06:45 | 49926.3496 | 20.016
Devonshire Building | 2017-02-24 07:00 | 49926.3546 | 20.016
Devonshire Building | 2017-02-24 07:15 | 49926.3596 | 20.016
Devonshire Building | 2017-02-24 07:30 | 49926.3596 | 0
Devonshire Building | 2017-02-24 07:45 | 49926.3696 | 39.996
Devonshire Building | 2017-02-24 08:00 | 49926.6546 | 1140.012
Devonshire Building | 2017-02-24 08:15 | 49926.6596 | 20.016
Devonshire Building | 2017-02-24 08:30 | 49926.6696 | 39.996
Devonshire Building | 2017-02-24 08:45 | 49926.6746 | 20.016
Devonshire Building | 2017-02-24 09:00 | 49926.6846 | 39.996
Devonshire Building | 2017-02-24 09:15 | 49926.6946 | 39.996
Devonshire Building | 2017-02-24 09:30 | 49926.6996 | 20.016
Devonshire Building | 2017-02-24 09:45 | 49926.7046 | 20.016
Devonshire Building | 2017-02-24 10:00 | 49926.7146 | 39.996
Devonshire Building | 2017-02-24 10:15 | 49926.7396 | 100.008
Devonshire Building | 2017-02-24 10:30 | 49926.9846 | 979.992
Devonshire Building | 2017-02-24 10:45 | 49927.1596 | 699.984
Devonshire Building | 2017-02-24 11:00 | 49927.2796 | 479.988
Devonshire Building | 2017-02-24 11:15 | 49927.3846 | 420.012
Devonshire Building | 2017-02-24 11:30 | 49927.4696 | 339.984
Devonshire Building | 2017-02-24 11:45 | 49927.5396 | 280.008
Devonshire Building | 2017-02-24 12:00 | 49927.6096 | 280.008
Devonshire Building | 2017-02-24 12:15 | 49927.6646 | 219.996
Devonshire Building | 2017-02-24 12:30 | 49927.9796 | 1260
Devonshire Building | 2017-02-24 12:45 | 49928.0046 | 100.008
Devonshire Building | 2017-02-24 13:00 | 49928.0296 | 100.008
Devonshire Building | 2017-02-24 13:15 | 49928.0596 | 119.988
Devonshire Building | 2017-02-24 13:30 | 49928.0996 | 159.984
Devonshire Building | 2017-02-24 13:45 | 49928.1496 | 200.016
Devonshire Building | 2017-02-24 14:00 | 49928.1896 | 159.984
Devonshire Building | 2017-02-24 14:15 | 49928.2396 | 200.016
Devonshire Building | 2017-02-24 14:30 | 49928.2846 | 180
Devonshire Building | 2017-02-24 14:45 | 49928.6196 | 1339.992
Devonshire Building | 2017-02-24 15:00 | 49928.6696 | 200.016
Devonshire Building | 2017-02-24 15:15 | 49928.7146 | 180
Devonshire Building | 2017-02-24 15:30 | 49928.7746 | 240.012
Devonshire Building | 2017-02-24 15:45 | 49928.8546 | 320.004
Devonshire Building | 2017-02-24 16:00 | 49928.9346 | 320.004
Devonshire Building | 2017-02-24 16:15 | 49929.0096 | 299.988
Devonshire Building | 2017-02-24 16:30 | 49929.0796 | 280.008
Devonshire Building | 2017-02-24 16:45 | 49929.4096 | 1320.012
Devonshire Building | 2017-02-24 17:00 | 49929.4596 | 200.016
Devonshire Building | 2017-02-24 17:15 | 49929.5146 | 219.996
Devonshire Building | 2017-02-24 17:30 | 49929.5596 | 180
Devonshire Building | 2017-02-24 17:45 | 49929.6046 | 180
Devonshire Building | 2017-02-24 18:00 | 49929.6496 | 180
Devonshire Building | 2017-02-24 18:15 | 49929.6846 | 140.004
Devonshire Building | 2017-02-24 18:30 | 49929.7196 | 140.004
Devonshire Building | 2017-02-24 18:45 | 49929.7446 | 100.008
Devonshire Building | 2017-02-24 19:00 | 49929.7696 | 100.008
Devonshire Building | 2017-02-24 19:15 | 49929.7946 | 100.008
Devonshire Building | 2017-02-24 19:30 | 49929.8146 | 79.992
Devonshire Building | 2017-02-24 19:45 | 49929.8296 | 60.012
Devonshire Building | 2017-02-24 20:00 | 49929.8446 | 60.012
Devonshire Building | 2017-02-24 20:15 | 49929.8596 | 60.012
Devonshire Building | 2017-02-24 20:30 | 49929.8746 | 60.012
Devonshire Building | 2017-02-24 20:45 | 49929.8846 | 39.996
Devonshire Building | 2017-02-24 21:00 | 49929.8946 | 39.996
Devonshire Building | 2017-02-24 21:15 | 49929.9046 | 39.996
Devonshire Building | 2017-02-24 21:30 | 49929.9146 | 39.996
Devonshire Building | 2017-02-24 21:45 | 49929.9246 | 39.996
Devonshire Building | 2017-02-24 22:00 | 49929.9496 | 100.008
Devonshire Building | 2017-02-24 22:15 | 49929.9546 | 20.016
Devonshire Building | 2017-02-24 22:30 | 49929.9546 | 0
Devonshire Building | 2017-02-24 22:45 | 49929.9596 | 20.016
Devonshire Building | 2017-02-24 23:00 | 49929.9647 | 20.016
Devonshire Building | 2017-02-24 23:15 | 49929.9647 | 0
Devonshire Building | 2017-02-24 23:30 | 49929.9697 | 20.016
Devonshire Building | 2017-02-24 23:45 | 49929.9697 | 0 | 0
Devonshire Building | 2017-02-25 | 49929.9766 | 20.016
Devonshire Building | 2017-02-25 00:15 | 49929.9766 | 0
Devonshire Building | 2017-02-25 00:30 | 49929.9816 | 20.016
Devonshire Building | 2017-02-25 00:45 | 49929.9816 | 0
Devonshire Building | 2017-02-25 01:00 | 49929.9866 | 20.016
Devonshire Building | 2017-02-25 01:15 | 49929.9866 | 0
Devonshire Building | 2017-02-25 01:30 | 49929.9916 | 20.016
Devonshire Building | 2017-02-25 01:45 | 49929.9916 | 0
Devonshire Building | 2017-02-25 02:00 | 49929.9966 | 20.016
Devonshire Building | 2017-02-25 02:15 | 49930.0016 | 20.016
Devonshire Building | 2017-02-25 02:30 | 49930.0016 | 0
Devonshire Building | 2017-02-25 02:45 | 49930.0066 | 20.016
Devonshire Building | 2017-02-25 03:00 | 49930.0066 | 0
Devonshire Building | 2017-02-25 03:15 | 49930.0116 | 20.016
Devonshire Building | 2017-02-25 03:30 | 49930.0116 | 0
Devonshire Building | 2017-02-25 03:45 | 49930.0166 | 20.016
Devonshire Building | 2017-02-25 04:00 | 49930.0166 | 0
Devonshire Building | 2017-02-25 04:15 | 49930.0216 | 20.016
Devonshire Building | 2017-02-25 04:30 | 49930.0216 | 0
Devonshire Building | 2017-02-25 04:45 | 49930.0266 | 20.016
Devonshire Building | 2017-02-25 05:00 | 49930.0266 | 0
Devonshire Building | 2017-02-25 05:15 | 49930.0316 | 20.016
Devonshire Building | 2017-02-25 05:30 | 49930.0316 | 0
Devonshire Building | 2017-02-25 05:45 | 49930.0366 | 20.016
Devonshire Building | 2017-02-25 06:00 | 49930.0366 | 0
Devonshire Building | 2017-02-25 06:15 | 49930.0416 | 20.016
Devonshire Building | 2017-02-25 06:30 | 49930.0416 | 0
Devonshire Building | 2017-02-25 06:45 | 49930.0466 | 20.016
Devonshire Building | 2017-02-25 07:00 | 49930.0466 | 0
Devonshire Building | 2017-02-25 07:15 | 49930.0516 | 20.016
Devonshire Building | 2017-02-25 07:30 | 49930.1316 | 320.004
Devonshire Building | 2017-02-25 07:45 | 49930.3066 | 699.984
Devonshire Building | 2017-02-25 08:00 | 49930.3116 | 20.016
Devonshire Building | 2017-02-25 08:15 | 49930.3116 | 0
Devonshire Building | 2017-02-25 08:30 | 49930.3116 | 0
Devonshire Building | 2017-02-25 08:45 | 49930.3166 | 20.016
Devonshire Building | 2017-02-25 09:00 | 49930.3166 | 0
Devonshire Building | 2017-02-25 09:15 | 49930.3216 | 20.016
Devonshire Building | 2017-02-25 09:30 | 49930.3216 | 0
Devonshire Building | 2017-02-25 09:45 | 49930.3266 | 20.016
Devonshire Building | 2017-02-25 10:00 | 49930.3266 | 0
Devonshire Building | 2017-02-25 10:15 | 49930.3316 | 20.016
Devonshire Building | 2017-02-25 10:30 | 49930.3316 | 0
Devonshire Building | 2017-02-25 10:45 | 49930.3366 | 20.016
Devonshire Building | 2017-02-25 11:00 | 49930.3416 | 20.016
Devonshire Building | 2017-02-25 11:15 | 49930.3416 | 0
Devonshire Building | 2017-02-25 11:30 | 49930.3466 | 20.016
Devonshire Building | 2017-02-25 11:45 | 49930.3466 | 0
Devonshire Building | 2017-02-25 12:00 | 49930.3517 | 20.016
Devonshire Building | 2017-02-25 12:15 | 49930.3517 | 0
Devonshire Building | 2017-02-25 12:30 | 49930.3567 | 20.016
Devonshire Building | 2017-02-25 12:45 | 49930.3567 | 0
Devonshire Building | 2017-02-25 13:00 | 49930.3617 | 20.016
Devonshire Building | 2017-02-25 13:15 | 49930.3617 | 0
Devonshire Building | 2017-02-25 13:30 | 49930.3667 | 20.016
Devonshire Building | 2017-02-25 13:45 | 49930.3867 | 79.992
Devonshire Building | 2017-02-25 14:00 | 49930.4067 | 79.992
Devonshire Building | 2017-02-25 14:15 | 49930.4267 | 79.992
Devonshire Building | 2017-02-25 14:30 | 49930.4467 | 79.992
Devonshire Building | 2017-02-25 14:45 | 49930.4617 | 60.012
Devonshire Building | 2017-02-25 15:00 | 49930.4817 | 79.992
Devonshire Building | 2017-02-25 15:15 | 49930.5017 | 79.992
Devonshire Building | 2017-02-25 15:30 | 49930.5217 | 79.992
Devonshire Building | 2017-02-25 15:45 | 49930.5367 | 60.012
Devonshire Building | 2017-02-25 16:00 | 49930.5467 | 39.996
Devonshire Building | 2017-02-25 16:15 | 49930.5517 | 20.016
Devonshire Building | 2017-02-25 16:30 | 49930.5517 | 0
Devonshire Building | 2017-02-25 16:45 | 49930.5567 | 20.016
Devonshire Building | 2017-02-25 17:00 | 49930.5567 | 0
Devonshire Building | 2017-02-25 17:15 | 49930.5617 | 20.016
Devonshire Building | 2017-02-25 17:30 | 49930.5617 | 0
Devonshire Building | 2017-02-25 17:45 | 49930.5667 | 20.016
Devonshire Building | 2017-02-25 18:00 | 49930.5667 | 0
Devonshire Building | 2017-02-25 18:15 | 49930.5717 | 20.016
Devonshire Building | 2017-02-25 18:30 | 49930.5717 | 0
Devonshire Building | 2017-02-25 18:45 | 49930.5767 | 20.016
Devonshire Building | 2017-02-25 19:00 | 49930.5767 | 0
Devonshire Building | 2017-02-25 19:15 | 49930.5817 | 20.016
Devonshire Building | 2017-02-25 19:30 | 49930.5817 | 0
Devonshire Building | 2017-02-25 19:45 | 49930.5867 | 20.016
Devonshire Building | 2017-02-25 20:00 | 49930.5867 | 0
Devonshire Building | 2017-02-25 20:15 | 49930.5917 | 20.016
Devonshire Building | 2017-02-25 20:30 | 49930.5917 | 0
Devonshire Building | 2017-02-25 20:45 | 49930.5967 | 20.016
Devonshire Building | 2017-02-25 21:00 | 49930.5967 | 0
Devonshire Building | 2017-02-25 21:15 | 49930.6017 | 20.016
Devonshire Building | 2017-02-25 21:30 | 49930.6017 | 0
Devonshire Building | 2017-02-25 21:45 | 49930.6067 | 20.016
Devonshire Building | 2017-02-25 22:00 | 49930.6317 | 100.008
Devonshire Building | 2017-02-25 22:15 | 49930.6367 | 20.016
Devonshire Building | 2017-02-25 22:30 | 49930.6367 | 0
Devonshire Building | 2017-02-25 22:45 | 49930.6417 | 20.016
Devonshire Building | 2017-02-25 23:00 | 49930.6417 | 0
Devonshire Building | 2017-02-25 23:15 | 49930.6467 | 20.016
Devonshire Building | 2017-02-25 23:30 | 49930.6467 | 0
Devonshire Building | 2017-02-25 23:45 | 49930.6517 | 20.016 | 0
Devonshire Building | 2017-02-26 | 49930.6484 | 0
Devonshire Building | 2017-02-26 00:15 | 49930.6534 | 20.016
Devonshire Building | 2017-02-26 00:30 | 49930.6534 | 0
Devonshire Building | 2017-02-26 00:45 | 49930.6584 | 20.016
Devonshire Building | 2017-02-26 01:00 | 49930.6584 | 0
Devonshire Building | 2017-02-26 01:15 | 49930.6635 | 20.016
Devonshire Building | 2017-02-26 01:30 | 49930.6635 | 0
Devonshire Building | 2017-02-26 01:45 | 49930.6685 | 20.016
Devonshire Building | 2017-02-26 02:00 | 49930.6685 | 0
Devonshire Building | 2017-02-26 02:15 | 49930.6735 | 20.016
Devonshire Building | 2017-02-26 02:30 | 49930.6735 | 0
Devonshire Building | 2017-02-26 02:45 | 49930.6785 | 20.016
Devonshire Building | 2017-02-26 03:00 | 49930.6785 | 0
Devonshire Building | 2017-02-26 03:15 | 49930.6835 | 20.016
Devonshire Building | 2017-02-26 03:30 | 49930.6835 | 0
Devonshire Building | 2017-02-26 03:45 | 49930.6885 | 20.016
Devonshire Building | 2017-02-26 04:00 | 49930.6885 | 0
Devonshire Building | 2017-02-26 04:15 | 49930.6935 | 20.016
Devonshire Building | 2017-02-26 04:30 | 49930.6935 | 0
Devonshire Building | 2017-02-26 04:45 | 49930.6985 | 20.016
Devonshire Building | 2017-02-26 05:00 | 49930.6985 | 0
Devonshire Building | 2017-02-26 05:15 | 49930.7035 | 20.016
Devonshire Building | 2017-02-26 05:30 | 49930.7035 | 0
Devonshire Building | 2017-02-26 05:45 | 49930.7035 | 0
Devonshire Building | 2017-02-26 06:00 | 49930.7085 | 20.016
Devonshire Building | 2017-02-26 06:15 | 49930.7085 | 0
Devonshire Building | 2017-02-26 06:30 | 49930.9135 | 820.008
Devonshire Building | 2017-02-26 06:45 | 49930.9685 | 219.996
Devonshire Building | 2017-02-26 07:00 | 49930.9735 | 20.016
Devonshire Building | 2017-02-26 07:15 | 49930.9735 | 0
Devonshire Building | 2017-02-26 07:30 | 49930.9785 | 20.016
Devonshire Building | 2017-02-26 07:45 | 49930.9785 | 0
Devonshire Building | 2017-02-26 08:00 | 49930.9785 | 0
Devonshire Building | 2017-02-26 08:15 | 49930.9835 | 20.016
Devonshire Building | 2017-02-26 08:30 | 49930.9835 | 0
Devonshire Building | 2017-02-26 08:45 | 49930.9885 | 20.016
Devonshire Building | 2017-02-26 09:00 | 49930.9885 | 0
Devonshire Building | 2017-02-26 09:15 | 49930.9935 | 20.016
Devonshire Building | 2017-02-26 09:30 | 49930.9935 | 0
Devonshire Building | 2017-02-26 09:45 | 49930.9985 | 20.016
Devonshire Building | 2017-02-26 10:00 | 49930.9985 | 0
Devonshire Building | 2017-02-26 10:15 | 49931.0035 | 20.016
Devonshire Building | 2017-02-26 10:30 | 49931.0035 | 0
Devonshire Building | 2017-02-26 10:45 | 49931.0085 | 20.016
Devonshire Building | 2017-02-26 11:00 | 49931.0085 | 0
Devonshire Building | 2017-02-26 11:15 | 49931.0135 | 20.016
Devonshire Building | 2017-02-26 11:30 | 49931.0135 | 0
Devonshire Building | 2017-02-26 11:45 | 49931.0235 | 39.996
Devonshire Building | 2017-02-26 12:00 | 49931.0285 | 20.016
Devonshire Building | 2017-02-26 12:15 | 49931.0285 | 0
Devonshire Building | 2017-02-26 12:30 | 49931.0335 | 20.016
Devonshire Building | 2017-02-26 12:45 | 49931.0335 | 0
Devonshire Building | 2017-02-26 13:00 | 49931.0385 | 20.016
Devonshire Building | 2017-02-26 13:15 | 49931.0385 | 0
Devonshire Building | 2017-02-26 13:30 | 49931.0485 | 39.996
Devonshire Building | 2017-02-26 13:45 | 49931.0685 | 79.992
Devonshire Building | 2017-02-26 14:00 | 49931.0885 | 79.992
Devonshire Building | 2017-02-26 14:15 | 49931.1035 | 60.012
Devonshire Building | 2017-02-26 14:30 | 49931.1235 | 79.992
Devonshire Building | 2017-02-26 14:45 | 49931.1435 | 79.992
Devonshire Building | 2017-02-26 15:00 | 49931.1635 | 79.992
Devonshire Building | 2017-02-26 15:15 | 49931.1835 | 79.992
Devonshire Building | 2017-02-26 15:30 | 49931.1985 | 60.012
Devonshire Building | 2017-02-26 15:45 | 49931.2185 | 79.992
Devonshire Building | 2017-02-26 16:00 | 49931.2335 | 60.012
Devonshire Building | 2017-02-26 16:15 | 49931.2335 | 0
Devonshire Building | 2017-02-26 16:30 | 49931.2385 | 20.016
Devonshire Building | 2017-02-26 16:45 | 49931.2385 | 0
Devonshire Building | 2017-02-26 17:00 | 49931.2435 | 20.016
Devonshire Building | 2017-02-26 17:15 | 49931.2435 | 0
Devonshire Building | 2017-02-26 17:30 | 49931.2485 | 20.016
Devonshire Building | 2017-02-26 17:45 | 49931.2485 | 0
Devonshire Building | 2017-02-26 18:00 | 49931.2535 | 20.016
Devonshire Building | 2017-02-26 18:15 | 49931.2535 | 0
Devonshire Building | 2017-02-26 18:30 | 49931.2585 | 20.016
Devonshire Building | 2017-02-26 18:45 | 49931.2585 | 0
Devonshire Building | 2017-02-26 19:00 | 49931.2636 | 20.016
Devonshire Building | 2017-02-26 19:15 | 49931.2636 | 0
Devonshire Building | 2017-02-26 19:30 | 49931.2686 | 20.016
Devonshire Building | 2017-02-26 19:45 | 49931.2686 | 0
Devonshire Building | 2017-02-26 20:00 | 49931.2736 | 20.016
Devonshire Building | 2017-02-26 20:15 | 49931.2736 | 0
Devonshire Building | 2017-02-26 20:30 | 49931.2786 | 20.016
Devonshire Building | 2017-02-26 20:45 | 49931.2786 | 0
Devonshire Building | 2017-02-26 21:00 | 49931.2836 | 20.016
Devonshire Building | 2017-02-26 21:15 | 49931.2886 | 20.016
Devonshire Building | 2017-02-26 21:30 | 49931.2886 | 0
Devonshire Building | 2017-02-26 21:45 | 49931.2936 | 20.016
Devonshire Building | 2017-02-26 22:00 | 49931.3186 | 100.008
Devonshire Building | 2017-02-26 22:15 | 49931.3186 | 0
Devonshire Building | 2017-02-26 22:30 | 49931.3236 | 20.016
Devonshire Building | 2017-02-26 22:45 | 49931.3236 | 0
Devonshire Building | 2017-02-26 23:00 | 49931.3286 | 20.016
Devonshire Building | 2017-02-26 23:15 | 49931.3286 | 0
Devonshire Building | 2017-02-26 23:30 | 49931.3336 | 20.016
Devonshire Building | 2017-02-26 23:45 | 49931.3336 | 0 | 0
Devonshire Building | 2017-02-27 | 49931.3398 | 20.016
Devonshire Building | 2017-02-27 00:15 | 49931.3398 | 0
Devonshire Building | 2017-02-27 00:30 | 49931.3448 | 20.016
Devonshire Building | 2017-02-27 00:45 | 49931.3448 | 0
Devonshire Building | 2017-02-27 01:00 | 49931.3498 | 20.016
Devonshire Building | 2017-02-27 01:15 | 49931.3498 | 0
Devonshire Building | 2017-02-27 01:30 | 49931.3549 | 20.016
Devonshire Building | 2017-02-27 01:45 | 49931.3549 | 0
Devonshire Building | 2017-02-27 02:00 | 49931.3599 | 20.016
Devonshire Building | 2017-02-27 02:15 | 49931.3599 | 0
Devonshire Building | 2017-02-27 02:30 | 49931.3649 | 20.016
Devonshire Building | 2017-02-27 02:45 | 49931.3649 | 0
Devonshire Building | 2017-02-27 03:00 | 49931.3699 | 20.016
Devonshire Building | 2017-02-27 03:15 | 49931.3699 | 0
Devonshire Building | 2017-02-27 03:30 | 49931.3749 | 20.016
Devonshire Building | 2017-02-27 03:45 | 49931.3749 | 0
Devonshire Building | 2017-02-27 04:00 | 49931.3799 | 20.016
Devonshire Building | 2017-02-27 04:15 | 49931.3799 | 0
Devonshire Building | 2017-02-27 04:30 | 49931.3849 | 20.016
Devonshire Building | 2017-02-27 04:45 | 49931.3849 | 0
Devonshire Building | 2017-02-27 05:00 | 49931.3899 | 20.016
Devonshire Building | 2017-02-27 05:15 | 49931.3899 | 0
Devonshire Building | 2017-02-27 05:30 | 49931.3949 | 20.016
Devonshire Building | 2017-02-27 05:45 | 49931.3949 | 0
Devonshire Building | 2017-02-27 06:00 | 49931.3999 | 20.016
Devonshire Building | 2017-02-27 06:15 | 49931.3999 | 0
Devonshire Building | 2017-02-27 06:30 | 49931.4049 | 20.016
Devonshire Building | 2017-02-27 06:45 | 49931.4099 | 20.016
Devonshire Building | 2017-02-27 07:00 | 49931.4149 | 20.016
Devonshire Building | 2017-02-27 07:15 | 49931.4149 | 0
Devonshire Building | 2017-02-27 07:30 | 49931.6949 | 1119.996
Devonshire Building | 2017-02-27 07:45 | 49931.6999 | 20.016
Devonshire Building | 2017-02-27 08:00 | 49931.7099 | 39.996
Devonshire Building | 2017-02-27 08:15 | 49931.7199 | 39.996
Devonshire Building | 2017-02-27 08:30 | 49931.7199 | 0
Devonshire Building | 2017-02-27 08:45 | 49931.7449 | 100.008
Devonshire Building | 2017-02-27 09:00 | 49931.7499 | 20.016
Devonshire Building | 2017-02-27 09:15 | 49931.7649 | 60.012
Devonshire Building | 2017-02-27 09:30 | 49931.7749 | 39.996
Devonshire Building | 2017-02-27 09:45 | 49931.8599 | 339.984
Devonshire Building | 2017-02-27 10:00 | 49932.2699 | 1640.016
Devonshire Building | 2017-02-27 10:15 | 49932.4999 | 920.016
Devonshire Building | 2017-02-27 10:30 | 49932.7749 | 1100.016
Devonshire Building | 2017-02-27 10:45 | 49932.9649 | 759.996
Devonshire Building | 2017-02-27 11:00 | 49933.1549 | 759.996
Devonshire Building | 2017-02-27 11:15 | 49933.4199 | 1059.984
Devonshire Building | 2017-02-27 11:30 | 49933.4799 | 240.012
Devonshire Building | 2017-02-27 11:45 | 49933.5399 | 240.012
Devonshire Building | 2017-02-27 12:00 | 49933.6149 | 299.988
Devonshire Building | 2017-02-27 12:15 | 49933.9749 | 1440
Devonshire Building | 2017-02-27 12:30 | 49934.0499 | 299.988
Devonshire Building | 2017-02-27 12:45 | 49934.1199 | 280.008
Devonshire Building | 2017-02-27 13:00 | 49934.1949 | 299.988
Devonshire Building | 2017-02-27 13:15 | 49934.2649 | 280.008
Devonshire Building | 2017-02-27 13:30 | 49934.3399 | 299.988
Devonshire Building | 2017-02-27 13:45 | 49934.7199 | 1519.992
Devonshire Building | 2017-02-27 14:00 | 49934.7649 | 180
Devonshire Building | 2017-02-27 14:15 | 49934.8049 | 159.984
Devonshire Building | 2017-02-27 14:30 | 49934.8449 | 159.984
Devonshire Building | 2017-02-27 14:45 | 49934.8899 | 180
Devonshire Building | 2017-02-27 15:00 | 49935.2249 | 1339.992
Devonshire Building | 2017-02-27 15:15 | 49935.2599 | 140.004
Devonshire Building | 2017-02-27 15:30 | 49935.2999 | 159.984
Devonshire Building | 2017-02-27 15:45 | 49935.3349 | 140.004
Devonshire Building | 2017-02-27 16:00 | 49935.3749 | 159.984
Devonshire Building | 2017-02-27 16:15 | 49935.4199 | 180
Devonshire Building | 2017-02-27 16:30 | 49935.4649 | 180
Devonshire Building | 2017-02-27 16:45 | 49935.4949 | 119.988
Devonshire Building | 2017-02-27 17:00 | 49935.8249 | 1320.012
Devonshire Building | 2017-02-27 17:15 | 49935.8549 | 119.988
Devonshire Building | 2017-02-27 17:30 | 49935.8799 | 100.008
Devonshire Building | 2017-02-27 17:45 | 49935.9099 | 119.988
Devonshire Building | 2017-02-27 18:00 | 49935.9399 | 119.988
Devonshire Building | 2017-02-27 18:15 | 49935.9699 | 119.988
Devonshire Building | 2017-02-27 18:30 | 49935.9949 | 100.008
Devonshire Building | 2017-02-27 18:45 | 49936.0249 | 119.988
Devonshire Building | 2017-02-27 19:00 | 49936.0499 | 100.008
Devonshire Building | 2017-02-27 19:15 | 49936.0749 | 100.008
Devonshire Building | 2017-02-27 19:30 | 49936.0999 | 100.008
Devonshire Building | 2017-02-27 19:45 | 49936.1199 | 79.992
Devonshire Building | 2017-02-27 20:00 | 49936.1399 | 79.992
Devonshire Building | 2017-02-27 20:15 | 49936.1599 | 79.992
Devonshire Building | 2017-02-27 20:30 | 49936.1749 | 60.012
Devonshire Building | 2017-02-27 20:45 | 49936.1949 | 79.992
Devonshire Building | 2017-02-27 21:00 | 49936.2099 | 60.012
Devonshire Building | 2017-02-27 21:15 | 49936.2249 | 60.012
Devonshire Building | 2017-02-27 21:30 | 49936.2399 | 60.012
Devonshire Building | 2017-02-27 21:45 | 49936.2499 | 39.996
Devonshire Building | 2017-02-27 22:00 | 49936.2799 | 119.988
Devonshire Building | 2017-02-27 22:15 | 49936.2849 | 20.016
Devonshire Building | 2017-02-27 22:30 | 49936.2899 | 20.016
Devonshire Building | 2017-02-27 22:45 | 49936.2899 | 0
Devonshire Building | 2017-02-27 23:00 | 49936.2949 | 20.016
Devonshire Building | 2017-02-27 23:15 | 49936.2999 | 20.016
Devonshire Building | 2017-02-27 23:30 | 49936.2999 | 0
Devonshire Building | 2017-02-27 23:45 | 49936.3049 | 20.016 | 0
Devonshire Building | 2017-02-28 | 49936.3086 | 20.016
Devonshire Building | 2017-02-28 00:15 | 49936.3136 | 20.016
Devonshire Building | 2017-02-28 00:30 | 49936.3136 | 0
Devonshire Building | 2017-02-28 00:45 | 49936.3186 | 20.016
Devonshire Building | 2017-02-28 01:00 | 49936.3236 | 20.016
Devonshire Building | 2017-02-28 01:15 | 49936.3236 | 0
Devonshire Building | 2017-02-28 01:30 | 49936.3286 | 20.016
Devonshire Building | 2017-02-28 01:45 | 49936.3336 | 20.016
Devonshire Building | 2017-02-28 02:00 | 49936.3336 | 0
Devonshire Building | 2017-02-28 02:15 | 49936.3386 | 20.016
Devonshire Building | 2017-02-28 02:30 | 49936.3386 | 0
Devonshire Building | 2017-02-28 02:45 | 49936.3436 | 20.016
Devonshire Building | 2017-02-28 03:00 | 49936.3486 | 20.016
Devonshire Building | 2017-02-28 03:15 | 49936.3486 | 0
Devonshire Building | 2017-02-28 03:30 | 49936.3536 | 20.016
Devonshire Building | 2017-02-28 03:45 | 49936.3586 | 20.016
Devonshire Building | 2017-02-28 04:00 | 49936.3586 | 0
Devonshire Building | 2017-02-28 04:15 | 49936.3636 | 20.016
Devonshire Building | 2017-02-28 04:30 | 49936.3636 | 0
Devonshire Building | 2017-02-28 04:45 | 49936.3686 | 20.016
Devonshire Building | 2017-02-28 05:00 | 49936.3736 | 20.016
Devonshire Building | 2017-02-28 05:15 | 49936.3736 | 0
Devonshire Building | 2017-02-28 05:30 | 49936.3786 | 20.016
Devonshire Building | 2017-02-28 05:45 | 49936.3786 | 0
Devonshire Building | 2017-02-28 06:00 | 49936.3837 | 20.016
Devonshire Building | 2017-02-28 06:15 | 49936.3887 | 20.016
Devonshire Building | 2017-02-28 06:30 | 49936.3937 | 20.016
Devonshire Building | 2017-02-28 06:45 | 49936.3937 | 0
Devonshire Building | 2017-02-28 07:00 | 49936.3987 | 20.016
Devonshire Building | 2017-02-28 07:15 | 49936.4037 | 20.016
Devonshire Building | 2017-02-28 07:30 | 49936.7137 | 1239.984
Devonshire Building | 2017-02-28 07:45 | 49936.7237 | 39.996
Devonshire Building | 2017-02-28 08:00 | 49936.7287 | 20.016
Devonshire Building | 2017-02-28 08:15 | 49936.7337 | 20.016
Devonshire Building | 2017-02-28 08:30 | 49936.7387 | 20.016
Devonshire Building | 2017-02-28 08:45 | 49936.7437 | 20.016
Devonshire Building | 2017-02-28 09:00 | 49936.7587 | 60.012
Devonshire Building | 2017-02-28 09:15 | 49936.7837 | 100.008
Devonshire Building | 2017-02-28 09:30 | 49936.8087 | 100.008
Devonshire Building | 2017-02-28 09:45 | 49936.8287 | 79.992
Devonshire Building | 2017-02-28 10:00 | 49936.8537 | 100.008
Devonshire Building | 2017-02-28 10:15 | 49937.1637 | 1239.984
Devonshire Building | 2017-02-28 10:30 | 49937.1937 | 119.988
Devonshire Building | 2017-02-28 10:45 | 49937.2287 | 140.004
Devonshire Building | 2017-02-28 11:00 | 49937.2587 | 119.988
Devonshire Building | 2017-02-28 11:15 | 49937.3087 | 200.016
Devonshire Building | 2017-02-28 11:30 | 49937.5437 | 939.996
Devonshire Building | 2017-02-28 11:45 | 49937.7087 | 659.988
Devonshire Building | 2017-02-28 12:00 | 49937.7887 | 320.004
Devonshire Building | 2017-02-28 12:15 | 49937.8587 | 280.008
Devonshire Building | 2017-02-28 12:30 | 49937.9237 | 259.992
Devonshire Building | 2017-02-28 12:45 | 49937.9887 | 259.992
Devonshire Building | 2017-02-28 13:00 | 49938.0537 | 259.992
Devonshire Building | 2017-02-28 13:15 | 49938.3987 | 1379.988
Devonshire Building | 2017-02-28 13:30 | 49938.4537 | 219.996
Devonshire Building | 2017-02-28 13:45 | 49938.5137 | 240.012
Devonshire Building | 2017-02-28 14:00 | 49938.5737 | 240.012
Devonshire Building | 2017-02-28 14:15 | 49938.6387 | 259.992
Devonshire Building | 2017-02-28 14:30 | 49938.6987 | 240.012
Devonshire Building | 2017-02-28 14:45 | 49938.7537 | 219.996
Devonshire Building | 2017-02-28 15:00 | 49939.0987 | 1379.988
Devonshire Building | 2017-02-28 15:15 | 49939.1437 | 180
Devonshire Building | 2017-02-28 15:30 | 49939.1887 | 180
Devonshire Building | 2017-02-28 15:45 | 49939.2487 | 240.012
Devonshire Building | 2017-02-28 16:00 | 49939.3037 | 219.996
Devonshire Building | 2017-02-28 16:15 | 49939.3587 | 219.996
Devonshire Building | 2017-02-28 16:30 | 49939.7037 | 1379.988
Devonshire Building | 2017-02-28 16:45 | 49939.7687 | 259.992
Devonshire Building | 2017-02-28 17:00 | 49939.8387 | 280.008
Devonshire Building | 2017-02-28 17:15 | 49939.8987 | 240.012
Devonshire Building | 2017-02-28 17:30 | 49939.9537 | 219.996
Devonshire Building | 2017-02-28 17:45 | 49939.9987 | 180
Devonshire Building | 2017-02-28 18:00 | 49940.0437 | 180
Devonshire Building | 2017-02-28 18:15 | 49940.0787 | 140.004
Devonshire Building | 2017-02-28 18:30 | 49940.1087 | 119.988
Devonshire Building | 2017-02-28 18:45 | 49940.1337 | 100.008
Devonshire Building | 2017-02-28 19:00 | 49940.1537 | 79.992
Devonshire Building | 2017-02-28 19:15 | 49940.2687 | 460.008
Devonshire Building | 2017-02-28 19:30 | 49940.4437 | 699.984
Devonshire Building | 2017-02-28 19:45 | 49940.4537 | 39.996
Devonshire Building | 2017-02-28 20:00 | 49940.4587 | 20.016
Devonshire Building | 2017-02-28 20:15 | 49940.4687 | 39.996
Devonshire Building | 2017-02-28 20:30 | 49940.4737 | 20.016
Devonshire Building | 2017-02-28 20:45 | 49940.4787 | 20.016
Devonshire Building | 2017-02-28 21:00 | 49940.4887 | 39.996
Devonshire Building | 2017-02-28 21:15 | 49940.4937 | 20.016
Devonshire Building | 2017-02-28 21:30 | 49940.4987 | 20.016
Devonshire Building | 2017-02-28 21:45 | 49940.5087 | 39.996
Devonshire Building | 2017-02-28 22:00 | 49940.5187 | 39.996
Devonshire Building | 2017-02-28 22:15 | 49940.5237 | 20.016
Devonshire Building | 2017-02-28 22:30 | 49940.5287 | 20.016
Devonshire Building | 2017-02-28 22:45 | 49940.5387 | 39.996
Devonshire Building | 2017-02-28 23:00 | 49940.5437 | 20.016
Devonshire Building | 2017-02-28 23:15 | 49940.5537 | 39.996
Devonshire Building | 2017-02-28 23:30 | 49940.5587 | 20.016
Devonshire Building | 2017-02-28 23:45 | 49940.5637 | 20.016 | 0
Devonshire Building | 2017-03-01 | 49940.5703 | 20.016
Devonshire Building | 2017-03-01 00:15 | 49940.5803 | 39.996
Devonshire Building | 2017-03-01 00:30 | 49940.5853 | 20.016
Devonshire Building | 2017-03-01 00:45 | 49940.5903 | 20.016
Devonshire Building | 2017-03-01 01:00 | 49940.5953 | 20.016
Devonshire Building | 2017-03-01 01:15 | 49940.6003 | 20.016
Devonshire Building | 2017-03-01 01:30 | 49940.6053 | 20.016
Devonshire Building | 2017-03-01 01:45 | 49940.6103 | 20.016
Devonshire Building | 2017-03-01 02:00 | 49940.6153 | 20.016
Devonshire Building | 2017-03-01 02:15 | 49940.6203 | 20.016
Devonshire Building | 2017-03-01 02:30 | 49940.6253 | 20.016
Devonshire Building | 2017-03-01 02:45 | 49940.6303 | 20.016
Devonshire Building | 2017-03-01 03:00 | 49940.6354 | 20.016
Devonshire Building | 2017-03-01 03:15 | 49940.6404 | 20.016
Devonshire Building | 2017-03-01 03:30 | 49940.6454 | 20.016
Devonshire Building | 2017-03-01 03:45 | 49940.6504 | 20.016
Devonshire Building | 2017-03-01 04:00 | 49940.6554 | 20.016
Devonshire Building | 2017-03-01 04:15 | 49940.6604 | 20.016
Devonshire Building | 2017-03-01 04:30 | 49940.6604 | 0
Devonshire Building | 2017-03-01 04:45 | 49940.6654 | 20.016
Devonshire Building | 2017-03-01 05:00 | 49940.6704 | 20.016
Devonshire Building | 2017-03-01 05:15 | 49940.6754 | 20.016
Devonshire Building | 2017-03-01 05:30 | 49940.6804 | 20.016
Devonshire Building | 2017-03-01 05:45 | 49940.6804 | 0
Devonshire Building | 2017-03-01 06:00 | 49940.6854 | 20.016
Devonshire Building | 2017-03-01 06:15 | 49940.6904 | 20.016
Devonshire Building | 2017-03-01 06:30 | 49940.6954 | 20.016
Devonshire Building | 2017-03-01 06:45 | 49940.7004 | 20.016
Devonshire Building | 2017-03-01 07:00 | 49940.7054 | 20.016
Devonshire Building | 2017-03-01 07:15 | 49940.7104 | 20.016
Devonshire Building | 2017-03-01 07:30 | 49940.7154 | 20.016
Devonshire Building | 2017-03-01 07:45 | 49940.7354 | 79.992
Devonshire Building | 2017-03-01 08:00 | 49940.7554 | 79.992
Devonshire Building | 2017-03-01 08:15 | 49940.7804 | 100.008
Devonshire Building | 2017-03-01 08:30 | 49940.8104 | 119.988
Devonshire Building | 2017-03-01 08:45 | 49940.8454 | 140.004
Devonshire Building | 2017-03-01 09:00 | 49941.1554 | 1239.984
Devonshire Building | 2017-03-01 09:15 | 49941.1904 | 140.004
Devonshire Building | 2017-03-01 09:30 | 49941.2154 | 100.008
Devonshire Building | 2017-03-01 09:45 | 49941.2554 | 159.984
Devonshire Building | 2017-03-01 10:00 | 49941.3104 | 219.996
Devonshire Building | 2017-03-01 10:15 | 49941.3854 | 299.988
Devonshire Building | 2017-03-01 10:30 | 49941.7704 | 1540.008
Devonshire Building | 2017-03-01 10:45 | 49941.8554 | 339.984
Devonshire Building | 2017-03-01 11:00 | 49941.9304 | 299.988
Devonshire Building | 2017-03-01 11:15 | 49942.0054 | 299.988
Devonshire Building | 2017-03-01 11:30 | 49942.0804 | 299.988
Devonshire Building | 2017-03-01 11:45 | 49942.4504 | 1479.996
Devonshire Building | 2017-03-01 12:00 | 49942.5154 | 259.992
Devonshire Building | 2017-03-01 12:15 | 49942.5804 | 259.992
Devonshire Building | 2017-03-01 12:30 | 49942.6504 | 280.008
Devonshire Building | 2017-03-01 12:45 | 49942.7104 | 240.012
Devonshire Building | 2017-03-01 13:00 | 49943.0454 | 1339.992
Devonshire Building | 2017-03-01 13:15 | 49943.1354 | 360
Devonshire Building | 2017-03-01 13:30 | 49943.2304 | 380.016
Devonshire Building | 2017-03-01 13:45 | 49943.3254 | 380.016
Devonshire Building | 2017-03-01 14:00 | 49943.4054 | 320.004
Devonshire Building | 2017-03-01 14:15 | 49943.4854 | 320.004
Devonshire Building | 2017-03-01 14:30 | 49943.5604 | 299.988
Devonshire Building | 2017-03-01 14:45 | 49943.9004 | 1360.008
Devonshire Building | 2017-03-01 15:00 | 49943.9754 | 299.988
Devonshire Building | 2017-03-01 15:15 | 49944.0304 | 219.996
Devonshire Building | 2017-03-01 15:30 | 49944.0954 | 259.992
Devonshire Building | 2017-03-01 15:45 | 49944.1554 | 240.012
Devonshire Building | 2017-03-01 16:00 | 49944.2054 | 200.016
Devonshire Building | 2017-03-01 16:15 | 49944.2604 | 219.996
Devonshire Building | 2017-03-01 16:30 | 49944.3054 | 180
Devonshire Building | 2017-03-01 16:45 | 49944.5954 | 1159.992
Devonshire Building | 2017-03-01 17:00 | 49944.6304 | 140.004
Devonshire Building | 2017-03-01 17:15 | 49944.6654 | 140.004
Devonshire Building | 2017-03-01 17:30 | 49944.7104 | 180
Devonshire Building | 2017-03-01 17:45 | 49944.7454 | 140.004
Devonshire Building | 2017-03-01 18:00 | 49944.7854 | 159.984
Devonshire Building | 2017-03-01 18:15 | 49944.8204 | 140.004
Devonshire Building | 2017-03-01 18:30 | 49944.8504 | 119.988
Devonshire Building | 2017-03-01 18:45 | 49944.8804 | 119.988
Devonshire Building | 2017-03-01 19:00 | 49944.9104 | 119.988
Devonshire Building | 2017-03-01 19:15 | 49944.9404 | 119.988
Devonshire Building | 2017-03-01 19:30 | 49944.9704 | 119.988
Devonshire Building | 2017-03-01 19:45 | 49944.9954 | 100.008
Devonshire Building | 2017-03-01 20:00 | 49945.0254 | 119.988
Devonshire Building | 2017-03-01 20:15 | 49945.0504 | 100.008
Devonshire Building | 2017-03-01 20:30 | 49945.0754 | 100.008
Devonshire Building | 2017-03-01 20:45 | 49945.1004 | 100.008
Devonshire Building | 2017-03-01 21:00 | 49945.1254 | 100.008
Devonshire Building | 2017-03-01 21:15 | 49945.1454 | 79.992
Devonshire Building | 2017-03-01 21:30 | 49945.1654 | 79.992
Devonshire Building | 2017-03-01 21:45 | 49945.1854 | 79.992
Devonshire Building | 2017-03-01 22:00 | 49945.4604 | 1100.016
Devonshire Building | 2017-03-01 22:15 | 49945.4704 | 39.996
Devonshire Building | 2017-03-01 22:30 | 49945.4754 | 20.016
Devonshire Building | 2017-03-01 22:45 | 49945.4804 | 20.016
Devonshire Building | 2017-03-01 23:00 | 49945.4854 | 20.016
Devonshire Building | 2017-03-01 23:15 | 49945.4904 | 20.016
Devonshire Building | 2017-03-01 23:30 | 49945.4954 | 20.016
Devonshire Building | 2017-03-01 23:45 | 49945.5004 | 20.016 | 0
Devonshire Building | 2017-03-02 | 49945.5039 | 20.016
Devonshire Building | 2017-03-02 00:15 | 49945.5139 | 39.996
Devonshire Building | 2017-03-02 00:30 | 49945.5189 | 20.016
Devonshire Building | 2017-03-02 00:45 | 49945.5239 | 20.016
Devonshire Building | 2017-03-02 01:00 | 49945.5289 | 20.016
Devonshire Building | 2017-03-02 01:15 | 49945.5339 | 20.016
Devonshire Building | 2017-03-02 01:30 | 49945.5439 | 39.996
Devonshire Building | 2017-03-02 01:45 | 49945.5689 | 100.008
Devonshire Building | 2017-03-02 02:00 | 49945.5889 | 79.992
Devonshire Building | 2017-03-02 02:15 | 49945.6139 | 100.008
Devonshire Building | 2017-03-02 02:30 | 49945.6339 | 79.992
Devonshire Building | 2017-03-02 02:45 | 49945.6539 | 79.992
Devonshire Building | 2017-03-02 03:00 | 49945.6789 | 100.008
Devonshire Building | 2017-03-02 03:15 | 49945.6989 | 79.992
Devonshire Building | 2017-03-02 03:30 | 49945.7189 | 79.992
Devonshire Building | 2017-03-02 03:45 | 49945.7439 | 100.008
Devonshire Building | 2017-03-02 04:00 | 49945.7639 | 79.992
Devonshire Building | 2017-03-02 04:15 | 49945.7789 | 60.012
Devonshire Building | 2017-03-02 04:30 | 49945.7839 | 20.016
Devonshire Building | 2017-03-02 04:45 | 49945.7889 | 20.016
Devonshire Building | 2017-03-02 05:00 | 49945.7939 | 20.016
Devonshire Building | 2017-03-02 05:15 | 49945.7989 | 20.016
Devonshire Building | 2017-03-02 05:30 | 49945.8039 | 20.016
Devonshire Building | 2017-03-02 05:45 | 49945.8089 | 20.016
Devonshire Building | 2017-03-02 06:00 | 49945.8089 | 0
Devonshire Building | 2017-03-02 06:15 | 49945.8189 | 39.996
Devonshire Building | 2017-03-02 06:30 | 49945.8239 | 20.016
Devonshire Building | 2017-03-02 06:45 | 49945.829 | 20.016
Devonshire Building | 2017-03-02 07:00 | 49945.834 | 20.016
Devonshire Building | 2017-03-02 07:15 | 49945.839 | 20.016
Devonshire Building | 2017-03-02 07:30 | 49945.844 | 20.016
Devonshire Building | 2017-03-02 07:45 | 49945.854 | 39.996
Devonshire Building | 2017-03-02 08:00 | 49945.859 | 20.016
Devonshire Building | 2017-03-02 08:15 | 49945.869 | 39.996
Devonshire Building | 2017-03-02 08:30 | 49945.879 | 39.996
Devonshire Building | 2017-03-02 08:45 | 49945.904 | 100.008
Devonshire Building | 2017-03-02 09:00 | 49945.919 | 60.012
Devonshire Building | 2017-03-02 09:15 | 49945.944 | 100.008
Devonshire Building | 2017-03-02 09:30 | 49946.209 | 1059.984
Devonshire Building | 2017-03-02 09:45 | 49946.304 | 380.016
Devonshire Building | 2017-03-02 10:00 | 49946.384 | 320.004
Devonshire Building | 2017-03-02 10:15 | 49946.479 | 380.016
Devonshire Building | 2017-03-02 10:30 | 49946.574 | 380.016
Devonshire Building | 2017-03-02 10:45 | 49946.669 | 380.016
Devonshire Building | 2017-03-02 11:00 | 49947.039 | 1479.996
Devonshire Building | 2017-03-02 11:15 | 49947.129 | 360
Devonshire Building | 2017-03-02 11:30 | 49947.224 | 380.016
Devonshire Building | 2017-03-02 11:45 | 49947.324 | 399.996
Devonshire Building | 2017-03-02 12:00 | 49947.419 | 380.016
Devonshire Building | 2017-03-02 12:15 | 49947.499 | 320.004
Devonshire Building | 2017-03-02 12:30 | 49947.874 | 1500.012
Devonshire Building | 2017-03-02 12:45 | 49947.939 | 259.992
Devonshire Building | 2017-03-02 13:00 | 49948.009 | 280.008
Devonshire Building | 2017-03-02 13:15 | 49948.074 | 259.992
Devonshire Building | 2017-03-02 13:30 | 49948.139 | 259.992
Devonshire Building | 2017-03-02 13:45 | 49948.199 | 240.012
Devonshire Building | 2017-03-02 14:00 | 49948.444 | 979.992
Devonshire Building | 2017-03-02 14:15 | 49948.569 | 500.004
Devonshire Building | 2017-03-02 14:30 | 49948.604 | 140.004
Devonshire Building | 2017-03-02 14:45 | 49948.649 | 180
Devonshire Building | 2017-03-02 15:00 | 49948.684 | 140.004
Devonshire Building | 2017-03-02 15:15 | 49948.734 | 200.016
Devonshire Building | 2017-03-02 15:30 | 49948.814 | 320.004
Devonshire Building | 2017-03-02 15:45 | 49948.914 | 399.996
Devonshire Building | 2017-03-02 16:00 | 49949.284 | 1479.996
Devonshire Building | 2017-03-02 16:15 | 49949.369 | 339.984
Devonshire Building | 2017-03-02 16:30 | 49949.449 | 320.004
Devonshire Building | 2017-03-02 16:45 | 49949.529 | 320.004
Devonshire Building | 2017-03-02 17:00 | 49949.604 | 299.988
Devonshire Building | 2017-03-02 17:15 | 49949.674 | 280.008
Devonshire Building | 2017-03-02 17:30 | 49949.734 | 240.012
Devonshire Building | 2017-03-02 17:45 | 49949.979 | 979.992
Devonshire Building | 2017-03-02 18:00 | 49950.104 | 500.004
Devonshire Building | 2017-03-02 18:15 | 49950.144 | 159.984
Devonshire Building | 2017-03-02 18:30 | 49950.179 | 140.004
Devonshire Building | 2017-03-02 18:45 | 49950.214 | 140.004
Devonshire Building | 2017-03-02 19:00 | 49950.249 | 140.004
Devonshire Building | 2017-03-02 19:15 | 49950.284 | 140.004
Devonshire Building | 2017-03-02 19:30 | 49950.324 | 159.984
Devonshire Building | 2017-03-02 19:45 | 49950.369 | 180
Devonshire Building | 2017-03-02 20:00 | 49950.409 | 159.984
Devonshire Building | 2017-03-02 20:15 | 49950.449 | 159.984
Devonshire Building | 2017-03-02 20:30 | 49950.489 | 159.984
Devonshire Building | 2017-03-02 20:45 | 49950.519 | 119.988
Devonshire Building | 2017-03-02 21:00 | 49950.554 | 140.004
Devonshire Building | 2017-03-02 21:15 | 49950.584 | 119.988
Devonshire Building | 2017-03-02 21:30 | 49950.614 | 119.988
Devonshire Building | 2017-03-02 21:45 | 49950.644 | 119.988
Devonshire Building | 2017-03-02 22:00 | 49950.679 | 140.004
Devonshire Building | 2017-03-02 22:15 | 49950.704 | 100.008
Devonshire Building | 2017-03-02 22:30 | 49950.724 | 79.992
Devonshire Building | 2017-03-02 22:45 | 49950.734 | 39.996
Devonshire Building | 2017-03-02 23:00 | 49950.744 | 39.996
Devonshire Building | 2017-03-02 23:15 | 49950.749 | 20.016
Devonshire Building | 2017-03-02 23:30 | 49950.759 | 39.996
Devonshire Building | 2017-03-02 23:45 | 49950.769 | 39.996 | 0
Devonshire Building | 2017-03-03 | 49950.7812 | 39.996
Devonshire Building | 2017-03-03 00:15 | 49950.7912 | 39.996
Devonshire Building | 2017-03-03 00:30 | 49950.8012 | 39.996
Devonshire Building | 2017-03-03 00:45 | 49950.8063 | 20.016
Devonshire Building | 2017-03-03 01:00 | 49950.8163 | 39.996
Devonshire Building | 2017-03-03 01:15 | 49950.8262 | 39.996
Devonshire Building | 2017-03-03 01:30 | 49950.8313 | 20.016
Devonshire Building | 2017-03-03 01:45 | 49950.8413 | 39.996
Devonshire Building | 2017-03-03 02:00 | 49950.8463 | 20.016
Devonshire Building | 2017-03-03 02:15 | 49950.8563 | 39.996
Devonshire Building | 2017-03-03 02:30 | 49950.8613 | 20.016
Devonshire Building | 2017-03-03 02:45 | 49950.8663 | 20.016
Devonshire Building | 2017-03-03 03:00 | 49950.8763 | 39.996
Devonshire Building | 2017-03-03 03:15 | 49950.8813 | 20.016
Devonshire Building | 2017-03-03 03:30 | 49950.8863 | 20.016
Devonshire Building | 2017-03-03 03:45 | 49950.8963 | 39.996
Devonshire Building | 2017-03-03 04:00 | 49950.9013 | 20.016
Devonshire Building | 2017-03-03 04:15 | 49950.9063 | 20.016
Devonshire Building | 2017-03-03 04:30 | 49950.9113 | 20.016
Devonshire Building | 2017-03-03 04:45 | 49950.9163 | 20.016
Devonshire Building | 2017-03-03 05:00 | 49950.9263 | 39.996
Devonshire Building | 2017-03-03 05:15 | 49950.9313 | 20.016
Devonshire Building | 2017-03-03 05:30 | 49950.9363 | 20.016
Devonshire Building | 2017-03-03 05:45 | 49950.9413 | 20.016
Devonshire Building | 2017-03-03 06:00 | 49950.9463 | 20.016
Devonshire Building | 2017-03-03 06:15 | 49950.9513 | 20.016
Devonshire Building | 2017-03-03 06:30 | 49950.9563 | 20.016
Devonshire Building | 2017-03-03 06:45 | 49950.9613 | 20.016
Devonshire Building | 2017-03-03 07:00 | 49950.9663 | 20.016
Devonshire Building | 2017-03-03 07:15 | 49950.9713 | 20.016
Devonshire Building | 2017-03-03 07:30 | 49950.9763 | 20.016
Devonshire Building | 2017-03-03 07:45 | 49950.9813 | 20.016
Devonshire Building | 2017-03-03 08:00 | 49950.9863 | 20.016
Devonshire Building | 2017-03-03 08:15 | 49950.9913 | 20.016
Devonshire Building | 2017-03-03 08:30 | 49951.0013 | 39.996
Devonshire Building | 2017-03-03 08:45 | 49951.0213 | 79.992
Devonshire Building | 2017-03-03 09:00 | 49951.2813 | 1040.004
Devonshire Building | 2017-03-03 09:15 | 49951.2913 | 39.996
Devonshire Building | 2017-03-03 09:30 | 49951.3063 | 60.012
Devonshire Building | 2017-03-03 09:45 | 49951.3313 | 100.008
Devonshire Building | 2017-03-03 10:00 | 49951.3563 | 100.008
Devonshire Building | 2017-03-03 10:15 | 49951.4163 | 240.012
Devonshire Building | 2017-03-03 10:30 | 49951.4813 | 259.992
Devonshire Building | 2017-03-03 10:45 | 49951.7713 | 1159.992
Devonshire Building | 2017-03-03 11:00 | 49951.9713 | 799.992
Devonshire Building | 2017-03-03 11:15 | 49952.0663 | 380.016
Devonshire Building | 2017-03-03 11:30 | 49952.1813 | 460.008
Devonshire Building | 2017-03-03 11:45 | 49952.3013 | 479.988
Devonshire Building | 2017-03-03 12:00 | 49952.4163 | 460.008
Devonshire Building | 2017-03-03 12:15 | 49952.8113 | 1580.004
Devonshire Building | 2017-03-03 12:30 | 49952.8863 | 299.988
Devonshire Building | 2017-03-03 12:45 | 49952.9463 | 240.012
Devonshire Building | 2017-03-03 13:00 | 49952.9963 | 200.016
Devonshire Building | 2017-03-03 13:15 | 49953.0564 | 240.012
Devonshire Building | 2017-03-03 13:30 | 49953.1113 | 219.996
Devonshire Building | 2017-03-03 13:45 | 49953.1663 | 219.996
Devonshire Building | 2017-03-03 14:00 | 49953.4514 | 1140.012
Devonshire Building | 2017-03-03 14:15 | 49953.5464 | 380.016
Devonshire Building | 2017-03-03 14:30 | 49953.5814 | 140.004
Devonshire Building | 2017-03-03 14:45 | 49953.6164 | 140.004
Devonshire Building | 2017-03-03 15:00 | 49953.6564 | 159.984
Devonshire Building | 2017-03-03 15:15 | 49953.6914 | 140.004
Devonshire Building | 2017-03-03 15:30 | 49953.7364 | 180
Devonshire Building | 2017-03-03 15:45 | 49953.7714 | 140.004
Devonshire Building | 2017-03-03 16:00 | 49954.0914 | 1280.016
Devonshire Building | 2017-03-03 16:15 | 49954.1364 | 180
Devonshire Building | 2017-03-03 16:30 | 49954.1814 | 180
Devonshire Building | 2017-03-03 16:45 | 49954.2114 | 119.988
Devonshire Building | 2017-03-03 17:00 | 49954.2464 | 140.004
Devonshire Building | 2017-03-03 17:15 | 49954.2764 | 119.988
Devonshire Building | 2017-03-03 17:30 | 49954.3114 | 140.004
Devonshire Building | 2017-03-03 17:45 | 49954.3414 | 119.988
Devonshire Building | 2017-03-03 18:00 | 49954.3664 | 100.008
Devonshire Building | 2017-03-03 18:15 | 49954.3964 | 119.988
Devonshire Building | 2017-03-03 18:30 | 49954.6914 | 1180.008
Devonshire Building | 2017-03-03 18:45 | 49954.7214 | 119.988
Devonshire Building | 2017-03-03 19:00 | 49954.7413 | 79.992
Devonshire Building | 2017-03-03 19:15 | 49954.7664 | 100.008
Devonshire Building | 2017-03-03 19:30 | 49954.7963 | 119.988
Devonshire Building | 2017-03-03 19:45 | 49954.8213 | 100.008
Devonshire Building | 2017-03-03 20:00 | 49954.8464 | 100.008
Devonshire Building | 2017-03-03 20:15 | 49954.8714 | 100.008
Devonshire Building | 2017-03-03 20:30 | 49954.8914 | 79.992
Devonshire Building | 2017-03-03 20:45 | 49954.9164 | 100.008
Devonshire Building | 2017-03-03 21:00 | 49954.9364 | 79.992
Devonshire Building | 2017-03-03 21:15 | 49954.9564 | 79.992
Devonshire Building | 2017-03-03 21:30 | 49954.9714 | 60.012
Devonshire Building | 2017-03-03 21:45 | 49954.9914 | 79.992
Devonshire Building | 2017-03-03 22:00 | 49955.0064 | 60.012
Devonshire Building | 2017-03-03 22:15 | 49955.0214 | 60.012
Devonshire Building | 2017-03-03 22:30 | 49955.0364 | 60.012
Devonshire Building | 2017-03-03 22:45 | 49955.0464 | 39.996
Devonshire Building | 2017-03-03 23:00 | 49955.0614 | 60.012
Devonshire Building | 2017-03-03 23:15 | 49955.0714 | 39.996
Devonshire Building | 2017-03-03 23:30 | 49955.0864 | 60.012
Devonshire Building | 2017-03-03 23:45 | 49955.0964 | 39.996 | 20.016
Devonshire Building | 2017-03-04 | 49955.1055 | 39.996
Devonshire Building | 2017-03-04 00:15 | 49955.1155 | 39.996
Devonshire Building | 2017-03-04 00:30 | 49955.1255 | 39.996
Devonshire Building | 2017-03-04 00:45 | 49955.1355 | 39.996
Devonshire Building | 2017-03-04 01:00 | 49955.1455 | 39.996
Devonshire Building | 2017-03-04 01:15 | 49955.1505 | 20.016
Devonshire Building | 2017-03-04 01:30 | 49955.1605 | 39.996
Devonshire Building | 2017-03-04 01:45 | 49955.1705 | 39.996
Devonshire Building | 2017-03-04 02:00 | 49955.1755 | 20.016
Devonshire Building | 2017-03-04 02:15 | 49955.1855 | 39.996
Devonshire Building | 2017-03-04 02:30 | 49955.1905 | 20.016
Devonshire Building | 2017-03-04 02:45 | 49955.2005 | 39.996
Devonshire Building | 2017-03-04 03:00 | 49955.2055 | 20.016
Devonshire Building | 2017-03-04 03:15 | 49955.2105 | 20.016
Devonshire Building | 2017-03-04 03:30 | 49955.2205 | 39.996
Devonshire Building | 2017-03-04 03:45 | 49955.2255 | 20.016
Devonshire Building | 2017-03-04 04:00 | 49955.2305 | 20.016
Devonshire Building | 2017-03-04 04:15 | 49955.2355 | 20.016
Devonshire Building | 2017-03-04 04:30 | 49955.2405 | 20.016
Devonshire Building | 2017-03-04 04:45 | 49955.2505 | 39.996
Devonshire Building | 2017-03-04 05:00 | 49955.2555 | 20.016
Devonshire Building | 2017-03-04 05:15 | 49955.2605 | 20.016
Devonshire Building | 2017-03-04 05:30 | 49955.2655 | 20.016
Devonshire Building | 2017-03-04 05:45 | 49955.2705 | 20.016
Devonshire Building | 2017-03-04 06:00 | 49955.2755 | 20.016
Devonshire Building | 2017-03-04 06:15 | 49955.2805 | 20.016
Devonshire Building | 2017-03-04 06:30 | 49955.2855 | 20.016
Devonshire Building | 2017-03-04 06:45 | 49955.2855 | 0
Devonshire Building | 2017-03-04 07:00 | 49955.2905 | 20.016
Devonshire Building | 2017-03-04 07:15 | 49955.2955 | 20.016
Devonshire Building | 2017-03-04 07:30 | 49955.3005 | 20.016
Devonshire Building | 2017-03-04 07:45 | 49955.3055 | 20.016
Devonshire Building | 2017-03-04 08:00 | 49955.3105 | 20.016
Devonshire Building | 2017-03-04 08:15 | 49955.3105 | 0
Devonshire Building | 2017-03-04 08:30 | 49955.3155 | 20.016
Devonshire Building | 2017-03-04 08:45 | 49955.3206 | 20.016
Devonshire Building | 2017-03-04 09:00 | 49955.3256 | 20.016
Devonshire Building | 2017-03-04 09:15 | 49955.3256 | 0
Devonshire Building | 2017-03-04 09:30 | 49955.3306 | 20.016
Devonshire Building | 2017-03-04 09:45 | 49955.3356 | 20.016
Devonshire Building | 2017-03-04 10:00 | 49955.3356 | 0
Devonshire Building | 2017-03-04 10:15 | 49955.3406 | 20.016
Devonshire Building | 2017-03-04 10:30 | 49955.3406 | 0
Devonshire Building | 2017-03-04 10:45 | 49955.3456 | 20.016
Devonshire Building | 2017-03-04 11:00 | 49955.3506 | 20.016
Devonshire Building | 2017-03-04 11:15 | 49955.3506 | 0
Devonshire Building | 2017-03-04 11:30 | 49955.3556 | 20.016
Devonshire Building | 2017-03-04 11:45 | 49955.3606 | 20.016
Devonshire Building | 2017-03-04 12:00 | 49955.3606 | 0
Devonshire Building | 2017-03-04 12:15 | 49955.3656 | 20.016
Devonshire Building | 2017-03-04 12:30 | 49955.3756 | 39.996
Devonshire Building | 2017-03-04 12:45 | 49955.3956 | 79.992
Devonshire Building | 2017-03-04 13:00 | 49955.4156 | 79.992
Devonshire Building | 2017-03-04 13:15 | 49955.4356 | 79.992
Devonshire Building | 2017-03-04 13:30 | 49955.4556 | 79.992
Devonshire Building | 2017-03-04 13:45 | 49955.4756 | 79.992
Devonshire Building | 2017-03-04 14:00 | 49955.5006 | 100.008
Devonshire Building | 2017-03-04 14:15 | 49955.5206 | 79.992
Devonshire Building | 2017-03-04 14:30 | 49955.5406 | 79.992
Devonshire Building | 2017-03-04 14:45 | 49955.5556 | 60.012
Devonshire Building | 2017-03-04 15:00 | 49955.5756 | 79.992
Devonshire Building | 2017-03-04 15:15 | 49955.5856 | 39.996
Devonshire Building | 2017-03-04 15:30 | 49955.5956 | 39.996
Devonshire Building | 2017-03-04 15:45 | 49955.6006 | 20.016
Devonshire Building | 2017-03-04 16:00 | 49955.6006 | 0
Devonshire Building | 2017-03-04 16:15 | 49955.6056 | 20.016
Devonshire Building | 2017-03-04 16:30 | 49955.6106 | 20.016
Devonshire Building | 2017-03-04 16:45 | 49955.6156 | 20.016
Devonshire Building | 2017-03-04 17:00 | 49955.6206 | 20.016
Devonshire Building | 2017-03-04 17:15 | 49955.6256 | 20.016
Devonshire Building | 2017-03-04 17:30 | 49955.6306 | 20.016
Devonshire Building | 2017-03-04 17:45 | 49955.6306 | 0
Devonshire Building | 2017-03-04 18:00 | 49955.8906 | 1040.004
Devonshire Building | 2017-03-04 18:15 | 49955.8906 | 0
Devonshire Building | 2017-03-04 18:30 | 49955.8956 | 20.016
Devonshire Building | 2017-03-04 18:45 | 49955.8956 | 0
Devonshire Building | 2017-03-04 19:00 | 49955.9006 | 20.016
Devonshire Building | 2017-03-04 19:15 | 49955.9006 | 0
Devonshire Building | 2017-03-04 19:30 | 49955.9056 | 20.016
Devonshire Building | 2017-03-04 19:45 | 49955.9056 | 0
Devonshire Building | 2017-03-04 20:00 | 49955.9106 | 20.016
Devonshire Building | 2017-03-04 20:15 | 49955.9156 | 20.016
Devonshire Building | 2017-03-04 20:30 | 49955.9156 | 0
Devonshire Building | 2017-03-04 20:45 | 49955.9206 | 20.016
Devonshire Building | 2017-03-04 21:00 | 49955.9206 | 0
Devonshire Building | 2017-03-04 21:15 | 49955.9256 | 20.016
Devonshire Building | 2017-03-04 21:30 | 49955.9256 | 0
Devonshire Building | 2017-03-04 21:45 | 49955.9306 | 20.016
Devonshire Building | 2017-03-04 22:00 | 49955.9356 | 20.016
Devonshire Building | 2017-03-04 22:15 | 49955.9406 | 20.016
Devonshire Building | 2017-03-04 22:30 | 49955.9406 | 0
Devonshire Building | 2017-03-04 22:45 | 49955.9456 | 20.016
Devonshire Building | 2017-03-04 23:00 | 49955.9456 | 0
Devonshire Building | 2017-03-04 23:15 | 49955.9507 | 20.016
Devonshire Building | 2017-03-04 23:30 | 49955.9557 | 20.016
Devonshire Building | 2017-03-04 23:45 | 49955.9557 | 0 | 0
Devonshire Building | 2017-03-05 | 49955.9609 | 20.016
Devonshire Building | 2017-03-05 00:15 | 49955.9609 | 0
Devonshire Building | 2017-03-05 00:30 | 49955.9659 | 20.016
Devonshire Building | 2017-03-05 00:45 | 49955.9659 | 0
Devonshire Building | 2017-03-05 01:00 | 49955.9709 | 20.016
Devonshire Building | 2017-03-05 01:15 | 49955.9709 | 0
Devonshire Building | 2017-03-05 01:30 | 49955.976 | 20.016
Devonshire Building | 2017-03-05 01:45 | 49955.976 | 0
Devonshire Building | 2017-03-05 02:00 | 49955.981 | 20.016
Devonshire Building | 2017-03-05 02:15 | 49955.981 | 0
Devonshire Building | 2017-03-05 02:30 | 49955.986 | 20.016
Devonshire Building | 2017-03-05 02:45 | 49955.986 | 0
Devonshire Building | 2017-03-05 03:00 | 49955.991 | 20.016
Devonshire Building | 2017-03-05 03:15 | 49955.991 | 0
Devonshire Building | 2017-03-05 03:30 | 49955.996 | 20.016
Devonshire Building | 2017-03-05 03:45 | 49955.996 | 0
Devonshire Building | 2017-03-05 04:00 | 49956.001 | 20.016
Devonshire Building | 2017-03-05 04:15 | 49956.001 | 0
Devonshire Building | 2017-03-05 04:30 | 49956.006 | 20.016
Devonshire Building | 2017-03-05 04:45 | 49956.006 | 0
Devonshire Building | 2017-03-05 05:00 | 49956.011 | 20.016
Devonshire Building | 2017-03-05 05:15 | 49956.011 | 0
Devonshire Building | 2017-03-05 05:30 | 49956.016 | 20.016
Devonshire Building | 2017-03-05 05:45 | 49956.016 | 0
Devonshire Building | 2017-03-05 06:00 | 49956.021 | 20.016
Devonshire Building | 2017-03-05 06:15 | 49956.021 | 0
Devonshire Building | 2017-03-05 06:30 | 49956.026 | 20.016
Devonshire Building | 2017-03-05 06:45 | 49956.026 | 0
Devonshire Building | 2017-03-05 07:00 | 49956.031 | 20.016
Devonshire Building | 2017-03-05 07:15 | 49956.031 | 0
Devonshire Building | 2017-03-05 07:30 | 49956.036 | 20.016
Devonshire Building | 2017-03-05 07:45 | 49956.041 | 20.016
Devonshire Building | 2017-03-05 08:00 | 49956.041 | 0
Devonshire Building | 2017-03-05 08:15 | 49956.041 | 0
Devonshire Building | 2017-03-05 08:30 | 49956.046 | 20.016
Devonshire Building | 2017-03-05 08:45 | 49956.051 | 20.016
Devonshire Building | 2017-03-05 09:00 | 49956.051 | 0
Devonshire Building | 2017-03-05 09:15 | 49956.051 | 0
Devonshire Building | 2017-03-05 09:30 | 49956.056 | 20.016
Devonshire Building | 2017-03-05 09:45 | 49956.061 | 20.016
Devonshire Building | 2017-03-05 10:00 | 49956.061 | 0
Devonshire Building | 2017-03-05 10:15 | 49956.066 | 20.016
Devonshire Building | 2017-03-05 10:30 | 49956.066 | 0
Devonshire Building | 2017-03-05 10:45 | 49956.071 | 20.016
Devonshire Building | 2017-03-05 11:00 | 49956.071 | 0
Devonshire Building | 2017-03-05 11:15 | 49956.076 | 20.016
Devonshire Building | 2017-03-05 11:30 | 49956.076 | 0
Devonshire Building | 2017-03-05 11:45 | 49956.081 | 20.016
Devonshire Building | 2017-03-05 12:00 | 49956.081 | 0
Devonshire Building | 2017-03-05 12:15 | 49956.086 | 20.016
Devonshire Building | 2017-03-05 12:30 | 49956.086 | 0
Devonshire Building | 2017-03-05 12:45 | 49956.091 | 20.016
Devonshire Building | 2017-03-05 13:00 | 49956.106 | 60.012
Devonshire Building | 2017-03-05 13:15 | 49956.1211 | 60.012
Devonshire Building | 2017-03-05 13:30 | 49956.141 | 79.992
Devonshire Building | 2017-03-05 13:45 | 49956.161 | 79.992
Devonshire Building | 2017-03-05 14:00 | 49956.181 | 79.992
Devonshire Building | 2017-03-05 14:15 | 49956.201 | 79.992
Devonshire Building | 2017-03-05 14:30 | 49956.221 | 79.992
Devonshire Building | 2017-03-05 14:45 | 49956.241 | 79.992
Devonshire Building | 2017-03-05 15:00 | 49956.261 | 79.992
Devonshire Building | 2017-03-05 15:15 | 49956.281 | 79.992
Devonshire Building | 2017-03-05 15:30 | 49956.301 | 79.992
Devonshire Building | 2017-03-05 15:45 | 49956.306 | 20.016
Devonshire Building | 2017-03-05 16:00 | 49956.311 | 20.016
Devonshire Building | 2017-03-05 16:15 | 49956.311 | 0
Devonshire Building | 2017-03-05 16:30 | 49956.316 | 20.016
Devonshire Building | 2017-03-05 16:45 | 49956.321 | 20.016
Devonshire Building | 2017-03-05 17:00 | 49956.3261 | 20.016
Devonshire Building | 2017-03-05 17:15 | 49956.3261 | 0
Devonshire Building | 2017-03-05 17:30 | 49956.3311 | 20.016
Devonshire Building | 2017-03-05 17:45 | 49956.3361 | 20.016
Devonshire Building | 2017-03-05 18:00 | 49956.3361 | 0
Devonshire Building | 2017-03-05 18:15 | 49956.3411 | 20.016
Devonshire Building | 2017-03-05 18:30 | 49956.3411 | 0
Devonshire Building | 2017-03-05 18:45 | 49956.3461 | 20.016
Devonshire Building | 2017-03-05 19:00 | 49956.3461 | 0
Devonshire Building | 2017-03-05 19:15 | 49956.3511 | 20.016
Devonshire Building | 2017-03-05 19:30 | 49956.3511 | 0
Devonshire Building | 2017-03-05 19:45 | 49956.3561 | 20.016
Devonshire Building | 2017-03-05 20:00 | 49956.3561 | 0
Devonshire Building | 2017-03-05 20:15 | 49956.3611 | 20.016
Devonshire Building | 2017-03-05 20:30 | 49956.4611 | 399.996
Devonshire Building | 2017-03-05 20:45 | 49956.6111 | 600.012
Devonshire Building | 2017-03-05 21:00 | 49956.6111 | 0
Devonshire Building | 2017-03-05 21:15 | 49956.6161 | 20.016
Devonshire Building | 2017-03-05 21:30 | 49956.6161 | 0
Devonshire Building | 2017-03-05 21:45 | 49956.6211 | 20.016
Devonshire Building | 2017-03-05 22:00 | 49956.6311 | 39.996
Devonshire Building | 2017-03-05 22:15 | 49956.6311 | 0
Devonshire Building | 2017-03-05 22:30 | 49956.6361 | 20.016
Devonshire Building | 2017-03-05 22:45 | 49956.6361 | 0
Devonshire Building | 2017-03-05 23:00 | 49956.6411 | 20.016
Devonshire Building | 2017-03-05 23:15 | 49956.6411 | 0
Devonshire Building | 2017-03-05 23:30 | 49956.6461 | 20.016
Devonshire Building | 2017-03-05 23:45 | 49956.6461 | 0 | 0
Devonshire Building | 2017-03-06 | 49956.6484 | 20.016
Devonshire Building | 2017-03-06 00:15 | 49956.6484 | 0
Devonshire Building | 2017-03-06 00:30 | 49956.6534 | 20.016
Devonshire Building | 2017-03-06 00:45 | 49956.6534 | 0
Devonshire Building | 2017-03-06 01:00 | 49956.6584 | 20.016
Devonshire Building | 2017-03-06 01:15 | 49956.6584 | 0
Devonshire Building | 2017-03-06 01:30 | 49956.6635 | 20.016
Devonshire Building | 2017-03-06 01:45 | 49956.6635 | 0
Devonshire Building | 2017-03-06 02:00 | 49956.6685 | 20.016
Devonshire Building | 2017-03-06 02:15 | 49956.6685 | 0
Devonshire Building | 2017-03-06 02:30 | 49956.6735 | 20.016
Devonshire Building | 2017-03-06 02:45 | 49956.6785 | 20.016
Devonshire Building | 2017-03-06 03:00 | 49956.6785 | 0
Devonshire Building | 2017-03-06 03:15 | 49956.6835 | 20.016
Devonshire Building | 2017-03-06 03:30 | 49956.6835 | 0
Devonshire Building | 2017-03-06 03:45 | 49956.6885 | 20.016
Devonshire Building | 2017-03-06 04:00 | 49956.6885 | 0
Devonshire Building | 2017-03-06 04:15 | 49956.6935 | 20.016
Devonshire Building | 2017-03-06 04:30 | 49956.6935 | 0
Devonshire Building | 2017-03-06 04:45 | 49956.6985 | 20.016
Devonshire Building | 2017-03-06 05:00 | 49956.6985 | 0
Devonshire Building | 2017-03-06 05:15 | 49956.7035 | 20.016
Devonshire Building | 2017-03-06 05:30 | 49956.7035 | 0
Devonshire Building | 2017-03-06 05:45 | 49956.7085 | 20.016
Devonshire Building | 2017-03-06 06:00 | 49956.7085 | 0
Devonshire Building | 2017-03-06 06:15 | 49956.7135 | 20.016
Devonshire Building | 2017-03-06 06:30 | 49956.7185 | 20.016
Devonshire Building | 2017-03-06 06:45 | 49956.7235 | 20.016
Devonshire Building | 2017-03-06 07:00 | 49956.7235 | 0
Devonshire Building | 2017-03-06 07:15 | 49956.7285 | 20.016
Devonshire Building | 2017-03-06 07:30 | 49956.7335 | 20.016
Devonshire Building | 2017-03-06 07:45 | 49956.7385 | 20.016
Devonshire Building | 2017-03-06 08:00 | 49956.7535 | 60.012
Devonshire Building | 2017-03-06 08:15 | 49956.7585 | 20.016
Devonshire Building | 2017-03-06 08:30 | 49956.7685 | 39.996
Devonshire Building | 2017-03-06 08:45 | 49956.7985 | 119.988
Devonshire Building | 2017-03-06 09:00 | 49957.1485 | 1400.004
Devonshire Building | 2017-03-06 09:15 | 49957.1935 | 180
Devonshire Building | 2017-03-06 09:30 | 49957.2685 | 299.988
Devonshire Building | 2017-03-06 09:45 | 49957.3635 | 380.016
Devonshire Building | 2017-03-06 10:00 | 49957.4435 | 320.004
Devonshire Building | 2017-03-06 10:15 | 49957.5185 | 299.988
Devonshire Building | 2017-03-06 10:30 | 49957.8385 | 1280.016
Devonshire Building | 2017-03-06 10:45 | 49957.9185 | 320.004
Devonshire Building | 2017-03-06 11:00 | 49957.9685 | 200.016
Devonshire Building | 2017-03-06 11:15 | 49958.0185 | 200.016
Devonshire Building | 2017-03-06 11:30 | 49958.0685 | 200.016
Devonshire Building | 2017-03-06 11:45 | 49958.3885 | 1280.016
Devonshire Building | 2017-03-06 12:00 | 49958.4485 | 240.012
Devonshire Building | 2017-03-06 12:15 | 49958.5135 | 259.992
Devonshire Building | 2017-03-06 12:30 | 49958.5785 | 259.992
Devonshire Building | 2017-03-06 12:45 | 49958.6635 | 339.984
Devonshire Building | 2017-03-06 13:00 | 49958.9935 | 1320.012
Devonshire Building | 2017-03-06 13:15 | 49959.0435 | 200.016
Devonshire Building | 2017-03-06 13:30 | 49959.0985 | 219.996
Devonshire Building | 2017-03-06 13:45 | 49959.1535 | 219.996
Devonshire Building | 2017-03-06 14:00 | 49959.2135 | 240.012
Devonshire Building | 2017-03-06 14:15 | 49959.2685 | 219.996
Devonshire Building | 2017-03-06 14:30 | 49959.6135 | 1379.988
Devonshire Building | 2017-03-06 14:45 | 49959.6685 | 219.996
Devonshire Building | 2017-03-06 15:00 | 49959.7185 | 200.016
Devonshire Building | 2017-03-06 15:15 | 49959.7785 | 240.012
Devonshire Building | 2017-03-06 15:30 | 49959.8385 | 240.012
Devonshire Building | 2017-03-06 15:45 | 49959.8785 | 159.984
Devonshire Building | 2017-03-06 16:00 | 49959.9235 | 180
Devonshire Building | 2017-03-06 16:15 | 49960.2635 | 1360.008
Devonshire Building | 2017-03-06 16:30 | 49960.3285 | 259.992
Devonshire Building | 2017-03-06 16:45 | 49960.4085 | 320.004
Devonshire Building | 2017-03-06 17:00 | 49960.4735 | 259.992
Devonshire Building | 2017-03-06 17:15 | 49960.5335 | 240.012
Devonshire Building | 2017-03-06 17:30 | 49960.5835 | 200.016
Devonshire Building | 2017-03-06 17:45 | 49960.6335 | 200.016
Devonshire Building | 2017-03-06 18:00 | 49960.6836 | 200.016
Devonshire Building | 2017-03-06 18:15 | 49960.7286 | 180
Devonshire Building | 2017-03-06 18:30 | 49960.7736 | 180
Devonshire Building | 2017-03-06 18:45 | 49961.0836 | 1239.984
Devonshire Building | 2017-03-06 19:00 | 49961.1235 | 159.984
Devonshire Building | 2017-03-06 19:15 | 49961.1735 | 200.016
Devonshire Building | 2017-03-06 19:30 | 49961.2336 | 240.012
Devonshire Building | 2017-03-06 19:45 | 49961.2735 | 159.984
Devonshire Building | 2017-03-06 20:00 | 49961.3135 | 159.984
Devonshire Building | 2017-03-06 20:15 | 49961.3435 | 119.988
Devonshire Building | 2017-03-06 20:30 | 49961.3735 | 119.988
Devonshire Building | 2017-03-06 20:45 | 49961.3985 | 100.008
Devonshire Building | 2017-03-06 21:00 | 49961.4185 | 79.992
Devonshire Building | 2017-03-06 21:15 | 49961.4385 | 79.992
Devonshire Building | 2017-03-06 21:30 | 49961.4535 | 60.012
Devonshire Building | 2017-03-06 21:45 | 49961.4735 | 79.992
Devonshire Building | 2017-03-06 22:00 | 49961.4885 | 60.012
Devonshire Building | 2017-03-06 22:15 | 49961.4985 | 39.996
Devonshire Building | 2017-03-06 22:30 | 49961.5135 | 60.012
Devonshire Building | 2017-03-06 22:45 | 49961.5235 | 39.996
Devonshire Building | 2017-03-06 23:00 | 49961.5335 | 39.996
Devonshire Building | 2017-03-06 23:15 | 49961.5485 | 60.012
Devonshire Building | 2017-03-06 23:30 | 49961.5585 | 39.996
Devonshire Building | 2017-03-06 23:45 | 49961.5685 | 39.996 | 0
Devonshire Building | 2017-03-07 | 49961.5781 | 39.996
Devonshire Building | 2017-03-07 00:15 | 49961.5881 | 39.996
Devonshire Building | 2017-03-07 00:30 | 49961.5931 | 20.016
Devonshire Building | 2017-03-07 00:45 | 49961.6031 | 39.996
Devonshire Building | 2017-03-07 01:00 | 49961.6131 | 39.996
Devonshire Building | 2017-03-07 01:15 | 49961.6181 | 20.016
Devonshire Building | 2017-03-07 01:30 | 49961.6281 | 39.996
Devonshire Building | 2017-03-07 01:45 | 49961.6381 | 39.996
Devonshire Building | 2017-03-07 02:00 | 49961.6431 | 20.016
Devonshire Building | 2017-03-07 02:15 | 49961.6531 | 39.996
Devonshire Building | 2017-03-07 02:30 | 49961.6581 | 20.016
Devonshire Building | 2017-03-07 02:45 | 49961.6631 | 20.016
Devonshire Building | 2017-03-07 03:00 | 49961.6681 | 20.016
Devonshire Building | 2017-03-07 03:15 | 49961.6781 | 39.996
Devonshire Building | 2017-03-07 03:30 | 49961.6832 | 20.016
Devonshire Building | 2017-03-07 03:45 | 49961.6882 | 20.016
Devonshire Building | 2017-03-07 04:00 | 49961.6932 | 20.016
Devonshire Building | 2017-03-07 04:15 | 49961.6982 | 20.016
Devonshire Building | 2017-03-07 04:30 | 49961.7032 | 20.016
Devonshire Building | 2017-03-07 04:45 | 49961.7082 | 20.016
Devonshire Building | 2017-03-07 05:00 | 49961.7132 | 20.016
Devonshire Building | 2017-03-07 05:15 | 49961.7182 | 20.016
Devonshire Building | 2017-03-07 05:30 | 49961.7232 | 20.016
Devonshire Building | 2017-03-07 05:45 | 49961.7282 | 20.016
Devonshire Building | 2017-03-07 06:00 | 49961.7332 | 20.016
Devonshire Building | 2017-03-07 06:15 | 49961.7432 | 39.996
Devonshire Building | 2017-03-07 06:30 | 49961.7482 | 20.016
Devonshire Building | 2017-03-07 06:45 | 49961.7532 | 20.016
Devonshire Building | 2017-03-07 07:00 | 49961.7582 | 20.016
Devonshire Building | 2017-03-07 07:15 | 49961.7632 | 20.016
Devonshire Building | 2017-03-07 07:30 | 49961.7732 | 39.996
Devonshire Building | 2017-03-07 07:45 | 49961.7782 | 20.016
Devonshire Building | 2017-03-07 08:00 | 49961.7882 | 39.996
Devonshire Building | 2017-03-07 08:15 | 49961.7982 | 39.996
Devonshire Building | 2017-03-07 08:30 | 49961.8032 | 20.016
Devonshire Building | 2017-03-07 08:45 | 49961.8132 | 39.996
Devonshire Building | 2017-03-07 09:00 | 49961.8282 | 60.012
Devonshire Building | 2017-03-07 09:15 | 49962.1232 | 1180.008
Devonshire Building | 2017-03-07 09:30 | 49962.1282 | 20.016
Devonshire Building | 2017-03-07 09:45 | 49962.1382 | 39.996
Devonshire Building | 2017-03-07 10:00 | 49962.1482 | 39.996
Devonshire Building | 2017-03-07 10:15 | 49962.1532 | 20.016
Devonshire Building | 2017-03-07 10:30 | 49962.2382 | 339.984
Devonshire Building | 2017-03-07 10:45 | 49962.4882 | 1000.008
Devonshire Building | 2017-03-07 11:00 | 49962.5482 | 240.012
Devonshire Building | 2017-03-07 11:15 | 49962.6132 | 259.992
Devonshire Building | 2017-03-07 11:30 | 49962.6882 | 299.988
Devonshire Building | 2017-03-07 11:45 | 49962.7582 | 280.008
Devonshire Building | 2017-03-07 12:00 | 49962.8232 | 259.992
Devonshire Building | 2017-03-07 12:15 | 49963.1832 | 1440
Devonshire Building | 2017-03-07 12:30 | 49963.2332 | 200.016
Devonshire Building | 2017-03-07 12:45 | 49963.2882 | 219.996
Devonshire Building | 2017-03-07 13:00 | 49963.3432 | 219.996
Devonshire Building | 2017-03-07 13:15 | 49963.3982 | 219.996
Devonshire Building | 2017-03-07 13:30 | 49963.4682 | 280.008
Devonshire Building | 2017-03-07 13:45 | 49963.8682 | 1599.984
Devonshire Building | 2017-03-07 14:00 | 49963.9782 | 439.992
Devonshire Building | 2017-03-07 14:15 | 49964.0932 | 460.008
Devonshire Building | 2017-03-07 14:30 | 49964.1882 | 380.016
Devonshire Building | 2017-03-07 14:45 | 49964.2732 | 339.984
Devonshire Building | 2017-03-07 15:00 | 49964.3632 | 360
Devonshire Building | 2017-03-07 15:15 | 49964.7282 | 1460.016
Devonshire Building | 2017-03-07 15:30 | 49964.7982 | 280.008
Devonshire Building | 2017-03-07 15:45 | 49964.8682 | 280.008
Devonshire Building | 2017-03-07 16:00 | 49964.9432 | 299.988
Devonshire Building | 2017-03-07 16:15 | 49965.0282 | 339.984
Devonshire Building | 2017-03-07 16:30 | 49965.0982 | 280.008
Devonshire Building | 2017-03-07 16:45 | 49965.1532 | 219.996
Devonshire Building | 2017-03-07 17:00 | 49965.2082 | 219.996
Devonshire Building | 2017-03-07 17:15 | 49965.5382 | 1320.012
Devonshire Building | 2017-03-07 17:30 | 49965.5832 | 180
Devonshire Building | 2017-03-07 17:45 | 49965.6282 | 180
Devonshire Building | 2017-03-07 18:00 | 49965.6782 | 200.016
Devonshire Building | 2017-03-07 18:15 | 49965.7182 | 159.984
Devonshire Building | 2017-03-07 18:30 | 49965.7532 | 140.004
Devonshire Building | 2017-03-07 18:45 | 49965.7832 | 119.988
Devonshire Building | 2017-03-07 19:00 | 49965.8082 | 100.008
Devonshire Building | 2017-03-07 19:15 | 49965.8332 | 100.008
Devonshire Building | 2017-03-07 19:30 | 49965.8532 | 79.992
Devonshire Building | 2017-03-07 19:45 | 49965.8732 | 79.992
Devonshire Building | 2017-03-07 20:00 | 49965.8882 | 60.012
Devonshire Building | 2017-03-07 20:15 | 49965.9032 | 60.012
Devonshire Building | 2017-03-07 20:30 | 49965.9182 | 60.012
Devonshire Building | 2017-03-07 20:45 | 49965.9332 | 60.012
Devonshire Building | 2017-03-07 21:00 | 49965.9482 | 60.012
Devonshire Building | 2017-03-07 21:15 | 49965.9632 | 60.012
Devonshire Building | 2017-03-07 21:30 | 49965.9732 | 39.996
Devonshire Building | 2017-03-07 21:45 | 49965.9832 | 39.996
Devonshire Building | 2017-03-07 22:00 | 49966.0082 | 100.008
Devonshire Building | 2017-03-07 22:15 | 49966.0132 | 20.016
Devonshire Building | 2017-03-07 22:30 | 49966.0182 | 20.016
Devonshire Building | 2017-03-07 22:45 | 49966.0182 | 0
Devonshire Building | 2017-03-07 23:00 | 49966.0232 | 20.016
Devonshire Building | 2017-03-07 23:15 | 49966.0283 | 20.016
Devonshire Building | 2017-03-07 23:30 | 49966.0283 | 0
Devonshire Building | 2017-03-07 23:45 | 49966.0333 | 20.016 | 0
Devonshire Building | 2017-03-08 | 49966.0352 | 0
Devonshire Building | 2017-03-08 00:15 | 49966.0402 | 20.016
Devonshire Building | 2017-03-08 00:30 | 49966.0452 | 20.016
Devonshire Building | 2017-03-08 00:45 | 49966.0452 | 0
Devonshire Building | 2017-03-08 01:00 | 49966.0502 | 20.016
Devonshire Building | 2017-03-08 01:15 | 49966.0502 | 0
Devonshire Building | 2017-03-08 01:30 | 49966.0552 | 20.016
Devonshire Building | 2017-03-08 01:45 | 49966.0602 | 20.016
Devonshire Building | 2017-03-08 02:00 | 49966.0602 | 0
Devonshire Building | 2017-03-08 02:15 | 49966.0652 | 20.016
Devonshire Building | 2017-03-08 02:30 | 49966.0652 | 0
Devonshire Building | 2017-03-08 02:45 | 49966.0702 | 20.016
Devonshire Building | 2017-03-08 03:00 | 49966.0702 | 0
Devonshire Building | 2017-03-08 03:15 | 49966.0752 | 20.016
Devonshire Building | 2017-03-08 03:30 | 49966.0802 | 20.016
Devonshire Building | 2017-03-08 03:45 | 49966.0802 | 0
Devonshire Building | 2017-03-08 04:00 | 49966.0852 | 20.016
Devonshire Building | 2017-03-08 04:15 | 49966.0852 | 0
Devonshire Building | 2017-03-08 04:30 | 49966.0902 | 20.016
Devonshire Building | 2017-03-08 04:45 | 49966.0902 | 0
Devonshire Building | 2017-03-08 05:00 | 49966.0952 | 20.016
Devonshire Building | 2017-03-08 05:15 | 49966.0952 | 0
Devonshire Building | 2017-03-08 05:30 | 49966.1002 | 20.016
Devonshire Building | 2017-03-08 05:45 | 49966.1002 | 0
Devonshire Building | 2017-03-08 06:00 | 49966.1052 | 20.016
Devonshire Building | 2017-03-08 06:15 | 49966.1052 | 0
Devonshire Building | 2017-03-08 06:30 | 49966.1102 | 20.016
Devonshire Building | 2017-03-08 06:45 | 49966.1152 | 20.016
Devonshire Building | 2017-03-08 07:00 | 49966.1152 | 0
Devonshire Building | 2017-03-08 07:15 | 49966.1202 | 20.016
Devonshire Building | 2017-03-08 07:30 | 49966.1202 | 0
Devonshire Building | 2017-03-08 07:45 | 49966.1352 | 60.012
Devonshire Building | 2017-03-08 08:00 | 49966.3952 | 1040.004
Devonshire Building | 2017-03-08 08:15 | 49966.4002 | 20.016
Devonshire Building | 2017-03-08 08:30 | 49966.4052 | 20.016
Devonshire Building | 2017-03-08 08:45 | 49966.4152 | 39.996
Devonshire Building | 2017-03-08 09:00 | 49966.4302 | 60.012
Devonshire Building | 2017-03-08 09:15 | 49966.4402 | 39.996
Devonshire Building | 2017-03-08 09:30 | 49966.4452 | 20.016
Devonshire Building | 2017-03-08 09:45 | 49966.4502 | 20.016
Devonshire Building | 2017-03-08 10:00 | 49966.5553 | 420.012
Devonshire Building | 2017-03-08 10:15 | 49966.8552 | 1199.988
Devonshire Building | 2017-03-08 10:30 | 49967.0053 | 600.012
Devonshire Building | 2017-03-08 10:45 | 49967.1352 | 519.984
Devonshire Building | 2017-03-08 11:00 | 49967.2652 | 519.984
Devonshire Building | 2017-03-08 11:15 | 49967.3802 | 460.008
Devonshire Building | 2017-03-08 11:30 | 49967.4753 | 380.016
Devonshire Building | 2017-03-08 11:45 | 49967.7503 | 1100.016
Devonshire Building | 2017-03-08 12:00 | 49967.7953 | 180
Devonshire Building | 2017-03-08 12:15 | 49967.8453 | 200.016
Devonshire Building | 2017-03-08 12:30 | 49967.8953 | 200.016
Devonshire Building | 2017-03-08 12:45 | 49967.9453 | 200.016
Devonshire Building | 2017-03-08 13:00 | 49968.0003 | 219.996
Devonshire Building | 2017-03-08 13:15 | 49968.1853 | 740.016
Devonshire Building | 2017-03-08 13:30 | 49968.5653 | 1519.992
Devonshire Building | 2017-03-08 13:45 | 49968.7153 | 600.012
Devonshire Building | 2017-03-08 14:00 | 49968.8253 | 439.992
Devonshire Building | 2017-03-08 14:15 | 49968.9203 | 380.016
Devonshire Building | 2017-03-08 14:30 | 49969.0203 | 399.996
Devonshire Building | 2017-03-08 14:45 | 49969.1153 | 380.016
Devonshire Building | 2017-03-08 15:00 | 49969.4853 | 1479.996
Devonshire Building | 2017-03-08 15:15 | 49969.5803 | 380.016
Devonshire Building | 2017-03-08 15:30 | 49969.6703 | 360
Devonshire Building | 2017-03-08 15:45 | 49969.7503 | 320.004
Devonshire Building | 2017-03-08 16:00 | 49969.8253 | 299.988
Devonshire Building | 2017-03-08 16:15 | 49969.8903 | 259.992
Devonshire Building | 2017-03-08 16:30 | 49969.9503 | 240.012
Devonshire Building | 2017-03-08 16:45 | 49970.0353 | 339.984
Devonshire Building | 2017-03-08 17:00 | 49970.3203 | 1140.012
Devonshire Building | 2017-03-08 17:15 | 49970.3353 | 60.012
Devonshire Building | 2017-03-08 17:30 | 49970.3503 | 60.012
Devonshire Building | 2017-03-08 17:45 | 49970.3603 | 39.996
Devonshire Building | 2017-03-08 18:00 | 49970.3703 | 39.996
Devonshire Building | 2017-03-08 18:15 | 49970.3853 | 60.012
Devonshire Building | 2017-03-08 18:30 | 49970.3953 | 39.996
Devonshire Building | 2017-03-08 18:45 | 49970.4103 | 60.012
Devonshire Building | 2017-03-08 19:00 | 49970.4203 | 39.996
Devonshire Building | 2017-03-08 19:15 | 49970.4353 | 60.012
Devonshire Building | 2017-03-08 19:30 | 49970.4453 | 39.996
Devonshire Building | 2017-03-08 19:45 | 49970.4603 | 60.012
Devonshire Building | 2017-03-08 20:00 | 49970.4703 | 39.996
Devonshire Building | 2017-03-08 20:15 | 49970.4803 | 39.996
Devonshire Building | 2017-03-08 20:30 | 49970.4903 | 39.996
Devonshire Building | 2017-03-08 20:45 | 49970.5003 | 39.996
Devonshire Building | 2017-03-08 21:00 | 49970.5103 | 39.996
Devonshire Building | 2017-03-08 21:15 | 49970.5203 | 39.996
Devonshire Building | 2017-03-08 21:30 | 49970.5253 | 20.016
Devonshire Building | 2017-03-08 21:45 | 49970.5353 | 39.996
Devonshire Building | 2017-03-08 22:00 | 49970.5653 | 119.988
Devonshire Building | 2017-03-08 22:15 | 49970.5753 | 39.996
Devonshire Building | 2017-03-08 22:30 | 49970.5853 | 39.996
Devonshire Building | 2017-03-08 22:45 | 49970.5953 | 39.996
Devonshire Building | 2017-03-08 23:00 | 49970.6003 | 20.016
Devonshire Building | 2017-03-08 23:15 | 49970.6103 | 39.996
Devonshire Building | 2017-03-08 23:30 | 49970.6203 | 39.996
Devonshire Building | 2017-03-08 23:45 | 49970.6253 | 20.016 | 0
Devonshire Building | 2017-03-09 | 49970.6328 | 39.996
Devonshire Building | 2017-03-09 00:15 | 49970.6378 | 20.016
Devonshire Building | 2017-03-09 00:30 | 49970.6428 | 20.016
Devonshire Building | 2017-03-09 00:45 | 49970.6528 | 39.996
Devonshire Building | 2017-03-09 01:00 | 49970.6578 | 20.016
Devonshire Building | 2017-03-09 01:15 | 49970.6678 | 39.996
Devonshire Building | 2017-03-09 01:30 | 49970.6728 | 20.016
Devonshire Building | 2017-03-09 01:45 | 49970.6778 | 20.016
Devonshire Building | 2017-03-09 02:00 | 49970.6878 | 39.996
Devonshire Building | 2017-03-09 02:15 | 49970.6928 | 20.016
Devonshire Building | 2017-03-09 02:30 | 49970.6978 | 20.016
Devonshire Building | 2017-03-09 02:45 | 49970.7028 | 20.016
Devonshire Building | 2017-03-09 03:00 | 49970.7128 | 39.996
Devonshire Building | 2017-03-09 03:15 | 49970.7178 | 20.016
Devonshire Building | 2017-03-09 03:30 | 49970.7228 | 20.016
Devonshire Building | 2017-03-09 03:45 | 49970.7279 | 20.016
Devonshire Building | 2017-03-09 04:00 | 49970.7329 | 20.016
Devonshire Building | 2017-03-09 04:15 | 49970.7429 | 39.996
Devonshire Building | 2017-03-09 04:30 | 49970.7479 | 20.016
Devonshire Building | 2017-03-09 04:45 | 49970.7529 | 20.016
Devonshire Building | 2017-03-09 05:00 | 49970.7579 | 20.016
Devonshire Building | 2017-03-09 05:15 | 49970.7629 | 20.016
Devonshire Building | 2017-03-09 05:30 | 49970.7679 | 20.016
Devonshire Building | 2017-03-09 05:45 | 49970.7729 | 20.016
Devonshire Building | 2017-03-09 06:00 | 49970.7779 | 20.016
Devonshire Building | 2017-03-09 06:15 | 49970.7829 | 20.016
Devonshire Building | 2017-03-09 06:30 | 49970.7879 | 20.016
Devonshire Building | 2017-03-09 06:45 | 49970.7979 | 39.996
Devonshire Building | 2017-03-09 07:00 | 49971.0629 | 1059.984
Devonshire Building | 2017-03-09 07:15 | 49971.0629 | 0
Devonshire Building | 2017-03-09 07:30 | 49971.0679 | 20.016
Devonshire Building | 2017-03-09 07:45 | 49971.0779 | 39.996
Devonshire Building | 2017-03-09 08:00 | 49971.0979 | 79.992
Devonshire Building | 2017-03-09 08:15 | 49971.1179 | 79.992
Devonshire Building | 2017-03-09 08:30 | 49971.1429 | 100.008
Devonshire Building | 2017-03-09 08:45 | 49971.1779 | 140.004
Devonshire Building | 2017-03-09 09:00 | 49971.2179 | 159.984
Devonshire Building | 2017-03-09 09:15 | 49971.2579 | 159.984
Devonshire Building | 2017-03-09 09:30 | 49971.3029 | 180
Devonshire Building | 2017-03-09 09:45 | 49971.3529 | 200.016
Devonshire Building | 2017-03-09 10:00 | 49971.6979 | 1379.988
Devonshire Building | 2017-03-09 10:15 | 49971.7779 | 320.004
Devonshire Building | 2017-03-09 10:30 | 49971.8679 | 360
Devonshire Building | 2017-03-09 10:45 | 49971.9629 | 380.016
Devonshire Building | 2017-03-09 11:00 | 49972.0429 | 320.004
Devonshire Building | 2017-03-09 11:15 | 49972.1229 | 320.004
Devonshire Building | 2017-03-09 11:30 | 49972.5379 | 1659.996
Devonshire Building | 2017-03-09 11:45 | 49972.6879 | 600.012
Devonshire Building | 2017-03-09 12:00 | 49972.8329 | 579.996
Devonshire Building | 2017-03-09 12:15 | 49972.9679 | 540
Devonshire Building | 2017-03-09 12:30 | 49973.0979 | 519.984
Devonshire Building | 2017-03-09 12:45 | 49973.2379 | 560.016
Devonshire Building | 2017-03-09 13:00 | 49973.6279 | 1559.988
Devonshire Building | 2017-03-09 13:15 | 49973.7429 | 460.008
Devonshire Building | 2017-03-09 13:30 | 49973.8379 | 380.016
Devonshire Building | 2017-03-09 13:45 | 49973.9329 | 380.016
Devonshire Building | 2017-03-09 14:00 | 49974.0079 | 299.988
Devonshire Building | 2017-03-09 14:15 | 49974.0679 | 240.012
Devonshire Building | 2017-03-09 14:30 | 49974.1279 | 240.012
Devonshire Building | 2017-03-09 14:45 | 49974.1779 | 200.016
Devonshire Building | 2017-03-09 15:00 | 49974.3279 | 600.012
Devonshire Building | 2017-03-09 15:15 | 49974.5429 | 860.004
Devonshire Building | 2017-03-09 15:30 | 49974.5629 | 79.992
Devonshire Building | 2017-03-09 15:45 | 49974.5779 | 60.012
Devonshire Building | 2017-03-09 16:00 | 49974.5979 | 79.992
Devonshire Building | 2017-03-09 16:15 | 49974.6129 | 60.012
Devonshire Building | 2017-03-09 16:30 | 49974.6379 | 100.008
Devonshire Building | 2017-03-09 16:45 | 49974.6579 | 79.992
Devonshire Building | 2017-03-09 17:00 | 49974.6829 | 100.008
Devonshire Building | 2017-03-09 17:15 | 49974.9979 | 1260
Devonshire Building | 2017-03-09 17:30 | 49975.0379 | 159.984
Devonshire Building | 2017-03-09 17:45 | 49975.0979 | 240.012
Devonshire Building | 2017-03-09 18:00 | 49975.1529 | 219.996
Devonshire Building | 2017-03-09 18:15 | 49975.2129 | 240.012
Devonshire Building | 2017-03-09 18:30 | 49975.2679 | 219.996
Devonshire Building | 2017-03-09 18:45 | 49975.3179 | 200.016
Devonshire Building | 2017-03-09 19:00 | 49975.3629 | 180
Devonshire Building | 2017-03-09 19:15 | 49975.4079 | 180
Devonshire Building | 2017-03-09 19:30 | 49975.4429 | 140.004
Devonshire Building | 2017-03-09 19:45 | 49975.4779 | 140.004
Devonshire Building | 2017-03-09 20:00 | 49975.5079 | 119.988
Devonshire Building | 2017-03-09 20:15 | 49975.5379 | 119.988
Devonshire Building | 2017-03-09 20:30 | 49975.5629 | 100.008
Devonshire Building | 2017-03-09 20:45 | 49975.5829 | 79.992
Devonshire Building | 2017-03-09 21:00 | 49975.6029 | 79.992
Devonshire Building | 2017-03-09 21:15 | 49975.6179 | 60.012
Devonshire Building | 2017-03-09 21:30 | 49975.6329 | 60.012
Devonshire Building | 2017-03-09 21:45 | 49975.6479 | 60.012
Devonshire Building | 2017-03-09 22:00 | 49975.6829 | 140.004
Devonshire Building | 2017-03-09 22:15 | 49975.6879 | 20.016
Devonshire Building | 2017-03-09 22:30 | 49975.6929 | 20.016
Devonshire Building | 2017-03-09 22:45 | 49975.6979 | 20.016
Devonshire Building | 2017-03-09 23:00 | 49975.6979 | 0
Devonshire Building | 2017-03-09 23:15 | 49975.7029 | 20.016
Devonshire Building | 2017-03-09 23:30 | 49975.7079 | 20.016
Devonshire Building | 2017-03-09 23:45 | 49975.7129 | 20.016 | 0
Devonshire Building | 2017-03-10 | 49975.7188 | 20.016
Devonshire Building | 2017-03-10 00:15 | 49975.7188 | 0
Devonshire Building | 2017-03-10 00:30 | 49975.7238 | 20.016
Devonshire Building | 2017-03-10 00:45 | 49975.7288 | 20.016
Devonshire Building | 2017-03-10 01:00 | 49975.7338 | 20.016
Devonshire Building | 2017-03-10 01:15 | 49975.7338 | 0
Devonshire Building | 2017-03-10 01:30 | 49975.7388 | 20.016
Devonshire Building | 2017-03-10 01:45 | 49975.7438 | 20.016
Devonshire Building | 2017-03-10 02:00 | 49975.7488 | 20.016
Devonshire Building | 2017-03-10 02:15 | 49975.7488 | 0
Devonshire Building | 2017-03-10 02:30 | 49975.7538 | 20.016
Devonshire Building | 2017-03-10 02:45 | 49975.7588 | 20.016
Devonshire Building | 2017-03-10 03:00 | 49975.7588 | 0
Devonshire Building | 2017-03-10 03:15 | 49975.7638 | 20.016
Devonshire Building | 2017-03-10 03:30 | 49975.7688 | 20.016
Devonshire Building | 2017-03-10 03:45 | 49975.7688 | 0
Devonshire Building | 2017-03-10 04:00 | 49975.7738 | 20.016
Devonshire Building | 2017-03-10 04:15 | 49975.7788 | 20.016
Devonshire Building | 2017-03-10 04:30 | 49975.7788 | 0
Devonshire Building | 2017-03-10 04:45 | 49975.7838 | 20.016
Devonshire Building | 2017-03-10 05:00 | 49975.7888 | 20.016
Devonshire Building | 2017-03-10 05:15 | 49975.7888 | 0
Devonshire Building | 2017-03-10 05:30 | 49975.7938 | 20.016
Devonshire Building | 2017-03-10 05:45 | 49975.7938 | 0
Devonshire Building | 2017-03-10 06:00 | 49975.7988 | 20.016
Devonshire Building | 2017-03-10 06:15 | 49975.8038 | 20.016
Devonshire Building | 2017-03-10 06:30 | 49975.8038 | 0
Devonshire Building | 2017-03-10 06:45 | 49975.8088 | 20.016
Devonshire Building | 2017-03-10 07:00 | 49975.8088 | 0
Devonshire Building | 2017-03-10 07:15 | 49975.8138 | 20.016
Devonshire Building | 2017-03-10 07:30 | 49975.8188 | 20.016
Devonshire Building | 2017-03-10 07:45 | 49976.1138 | 1180.008
Devonshire Building | 2017-03-10 08:00 | 49976.1438 | 119.988
Devonshire Building | 2017-03-10 08:15 | 49976.1638 | 79.992
Devonshire Building | 2017-03-10 08:30 | 49976.1938 | 119.988
Devonshire Building | 2017-03-10 08:45 | 49976.2238 | 119.988
Devonshire Building | 2017-03-10 09:00 | 49976.2488 | 100.008
Devonshire Building | 2017-03-10 09:15 | 49976.2688 | 79.992
Devonshire Building | 2017-03-10 09:30 | 49976.2888 | 79.992
Devonshire Building | 2017-03-10 09:45 | 49976.3088 | 79.992
Devonshire Building | 2017-03-10 10:00 | 49976.3338 | 100.008
Devonshire Building | 2017-03-10 10:15 | 49976.3588 | 100.008
Devonshire Building | 2017-03-10 10:30 | 49976.6838 | 1299.996
Devonshire Building | 2017-03-10 10:45 | 49976.7088 | 100.008
Devonshire Building | 2017-03-10 11:00 | 49976.7488 | 159.984
Devonshire Building | 2017-03-10 11:15 | 49976.7838 | 140.004
Devonshire Building | 2017-03-10 11:30 | 49976.8388 | 219.996
Devonshire Building | 2017-03-10 11:45 | 49976.8938 | 219.996
Devonshire Building | 2017-03-10 12:00 | 49977.2438 | 1400.004
Devonshire Building | 2017-03-10 12:15 | 49977.2888 | 180
Devonshire Building | 2017-03-10 12:30 | 49977.3488 | 240.012
Devonshire Building | 2017-03-10 12:45 | 49977.3988 | 200.016
Devonshire Building | 2017-03-10 13:00 | 49977.4588 | 240.012
Devonshire Building | 2017-03-10 13:15 | 49977.5088 | 200.016
Devonshire Building | 2017-03-10 13:30 | 49977.5588 | 200.016
Devonshire Building | 2017-03-10 13:45 | 49977.6088 | 200.016
Devonshire Building | 2017-03-10 14:00 | 49977.9338 | 1299.996
Devonshire Building | 2017-03-10 14:15 | 49977.9688 | 140.004
Devonshire Building | 2017-03-10 14:30 | 49978.0088 | 159.984
Devonshire Building | 2017-03-10 14:45 | 49978.0538 | 180
Devonshire Building | 2017-03-10 15:00 | 49978.0938 | 159.984
Devonshire Building | 2017-03-10 15:15 | 49978.1388 | 180
Devonshire Building | 2017-03-10 15:30 | 49978.1788 | 159.984
Devonshire Building | 2017-03-10 15:45 | 49978.2238 | 180
Devonshire Building | 2017-03-10 16:00 | 49978.5188 | 1180.008
Devonshire Building | 2017-03-10 16:15 | 49978.5788 | 240.012
Devonshire Building | 2017-03-10 16:30 | 49978.6188 | 159.984
Devonshire Building | 2017-03-10 16:45 | 49978.6538 | 140.004
Devonshire Building | 2017-03-10 17:00 | 49978.6938 | 159.984
Devonshire Building | 2017-03-10 17:15 | 49978.7338 | 159.984
Devonshire Building | 2017-03-10 17:30 | 49978.7688 | 140.004
Devonshire Building | 2017-03-10 17:45 | 49978.8038 | 140.004
Devonshire Building | 2017-03-10 18:00 | 49978.8388 | 140.004
Devonshire Building | 2017-03-10 18:15 | 49978.8688 | 119.988
Devonshire Building | 2017-03-10 18:30 | 49978.9088 | 159.984
Devonshire Building | 2017-03-10 18:45 | 49978.9588 | 200.016
Devonshire Building | 2017-03-10 19:00 | 49979.0138 | 219.996
Devonshire Building | 2017-03-10 19:15 | 49979.0688 | 219.996
Devonshire Building | 2017-03-10 19:30 | 49979.1188 | 200.016
Devonshire Building | 2017-03-10 19:45 | 49979.1688 | 200.016
Devonshire Building | 2017-03-10 20:00 | 49979.2138 | 180
Devonshire Building | 2017-03-10 20:15 | 49979.2538 | 159.984
Devonshire Building | 2017-03-10 20:30 | 49979.2888 | 140.004
Devonshire Building | 2017-03-10 20:45 | 49979.3238 | 140.004
Devonshire Building | 2017-03-10 21:00 | 49979.3488 | 100.008
Devonshire Building | 2017-03-10 21:15 | 49979.3738 | 100.008
Devonshire Building | 2017-03-10 21:30 | 49979.3938 | 79.992
Devonshire Building | 2017-03-10 21:45 | 49979.6738 | 1119.996
Devonshire Building | 2017-03-10 22:00 | 49979.6838 | 39.996
Devonshire Building | 2017-03-10 22:15 | 49979.6938 | 39.996
Devonshire Building | 2017-03-10 22:30 | 49979.7038 | 39.996
Devonshire Building | 2017-03-10 22:45 | 49979.7088 | 20.016
Devonshire Building | 2017-03-10 23:00 | 49979.7188 | 39.996
Devonshire Building | 2017-03-10 23:15 | 49979.7238 | 20.016
Devonshire Building | 2017-03-10 23:30 | 49979.7338 | 39.996
Devonshire Building | 2017-03-10 23:45 | 49979.7438 | 39.996 | 0
Devonshire Building | 2017-03-11 | 49979.75 | 20.016
Devonshire Building | 2017-03-11 00:15 | 49979.76 | 39.996
Devonshire Building | 2017-03-11 00:30 | 49979.77 | 39.996
Devonshire Building | 2017-03-11 00:45 | 49979.78 | 39.996
Devonshire Building | 2017-03-11 01:00 | 49979.785 | 20.016
Devonshire Building | 2017-03-11 01:15 | 49979.795 | 39.996
Devonshire Building | 2017-03-11 01:30 | 49979.805 | 39.996
Devonshire Building | 2017-03-11 01:45 | 49979.81 | 20.016
Devonshire Building | 2017-03-11 02:00 | 49979.82 | 39.996
Devonshire Building | 2017-03-11 02:15 | 49979.825 | 20.016
Devonshire Building | 2017-03-11 02:30 | 49979.835 | 39.996
Devonshire Building | 2017-03-11 02:45 | 49979.84 | 20.016
Devonshire Building | 2017-03-11 03:00 | 49979.85 | 39.996
Devonshire Building | 2017-03-11 03:15 | 49979.855 | 20.016
Devonshire Building | 2017-03-11 03:30 | 49979.86 | 20.016
Devonshire Building | 2017-03-11 03:45 | 49979.87 | 39.996
Devonshire Building | 2017-03-11 04:00 | 49979.875 | 20.016
Devonshire Building | 2017-03-11 04:15 | 49979.88 | 20.016
Devonshire Building | 2017-03-11 04:30 | 49979.885 | 20.016
Devonshire Building | 2017-03-11 04:45 | 49979.89 | 20.016
Devonshire Building | 2017-03-11 05:00 | 49979.895 | 20.016
Devonshire Building | 2017-03-11 05:15 | 49979.9 | 20.016
Devonshire Building | 2017-03-11 05:30 | 49979.905 | 20.016
Devonshire Building | 2017-03-11 05:45 | 49979.91 | 20.016
Devonshire Building | 2017-03-11 06:00 | 49979.9151 | 20.016
Devonshire Building | 2017-03-11 06:15 | 49979.9201 | 20.016
Devonshire Building | 2017-03-11 06:30 | 49979.9251 | 20.016
Devonshire Building | 2017-03-11 06:45 | 49979.9301 | 20.016
Devonshire Building | 2017-03-11 07:00 | 49979.9351 | 20.016
Devonshire Building | 2017-03-11 07:15 | 49979.9401 | 20.016
Devonshire Building | 2017-03-11 07:30 | 49979.9401 | 0
Devonshire Building | 2017-03-11 07:45 | 49979.9601 | 79.992
Devonshire Building | 2017-03-11 08:00 | 49979.9801 | 79.992
Devonshire Building | 2017-03-11 08:15 | 49980.0001 | 79.992
Devonshire Building | 2017-03-11 08:30 | 49980.0201 | 79.992
Devonshire Building | 2017-03-11 08:45 | 49980.0401 | 79.992
Devonshire Building | 2017-03-11 09:00 | 49980.0601 | 79.992
Devonshire Building | 2017-03-11 09:15 | 49980.0801 | 79.992
Devonshire Building | 2017-03-11 09:30 | 49980.1001 | 79.992
Devonshire Building | 2017-03-11 09:45 | 49980.1201 | 79.992
Devonshire Building | 2017-03-11 10:00 | 49980.1351 | 60.012
Devonshire Building | 2017-03-11 10:15 | 49980.1551 | 79.992
Devonshire Building | 2017-03-11 10:30 | 49980.1551 | 0
Devonshire Building | 2017-03-11 10:45 | 49980.1601 | 20.016
Devonshire Building | 2017-03-11 11:00 | 49980.1601 | 0
Devonshire Building | 2017-03-11 11:15 | 49980.1651 | 20.016
Devonshire Building | 2017-03-11 11:30 | 49980.1701 | 20.016
Devonshire Building | 2017-03-11 11:45 | 49980.1701 | 0
Devonshire Building | 2017-03-11 12:00 | 49980.1751 | 20.016
Devonshire Building | 2017-03-11 12:15 | 49980.1751 | 0
Devonshire Building | 2017-03-11 12:30 | 49980.1801 | 20.016
Devonshire Building | 2017-03-11 12:45 | 49980.1801 | 0
Devonshire Building | 2017-03-11 13:00 | 49980.1851 | 20.016
Devonshire Building | 2017-03-11 13:15 | 49980.1901 | 20.016
Devonshire Building | 2017-03-11 13:30 | 49980.1901 | 0
Devonshire Building | 2017-03-11 13:45 | 49980.1951 | 20.016
Devonshire Building | 2017-03-11 14:00 | 49980.2001 | 20.016
Devonshire Building | 2017-03-11 14:15 | 49980.2051 | 20.016
Devonshire Building | 2017-03-11 14:30 | 49980.2101 | 20.016
Devonshire Building | 2017-03-11 14:45 | 49980.2101 | 0
Devonshire Building | 2017-03-11 15:00 | 49980.2151 | 20.016
Devonshire Building | 2017-03-11 15:15 | 49980.2201 | 20.016
Devonshire Building | 2017-03-11 15:30 | 49980.2251 | 20.016
Devonshire Building | 2017-03-11 15:45 | 49980.2251 | 0
Devonshire Building | 2017-03-11 16:00 | 49980.2301 | 20.016
Devonshire Building | 2017-03-11 16:15 | 49980.2351 | 20.016
Devonshire Building | 2017-03-11 16:30 | 49980.2351 | 0
Devonshire Building | 2017-03-11 16:45 | 49980.2401 | 20.016
Devonshire Building | 2017-03-11 17:00 | 49980.2401 | 0
Devonshire Building | 2017-03-11 17:15 | 49980.2451 | 20.016
Devonshire Building | 2017-03-11 17:30 | 49980.2451 | 0
Devonshire Building | 2017-03-11 17:45 | 49980.2501 | 20.016
Devonshire Building | 2017-03-11 18:00 | 49980.2551 | 20.016
Devonshire Building | 2017-03-11 18:15 | 49980.2601 | 20.016
Devonshire Building | 2017-03-11 18:30 | 49980.2601 | 0
Devonshire Building | 2017-03-11 18:45 | 49980.2651 | 20.016
Devonshire Building | 2017-03-11 19:00 | 49980.2651 | 0
Devonshire Building | 2017-03-11 19:15 | 49980.2701 | 20.016
Devonshire Building | 2017-03-11 19:30 | 49980.5351 | 1059.984
Devonshire Building | 2017-03-11 19:45 | 49980.5401 | 20.016
Devonshire Building | 2017-03-11 20:00 | 49980.5451 | 20.016
Devonshire Building | 2017-03-11 20:15 | 49980.5451 | 0
Devonshire Building | 2017-03-11 20:30 | 49980.5502 | 20.016
Devonshire Building | 2017-03-11 20:45 | 49980.5502 | 0
Devonshire Building | 2017-03-11 21:00 | 49980.5552 | 20.016
Devonshire Building | 2017-03-11 21:15 | 49980.5602 | 20.016
Devonshire Building | 2017-03-11 21:30 | 49980.5602 | 0
Devonshire Building | 2017-03-11 21:45 | 49980.5652 | 20.016
Devonshire Building | 2017-03-11 22:00 | 49980.5702 | 20.016
Devonshire Building | 2017-03-11 22:15 | 49980.5752 | 20.016
Devonshire Building | 2017-03-11 22:30 | 49980.5752 | 0
Devonshire Building | 2017-03-11 22:45 | 49980.5802 | 20.016
Devonshire Building | 2017-03-11 23:00 | 49980.5802 | 0
Devonshire Building | 2017-03-11 23:15 | 49980.5852 | 20.016
Devonshire Building | 2017-03-11 23:30 | 49980.5852 | 0
Devonshire Building | 2017-03-11 23:45 | 49980.5902 | 20.016 | 0
Devonshire Building | 2017-03-12 | 49980.5938 | 20.016
Devonshire Building | 2017-03-12 00:15 | 49980.5938 | 0
Devonshire Building | 2017-03-12 00:30 | 49980.5988 | 20.016
Devonshire Building | 2017-03-12 00:45 | 49980.5988 | 0
Devonshire Building | 2017-03-12 01:00 | 49980.6038 | 20.016
Devonshire Building | 2017-03-12 01:15 | 49980.6088 | 20.016
Devonshire Building | 2017-03-12 01:30 | 49980.6088 | 0
Devonshire Building | 2017-03-12 01:45 | 49980.6138 | 20.016
Devonshire Building | 2017-03-12 02:00 | 49980.6188 | 20.016
Devonshire Building | 2017-03-12 02:15 | 49980.6188 | 0
Devonshire Building | 2017-03-12 02:30 | 49980.6238 | 20.016
Devonshire Building | 2017-03-12 02:45 | 49980.6288 | 20.016
Devonshire Building | 2017-03-12 03:00 | 49980.6288 | 0
Devonshire Building | 2017-03-12 03:15 | 49980.6338 | 20.016
Devonshire Building | 2017-03-12 03:30 | 49980.6388 | 20.016
Devonshire Building | 2017-03-12 03:45 | 49980.6388 | 0
Devonshire Building | 2017-03-12 04:00 | 49980.6438 | 20.016
Devonshire Building | 2017-03-12 04:15 | 49980.6488 | 20.016
Devonshire Building | 2017-03-12 04:30 | 49980.6488 | 0
Devonshire Building | 2017-03-12 04:45 | 49980.6538 | 20.016
Devonshire Building | 2017-03-12 05:00 | 49980.6588 | 20.016
Devonshire Building | 2017-03-12 05:15 | 49980.6588 | 0
Devonshire Building | 2017-03-12 05:30 | 49980.6638 | 20.016
Devonshire Building | 2017-03-12 05:45 | 49980.6688 | 20.016
Devonshire Building | 2017-03-12 06:00 | 49980.6688 | 0
Devonshire Building | 2017-03-12 06:15 | 49980.6738 | 20.016
Devonshire Building | 2017-03-12 06:30 | 49980.6788 | 20.016
Devonshire Building | 2017-03-12 06:45 | 49980.6788 | 0
Devonshire Building | 2017-03-12 07:00 | 49980.6838 | 20.016
Devonshire Building | 2017-03-12 07:15 | 49980.6888 | 20.016
Devonshire Building | 2017-03-12 07:30 | 49980.6888 | 0
Devonshire Building | 2017-03-12 07:45 | 49980.6988 | 39.996
Devonshire Building | 2017-03-12 08:00 | 49980.7188 | 79.992
Devonshire Building | 2017-03-12 08:15 | 49980.7388 | 79.992
Devonshire Building | 2017-03-12 08:30 | 49980.7538 | 60.012
Devonshire Building | 2017-03-12 08:45 | 49980.7738 | 79.992
Devonshire Building | 2017-03-12 09:00 | 49980.7938 | 79.992
Devonshire Building | 2017-03-12 09:15 | 49980.8138 | 79.992
Devonshire Building | 2017-03-12 09:30 | 49980.8338 | 79.992
Devonshire Building | 2017-03-12 09:45 | 49980.8538 | 79.992
Devonshire Building | 2017-03-12 10:00 | 49980.8738 | 79.992
Devonshire Building | 2017-03-12 10:15 | 49980.8888 | 60.012
Devonshire Building | 2017-03-12 10:30 | 49980.8938 | 20.016
Devonshire Building | 2017-03-12 10:45 | 49980.8988 | 20.016
Devonshire Building | 2017-03-12 11:00 | 49980.8988 | 0
Devonshire Building | 2017-03-12 11:15 | 49980.9038 | 20.016
Devonshire Building | 2017-03-12 11:30 | 49980.9088 | 20.016
Devonshire Building | 2017-03-12 11:45 | 49980.9088 | 0
Devonshire Building | 2017-03-12 12:00 | 49980.9138 | 20.016
Devonshire Building | 2017-03-12 12:15 | 49980.9188 | 20.016
Devonshire Building | 2017-03-12 12:30 | 49980.9238 | 20.016
Devonshire Building | 2017-03-12 12:45 | 49980.9288 | 20.016
Devonshire Building | 2017-03-12 13:00 | 49980.9339 | 20.016
Devonshire Building | 2017-03-12 13:15 | 49980.9389 | 20.016
Devonshire Building | 2017-03-12 13:30 | 49980.9389 | 0
Devonshire Building | 2017-03-12 13:45 | 49980.9439 | 20.016
Devonshire Building | 2017-03-12 14:00 | 49980.9489 | 20.016
Devonshire Building | 2017-03-12 14:15 | 49980.9489 | 0
Devonshire Building | 2017-03-12 14:30 | 49980.9539 | 20.016
Devonshire Building | 2017-03-12 14:45 | 49980.9589 | 20.016
Devonshire Building | 2017-03-12 15:00 | 49980.9589 | 0
Devonshire Building | 2017-03-12 15:15 | 49980.9639 | 20.016
Devonshire Building | 2017-03-12 15:30 | 49980.9639 | 0
Devonshire Building | 2017-03-12 15:45 | 49980.9689 | 20.016
Devonshire Building | 2017-03-12 16:00 | 49980.9739 | 20.016
Devonshire Building | 2017-03-12 16:15 | 49980.9789 | 20.016
Devonshire Building | 2017-03-12 16:30 | 49980.9839 | 20.016
Devonshire Building | 2017-03-12 16:45 | 49980.9889 | 20.016
Devonshire Building | 2017-03-12 17:00 | 49980.9889 | 0
Devonshire Building | 2017-03-12 17:15 | 49980.9939 | 20.016
Devonshire Building | 2017-03-12 17:30 | 49980.9989 | 20.016
Devonshire Building | 2017-03-12 17:45 | 49981.0039 | 20.016
Devonshire Building | 2017-03-12 18:00 | 49981.0039 | 0
Devonshire Building | 2017-03-12 18:15 | 49981.0089 | 20.016
Devonshire Building | 2017-03-12 18:30 | 49981.2689 | 1040.004
Devonshire Building | 2017-03-12 18:45 | 49981.2689 | 0
Devonshire Building | 2017-03-12 19:00 | 49981.2739 | 20.016
Devonshire Building | 2017-03-12 19:15 | 49981.2739 | 0
Devonshire Building | 2017-03-12 19:30 | 49981.2789 | 20.016
Devonshire Building | 2017-03-12 19:45 | 49981.2839 | 20.016
Devonshire Building | 2017-03-12 20:00 | 49981.2839 | 0
Devonshire Building | 2017-03-12 20:15 | 49981.2889 | 20.016
Devonshire Building | 2017-03-12 20:30 | 49981.2889 | 0
Devonshire Building | 2017-03-12 20:45 | 49981.2939 | 20.016
Devonshire Building | 2017-03-12 21:00 | 49981.2989 | 20.016
Devonshire Building | 2017-03-12 21:15 | 49981.2989 | 0
Devonshire Building | 2017-03-12 21:30 | 49981.3039 | 20.016
Devonshire Building | 2017-03-12 21:45 | 49981.3089 | 20.016
Devonshire Building | 2017-03-12 22:00 | 49981.3139 | 20.016
Devonshire Building | 2017-03-12 22:15 | 49981.319 | 20.016
Devonshire Building | 2017-03-12 22:30 | 49981.319 | 0
Devonshire Building | 2017-03-12 22:45 | 49981.324 | 20.016
Devonshire Building | 2017-03-12 23:00 | 49981.324 | 0
Devonshire Building | 2017-03-12 23:15 | 49981.329 | 20.016
Devonshire Building | 2017-03-12 23:30 | 49981.334 | 20.016
Devonshire Building | 2017-03-12 23:45 | 49981.334 | 0 | 0
Devonshire Building | 2017-03-13 | 49981.3398 | 20.016
Devonshire Building | 2017-03-13 00:15 | 49981.3448 | 20.016
Devonshire Building | 2017-03-13 00:30 | 49981.3448 | 0
Devonshire Building | 2017-03-13 00:45 | 49981.3498 | 20.016
Devonshire Building | 2017-03-13 01:00 | 49981.3549 | 20.016
Devonshire Building | 2017-03-13 01:15 | 49981.3549 | 0
Devonshire Building | 2017-03-13 01:30 | 49981.3599 | 20.016
Devonshire Building | 2017-03-13 01:45 | 49981.3649 | 20.016
Devonshire Building | 2017-03-13 02:00 | 49981.3649 | 0
Devonshire Building | 2017-03-13 02:15 | 49981.3699 | 20.016
Devonshire Building | 2017-03-13 02:30 | 49981.3749 | 20.016
Devonshire Building | 2017-03-13 02:45 | 49981.3799 | 20.016
Devonshire Building | 2017-03-13 03:00 | 49981.3799 | 0
Devonshire Building | 2017-03-13 03:15 | 49981.3849 | 20.016
Devonshire Building | 2017-03-13 03:30 | 49981.3899 | 20.016
Devonshire Building | 2017-03-13 03:45 | 49981.3899 | 0
Devonshire Building | 2017-03-13 04:00 | 49981.3949 | 20.016
Devonshire Building | 2017-03-13 04:15 | 49981.3999 | 20.016
Devonshire Building | 2017-03-13 04:30 | 49981.3999 | 0
Devonshire Building | 2017-03-13 04:45 | 49981.4049 | 20.016
Devonshire Building | 2017-03-13 05:00 | 49981.4099 | 20.016
Devonshire Building | 2017-03-13 05:15 | 49981.4149 | 20.016
Devonshire Building | 2017-03-13 05:30 | 49981.4149 | 0
Devonshire Building | 2017-03-13 05:45 | 49981.4199 | 20.016
Devonshire Building | 2017-03-13 06:00 | 49981.4249 | 20.016
Devonshire Building | 2017-03-13 06:15 | 49981.4299 | 20.016
Devonshire Building | 2017-03-13 06:30 | 49981.4299 | 0
Devonshire Building | 2017-03-13 06:45 | 49981.4349 | 20.016
Devonshire Building | 2017-03-13 07:00 | 49981.4399 | 20.016
Devonshire Building | 2017-03-13 07:15 | 49981.4449 | 20.016
Devonshire Building | 2017-03-13 07:30 | 49981.4499 | 20.016
Devonshire Building | 2017-03-13 07:45 | 49981.4649 | 60.012
Devonshire Building | 2017-03-13 08:00 | 49981.4899 | 100.008
Devonshire Building | 2017-03-13 08:15 | 49981.5199 | 119.988
Devonshire Building | 2017-03-13 08:30 | 49981.5499 | 119.988
Devonshire Building | 2017-03-13 08:45 | 49981.8049 | 1019.988
Devonshire Building | 2017-03-13 09:00 | 49981.8349 | 119.988
Devonshire Building | 2017-03-13 09:15 | 49981.8599 | 100.008
Devonshire Building | 2017-03-13 09:30 | 49981.8849 | 100.008
Devonshire Building | 2017-03-13 09:45 | 49981.9099 | 100.008
Devonshire Building | 2017-03-13 10:00 | 49981.9449 | 140.004
Devonshire Building | 2017-03-13 10:15 | 49982.3849 | 1760.004
Devonshire Building | 2017-03-13 10:30 | 49982.6199 | 939.996
Devonshire Building | 2017-03-13 10:45 | 49982.7899 | 680.004
Devonshire Building | 2017-03-13 11:00 | 49982.9449 | 619.992
Devonshire Building | 2017-03-13 11:15 | 49983.0499 | 420.012
Devonshire Building | 2017-03-13 11:30 | 49983.1299 | 320.004
Devonshire Building | 2017-03-13 11:45 | 49983.4799 | 1400.004
Devonshire Building | 2017-03-13 12:00 | 49983.5399 | 240.012
Devonshire Building | 2017-03-13 12:15 | 49983.6049 | 259.992
Devonshire Building | 2017-03-13 12:30 | 49983.6699 | 259.992
Devonshire Building | 2017-03-13 12:45 | 49983.7549 | 339.984
Devonshire Building | 2017-03-13 13:00 | 49984.0849 | 1320.012
Devonshire Building | 2017-03-13 13:15 | 49984.2299 | 579.996
Devonshire Building | 2017-03-13 13:30 | 49984.3449 | 460.008
Devonshire Building | 2017-03-13 13:45 | 49984.4799 | 540
Devonshire Building | 2017-03-13 14:00 | 49984.5899 | 439.992
Devonshire Building | 2017-03-13 14:15 | 49984.6999 | 439.992
Devonshire Building | 2017-03-13 14:30 | 49984.7849 | 339.984
Devonshire Building | 2017-03-13 14:45 | 49985.1399 | 1419.984
Devonshire Building | 2017-03-13 15:00 | 49985.1849 | 180
Devonshire Building | 2017-03-13 15:15 | 49985.2249 | 159.984
Devonshire Building | 2017-03-13 15:30 | 49985.2699 | 180
Devonshire Building | 2017-03-13 15:45 | 49985.3099 | 159.984
Devonshire Building | 2017-03-13 16:00 | 49985.3549 | 180
Devonshire Building | 2017-03-13 16:15 | 49985.3899 | 140.004
Devonshire Building | 2017-03-13 16:30 | 49985.7049 | 1260
Devonshire Building | 2017-03-13 16:45 | 49985.7399 | 140.004
Devonshire Building | 2017-03-13 17:00 | 49985.7749 | 140.004
Devonshire Building | 2017-03-13 17:15 | 49985.8149 | 159.984
Devonshire Building | 2017-03-13 17:30 | 49985.8499 | 140.004
Devonshire Building | 2017-03-13 17:45 | 49985.8849 | 140.004
Devonshire Building | 2017-03-13 18:00 | 49985.9199 | 140.004
Devonshire Building | 2017-03-13 18:15 | 49985.9549 | 140.004
Devonshire Building | 2017-03-13 18:30 | 49985.9849 | 119.988
Devonshire Building | 2017-03-13 18:45 | 49986.0149 | 119.988
Devonshire Building | 2017-03-13 19:00 | 49986.0449 | 119.988
Devonshire Building | 2017-03-13 19:15 | 49986.0749 | 119.988
Devonshire Building | 2017-03-13 19:30 | 49986.0999 | 100.008
Devonshire Building | 2017-03-13 19:45 | 49986.1249 | 100.008
Devonshire Building | 2017-03-13 20:00 | 49986.1449 | 79.992
Devonshire Building | 2017-03-13 20:15 | 49986.1649 | 79.992
Devonshire Building | 2017-03-13 20:30 | 49986.1849 | 79.992
Devonshire Building | 2017-03-13 20:45 | 49986.1999 | 60.012
Devonshire Building | 2017-03-13 21:00 | 49986.2149 | 60.012
Devonshire Building | 2017-03-13 21:15 | 49986.2299 | 60.012
Devonshire Building | 2017-03-13 21:30 | 49986.2399 | 39.996
Devonshire Building | 2017-03-13 21:45 | 49986.2549 | 60.012
Devonshire Building | 2017-03-13 22:00 | 49986.2799 | 100.008
Devonshire Building | 2017-03-13 22:15 | 49986.2849 | 20.016
Devonshire Building | 2017-03-13 22:30 | 49986.2899 | 20.016
Devonshire Building | 2017-03-13 22:45 | 49986.2899 | 0
Devonshire Building | 2017-03-13 23:00 | 49986.2949 | 20.016
Devonshire Building | 2017-03-13 23:15 | 49986.2999 | 20.016
Devonshire Building | 2017-03-13 23:30 | 49986.2999 | 0
Devonshire Building | 2017-03-13 23:45 | 49986.3049 | 20.016 | 0
Devonshire Building | 2017-03-14 | 49986.3086 | 20.016
Devonshire Building | 2017-03-14 00:15 | 49986.3086 | 0
Devonshire Building | 2017-03-14 00:30 | 49986.3136 | 20.016
Devonshire Building | 2017-03-14 00:45 | 49986.3186 | 20.016
Devonshire Building | 2017-03-14 01:00 | 49986.3186 | 0
Devonshire Building | 2017-03-14 01:15 | 49986.3236 | 20.016
Devonshire Building | 2017-03-14 01:30 | 49986.3286 | 20.016
Devonshire Building | 2017-03-14 01:45 | 49986.3286 | 0
Devonshire Building | 2017-03-14 02:00 | 49986.3336 | 20.016
Devonshire Building | 2017-03-14 02:15 | 49986.5936 | 1040.004
Devonshire Building | 2017-03-14 02:30 | 49986.5986 | 20.016
Devonshire Building | 2017-03-14 02:45 | 49986.5986 | 0
Devonshire Building | 2017-03-14 03:00 | 49986.6036 | 20.016
Devonshire Building | 2017-03-14 03:15 | 49986.6036 | 0
Devonshire Building | 2017-03-14 03:30 | 49986.6086 | 20.016
Devonshire Building | 2017-03-14 03:45 | 49986.6136 | 20.016
Devonshire Building | 2017-03-14 04:00 | 49986.6136 | 0
Devonshire Building | 2017-03-14 04:15 | 49986.6186 | 20.016
Devonshire Building | 2017-03-14 04:30 | 49986.6186 | 0
Devonshire Building | 2017-03-14 04:45 | 49986.6236 | 20.016
Devonshire Building | 2017-03-14 05:00 | 49986.6236 | 0
Devonshire Building | 2017-03-14 05:15 | 49986.6286 | 20.016
Devonshire Building | 2017-03-14 05:30 | 49986.6286 | 0
Devonshire Building | 2017-03-14 05:45 | 49986.6336 | 20.016
Devonshire Building | 2017-03-14 06:00 | 49986.6336 | 0
Devonshire Building | 2017-03-14 06:15 | 49986.6386 | 20.016
Devonshire Building | 2017-03-14 06:30 | 49986.6437 | 20.016
Devonshire Building | 2017-03-14 06:45 | 49986.6487 | 20.016
Devonshire Building | 2017-03-14 07:00 | 49986.6537 | 20.016
Devonshire Building | 2017-03-14 07:15 | 49986.6537 | 0
Devonshire Building | 2017-03-14 07:30 | 49986.6587 | 20.016
Devonshire Building | 2017-03-14 07:45 | 49986.6787 | 79.992
Devonshire Building | 2017-03-14 08:00 | 49986.7037 | 100.008
Devonshire Building | 2017-03-14 08:15 | 49986.7237 | 79.992
Devonshire Building | 2017-03-14 08:30 | 49986.7537 | 119.988
Devonshire Building | 2017-03-14 08:45 | 49986.7837 | 119.988
Devonshire Building | 2017-03-14 09:00 | 49986.8037 | 79.992
Devonshire Building | 2017-03-14 09:15 | 49986.8287 | 100.008
Devonshire Building | 2017-03-14 09:30 | 49987.1387 | 1239.984
Devonshire Building | 2017-03-14 09:45 | 49987.1686 | 119.988
Devonshire Building | 2017-03-14 10:00 | 49987.2086 | 159.984
Devonshire Building | 2017-03-14 10:15 | 49987.2436 | 140.004
Devonshire Building | 2017-03-14 10:30 | 49987.2836 | 159.984
Devonshire Building | 2017-03-14 10:45 | 49987.6636 | 1519.992
Devonshire Building | 2017-03-14 11:00 | 49987.8036 | 560.016
Devonshire Building | 2017-03-14 11:15 | 49987.9386 | 540
Devonshire Building | 2017-03-14 11:30 | 49988.0486 | 439.992
Devonshire Building | 2017-03-14 11:45 | 49988.1486 | 399.996
Devonshire Building | 2017-03-14 12:00 | 49988.2536 | 420.012
Devonshire Building | 2017-03-14 12:15 | 49988.6136 | 1440
Devonshire Building | 2017-03-14 12:30 | 49988.6986 | 339.984
Devonshire Building | 2017-03-14 12:45 | 49988.7786 | 320.004
Devonshire Building | 2017-03-14 13:00 | 49988.8486 | 280.008
Devonshire Building | 2017-03-14 13:15 | 49989.1736 | 1299.996
Devonshire Building | 2017-03-14 13:30 | 49989.2136 | 159.984
Devonshire Building | 2017-03-14 13:45 | 49989.2486 | 140.004
Devonshire Building | 2017-03-14 14:00 | 49989.3236 | 299.988
Devonshire Building | 2017-03-14 14:15 | 49989.3536 | 119.988
Devonshire Building | 2017-03-14 14:30 | 49989.3936 | 159.984
Devonshire Building | 2017-03-14 14:45 | 49989.4336 | 159.984
Devonshire Building | 2017-03-14 15:00 | 49989.8036 | 1479.996
Devonshire Building | 2017-03-14 15:15 | 49989.8586 | 219.996
Devonshire Building | 2017-03-14 15:30 | 49989.9086 | 200.016
Devonshire Building | 2017-03-14 15:45 | 49989.9586 | 200.016
Devonshire Building | 2017-03-14 16:00 | 49990.0136 | 219.996
Devonshire Building | 2017-03-14 16:15 | 49990.0586 | 180
Devonshire Building | 2017-03-14 16:30 | 49990.1086 | 200.016
Devonshire Building | 2017-03-14 16:45 | 49990.4286 | 1280.016
Devonshire Building | 2017-03-14 17:00 | 49990.4736 | 180
Devonshire Building | 2017-03-14 17:15 | 49990.5186 | 180
Devonshire Building | 2017-03-14 17:30 | 49990.5636 | 180
Devonshire Building | 2017-03-14 17:45 | 49990.6086 | 180
Devonshire Building | 2017-03-14 18:00 | 49990.6486 | 159.984
Devonshire Building | 2017-03-14 18:15 | 49990.6836 | 140.004
Devonshire Building | 2017-03-14 18:30 | 49990.7136 | 119.988
Devonshire Building | 2017-03-14 18:45 | 49990.7386 | 100.008
Devonshire Building | 2017-03-14 19:00 | 49990.7636 | 100.008
Devonshire Building | 2017-03-14 19:15 | 49990.7836 | 79.992
Devonshire Building | 2017-03-14 19:30 | 49990.8036 | 79.992
Devonshire Building | 2017-03-14 19:45 | 49990.8186 | 60.012
Devonshire Building | 2017-03-14 20:00 | 49990.8386 | 79.992
Devonshire Building | 2017-03-14 20:15 | 49990.8536 | 60.012
Devonshire Building | 2017-03-14 20:30 | 49990.8636 | 39.996
Devonshire Building | 2017-03-14 20:45 | 49990.8786 | 60.012
Devonshire Building | 2017-03-14 21:00 | 49990.8886 | 39.996
Devonshire Building | 2017-03-14 21:15 | 49990.8986 | 39.996
Devonshire Building | 2017-03-14 21:30 | 49990.9086 | 39.996
Devonshire Building | 2017-03-14 21:45 | 49990.9186 | 39.996
Devonshire Building | 2017-03-14 22:00 | 49990.9486 | 119.988
Devonshire Building | 2017-03-14 22:15 | 49990.9486 | 0
Devonshire Building | 2017-03-14 22:30 | 49990.9536 | 20.016
Devonshire Building | 2017-03-14 22:45 | 49990.9536 | 0
Devonshire Building | 2017-03-14 23:00 | 49990.9586 | 20.016
Devonshire Building | 2017-03-14 23:15 | 49990.9636 | 20.016
Devonshire Building | 2017-03-14 23:30 | 49990.9636 | 0
Devonshire Building | 2017-03-14 23:45 | 49990.9686 | 20.016 | 0
Devonshire Building | 2017-03-15 | 49990.9688 | 0
Devonshire Building | 2017-03-15 00:15 | 49990.9738 | 20.016
Devonshire Building | 2017-03-15 00:30 | 49991.0038 | 119.988
Devonshire Building | 2017-03-15 00:45 | 49991.2387 | 939.996
Devonshire Building | 2017-03-15 01:00 | 49991.2438 | 20.016
Devonshire Building | 2017-03-15 01:15 | 49991.2438 | 0
Devonshire Building | 2017-03-15 01:30 | 49991.2538 | 39.996
Devonshire Building | 2017-03-15 01:45 | 49991.2688 | 60.012
Devonshire Building | 2017-03-15 02:00 | 49991.2888 | 79.992
Devonshire Building | 2017-03-15 02:15 | 49991.3088 | 79.992
Devonshire Building | 2017-03-15 02:30 | 49991.3238 | 60.012
Devonshire Building | 2017-03-15 02:45 | 49991.3438 | 79.992
Devonshire Building | 2017-03-15 03:00 | 49991.3638 | 79.992
Devonshire Building | 2017-03-15 03:15 | 49991.3788 | 60.012
Devonshire Building | 2017-03-15 03:30 | 49991.3988 | 79.992
Devonshire Building | 2017-03-15 03:45 | 49991.4187 | 79.992
Devonshire Building | 2017-03-15 04:00 | 49991.4338 | 60.012
Devonshire Building | 2017-03-15 04:15 | 49991.4538 | 79.992
Devonshire Building | 2017-03-15 04:30 | 49991.4538 | 0
Devonshire Building | 2017-03-15 04:45 | 49991.4588 | 20.016
Devonshire Building | 2017-03-15 05:00 | 49991.4588 | 0
Devonshire Building | 2017-03-15 05:15 | 49991.4638 | 20.016
Devonshire Building | 2017-03-15 05:30 | 49991.4638 | 0
Devonshire Building | 2017-03-15 05:45 | 49991.4688 | 20.016
Devonshire Building | 2017-03-15 06:00 | 49991.4688 | 0
Devonshire Building | 2017-03-15 06:15 | 49991.4738 | 20.016
Devonshire Building | 2017-03-15 06:30 | 49991.4788 | 20.016
Devonshire Building | 2017-03-15 06:45 | 49991.4838 | 20.016
Devonshire Building | 2017-03-15 07:00 | 49991.4888 | 20.016
Devonshire Building | 2017-03-15 07:15 | 49991.4888 | 0
Devonshire Building | 2017-03-15 07:30 | 49991.4938 | 20.016
Devonshire Building | 2017-03-15 07:45 | 49991.5138 | 79.992
Devonshire Building | 2017-03-15 08:00 | 49991.5138 | 0
Devonshire Building | 2017-03-15 08:15 | 49991.5238 | 39.996
Devonshire Building | 2017-03-15 08:30 | 49991.5288 | 20.016
Devonshire Building | 2017-03-15 08:45 | 49991.5388 | 39.996
Devonshire Building | 2017-03-15 09:00 | 49991.5538 | 60.012
Devonshire Building | 2017-03-15 09:15 | 49991.5638 | 39.996
Devonshire Building | 2017-03-15 09:30 | 49991.5738 | 39.996
Devonshire Building | 2017-03-15 09:45 | 49991.8788 | 1220.004
Devonshire Building | 2017-03-15 10:00 | 49991.8888 | 39.996
Devonshire Building | 2017-03-15 10:15 | 49991.8988 | 39.996
Devonshire Building | 2017-03-15 10:30 | 49991.9138 | 60.012
Devonshire Building | 2017-03-15 10:45 | 49991.9388 | 100.008
Devonshire Building | 2017-03-15 11:00 | 49992.2838 | 1379.988
Devonshire Building | 2017-03-15 11:15 | 49992.3638 | 320.004
Devonshire Building | 2017-03-15 11:30 | 49992.4538 | 360
Devonshire Building | 2017-03-15 11:45 | 49992.5388 | 339.984
Devonshire Building | 2017-03-15 12:00 | 49992.9288 | 1559.988
Devonshire Building | 2017-03-15 12:15 | 49992.9988 | 280.008
Devonshire Building | 2017-03-15 12:30 | 49993.0788 | 320.004
Devonshire Building | 2017-03-15 12:45 | 49993.1438 | 259.992
Devonshire Building | 2017-03-15 13:00 | 49993.2088 | 259.992
Devonshire Building | 2017-03-15 13:15 | 49993.4438 | 939.996
Devonshire Building | 2017-03-15 13:30 | 49993.6388 | 780.012
Devonshire Building | 2017-03-15 13:45 | 49993.7038 | 259.992
Devonshire Building | 2017-03-15 14:00 | 49993.7688 | 259.992
Devonshire Building | 2017-03-15 14:15 | 49993.8338 | 259.992
Devonshire Building | 2017-03-15 14:30 | 49993.8938 | 240.012
Devonshire Building | 2017-03-15 14:45 | 49993.9588 | 259.992
Devonshire Building | 2017-03-15 15:00 | 49994.3238 | 1460.016
Devonshire Building | 2017-03-15 15:15 | 49994.3988 | 299.988
Devonshire Building | 2017-03-15 15:30 | 49994.4738 | 299.988
Devonshire Building | 2017-03-15 15:45 | 49994.5688 | 380.016
Devonshire Building | 2017-03-15 16:00 | 49994.6838 | 460.008
Devonshire Building | 2017-03-15 16:15 | 49995.0588 | 1500.012
Devonshire Building | 2017-03-15 16:30 | 49995.1588 | 399.996
Devonshire Building | 2017-03-15 16:45 | 49995.2338 | 299.988
Devonshire Building | 2017-03-15 17:00 | 49995.2988 | 259.992
Devonshire Building | 2017-03-15 17:15 | 49995.3488 | 200.016
Devonshire Building | 2017-03-15 17:30 | 49995.3888 | 159.984
Devonshire Building | 2017-03-15 17:45 | 49995.4288 | 159.984
Devonshire Building | 2017-03-15 18:00 | 49995.7538 | 1299.996
Devonshire Building | 2017-03-15 18:15 | 49995.7688 | 60.012
Devonshire Building | 2017-03-15 18:30 | 49995.7838 | 60.012
Devonshire Building | 2017-03-15 18:45 | 49995.7988 | 60.012
Devonshire Building | 2017-03-15 19:00 | 49995.8138 | 60.012
Devonshire Building | 2017-03-15 19:15 | 49995.8288 | 60.012
Devonshire Building | 2017-03-15 19:30 | 49995.8438 | 60.012
Devonshire Building | 2017-03-15 19:45 | 49995.8588 | 60.012
Devonshire Building | 2017-03-15 20:00 | 49995.8738 | 60.012
Devonshire Building | 2017-03-15 20:15 | 49995.8888 | 60.012
Devonshire Building | 2017-03-15 20:30 | 49995.9038 | 60.012
Devonshire Building | 2017-03-15 20:45 | 49995.9138 | 39.996
Devonshire Building | 2017-03-15 21:00 | 49995.9288 | 60.012
Devonshire Building | 2017-03-15 21:15 | 49995.9388 | 39.996
Devonshire Building | 2017-03-15 21:30 | 49995.9538 | 60.012
Devonshire Building | 2017-03-15 21:45 | 49995.9638 | 39.996
Devonshire Building | 2017-03-15 22:00 | 49995.9788 | 60.012
Devonshire Building | 2017-03-15 22:15 | 49995.9888 | 39.996
Devonshire Building | 2017-03-15 22:30 | 49995.9988 | 39.996
Devonshire Building | 2017-03-15 22:45 | 49996.0088 | 39.996
Devonshire Building | 2017-03-15 23:00 | 49996.0188 | 39.996
Devonshire Building | 2017-03-15 23:15 | 49996.0288 | 39.996
Devonshire Building | 2017-03-15 23:30 | 49996.0338 | 20.016
Devonshire Building | 2017-03-15 23:45 | 49996.0438 | 39.996 | 0
Devonshire Building | 2017-03-16 | 49996.0547 | 39.996
Devonshire Building | 2017-03-16 00:15 | 49996.0597 | 20.016
Devonshire Building | 2017-03-16 00:30 | 49996.0697 | 39.996
Devonshire Building | 2017-03-16 00:45 | 49996.0747 | 20.016
Devonshire Building | 2017-03-16 01:00 | 49996.0847 | 39.996
Devonshire Building | 2017-03-16 01:15 | 49996.0897 | 20.016
Devonshire Building | 2017-03-16 01:30 | 49996.0947 | 20.016
Devonshire Building | 2017-03-16 01:45 | 49996.1047 | 39.996
Devonshire Building | 2017-03-16 02:00 | 49996.1097 | 20.016
Devonshire Building | 2017-03-16 02:15 | 49996.1147 | 20.016
Devonshire Building | 2017-03-16 02:30 | 49996.1197 | 20.016
Devonshire Building | 2017-03-16 02:45 | 49996.1247 | 20.016
Devonshire Building | 2017-03-16 03:00 | 49996.1297 | 20.016
Devonshire Building | 2017-03-16 03:15 | 49996.1347 | 20.016
Devonshire Building | 2017-03-16 03:30 | 49996.1397 | 20.016
Devonshire Building | 2017-03-16 03:45 | 49996.1447 | 20.016
Devonshire Building | 2017-03-16 04:00 | 49996.1497 | 20.016
Devonshire Building | 2017-03-16 04:15 | 49996.1547 | 20.016
Devonshire Building | 2017-03-16 04:30 | 49996.1597 | 20.016
Devonshire Building | 2017-03-16 04:45 | 49996.1648 | 20.016
Devonshire Building | 2017-03-16 05:00 | 49996.1698 | 20.016
Devonshire Building | 2017-03-16 05:15 | 49996.1748 | 20.016
Devonshire Building | 2017-03-16 05:30 | 49996.1798 | 20.016
Devonshire Building | 2017-03-16 05:45 | 49996.1848 | 20.016
Devonshire Building | 2017-03-16 06:00 | 49996.1848 | 0
Devonshire Building | 2017-03-16 06:15 | 49996.1898 | 20.016
Devonshire Building | 2017-03-16 06:30 | 49996.1948 | 20.016
Devonshire Building | 2017-03-16 06:45 | 49996.2048 | 39.996
Devonshire Building | 2017-03-16 07:00 | 49996.2048 | 0
Devonshire Building | 2017-03-16 07:15 | 49996.2098 | 20.016
Devonshire Building | 2017-03-16 07:30 | 49996.2148 | 20.016
Devonshire Building | 2017-03-16 07:45 | 49996.2198 | 20.016
Devonshire Building | 2017-03-16 08:00 | 49996.2348 | 60.012
Devonshire Building | 2017-03-16 08:15 | 49996.2598 | 100.008
Devonshire Building | 2017-03-16 08:30 | 49996.2798 | 79.992
Devonshire Building | 2017-03-16 08:45 | 49996.3048 | 100.008
Devonshire Building | 2017-03-16 09:00 | 49996.6348 | 1320.012
Devonshire Building | 2017-03-16 09:15 | 49996.6548 | 79.992
Devonshire Building | 2017-03-16 09:30 | 49996.6798 | 100.008
Devonshire Building | 2017-03-16 09:45 | 49996.6998 | 79.992
Devonshire Building | 2017-03-16 10:00 | 49996.7248 | 100.008
Devonshire Building | 2017-03-16 10:15 | 49996.7448 | 79.992
Devonshire Building | 2017-03-16 10:30 | 49996.7598 | 60.012
Devonshire Building | 2017-03-16 10:45 | 49997.0848 | 1299.996
Devonshire Building | 2017-03-16 11:00 | 49997.1648 | 320.004
Devonshire Building | 2017-03-16 11:15 | 49997.2748 | 439.992
Devonshire Building | 2017-03-16 11:30 | 49997.3848 | 439.992
Devonshire Building | 2017-03-16 11:45 | 49997.4848 | 399.996
Devonshire Building | 2017-03-16 12:00 | 49997.5698 | 339.984
Devonshire Building | 2017-03-16 12:15 | 49997.7448 | 699.984
Devonshire Building | 2017-03-16 12:30 | 49997.9698 | 900
Devonshire Building | 2017-03-16 12:45 | 49998.0148 | 180
Devonshire Building | 2017-03-16 13:00 | 49998.0748 | 240.012
Devonshire Building | 2017-03-16 13:15 | 49998.1248 | 200.016
Devonshire Building | 2017-03-16 13:30 | 49998.1748 | 200.016
Devonshire Building | 2017-03-16 13:45 | 49998.2248 | 200.016
Devonshire Building | 2017-03-16 14:00 | 49998.5498 | 1299.996
Devonshire Building | 2017-03-16 14:15 | 49998.6048 | 219.996
Devonshire Building | 2017-03-16 14:30 | 49998.6598 | 219.996
Devonshire Building | 2017-03-16 14:45 | 49998.7148 | 219.996
Devonshire Building | 2017-03-16 15:00 | 49998.7698 | 219.996
Devonshire Building | 2017-03-16 15:15 | 49998.8198 | 200.016
Devonshire Building | 2017-03-16 15:30 | 49999.1198 | 1199.988
Devonshire Building | 2017-03-16 15:45 | 49999.1748 | 219.996
Devonshire Building | 2017-03-16 16:00 | 49999.2148 | 159.984
Devonshire Building | 2017-03-16 16:15 | 49999.2548 | 159.984
Devonshire Building | 2017-03-16 16:30 | 49999.2998 | 180
Devonshire Building | 2017-03-16 16:45 | 49999.3398 | 159.984
Devonshire Building | 2017-03-16 17:00 | 49999.3798 | 159.984
Devonshire Building | 2017-03-16 17:15 | 49999.4198 | 159.984
Devonshire Building | 2017-03-16 17:30 | 49999.6998 | 1119.996
Devonshire Building | 2017-03-16 17:45 | 49999.7448 | 180
Devonshire Building | 2017-03-16 18:00 | 49999.7648 | 79.992
Devonshire Building | 2017-03-16 18:15 | 49999.7848 | 79.992
Devonshire Building | 2017-03-16 18:30 | 49999.8098 | 100.008
Devonshire Building | 2017-03-16 18:45 | 49999.8298 | 79.992
Devonshire Building | 2017-03-16 19:00 | 49999.8548 | 100.008
Devonshire Building | 2017-03-16 19:15 | 49999.8798 | 100.008
Devonshire Building | 2017-03-16 19:30 | 49999.8998 | 79.992
Devonshire Building | 2017-03-16 19:45 | 49999.9198 | 79.992
Devonshire Building | 2017-03-16 20:00 | 49999.9398 | 79.992
Devonshire Building | 2017-03-16 20:15 | 49999.9548 | 60.012
Devonshire Building | 2017-03-16 20:30 | 49999.9698 | 60.012
Devonshire Building | 2017-03-16 20:45 | 49999.9898 | 79.992
Devonshire Building | 2017-03-16 21:00 | 49999.9998 | 39.996
Devonshire Building | 2017-03-16 21:15 | 50000.0148 | 60.012
Devonshire Building | 2017-03-16 21:30 | 50000.0248 | 39.996
Devonshire Building | 2017-03-16 21:45 | 50000.0348 | 39.996
Devonshire Building | 2017-03-16 22:00 | 50000.0648 | 119.988
Devonshire Building | 2017-03-16 22:15 | 50000.0698 | 20.016
Devonshire Building | 2017-03-16 22:30 | 50000.0698 | 0
Devonshire Building | 2017-03-16 22:45 | 50000.0748 | 20.016
Devonshire Building | 2017-03-16 23:00 | 50000.0798 | 20.016
Devonshire Building | 2017-03-16 23:15 | 50000.0798 | 0
Devonshire Building | 2017-03-16 23:30 | 50000.0848 | 20.016
Devonshire Building | 2017-03-16 23:45 | 50000.0898 | 20.016 | 0
Devonshire Building | 2017-03-17 | 50000.0898 | 0
Devonshire Building | 2017-03-17 00:15 | 50000.0948 | 20.016
Devonshire Building | 2017-03-17 00:30 | 50000.0948 | 0
Devonshire Building | 2017-03-17 00:45 | 50000.0998 | 20.016
Devonshire Building | 2017-03-17 01:00 | 50000.1049 | 20.016
Devonshire Building | 2017-03-17 01:15 | 50000.1049 | 0
Devonshire Building | 2017-03-17 01:30 | 50000.1099 | 20.016
Devonshire Building | 2017-03-17 01:45 | 50000.1299 | 79.992
Devonshire Building | 2017-03-17 02:00 | 50000.1499 | 79.992
Devonshire Building | 2017-03-17 02:15 | 50000.1649 | 60.012
Devonshire Building | 2017-03-17 02:30 | 50000.1849 | 79.992
Devonshire Building | 2017-03-17 02:45 | 50000.2049 | 79.992
Devonshire Building | 2017-03-17 03:00 | 50000.2248 | 79.992
Devonshire Building | 2017-03-17 03:15 | 50000.2448 | 79.992
Devonshire Building | 2017-03-17 03:30 | 50000.2599 | 60.012
Devonshire Building | 2017-03-17 03:45 | 50000.2798 | 79.992
Devonshire Building | 2017-03-17 04:00 | 50000.2898 | 39.996
Devonshire Building | 2017-03-17 04:15 | 50000.2949 | 20.016
Devonshire Building | 2017-03-17 04:30 | 50000.2999 | 20.016
Devonshire Building | 2017-03-17 04:45 | 50000.2999 | 0
Devonshire Building | 2017-03-17 05:00 | 50000.3049 | 20.016
Devonshire Building | 2017-03-17 05:15 | 50000.3049 | 0
Devonshire Building | 2017-03-17 05:30 | 50000.3099 | 20.016
Devonshire Building | 2017-03-17 05:45 | 50000.3149 | 20.016
Devonshire Building | 2017-03-17 06:00 | 50000.3149 | 0
Devonshire Building | 2017-03-17 06:15 | 50000.3199 | 20.016
Devonshire Building | 2017-03-17 06:30 | 50000.3249 | 20.016
Devonshire Building | 2017-03-17 06:45 | 50000.3299 | 20.016
Devonshire Building | 2017-03-17 07:00 | 50000.3299 | 0
Devonshire Building | 2017-03-17 07:15 | 50000.3349 | 20.016
Devonshire Building | 2017-03-17 07:30 | 50000.3499 | 60.012
Devonshire Building | 2017-03-17 07:45 | 50000.3549 | 20.016
Devonshire Building | 2017-03-17 08:00 | 50000.3599 | 20.016
Devonshire Building | 2017-03-17 08:15 | 50000.3649 | 20.016
Devonshire Building | 2017-03-17 08:30 | 50000.6399 | 1100.016
Devonshire Building | 2017-03-17 08:45 | 50000.6599 | 79.992
Devonshire Building | 2017-03-17 09:00 | 50000.6699 | 39.996
Devonshire Building | 2017-03-17 09:15 | 50000.6749 | 20.016
Devonshire Building | 2017-03-17 09:30 | 50000.6999 | 100.008
Devonshire Building | 2017-03-17 09:45 | 50000.7599 | 240.012
Devonshire Building | 2017-03-17 10:00 | 50000.8449 | 339.984
Devonshire Building | 2017-03-17 10:15 | 50000.9349 | 360
Devonshire Building | 2017-03-17 10:30 | 50001.2549 | 1280.016
Devonshire Building | 2017-03-17 10:45 | 50001.4299 | 699.984
Devonshire Building | 2017-03-17 11:00 | 50001.5599 | 519.984
Devonshire Building | 2017-03-17 11:15 | 50001.6649 | 420.012
Devonshire Building | 2017-03-17 11:30 | 50001.7649 | 399.996
Devonshire Building | 2017-03-17 11:45 | 50001.8849 | 479.988
Devonshire Building | 2017-03-17 12:00 | 50002.2949 | 1640.016
Devonshire Building | 2017-03-17 12:15 | 50002.4099 | 460.008
Devonshire Building | 2017-03-17 12:30 | 50002.5149 | 420.012
Devonshire Building | 2017-03-17 12:45 | 50002.6199 | 420.012
Devonshire Building | 2017-03-17 13:00 | 50002.7199 | 399.996
Devonshire Building | 2017-03-17 13:15 | 50002.8199 | 399.996
Devonshire Building | 2017-03-17 13:30 | 50003.1899 | 1479.996
Devonshire Building | 2017-03-17 13:45 | 50003.2649 | 299.988
Devonshire Building | 2017-03-17 14:00 | 50003.3299 | 259.992
Devonshire Building | 2017-03-17 14:15 | 50003.3849 | 219.996
Devonshire Building | 2017-03-17 14:30 | 50003.4299 | 180
Devonshire Building | 2017-03-17 14:45 | 50003.4699 | 159.984
Devonshire Building | 2017-03-17 15:00 | 50003.5149 | 180
Devonshire Building | 2017-03-17 15:15 | 50003.5499 | 140.004
Devonshire Building | 2017-03-17 15:30 | 50003.8499 | 1199.988
Devonshire Building | 2017-03-17 15:45 | 50003.8699 | 79.992
Devonshire Building | 2017-03-17 16:00 | 50003.8849 | 60.012
Devonshire Building | 2017-03-17 16:15 | 50003.8999 | 60.012
Devonshire Building | 2017-03-17 16:30 | 50003.9249 | 100.008
Devonshire Building | 2017-03-17 16:45 | 50003.9399 | 60.012
Devonshire Building | 2017-03-17 17:00 | 50003.9549 | 60.012
Devonshire Building | 2017-03-17 17:15 | 50003.9649 | 39.996
Devonshire Building | 2017-03-17 17:30 | 50004.2549 | 1159.992
Devonshire Building | 2017-03-17 17:45 | 50004.2699 | 60.012
Devonshire Building | 2017-03-17 18:00 | 50004.2899 | 79.992
Devonshire Building | 2017-03-17 18:15 | 50004.3049 | 60.012
Devonshire Building | 2017-03-17 18:30 | 50004.3199 | 60.012
Devonshire Building | 2017-03-17 18:45 | 50004.3349 | 60.012
Devonshire Building | 2017-03-17 19:00 | 50004.3499 | 60.012
Devonshire Building | 2017-03-17 19:15 | 50004.3699 | 79.992
Devonshire Building | 2017-03-17 19:30 | 50004.3849 | 60.012
Devonshire Building | 2017-03-17 19:45 | 50004.4149 | 119.988
Devonshire Building | 2017-03-17 20:00 | 50004.4449 | 119.988
Devonshire Building | 2017-03-17 20:15 | 50004.4749 | 119.988
Devonshire Building | 2017-03-17 20:30 | 50004.5049 | 119.988
Devonshire Building | 2017-03-17 20:45 | 50004.5299 | 100.008
Devonshire Building | 2017-03-17 21:00 | 50004.5599 | 119.988
Devonshire Building | 2017-03-17 21:15 | 50004.5899 | 119.988
Devonshire Building | 2017-03-17 21:30 | 50004.6149 | 100.008
Devonshire Building | 2017-03-17 21:45 | 50004.6449 | 119.988
Devonshire Building | 2017-03-17 22:00 | 50004.6799 | 140.004
Devonshire Building | 2017-03-17 22:15 | 50004.6949 | 60.012
Devonshire Building | 2017-03-17 22:30 | 50004.7049 | 39.996
Devonshire Building | 2017-03-17 22:45 | 50004.7099 | 20.016
Devonshire Building | 2017-03-17 23:00 | 50004.7199 | 39.996
Devonshire Building | 2017-03-17 23:15 | 50004.7299 | 39.996
Devonshire Building | 2017-03-17 23:30 | 50004.7399 | 39.996
Devonshire Building | 2017-03-17 23:45 | 50004.7449 | 20.016 | 0
Devonshire Building | 2017-03-18 | 50004.7539 | 39.996
Devonshire Building | 2017-03-18 00:15 | 50004.7639 | 39.996
Devonshire Building | 2017-03-18 00:30 | 50004.7689 | 20.016
Devonshire Building | 2017-03-18 00:45 | 50004.7789 | 39.996
Devonshire Building | 2017-03-18 01:00 | 50004.7839 | 20.016
Devonshire Building | 2017-03-18 01:15 | 50004.7939 | 39.996
Devonshire Building | 2017-03-18 01:30 | 50004.7989 | 20.016
Devonshire Building | 2017-03-18 01:45 | 50004.8089 | 39.996
Devonshire Building | 2017-03-18 02:00 | 50004.8139 | 20.016
Devonshire Building | 2017-03-18 02:15 | 50004.8239 | 39.996
Devonshire Building | 2017-03-18 02:30 | 50004.8289 | 20.016
Devonshire Building | 2017-03-18 02:45 | 50004.8339 | 20.016
Devonshire Building | 2017-03-18 03:00 | 50004.8439 | 39.996
Devonshire Building | 2017-03-18 03:15 | 50004.8489 | 20.016
Devonshire Building | 2017-03-18 03:30 | 50004.8539 | 20.016
Devonshire Building | 2017-03-18 03:45 | 50004.8589 | 20.016
Devonshire Building | 2017-03-18 04:00 | 50004.8689 | 39.996
Devonshire Building | 2017-03-18 04:15 | 50004.8739 | 20.016
Devonshire Building | 2017-03-18 04:30 | 50004.8789 | 20.016
Devonshire Building | 2017-03-18 04:45 | 50004.884 | 20.016
Devonshire Building | 2017-03-18 05:00 | 50004.889 | 20.016
Devonshire Building | 2017-03-18 05:15 | 50004.894 | 20.016
Devonshire Building | 2017-03-18 05:30 | 50004.899 | 20.016
Devonshire Building | 2017-03-18 05:45 | 50004.904 | 20.016
Devonshire Building | 2017-03-18 06:00 | 50004.909 | 20.016
Devonshire Building | 2017-03-18 06:15 | 50004.914 | 20.016
Devonshire Building | 2017-03-18 06:30 | 50004.919 | 20.016
Devonshire Building | 2017-03-18 06:45 | 50004.924 | 20.016
Devonshire Building | 2017-03-18 07:00 | 50004.929 | 20.016
Devonshire Building | 2017-03-18 07:15 | 50004.934 | 20.016
Devonshire Building | 2017-03-18 07:30 | 50004.939 | 20.016
Devonshire Building | 2017-03-18 07:45 | 50004.944 | 20.016
Devonshire Building | 2017-03-18 08:00 | 50004.944 | 0
Devonshire Building | 2017-03-18 08:15 | 50004.949 | 20.016
Devonshire Building | 2017-03-18 08:30 | 50004.954 | 20.016
Devonshire Building | 2017-03-18 08:45 | 50004.959 | 20.016
Devonshire Building | 2017-03-18 09:00 | 50004.964 | 20.016
Devonshire Building | 2017-03-18 09:15 | 50004.964 | 0
Devonshire Building | 2017-03-18 09:30 | 50004.969 | 20.016
Devonshire Building | 2017-03-18 09:45 | 50004.974 | 20.016
Devonshire Building | 2017-03-18 10:00 | 50004.979 | 20.016
Devonshire Building | 2017-03-18 10:15 | 50004.979 | 0
Devonshire Building | 2017-03-18 10:30 | 50004.984 | 20.016
Devonshire Building | 2017-03-18 10:45 | 50004.989 | 20.016
Devonshire Building | 2017-03-18 11:00 | 50004.994 | 20.016
Devonshire Building | 2017-03-18 11:15 | 50004.994 | 0
Devonshire Building | 2017-03-18 11:30 | 50004.999 | 20.016
Devonshire Building | 2017-03-18 11:45 | 50005.004 | 20.016
Devonshire Building | 2017-03-18 12:00 | 50005.004 | 0
Devonshire Building | 2017-03-18 12:15 | 50005.0091 | 20.016
Devonshire Building | 2017-03-18 12:30 | 50005.274 | 1059.984
Devonshire Building | 2017-03-18 12:45 | 50005.2791 | 20.016
Devonshire Building | 2017-03-18 13:00 | 50005.2791 | 0
Devonshire Building | 2017-03-18 13:15 | 50005.2841 | 20.016
Devonshire Building | 2017-03-18 13:30 | 50005.2841 | 0
Devonshire Building | 2017-03-18 13:45 | 50005.2891 | 20.016
Devonshire Building | 2017-03-18 14:00 | 50005.2891 | 0
Devonshire Building | 2017-03-18 14:15 | 50005.2941 | 20.016
Devonshire Building | 2017-03-18 14:30 | 50005.2991 | 20.016
Devonshire Building | 2017-03-18 14:45 | 50005.2991 | 0
Devonshire Building | 2017-03-18 15:00 | 50005.3041 | 20.016
Devonshire Building | 2017-03-18 15:15 | 50005.3091 | 20.016
Devonshire Building | 2017-03-18 15:30 | 50005.3091 | 0
Devonshire Building | 2017-03-18 15:45 | 50005.3141 | 20.016
Devonshire Building | 2017-03-18 16:00 | 50005.3141 | 0
Devonshire Building | 2017-03-18 16:15 | 50005.3191 | 20.016
Devonshire Building | 2017-03-18 16:30 | 50005.3241 | 20.016
Devonshire Building | 2017-03-18 16:45 | 50005.3241 | 0
Devonshire Building | 2017-03-18 17:00 | 50005.3291 | 20.016
Devonshire Building | 2017-03-18 17:15 | 50005.3291 | 0
Devonshire Building | 2017-03-18 17:30 | 50005.3341 | 20.016
Devonshire Building | 2017-03-18 17:45 | 50005.3341 | 0
Devonshire Building | 2017-03-18 18:00 | 50005.3391 | 20.016
Devonshire Building | 2017-03-18 18:15 | 50005.3441 | 20.016
Devonshire Building | 2017-03-18 18:30 | 50005.3441 | 0
Devonshire Building | 2017-03-18 18:45 | 50005.3491 | 20.016
Devonshire Building | 2017-03-18 19:00 | 50005.3491 | 0
Devonshire Building | 2017-03-18 19:15 | 50005.3541 | 20.016
Devonshire Building | 2017-03-18 19:30 | 50005.3591 | 20.016
Devonshire Building | 2017-03-18 19:45 | 50005.3791 | 79.992
Devonshire Building | 2017-03-18 20:00 | 50005.3941 | 60.012
Devonshire Building | 2017-03-18 20:15 | 50005.4141 | 79.992
Devonshire Building | 2017-03-18 20:30 | 50005.4341 | 79.992
Devonshire Building | 2017-03-18 20:45 | 50005.4541 | 79.992
Devonshire Building | 2017-03-18 21:00 | 50005.4741 | 79.992
Devonshire Building | 2017-03-18 21:15 | 50005.4891 | 60.012
Devonshire Building | 2017-03-18 21:30 | 50005.5091 | 79.992
Devonshire Building | 2017-03-18 21:45 | 50005.5291 | 79.992
Devonshire Building | 2017-03-18 22:00 | 50005.5491 | 79.992
Devonshire Building | 2017-03-18 22:15 | 50005.5491 | 0
Devonshire Building | 2017-03-18 22:30 | 50005.5541 | 20.016
Devonshire Building | 2017-03-18 22:45 | 50005.5591 | 20.016
Devonshire Building | 2017-03-18 23:00 | 50005.5591 | 0
Devonshire Building | 2017-03-18 23:15 | 50005.5641 | 20.016
Devonshire Building | 2017-03-18 23:30 | 50005.5641 | 0
Devonshire Building | 2017-03-18 23:45 | 50005.5691 | 20.016 | 0
Devonshire Building | 2017-03-19 | 50005.5703 | 0
Devonshire Building | 2017-03-19 00:15 | 50005.5753 | 20.016
Devonshire Building | 2017-03-19 00:30 | 50005.5803 | 20.016
Devonshire Building | 2017-03-19 00:45 | 50005.5803 | 0
Devonshire Building | 2017-03-19 01:00 | 50005.5853 | 20.016
Devonshire Building | 2017-03-19 01:15 | 50005.5853 | 0
Devonshire Building | 2017-03-19 01:30 | 50005.5903 | 20.016
Devonshire Building | 2017-03-19 01:45 | 50005.5903 | 0
Devonshire Building | 2017-03-19 02:00 | 50005.5953 | 20.016
Devonshire Building | 2017-03-19 02:15 | 50005.6003 | 20.016
Devonshire Building | 2017-03-19 02:30 | 50005.6003 | 0
Devonshire Building | 2017-03-19 02:45 | 50005.6053 | 20.016
Devonshire Building | 2017-03-19 03:00 | 50005.6053 | 0
Devonshire Building | 2017-03-19 03:15 | 50005.6103 | 20.016
Devonshire Building | 2017-03-19 03:30 | 50005.6103 | 0
Devonshire Building | 2017-03-19 03:45 | 50005.6153 | 20.016
Devonshire Building | 2017-03-19 04:00 | 50005.6153 | 0
Devonshire Building | 2017-03-19 04:15 | 50005.6203 | 20.016
Devonshire Building | 2017-03-19 04:30 | 50005.6203 | 0
Devonshire Building | 2017-03-19 04:45 | 50005.6254 | 20.016
Devonshire Building | 2017-03-19 05:00 | 50005.6254 | 0
Devonshire Building | 2017-03-19 05:15 | 50005.6304 | 20.016
Devonshire Building | 2017-03-19 05:30 | 50005.6304 | 0
Devonshire Building | 2017-03-19 05:45 | 50005.6354 | 20.016
Devonshire Building | 2017-03-19 06:00 | 50005.6354 | 0
Devonshire Building | 2017-03-19 06:15 | 50005.6404 | 20.016
Devonshire Building | 2017-03-19 06:30 | 50005.6454 | 20.016
Devonshire Building | 2017-03-19 06:45 | 50005.6454 | 0
Devonshire Building | 2017-03-19 07:00 | 50005.6504 | 20.016
Devonshire Building | 2017-03-19 07:15 | 50005.6504 | 0
Devonshire Building | 2017-03-19 07:30 | 50005.6554 | 20.016
Devonshire Building | 2017-03-19 07:45 | 50005.6554 | 0
Devonshire Building | 2017-03-19 08:00 | 50005.6604 | 20.016
Devonshire Building | 2017-03-19 08:15 | 50005.6604 | 0
Devonshire Building | 2017-03-19 08:30 | 50005.6654 | 20.016
Devonshire Building | 2017-03-19 08:45 | 50005.6654 | 0
Devonshire Building | 2017-03-19 09:00 | 50005.6704 | 20.016
Devonshire Building | 2017-03-19 09:15 | 50005.6704 | 0
Devonshire Building | 2017-03-19 09:30 | 50005.6754 | 20.016
Devonshire Building | 2017-03-19 09:45 | 50005.6804 | 20.016
Devonshire Building | 2017-03-19 10:00 | 50005.6804 | 0
Devonshire Building | 2017-03-19 10:15 | 50005.6854 | 20.016
Devonshire Building | 2017-03-19 10:30 | 50005.6854 | 0
Devonshire Building | 2017-03-19 10:45 | 50005.6904 | 20.016
Devonshire Building | 2017-03-19 11:00 | 50005.6954 | 20.016
Devonshire Building | 2017-03-19 11:15 | 50005.6954 | 0
Devonshire Building | 2017-03-19 11:30 | 50005.7004 | 20.016
Devonshire Building | 2017-03-19 11:45 | 50005.7004 | 0
Devonshire Building | 2017-03-19 12:00 | 50005.7054 | 20.016
Devonshire Building | 2017-03-19 12:15 | 50005.7054 | 0
Devonshire Building | 2017-03-19 12:30 | 50005.9754 | 1080
Devonshire Building | 2017-03-19 12:45 | 50005.9754 | 0
Devonshire Building | 2017-03-19 13:00 | 50005.9804 | 20.016
Devonshire Building | 2017-03-19 13:15 | 50005.9804 | 0
Devonshire Building | 2017-03-19 13:30 | 50005.9854 | 20.016
Devonshire Building | 2017-03-19 13:45 | 50005.9904 | 20.016
Devonshire Building | 2017-03-19 14:00 | 50005.9904 | 0
Devonshire Building | 2017-03-19 14:15 | 50005.9954 | 20.016
Devonshire Building | 2017-03-19 14:30 | 50005.9954 | 0
Devonshire Building | 2017-03-19 14:45 | 50006.0004 | 20.016
Devonshire Building | 2017-03-19 15:00 | 50006.0004 | 0
Devonshire Building | 2017-03-19 15:15 | 50006.0054 | 20.016
Devonshire Building | 2017-03-19 15:30 | 50006.0104 | 20.016
Devonshire Building | 2017-03-19 15:45 | 50006.0104 | 0
Devonshire Building | 2017-03-19 16:00 | 50006.0154 | 20.016
Devonshire Building | 2017-03-19 16:15 | 50006.0154 | 0
Devonshire Building | 2017-03-19 16:30 | 50006.0205 | 20.016
Devonshire Building | 2017-03-19 16:45 | 50006.0205 | 0
Devonshire Building | 2017-03-19 17:00 | 50006.0255 | 20.016
Devonshire Building | 2017-03-19 17:15 | 50006.0255 | 0
Devonshire Building | 2017-03-19 17:30 | 50006.0305 | 20.016
Devonshire Building | 2017-03-19 17:45 | 50006.0355 | 20.016
Devonshire Building | 2017-03-19 18:00 | 50006.0355 | 0
Devonshire Building | 2017-03-19 18:15 | 50006.0405 | 20.016
Devonshire Building | 2017-03-19 18:30 | 50006.0405 | 0
Devonshire Building | 2017-03-19 18:45 | 50006.0455 | 20.016
Devonshire Building | 2017-03-19 19:00 | 50006.0455 | 0
Devonshire Building | 2017-03-19 19:15 | 50006.0505 | 20.016
Devonshire Building | 2017-03-19 19:30 | 50006.0555 | 20.016
Devonshire Building | 2017-03-19 19:45 | 50006.0755 | 79.992
Devonshire Building | 2017-03-19 20:00 | 50006.0955 | 79.992
Devonshire Building | 2017-03-19 20:15 | 50006.1105 | 60.012
Devonshire Building | 2017-03-19 20:30 | 50006.1305 | 79.992
Devonshire Building | 2017-03-19 20:45 | 50006.1505 | 79.992
Devonshire Building | 2017-03-19 21:00 | 50006.1705 | 79.992
Devonshire Building | 2017-03-19 21:15 | 50006.1905 | 79.992
Devonshire Building | 2017-03-19 21:30 | 50006.2055 | 60.012
Devonshire Building | 2017-03-19 21:45 | 50006.2255 | 79.992
Devonshire Building | 2017-03-19 22:00 | 50006.2405 | 60.012
Devonshire Building | 2017-03-19 22:15 | 50006.2455 | 20.016
Devonshire Building | 2017-03-19 22:30 | 50006.2455 | 0
Devonshire Building | 2017-03-19 22:45 | 50006.2505 | 20.016
Devonshire Building | 2017-03-19 23:00 | 50006.2505 | 0
Devonshire Building | 2017-03-19 23:15 | 50006.2555 | 20.016
Devonshire Building | 2017-03-19 23:30 | 50006.2605 | 20.016
Devonshire Building | 2017-03-19 23:45 | 50006.2605 | 0 | 0
Devonshire Building | 2017-03-20 | 50006.2656 | 20.016
Devonshire Building | 2017-03-20 00:15 | 50006.2656 | 0
Devonshire Building | 2017-03-20 00:30 | 50006.2706 | 20.016
Devonshire Building | 2017-03-20 00:45 | 50006.2706 | 0
Devonshire Building | 2017-03-20 01:00 | 50006.2756 | 20.016
Devonshire Building | 2017-03-20 01:15 | 50006.2756 | 0
Devonshire Building | 2017-03-20 01:30 | 50006.2806 | 20.016
Devonshire Building | 2017-03-20 01:45 | 50006.2806 | 0
Devonshire Building | 2017-03-20 02:00 | 50006.2856 | 20.016
Devonshire Building | 2017-03-20 02:15 | 50006.2907 | 20.016
Devonshire Building | 2017-03-20 02:30 | 50006.2907 | 0
Devonshire Building | 2017-03-20 02:45 | 50006.2957 | 20.016
Devonshire Building | 2017-03-20 03:00 | 50006.2957 | 0
Devonshire Building | 2017-03-20 03:15 | 50006.3007 | 20.016
Devonshire Building | 2017-03-20 03:30 | 50006.3007 | 0
Devonshire Building | 2017-03-20 03:45 | 50006.3057 | 20.016
Devonshire Building | 2017-03-20 04:00 | 50006.3057 | 0
Devonshire Building | 2017-03-20 04:15 | 50006.3107 | 20.016
Devonshire Building | 2017-03-20 04:30 | 50006.3107 | 0
Devonshire Building | 2017-03-20 04:45 | 50006.3157 | 20.016
Devonshire Building | 2017-03-20 05:00 | 50006.3157 | 0
Devonshire Building | 2017-03-20 05:15 | 50006.3207 | 20.016
Devonshire Building | 2017-03-20 05:30 | 50006.3257 | 20.016
Devonshire Building | 2017-03-20 05:45 | 50006.3257 | 0
Devonshire Building | 2017-03-20 06:00 | 50006.3307 | 20.016
Devonshire Building | 2017-03-20 06:15 | 50006.3307 | 0
Devonshire Building | 2017-03-20 06:30 | 50006.3357 | 20.016
Devonshire Building | 2017-03-20 06:45 | 50006.3407 | 20.016
Devonshire Building | 2017-03-20 07:00 | 50006.3457 | 20.016
Devonshire Building | 2017-03-20 07:15 | 50006.3507 | 20.016
Devonshire Building | 2017-03-20 07:30 | 50006.3707 | 79.992
Devonshire Building | 2017-03-20 07:45 | 50006.3857 | 60.012
Devonshire Building | 2017-03-20 08:00 | 50006.6407 | 1019.988
Devonshire Building | 2017-03-20 08:15 | 50006.6557 | 60.012
Devonshire Building | 2017-03-20 08:30 | 50006.6707 | 60.012
Devonshire Building | 2017-03-20 08:45 | 50006.6807 | 39.996
Devonshire Building | 2017-03-20 09:00 | 50006.7007 | 79.992
Devonshire Building | 2017-03-20 09:15 | 50006.7057 | 20.016
Devonshire Building | 2017-03-20 09:30 | 50006.7157 | 39.996
Devonshire Building | 2017-03-20 09:45 | 50006.7207 | 20.016
Devonshire Building | 2017-03-20 10:00 | 50006.7307 | 39.996
Devonshire Building | 2017-03-20 10:15 | 50007.0507 | 1280.016
Devonshire Building | 2017-03-20 10:30 | 50007.0957 | 180
Devonshire Building | 2017-03-20 10:45 | 50007.1957 | 399.996
Devonshire Building | 2017-03-20 11:00 | 50007.3107 | 460.008
Devonshire Building | 2017-03-20 11:15 | 50007.4107 | 399.996
Devonshire Building | 2017-03-20 11:30 | 50007.6857 | 1100.016
Devonshire Building | 2017-03-20 11:45 | 50007.8457 | 640.008
Devonshire Building | 2017-03-20 12:00 | 50007.9107 | 259.992
Devonshire Building | 2017-03-20 12:15 | 50007.9807 | 280.008
Devonshire Building | 2017-03-20 12:30 | 50008.0507 | 280.008
Devonshire Building | 2017-03-20 12:45 | 50008.1207 | 280.008
Devonshire Building | 2017-03-20 13:00 | 50008.1757 | 219.996
Devonshire Building | 2017-03-20 13:15 | 50008.5307 | 1419.984
Devonshire Building | 2017-03-20 13:30 | 50008.5857 | 219.996
Devonshire Building | 2017-03-20 13:45 | 50008.6507 | 259.992
Devonshire Building | 2017-03-20 14:00 | 50008.7007 | 200.016
Devonshire Building | 2017-03-20 14:15 | 50008.7557 | 219.996
Devonshire Building | 2017-03-20 14:30 | 50009.1007 | 1379.988
Devonshire Building | 2017-03-20 14:45 | 50009.1457 | 180
Devonshire Building | 2017-03-20 15:00 | 50009.2007 | 219.996
Devonshire Building | 2017-03-20 15:15 | 50009.2507 | 200.016
Devonshire Building | 2017-03-20 15:30 | 50009.3007 | 200.016
Devonshire Building | 2017-03-20 15:45 | 50009.3507 | 200.016
Devonshire Building | 2017-03-20 16:00 | 50009.3957 | 180
Devonshire Building | 2017-03-20 16:15 | 50009.7257 | 1320.012
Devonshire Building | 2017-03-20 16:30 | 50009.7507 | 100.008
Devonshire Building | 2017-03-20 16:45 | 50009.7757 | 100.008
Devonshire Building | 2017-03-20 17:00 | 50009.8057 | 119.988
Devonshire Building | 2017-03-20 17:15 | 50009.8307 | 100.008
Devonshire Building | 2017-03-20 17:30 | 50009.8607 | 119.988
Devonshire Building | 2017-03-20 17:45 | 50009.8857 | 100.008
Devonshire Building | 2017-03-20 18:00 | 50009.9057 | 79.992
Devonshire Building | 2017-03-20 18:15 | 50010.2057 | 1199.988
Devonshire Building | 2017-03-20 18:30 | 50010.2257 | 79.992
Devonshire Building | 2017-03-20 18:45 | 50010.2507 | 100.008
Devonshire Building | 2017-03-20 19:00 | 50010.2707 | 79.992
Devonshire Building | 2017-03-20 19:15 | 50010.2957 | 100.008
Devonshire Building | 2017-03-20 19:30 | 50010.3257 | 119.988
Devonshire Building | 2017-03-20 19:45 | 50010.3607 | 140.004
Devonshire Building | 2017-03-20 20:00 | 50010.4057 | 180
Devonshire Building | 2017-03-20 20:15 | 50010.4457 | 159.984
Devonshire Building | 2017-03-20 20:30 | 50010.4807 | 140.004
Devonshire Building | 2017-03-20 20:45 | 50010.5107 | 119.988
Devonshire Building | 2017-03-20 21:00 | 50010.5457 | 140.004
Devonshire Building | 2017-03-20 21:15 | 50010.5757 | 119.988
Devonshire Building | 2017-03-20 21:30 | 50010.6057 | 119.988
Devonshire Building | 2017-03-20 21:45 | 50010.6357 | 119.988
Devonshire Building | 2017-03-20 22:00 | 50010.6657 | 119.988
Devonshire Building | 2017-03-20 22:15 | 50010.6907 | 100.008
Devonshire Building | 2017-03-20 22:30 | 50010.7107 | 79.992
Devonshire Building | 2017-03-20 22:45 | 50010.7207 | 39.996
Devonshire Building | 2017-03-20 23:00 | 50010.7307 | 39.996
Devonshire Building | 2017-03-20 23:15 | 50010.7357 | 20.016
Devonshire Building | 2017-03-20 23:30 | 50010.7457 | 39.996
Devonshire Building | 2017-03-20 23:45 | 50010.7557 | 39.996 | 0
Devonshire Building | 2017-03-21 | 50010.7656 | 39.996
Devonshire Building | 2017-03-21 00:15 | 50010.7756 | 39.996
Devonshire Building | 2017-03-21 00:30 | 50010.7856 | 39.996
Devonshire Building | 2017-03-21 00:45 | 50010.7956 | 39.996
Devonshire Building | 2017-03-21 01:00 | 50010.8056 | 39.996
Devonshire Building | 2017-03-21 01:15 | 50010.8106 | 20.016
Devonshire Building | 2017-03-21 01:30 | 50010.8206 | 39.996
Devonshire Building | 2017-03-21 01:45 | 50010.8256 | 20.016
Devonshire Building | 2017-03-21 02:00 | 50010.8356 | 39.996
Devonshire Building | 2017-03-21 02:15 | 50010.8406 | 20.016
Devonshire Building | 2017-03-21 02:30 | 50010.8506 | 39.996
Devonshire Building | 2017-03-21 02:45 | 50010.8556 | 20.016
Devonshire Building | 2017-03-21 03:00 | 50010.8606 | 20.016
Devonshire Building | 2017-03-21 03:15 | 50010.8706 | 39.996
Devonshire Building | 2017-03-21 03:30 | 50010.8756 | 20.016
Devonshire Building | 2017-03-21 03:45 | 50010.8806 | 20.016
Devonshire Building | 2017-03-21 04:00 | 50010.8906 | 39.996
Devonshire Building | 2017-03-21 04:15 | 50010.8957 | 20.016
Devonshire Building | 2017-03-21 04:30 | 50010.9007 | 20.016
Devonshire Building | 2017-03-21 04:45 | 50010.9057 | 20.016
Devonshire Building | 2017-03-21 05:00 | 50010.9107 | 20.016
Devonshire Building | 2017-03-21 05:15 | 50010.9207 | 39.996
Devonshire Building | 2017-03-21 05:30 | 50010.9257 | 20.016
Devonshire Building | 2017-03-21 05:45 | 50010.9307 | 20.016
Devonshire Building | 2017-03-21 06:00 | 50010.9357 | 20.016
Devonshire Building | 2017-03-21 06:15 | 50010.9407 | 20.016
Devonshire Building | 2017-03-21 06:30 | 50010.9457 | 20.016
Devonshire Building | 2017-03-21 06:45 | 50010.9557 | 39.996
Devonshire Building | 2017-03-21 07:00 | 50010.9607 | 20.016
Devonshire Building | 2017-03-21 07:15 | 50010.9657 | 20.016
Devonshire Building | 2017-03-21 07:30 | 50010.9707 | 20.016
Devonshire Building | 2017-03-21 07:45 | 50010.9807 | 39.996
Devonshire Building | 2017-03-21 08:00 | 50010.9857 | 20.016
Devonshire Building | 2017-03-21 08:15 | 50010.9957 | 39.996
Devonshire Building | 2017-03-21 08:30 | 50011.0057 | 39.996
Devonshire Building | 2017-03-21 08:45 | 50011.0157 | 39.996
Devonshire Building | 2017-03-21 09:00 | 50011.3207 | 1220.004
Devonshire Building | 2017-03-21 09:15 | 50011.3257 | 20.016
Devonshire Building | 2017-03-21 09:30 | 50011.3357 | 39.996
Devonshire Building | 2017-03-21 09:45 | 50011.3457 | 39.996
Devonshire Building | 2017-03-21 10:00 | 50011.3507 | 20.016
Devonshire Building | 2017-03-21 10:15 | 50011.3557 | 20.016
Devonshire Building | 2017-03-21 10:30 | 50011.6507 | 1180.008
Devonshire Building | 2017-03-21 10:45 | 50011.6557 | 20.016
Devonshire Building | 2017-03-21 11:00 | 50011.6757 | 79.992
Devonshire Building | 2017-03-21 11:15 | 50011.6857 | 39.996
Devonshire Building | 2017-03-21 11:30 | 50011.7007 | 60.012
Devonshire Building | 2017-03-21 11:45 | 50011.7157 | 60.012
Devonshire Building | 2017-03-21 12:00 | 50011.7407 | 100.008
Devonshire Building | 2017-03-21 12:15 | 50012.0607 | 1280.016
Devonshire Building | 2017-03-21 12:30 | 50012.1157 | 219.996
Devonshire Building | 2017-03-21 12:45 | 50012.1657 | 200.016
Devonshire Building | 2017-03-21 13:00 | 50012.2257 | 240.012
Devonshire Building | 2017-03-21 13:15 | 50012.2807 | 219.996
Devonshire Building | 2017-03-21 13:30 | 50012.3457 | 259.992
Devonshire Building | 2017-03-21 13:45 | 50012.4457 | 399.996
Devonshire Building | 2017-03-21 14:00 | 50012.7957 | 1400.004
Devonshire Building | 2017-03-21 14:15 | 50012.9107 | 460.008
Devonshire Building | 2017-03-21 14:30 | 50013.0157 | 420.012
Devonshire Building | 2017-03-21 14:45 | 50013.1107 | 380.016
Devonshire Building | 2017-03-21 15:00 | 50013.1957 | 339.984
Devonshire Building | 2017-03-21 15:15 | 50013.2907 | 380.016
Devonshire Building | 2017-03-21 15:30 | 50013.3807 | 360
Devonshire Building | 2017-03-21 15:45 | 50013.4757 | 380.016
Devonshire Building | 2017-03-21 16:00 | 50013.8457 | 1479.996
Devonshire Building | 2017-03-21 16:15 | 50013.9307 | 339.984
Devonshire Building | 2017-03-21 16:30 | 50014.0107 | 320.004
Devonshire Building | 2017-03-21 16:45 | 50014.0757 | 259.992
Devonshire Building | 2017-03-21 17:00 | 50014.1307 | 219.996
Devonshire Building | 2017-03-21 17:15 | 50014.1807 | 200.016
Devonshire Building | 2017-03-21 17:30 | 50014.2257 | 180
Devonshire Building | 2017-03-21 17:45 | 50014.2707 | 180
Devonshire Building | 2017-03-21 18:00 | 50014.5707 | 1199.988
Devonshire Building | 2017-03-21 18:15 | 50014.5907 | 79.992
Devonshire Building | 2017-03-21 18:30 | 50014.6107 | 79.992
Devonshire Building | 2017-03-21 18:45 | 50014.6307 | 79.992
Devonshire Building | 2017-03-21 19:00 | 50014.6457 | 60.012
Devonshire Building | 2017-03-21 19:15 | 50014.6657 | 79.992
Devonshire Building | 2017-03-21 19:30 | 50014.6857 | 79.992
Devonshire Building | 2017-03-21 19:45 | 50014.7007 | 60.012
Devonshire Building | 2017-03-21 20:00 | 50014.7207 | 79.992
Devonshire Building | 2017-03-21 20:15 | 50014.7357 | 60.012
Devonshire Building | 2017-03-21 20:30 | 50014.7507 | 60.012
Devonshire Building | 2017-03-21 20:45 | 50014.7607 | 39.996
Devonshire Building | 2017-03-21 21:00 | 50014.7757 | 60.012
Devonshire Building | 2017-03-21 21:15 | 50014.7857 | 39.996
Devonshire Building | 2017-03-21 21:30 | 50014.7957 | 39.996
Devonshire Building | 2017-03-21 21:45 | 50014.8057 | 39.996
Devonshire Building | 2017-03-21 22:00 | 50014.8207 | 60.012
Devonshire Building | 2017-03-21 22:15 | 50014.8307 | 39.996
Devonshire Building | 2017-03-21 22:30 | 50014.8357 | 20.016
Devonshire Building | 2017-03-21 22:45 | 50014.8457 | 39.996
Devonshire Building | 2017-03-21 23:00 | 50014.8507 | 20.016
Devonshire Building | 2017-03-21 23:15 | 50014.8557 | 20.016
Devonshire Building | 2017-03-21 23:30 | 50014.8657 | 39.996
Devonshire Building | 2017-03-21 23:45 | 50014.8707 | 20.016 | 20.016
Devonshire Building | 2017-03-22 | 50014.875 | 20.016
Devonshire Building | 2017-03-22 00:15 | 50014.88 | 20.016
Devonshire Building | 2017-03-22 00:30 | 50014.89 | 39.996
Devonshire Building | 2017-03-22 00:45 | 50014.895 | 20.016
Devonshire Building | 2017-03-22 01:00 | 50014.9 | 20.016
Devonshire Building | 2017-03-22 01:15 | 50014.905 | 20.016
Devonshire Building | 2017-03-22 01:30 | 50014.91 | 20.016
Devonshire Building | 2017-03-22 01:45 | 50014.915 | 20.016
Devonshire Building | 2017-03-22 02:00 | 50014.925 | 39.996
Devonshire Building | 2017-03-22 02:15 | 50014.93 | 20.016
Devonshire Building | 2017-03-22 02:30 | 50014.935 | 20.016
Devonshire Building | 2017-03-22 02:45 | 50014.94 | 20.016
Devonshire Building | 2017-03-22 03:00 | 50014.945 | 20.016
Devonshire Building | 2017-03-22 03:15 | 50014.95 | 20.016
Devonshire Building | 2017-03-22 03:30 | 50014.955 | 20.016
Devonshire Building | 2017-03-22 03:45 | 50014.9601 | 20.016
Devonshire Building | 2017-03-22 04:00 | 50014.9651 | 20.016
Devonshire Building | 2017-03-22 04:15 | 50014.9701 | 20.016
Devonshire Building | 2017-03-22 04:30 | 50014.9751 | 20.016
Devonshire Building | 2017-03-22 04:45 | 50014.9751 | 0
Devonshire Building | 2017-03-22 05:00 | 50014.9801 | 20.016
Devonshire Building | 2017-03-22 05:15 | 50014.9851 | 20.016
Devonshire Building | 2017-03-22 05:30 | 50014.9901 | 20.016
Devonshire Building | 2017-03-22 05:45 | 50014.9951 | 20.016
Devonshire Building | 2017-03-22 06:00 | 50015.0001 | 20.016
Devonshire Building | 2017-03-22 06:15 | 50015.0051 | 20.016
Devonshire Building | 2017-03-22 06:30 | 50015.0101 | 20.016
Devonshire Building | 2017-03-22 06:45 | 50015.0101 | 0
Devonshire Building | 2017-03-22 07:00 | 50015.0151 | 20.016
Devonshire Building | 2017-03-22 07:15 | 50015.0201 | 20.016
Devonshire Building | 2017-03-22 07:30 | 50015.0401 | 79.992
Devonshire Building | 2017-03-22 07:45 | 50015.0451 | 20.016
Devonshire Building | 2017-03-22 08:00 | 50015.0501 | 20.016
Devonshire Building | 2017-03-22 08:15 | 50015.0601 | 39.996
Devonshire Building | 2017-03-22 08:30 | 50015.0651 | 20.016
Devonshire Building | 2017-03-22 08:45 | 50015.3501 | 1140.012
Devonshire Building | 2017-03-22 09:00 | 50015.3701 | 79.992
Devonshire Building | 2017-03-22 09:15 | 50015.3851 | 60.012
Devonshire Building | 2017-03-22 09:30 | 50015.3951 | 39.996
Devonshire Building | 2017-03-22 09:45 | 50015.4001 | 20.016
Devonshire Building | 2017-03-22 10:00 | 50015.4051 | 20.016
Devonshire Building | 2017-03-22 10:15 | 50015.4151 | 39.996
Devonshire Building | 2017-03-22 10:30 | 50015.7151 | 1199.988
Devonshire Building | 2017-03-22 10:45 | 50015.7251 | 39.996
Devonshire Building | 2017-03-22 11:00 | 50015.7301 | 20.016
Devonshire Building | 2017-03-22 11:15 | 50015.7401 | 39.996
Devonshire Building | 2017-03-22 11:30 | 50015.7451 | 20.016
Devonshire Building | 2017-03-22 11:45 | 50015.7601 | 60.012
Devonshire Building | 2017-03-22 12:00 | 50016.0851 | 1299.996
Devonshire Building | 2017-03-22 12:15 | 50016.1301 | 180
Devonshire Building | 2017-03-22 12:30 | 50016.2051 | 299.988
Devonshire Building | 2017-03-22 12:45 | 50016.3201 | 460.008
Devonshire Building | 2017-03-22 13:00 | 50016.4901 | 680.004
Devonshire Building | 2017-03-22 13:15 | 50016.8351 | 1379.988
Devonshire Building | 2017-03-22 13:30 | 50016.9651 | 519.984
Devonshire Building | 2017-03-22 13:45 | 50017.0901 | 500.004
Devonshire Building | 2017-03-22 14:00 | 50017.2101 | 479.988
Devonshire Building | 2017-03-22 14:15 | 50017.3151 | 420.012
Devonshire Building | 2017-03-22 14:30 | 50017.4001 | 339.984
Devonshire Building | 2017-03-22 14:45 | 50017.4751 | 299.988
Devonshire Building | 2017-03-22 15:00 | 50017.5501 | 299.988
Devonshire Building | 2017-03-22 15:15 | 50017.8801 | 1320.012
Devonshire Building | 2017-03-22 15:30 | 50017.9301 | 200.016
Devonshire Building | 2017-03-22 15:45 | 50017.9801 | 200.016
Devonshire Building | 2017-03-22 16:00 | 50018.0301 | 200.016
Devonshire Building | 2017-03-22 16:15 | 50018.0801 | 200.016
Devonshire Building | 2017-03-22 16:30 | 50018.1201 | 159.984
Devonshire Building | 2017-03-22 16:45 | 50018.1501 | 119.988
Devonshire Building | 2017-03-22 17:00 | 50018.4501 | 1199.988
Devonshire Building | 2017-03-22 17:15 | 50018.4751 | 100.008
Devonshire Building | 2017-03-22 17:30 | 50018.5051 | 119.988
Devonshire Building | 2017-03-22 17:45 | 50018.5301 | 100.008
Devonshire Building | 2017-03-22 18:00 | 50018.5601 | 119.988
Devonshire Building | 2017-03-22 18:15 | 50018.5901 | 119.988
Devonshire Building | 2017-03-22 18:30 | 50018.6151 | 100.008
Devonshire Building | 2017-03-22 18:45 | 50018.6401 | 100.008
Devonshire Building | 2017-03-22 19:00 | 50018.6701 | 119.988
Devonshire Building | 2017-03-22 19:15 | 50018.7101 | 159.984
Devonshire Building | 2017-03-22 19:30 | 50018.7451 | 140.004
Devonshire Building | 2017-03-22 19:45 | 50018.7851 | 159.984
Devonshire Building | 2017-03-22 20:00 | 50018.8251 | 159.984
Devonshire Building | 2017-03-22 20:15 | 50018.8601 | 140.004
Devonshire Building | 2017-03-22 20:30 | 50018.8951 | 140.004
Devonshire Building | 2017-03-22 20:45 | 50018.9351 | 159.984
Devonshire Building | 2017-03-22 21:00 | 50018.9651 | 119.988
Devonshire Building | 2017-03-22 21:15 | 50019.0001 | 140.004
Devonshire Building | 2017-03-22 21:30 | 50019.0301 | 119.988
Devonshire Building | 2017-03-22 21:45 | 50019.0551 | 100.008
Devonshire Building | 2017-03-22 22:00 | 50019.0951 | 159.984
Devonshire Building | 2017-03-22 22:15 | 50019.1101 | 60.012
Devonshire Building | 2017-03-22 22:30 | 50019.1251 | 60.012
Devonshire Building | 2017-03-22 22:45 | 50019.1401 | 60.012
Devonshire Building | 2017-03-22 23:00 | 50019.1551 | 60.012
Devonshire Building | 2017-03-22 23:15 | 50019.1701 | 60.012
Devonshire Building | 2017-03-22 23:30 | 50019.1851 | 60.012
Devonshire Building | 2017-03-22 23:45 | 50019.2001 | 60.012 | 0
Devonshire Building | 2017-03-23 | 50019.2109 | 39.996
Devonshire Building | 2017-03-23 00:15 | 50019.2259 | 60.012
Devonshire Building | 2017-03-23 00:30 | 50019.2359 | 39.996
Devonshire Building | 2017-03-23 00:45 | 50019.2459 | 39.996
Devonshire Building | 2017-03-23 01:00 | 50019.2609 | 60.012
Devonshire Building | 2017-03-23 01:15 | 50019.2709 | 39.996
Devonshire Building | 2017-03-23 01:30 | 50019.2809 | 39.996
Devonshire Building | 2017-03-23 01:45 | 50019.2909 | 39.996
Devonshire Building | 2017-03-23 02:00 | 50019.5559 | 1059.984
Devonshire Building | 2017-03-23 02:15 | 50019.5559 | 0
Devonshire Building | 2017-03-23 02:30 | 50019.5609 | 20.016
Devonshire Building | 2017-03-23 02:45 | 50019.5659 | 20.016
Devonshire Building | 2017-03-23 03:00 | 50019.5659 | 0
Devonshire Building | 2017-03-23 03:15 | 50019.5709 | 20.016
Devonshire Building | 2017-03-23 03:30 | 50019.576 | 20.016
Devonshire Building | 2017-03-23 03:45 | 50019.576 | 0
Devonshire Building | 2017-03-23 04:00 | 50019.581 | 20.016
Devonshire Building | 2017-03-23 04:15 | 50019.586 | 20.016
Devonshire Building | 2017-03-23 04:30 | 50019.586 | 0
Devonshire Building | 2017-03-23 04:45 | 50019.591 | 20.016
Devonshire Building | 2017-03-23 05:00 | 50019.591 | 0
Devonshire Building | 2017-03-23 05:15 | 50019.596 | 20.016
Devonshire Building | 2017-03-23 05:30 | 50019.601 | 20.016
Devonshire Building | 2017-03-23 05:45 | 50019.601 | 0
Devonshire Building | 2017-03-23 06:00 | 50019.606 | 20.016
Devonshire Building | 2017-03-23 06:15 | 50019.611 | 20.016
Devonshire Building | 2017-03-23 06:30 | 50019.616 | 20.016
Devonshire Building | 2017-03-23 06:45 | 50019.621 | 20.016
Devonshire Building | 2017-03-23 07:00 | 50019.626 | 20.016
Devonshire Building | 2017-03-23 07:15 | 50019.626 | 0
Devonshire Building | 2017-03-23 07:30 | 50019.631 | 20.016
Devonshire Building | 2017-03-23 07:45 | 50019.636 | 20.016
Devonshire Building | 2017-03-23 08:00 | 50019.651 | 60.012
Devonshire Building | 2017-03-23 08:15 | 50019.661 | 39.996
Devonshire Building | 2017-03-23 08:30 | 50019.666 | 20.016
Devonshire Building | 2017-03-23 08:45 | 50019.671 | 20.016
Devonshire Building | 2017-03-23 09:00 | 50019.696 | 100.008
Devonshire Building | 2017-03-23 09:15 | 50019.706 | 39.996
Devonshire Building | 2017-03-23 09:30 | 50019.716 | 39.996
Devonshire Building | 2017-03-23 09:45 | 50019.721 | 20.016
Devonshire Building | 2017-03-23 10:00 | 50020.006 | 1140.012
Devonshire Building | 2017-03-23 10:15 | 50020.016 | 39.996
Devonshire Building | 2017-03-23 10:30 | 50020.026 | 39.996
Devonshire Building | 2017-03-23 10:45 | 50020.046 | 79.992
Devonshire Building | 2017-03-23 11:00 | 50020.076 | 119.988
Devonshire Building | 2017-03-23 11:15 | 50020.111 | 140.004
Devonshire Building | 2017-03-23 11:30 | 50020.151 | 159.984
Devonshire Building | 2017-03-23 11:45 | 50020.491 | 1360.008
Devonshire Building | 2017-03-23 12:00 | 50020.571 | 320.004
Devonshire Building | 2017-03-23 12:15 | 50020.686 | 460.008
Devonshire Building | 2017-03-23 12:30 | 50020.796 | 439.992
Devonshire Building | 2017-03-23 12:45 | 50020.906 | 439.992
Devonshire Building | 2017-03-23 13:00 | 50021.001 | 380.016
Devonshire Building | 2017-03-23 13:15 | 50021.086 | 339.984
Devonshire Building | 2017-03-23 13:30 | 50021.426 | 1360.008
Devonshire Building | 2017-03-23 13:45 | 50021.486 | 240.012
Devonshire Building | 2017-03-23 14:00 | 50021.541 | 219.996
Devonshire Building | 2017-03-23 14:15 | 50021.601 | 240.012
Devonshire Building | 2017-03-23 14:30 | 50021.651 | 200.016
Devonshire Building | 2017-03-23 14:45 | 50021.696 | 180
Devonshire Building | 2017-03-23 15:00 | 50021.726 | 119.988
Devonshire Building | 2017-03-23 15:15 | 50021.751 | 100.008
Devonshire Building | 2017-03-23 15:30 | 50022.061 | 1239.984
Devonshire Building | 2017-03-23 15:45 | 50022.086 | 100.008
Devonshire Building | 2017-03-23 16:00 | 50022.101 | 60.012
Devonshire Building | 2017-03-23 16:15 | 50022.121 | 79.992
Devonshire Building | 2017-03-23 16:30 | 50022.141 | 79.992
Devonshire Building | 2017-03-23 16:45 | 50022.156 | 60.012
Devonshire Building | 2017-03-23 17:00 | 50022.176 | 79.992
Devonshire Building | 2017-03-23 17:15 | 50022.196 | 79.992
Devonshire Building | 2017-03-23 17:30 | 50022.221 | 100.008
Devonshire Building | 2017-03-23 17:45 | 50022.501 | 1119.996
Devonshire Building | 2017-03-23 18:00 | 50022.526 | 100.008
Devonshire Building | 2017-03-23 18:15 | 50022.546 | 79.992
Devonshire Building | 2017-03-23 18:30 | 50022.571 | 100.008
Devonshire Building | 2017-03-23 18:45 | 50022.601 | 119.988
Devonshire Building | 2017-03-23 19:00 | 50022.631 | 119.988
Devonshire Building | 2017-03-23 19:15 | 50022.676 | 180
Devonshire Building | 2017-03-23 19:30 | 50022.741 | 259.992
Devonshire Building | 2017-03-23 19:45 | 50022.801 | 240.012
Devonshire Building | 2017-03-23 20:00 | 50022.856 | 219.996
Devonshire Building | 2017-03-23 20:15 | 50022.911 | 219.996
Devonshire Building | 2017-03-23 20:30 | 50022.961 | 200.016
Devonshire Building | 2017-03-23 20:45 | 50023.006 | 180
Devonshire Building | 2017-03-23 21:00 | 50023.041 | 140.004
Devonshire Building | 2017-03-23 21:15 | 50023.076 | 140.004
Devonshire Building | 2017-03-23 21:30 | 50023.101 | 100.008
Devonshire Building | 2017-03-23 21:45 | 50023.126 | 100.008
Devonshire Building | 2017-03-23 22:00 | 50023.161 | 140.004
Devonshire Building | 2017-03-23 22:15 | 50023.171 | 39.996
Devonshire Building | 2017-03-23 22:30 | 50023.181 | 39.996
Devonshire Building | 2017-03-23 22:45 | 50023.191 | 39.996
Devonshire Building | 2017-03-23 23:00 | 50023.201 | 39.996
Devonshire Building | 2017-03-23 23:15 | 50023.211 | 39.996
Devonshire Building | 2017-03-23 23:30 | 50023.221 | 39.996
Devonshire Building | 2017-03-23 23:45 | 50023.231 | 39.996 | 0
Devonshire Building | 2017-03-24 | 50023.2383 | 39.996
Devonshire Building | 2017-03-24 00:15 | 50023.2483 | 39.996
Devonshire Building | 2017-03-24 00:30 | 50023.2583 | 39.996
Devonshire Building | 2017-03-24 00:45 | 50023.2683 | 39.996
Devonshire Building | 2017-03-24 01:00 | 50023.2733 | 20.016
Devonshire Building | 2017-03-24 01:15 | 50023.2833 | 39.996
Devonshire Building | 2017-03-24 01:30 | 50023.2933 | 39.996
Devonshire Building | 2017-03-24 01:45 | 50023.2983 | 20.016
Devonshire Building | 2017-03-24 02:00 | 50023.3083 | 39.996
Devonshire Building | 2017-03-24 02:15 | 50023.3133 | 20.016
Devonshire Building | 2017-03-24 02:30 | 50023.3183 | 20.016
Devonshire Building | 2017-03-24 02:45 | 50023.3283 | 39.996
Devonshire Building | 2017-03-24 03:00 | 50023.3333 | 20.016
Devonshire Building | 2017-03-24 03:15 | 50023.3383 | 20.016
Devonshire Building | 2017-03-24 03:30 | 50023.3433 | 20.016
Devonshire Building | 2017-03-24 03:45 | 50023.3533 | 39.996
Devonshire Building | 2017-03-24 04:00 | 50023.3583 | 20.016
Devonshire Building | 2017-03-24 04:15 | 50023.3633 | 20.016
Devonshire Building | 2017-03-24 04:30 | 50023.3683 | 20.016
Devonshire Building | 2017-03-24 04:45 | 50023.3733 | 20.016
Devonshire Building | 2017-03-24 05:00 | 50023.3783 | 20.016
Devonshire Building | 2017-03-24 05:15 | 50023.3833 | 20.016
Devonshire Building | 2017-03-24 05:30 | 50023.3883 | 20.016
Devonshire Building | 2017-03-24 05:45 | 50023.3933 | 20.016
Devonshire Building | 2017-03-24 06:00 | 50023.3983 | 20.016
Devonshire Building | 2017-03-24 06:15 | 50023.4033 | 20.016
Devonshire Building | 2017-03-24 06:30 | 50023.4083 | 20.016
Devonshire Building | 2017-03-24 06:45 | 50023.4183 | 39.996
Devonshire Building | 2017-03-24 07:00 | 50023.4233 | 20.016
Devonshire Building | 2017-03-24 07:15 | 50023.4284 | 20.016
Devonshire Building | 2017-03-24 07:30 | 50023.4383 | 39.996
Devonshire Building | 2017-03-24 07:45 | 50023.4383 | 0
Devonshire Building | 2017-03-24 08:00 | 50023.4583 | 79.992
Devonshire Building | 2017-03-24 08:15 | 50023.7434 | 1140.012
Devonshire Building | 2017-03-24 08:30 | 50023.7633 | 79.992
Devonshire Building | 2017-03-24 08:45 | 50023.7933 | 119.988
Devonshire Building | 2017-03-24 09:00 | 50023.8233 | 119.988
Devonshire Building | 2017-03-24 09:15 | 50023.8583 | 140.004
Devonshire Building | 2017-03-24 09:30 | 50023.8983 | 159.984
Devonshire Building | 2017-03-24 09:45 | 50023.9283 | 119.988
Devonshire Building | 2017-03-24 10:00 | 50023.9483 | 79.992
Devonshire Building | 2017-03-24 10:15 | 50023.9733 | 100.008
Devonshire Building | 2017-03-24 10:30 | 50023.9883 | 60.012
Devonshire Building | 2017-03-24 10:45 | 50024.2733 | 1140.012
Devonshire Building | 2017-03-24 11:00 | 50024.3033 | 119.988
Devonshire Building | 2017-03-24 11:15 | 50024.3633 | 240.012
Devonshire Building | 2017-03-24 11:30 | 50024.4433 | 320.004
Devonshire Building | 2017-03-24 11:45 | 50024.5233 | 320.004
Devonshire Building | 2017-03-24 12:00 | 50024.5983 | 299.988
Devonshire Building | 2017-03-24 12:15 | 50024.7783 | 720
Devonshire Building | 2017-03-24 12:30 | 50025.0333 | 1019.988
Devonshire Building | 2017-03-24 12:45 | 50025.1133 | 320.004
Devonshire Building | 2017-03-24 13:00 | 50025.1833 | 280.008
Devonshire Building | 2017-03-24 13:15 | 50025.2383 | 219.996
Devonshire Building | 2017-03-24 13:30 | 50025.3083 | 280.008
Devonshire Building | 2017-03-24 13:45 | 50025.3683 | 240.012
Devonshire Building | 2017-03-24 14:00 | 50025.4233 | 219.996
Devonshire Building | 2017-03-24 14:15 | 50025.7383 | 1260
Devonshire Building | 2017-03-24 14:30 | 50025.7783 | 159.984
Devonshire Building | 2017-03-24 14:45 | 50025.8233 | 180
Devonshire Building | 2017-03-24 15:00 | 50025.8633 | 159.984
Devonshire Building | 2017-03-24 15:15 | 50025.9083 | 180
Devonshire Building | 2017-03-24 15:30 | 50025.9483 | 159.984
Devonshire Building | 2017-03-24 15:45 | 50025.9883 | 159.984
Devonshire Building | 2017-03-24 16:00 | 50026.0233 | 140.004
Devonshire Building | 2017-03-24 16:15 | 50026.0533 | 119.988
Devonshire Building | 2017-03-24 16:30 | 50026.0933 | 159.984
Devonshire Building | 2017-03-24 16:45 | 50026.1233 | 119.988
Devonshire Building | 2017-03-24 17:00 | 50026.4233 | 1199.988
Devonshire Building | 2017-03-24 17:15 | 50026.4533 | 119.988
Devonshire Building | 2017-03-24 17:30 | 50026.4833 | 119.988
Devonshire Building | 2017-03-24 17:45 | 50026.5133 | 119.988
Devonshire Building | 2017-03-24 18:00 | 50026.5433 | 119.988
Devonshire Building | 2017-03-24 18:15 | 50026.5733 | 119.988
Devonshire Building | 2017-03-24 18:30 | 50026.6033 | 119.988
Devonshire Building | 2017-03-24 18:45 | 50026.6283 | 100.008
Devonshire Building | 2017-03-24 19:00 | 50026.6533 | 100.008
Devonshire Building | 2017-03-24 19:15 | 50026.6733 | 79.992
Devonshire Building | 2017-03-24 19:30 | 50026.6933 | 79.992
Devonshire Building | 2017-03-24 19:45 | 50026.7133 | 79.992
Devonshire Building | 2017-03-24 20:00 | 50026.7283 | 60.012
Devonshire Building | 2017-03-24 20:15 | 50026.7433 | 60.012
Devonshire Building | 2017-03-24 20:30 | 50026.7533 | 39.996
Devonshire Building | 2017-03-24 20:45 | 50026.7683 | 60.012
Devonshire Building | 2017-03-24 21:00 | 50026.7783 | 39.996
Devonshire Building | 2017-03-24 21:15 | 50026.7883 | 39.996
Devonshire Building | 2017-03-24 21:30 | 50026.7983 | 39.996
Devonshire Building | 2017-03-24 21:45 | 50026.8083 | 39.996
Devonshire Building | 2017-03-24 22:00 | 50026.8383 | 119.988
Devonshire Building | 2017-03-24 22:15 | 50026.8383 | 0
Devonshire Building | 2017-03-24 22:30 | 50026.8433 | 20.016
Devonshire Building | 2017-03-24 22:45 | 50026.8433 | 0
Devonshire Building | 2017-03-24 23:00 | 50026.8483 | 20.016
Devonshire Building | 2017-03-24 23:15 | 50026.8533 | 20.016
Devonshire Building | 2017-03-24 23:30 | 50026.8533 | 0
Devonshire Building | 2017-03-24 23:45 | 50026.8583 | 20.016 | 0
Devonshire Building | 2017-03-25 | 50026.8594 | 0
Devonshire Building | 2017-03-25 00:15 | 50026.8644 | 20.016
Devonshire Building | 2017-03-25 00:30 | 50026.8694 | 20.016
Devonshire Building | 2017-03-25 00:45 | 50026.8694 | 0
Devonshire Building | 2017-03-25 01:00 | 50026.8744 | 20.016
Devonshire Building | 2017-03-25 01:15 | 50026.8744 | 0
Devonshire Building | 2017-03-25 01:30 | 50026.8794 | 20.016
Devonshire Building | 2017-03-25 01:45 | 50026.8844 | 20.016
Devonshire Building | 2017-03-25 02:00 | 50026.8844 | 0
Devonshire Building | 2017-03-25 02:15 | 50026.8894 | 20.016
Devonshire Building | 2017-03-25 02:30 | 50026.8894 | 0
Devonshire Building | 2017-03-25 02:45 | 50026.8944 | 20.016
Devonshire Building | 2017-03-25 03:00 | 50026.8944 | 0
Devonshire Building | 2017-03-25 03:15 | 50026.8994 | 20.016
Devonshire Building | 2017-03-25 03:30 | 50026.9044 | 20.016
Devonshire Building | 2017-03-25 03:45 | 50026.9044 | 0
Devonshire Building | 2017-03-25 04:00 | 50026.9094 | 20.016
Devonshire Building | 2017-03-25 04:15 | 50026.9094 | 0
Devonshire Building | 2017-03-25 04:30 | 50026.9144 | 20.016
Devonshire Building | 2017-03-25 04:45 | 50026.9144 | 0
Devonshire Building | 2017-03-25 05:00 | 50026.9194 | 20.016
Devonshire Building | 2017-03-25 05:15 | 50026.9194 | 0
Devonshire Building | 2017-03-25 05:30 | 50026.9244 | 20.016
Devonshire Building | 2017-03-25 05:45 | 50026.9244 | 0
Devonshire Building | 2017-03-25 06:00 | 50026.9294 | 20.016
Devonshire Building | 2017-03-25 06:15 | 50026.9344 | 20.016
Devonshire Building | 2017-03-25 06:30 | 50026.9344 | 0
Devonshire Building | 2017-03-25 06:45 | 50026.9394 | 20.016
Devonshire Building | 2017-03-25 07:00 | 50026.9394 | 0
Devonshire Building | 2017-03-25 07:15 | 50026.9444 | 20.016
Devonshire Building | 2017-03-25 07:30 | 50026.9444 | 0
Devonshire Building | 2017-03-25 07:45 | 50026.9644 | 79.992
Devonshire Building | 2017-03-25 08:00 | 50027.2444 | 1119.996
Devonshire Building | 2017-03-25 08:15 | 50027.2594 | 60.012
Devonshire Building | 2017-03-25 08:30 | 50027.2794 | 79.992
Devonshire Building | 2017-03-25 08:45 | 50027.2944 | 60.012
Devonshire Building | 2017-03-25 09:00 | 50027.3144 | 79.992
Devonshire Building | 2017-03-25 09:15 | 50027.3344 | 79.992
Devonshire Building | 2017-03-25 09:30 | 50027.3494 | 60.012
Devonshire Building | 2017-03-25 09:45 | 50027.3694 | 79.992
Devonshire Building | 2017-03-25 10:00 | 50027.3844 | 60.012
Devonshire Building | 2017-03-25 10:15 | 50027.4044 | 79.992
Devonshire Building | 2017-03-25 10:30 | 50027.4244 | 79.992
Devonshire Building | 2017-03-25 10:45 | 50027.4344 | 39.996
Devonshire Building | 2017-03-25 11:00 | 50027.4344 | 0
Devonshire Building | 2017-03-25 11:15 | 50027.4394 | 20.016
Devonshire Building | 2017-03-25 11:30 | 50027.4445 | 20.016
Devonshire Building | 2017-03-25 11:45 | 50027.4445 | 0
Devonshire Building | 2017-03-25 12:00 | 50027.4495 | 20.016
Devonshire Building | 2017-03-25 12:15 | 50027.4495 | 0
Devonshire Building | 2017-03-25 12:30 | 50027.4545 | 20.016
Devonshire Building | 2017-03-25 12:45 | 50027.4545 | 0
Devonshire Building | 2017-03-25 13:00 | 50027.4595 | 20.016
Devonshire Building | 2017-03-25 13:15 | 50027.4595 | 0
Devonshire Building | 2017-03-25 13:30 | 50027.4645 | 20.016
Devonshire Building | 2017-03-25 13:45 | 50027.4695 | 20.016
Devonshire Building | 2017-03-25 14:00 | 50027.4695 | 0
Devonshire Building | 2017-03-25 14:15 | 50027.4745 | 20.016
Devonshire Building | 2017-03-25 14:30 | 50027.4745 | 0
Devonshire Building | 2017-03-25 14:45 | 50027.4795 | 20.016
Devonshire Building | 2017-03-25 15:00 | 50027.4795 | 0
Devonshire Building | 2017-03-25 15:15 | 50027.4895 | 39.996
Devonshire Building | 2017-03-25 15:30 | 50027.4895 | 0
Devonshire Building | 2017-03-25 15:45 | 50027.4945 | 20.016
Devonshire Building | 2017-03-25 16:00 | 50027.4945 | 0
Devonshire Building | 2017-03-25 16:15 | 50027.4995 | 20.016
Devonshire Building | 2017-03-25 16:30 | 50027.5045 | 20.016
Devonshire Building | 2017-03-25 16:45 | 50027.5045 | 0
Devonshire Building | 2017-03-25 17:00 | 50027.5095 | 20.016
Devonshire Building | 2017-03-25 17:15 | 50027.5145 | 20.016
Devonshire Building | 2017-03-25 17:30 | 50027.5145 | 0
Devonshire Building | 2017-03-25 17:45 | 50027.5195 | 20.016
Devonshire Building | 2017-03-25 18:00 | 50027.5195 | 0
Devonshire Building | 2017-03-25 18:15 | 50027.5245 | 20.016
Devonshire Building | 2017-03-25 18:30 | 50027.5245 | 0
Devonshire Building | 2017-03-25 18:45 | 50027.5295 | 20.016
Devonshire Building | 2017-03-25 19:00 | 50027.5295 | 0
Devonshire Building | 2017-03-25 19:15 | 50027.5345 | 20.016
Devonshire Building | 2017-03-25 19:30 | 50027.5345 | 0
Devonshire Building | 2017-03-25 19:45 | 50027.5395 | 20.016
Devonshire Building | 2017-03-25 20:00 | 50027.5395 | 0
Devonshire Building | 2017-03-25 20:15 | 50027.5445 | 20.016
Devonshire Building | 2017-03-25 20:30 | 50027.5445 | 0
Devonshire Building | 2017-03-25 20:45 | 50027.5495 | 20.016
Devonshire Building | 2017-03-25 21:00 | 50027.5495 | 0
Devonshire Building | 2017-03-25 21:15 | 50027.5545 | 20.016
Devonshire Building | 2017-03-25 21:30 | 50027.5545 | 0
Devonshire Building | 2017-03-25 21:45 | 50027.5595 | 20.016
Devonshire Building | 2017-03-25 22:00 | 50027.5845 | 100.008
Devonshire Building | 2017-03-25 22:15 | 50027.5845 | 0
Devonshire Building | 2017-03-25 22:30 | 50027.5895 | 20.016
Devonshire Building | 2017-03-25 22:45 | 50027.5895 | 0
Devonshire Building | 2017-03-25 23:00 | 50027.5945 | 20.016
Devonshire Building | 2017-03-25 23:15 | 50027.5945 | 0
Devonshire Building | 2017-03-25 23:30 | 50027.5995 | 20.016
Devonshire Building | 2017-03-25 23:45 | 50027.5995 | 0 | 0
Devonshire Building | 2017-03-26 | 50027.6055 | 20.016
Devonshire Building | 2017-03-26 00:15 | 50027.6105 | 20.016
Devonshire Building | 2017-03-26 00:30 | 50027.6105 | 0
Devonshire Building | 2017-03-26 00:45 | 50027.6155 | 20.016
Devonshire Building | 2017-03-26 01:00 | 50027.6155 | 0
Devonshire Building | 2017-03-26 01:15 | 50027.6205 | 20.016
Devonshire Building | 2017-03-26 01:30 | 50027.6205 | 0
Devonshire Building | 2017-03-26 01:45 | 50027.6255 | 20.016
Devonshire Building | 2017-03-26 02:00 | 50027.6255 | 0
Devonshire Building | 2017-03-26 02:15 | 50027.6305 | 20.016
Devonshire Building | 2017-03-26 02:30 | 50027.6305 | 0
Devonshire Building | 2017-03-26 02:45 | 50027.6355 | 20.016
Devonshire Building | 2017-03-26 03:00 | 50027.6355 | 0
Devonshire Building | 2017-03-26 03:15 | 50027.6405 | 20.016
Devonshire Building | 2017-03-26 03:30 | 50027.6405 | 0
Devonshire Building | 2017-03-26 03:45 | 50027.6455 | 20.016
Devonshire Building | 2017-03-26 04:00 | 50027.6455 | 0
Devonshire Building | 2017-03-26 04:15 | 50027.6505 | 20.016
Devonshire Building | 2017-03-26 04:30 | 50027.6505 | 0
Devonshire Building | 2017-03-26 04:45 | 50027.6555 | 20.016
Devonshire Building | 2017-03-26 05:00 | 50027.6555 | 0
Devonshire Building | 2017-03-26 05:15 | 50027.6605 | 20.016
Devonshire Building | 2017-03-26 05:30 | 50027.6605 | 0
Devonshire Building | 2017-03-26 05:45 | 50027.6655 | 20.016
Devonshire Building | 2017-03-26 06:00 | 50027.6655 | 0
Devonshire Building | 2017-03-26 06:15 | 50027.6705 | 20.016
Devonshire Building | 2017-03-26 06:30 | 50027.6705 | 0
Devonshire Building | 2017-03-26 06:45 | 50027.6755 | 20.016
Devonshire Building | 2017-03-26 07:00 | 50027.6755 | 0
Devonshire Building | 2017-03-26 07:15 | 50027.6805 | 20.016
Devonshire Building | 2017-03-26 07:30 | 50027.6805 | 0
Devonshire Building | 2017-03-26 07:45 | 50027.7005 | 79.992
Devonshire Building | 2017-03-26 08:00 | 50027.7205 | 79.992
Devonshire Building | 2017-03-26 08:15 | 50027.7355 | 60.012
Devonshire Building | 2017-03-26 08:30 | 50027.7555 | 79.992
Devonshire Building | 2017-03-26 08:45 | 50027.7755 | 79.992
Devonshire Building | 2017-03-26 09:00 | 50027.7955 | 79.992
Devonshire Building | 2017-03-26 09:15 | 50027.8155 | 79.992
Devonshire Building | 2017-03-26 09:30 | 50027.8405 | 100.008
Devonshire Building | 2017-03-26 09:45 | 50027.8555 | 60.012
Devonshire Building | 2017-03-26 10:00 | 50027.8755 | 79.992
Devonshire Building | 2017-03-26 10:15 | 50027.8905 | 60.012
Devonshire Building | 2017-03-26 10:30 | 50027.8905 | 0
Devonshire Building | 2017-03-26 10:45 | 50028.1555 | 1059.984
Devonshire Building | 2017-03-26 11:00 | 50028.1555 | 0
Devonshire Building | 2017-03-26 11:15 | 50028.1605 | 20.016
Devonshire Building | 2017-03-26 11:30 | 50028.1605 | 0
Devonshire Building | 2017-03-26 11:45 | 50028.1655 | 20.016
Devonshire Building | 2017-03-26 12:00 | 50028.1655 | 0
Devonshire Building | 2017-03-26 12:15 | 50028.1705 | 20.016
Devonshire Building | 2017-03-26 12:30 | 50028.1705 | 0
Devonshire Building | 2017-03-26 12:45 | 50028.1755 | 20.016
Devonshire Building | 2017-03-26 13:00 | 50028.1805 | 20.016
Devonshire Building | 2017-03-26 13:15 | 50028.1805 | 0
Devonshire Building | 2017-03-26 13:30 | 50028.1855 | 20.016
Devonshire Building | 2017-03-26 13:45 | 50028.1855 | 0
Devonshire Building | 2017-03-26 14:00 | 50028.1906 | 20.016
Devonshire Building | 2017-03-26 14:15 | 50028.1906 | 0
Devonshire Building | 2017-03-26 14:30 | 50028.1956 | 20.016
Devonshire Building | 2017-03-26 14:45 | 50028.1956 | 0
Devonshire Building | 2017-03-26 15:00 | 50028.2006 | 20.016
Devonshire Building | 2017-03-26 15:15 | 50028.2006 | 0
Devonshire Building | 2017-03-26 15:30 | 50028.2056 | 20.016
Devonshire Building | 2017-03-26 15:45 | 50028.2056 | 0
Devonshire Building | 2017-03-26 16:00 | 50028.2106 | 20.016
Devonshire Building | 2017-03-26 16:15 | 50028.2156 | 20.016
Devonshire Building | 2017-03-26 16:30 | 50028.2156 | 0
Devonshire Building | 2017-03-26 16:45 | 50028.2206 | 20.016
Devonshire Building | 2017-03-26 17:00 | 50028.2206 | 0
Devonshire Building | 2017-03-26 17:15 | 50028.2256 | 20.016
Devonshire Building | 2017-03-26 17:30 | 50028.2256 | 0
Devonshire Building | 2017-03-26 17:45 | 50028.2306 | 20.016
Devonshire Building | 2017-03-26 18:00 | 50028.2306 | 0
Devonshire Building | 2017-03-26 18:15 | 50028.2356 | 20.016
Devonshire Building | 2017-03-26 18:30 | 50028.2356 | 0
Devonshire Building | 2017-03-26 18:45 | 50028.2406 | 20.016
Devonshire Building | 2017-03-26 19:00 | 50028.2406 | 0
Devonshire Building | 2017-03-26 19:15 | 50028.2456 | 20.016
Devonshire Building | 2017-03-26 19:30 | 50028.2456 | 0
Devonshire Building | 2017-03-26 19:45 | 50028.2506 | 20.016
Devonshire Building | 2017-03-26 20:00 | 50028.2506 | 0
Devonshire Building | 2017-03-26 20:15 | 50028.2556 | 20.016
Devonshire Building | 2017-03-26 20:30 | 50028.2556 | 0
Devonshire Building | 2017-03-26 20:45 | 50028.2606 | 20.016
Devonshire Building | 2017-03-26 21:00 | 50028.2706 | 39.996
Devonshire Building | 2017-03-26 21:15 | 50028.2706 | 0
Devonshire Building | 2017-03-26 21:30 | 50028.2756 | 20.016
Devonshire Building | 2017-03-26 21:45 | 50028.2806 | 20.016
Devonshire Building | 2017-03-26 22:00 | 50028.2806 | 0
Devonshire Building | 2017-03-26 22:15 | 50028.2856 | 20.016
Devonshire Building | 2017-03-26 22:30 | 50028.2856 | 0
Devonshire Building | 2017-03-26 22:45 | 50028.2906 | 20.016
Devonshire Building | 2017-03-26 23:00 | 50028.2906 | 0
Devonshire Building | 2017-03-26 23:15 | 50028.2956 | 20.016
Devonshire Building | 2017-03-26 23:30 | 50028.2956 | 0
Devonshire Building | 2017-03-26 23:45 | 50028.3006 | 20.016 | 0
Devonshire Building | 2017-03-27 | 50028.3008 | 0
Devonshire Building | 2017-03-27 00:15 | 50028.3058 | 20.016
Devonshire Building | 2017-03-27 00:30 | 50028.3058 | 0
Devonshire Building | 2017-03-27 00:45 | 50028.3108 | 20.016
Devonshire Building | 2017-03-27 01:00 | 50028.3108 | 0
Devonshire Building | 2017-03-27 01:15 | 50028.3158 | 20.016
Devonshire Building | 2017-03-27 01:30 | 50028.3158 | 0
Devonshire Building | 2017-03-27 01:45 | 50028.3208 | 20.016
Devonshire Building | 2017-03-27 02:00 | 50028.3208 | 0
Devonshire Building | 2017-03-27 02:15 | 50028.3258 | 20.016
Devonshire Building | 2017-03-27 02:30 | 50028.3258 | 0
Devonshire Building | 2017-03-27 02:45 | 50028.3308 | 20.016
Devonshire Building | 2017-03-27 03:00 | 50028.3308 | 0
Devonshire Building | 2017-03-27 03:15 | 50028.3358 | 20.016
Devonshire Building | 2017-03-27 03:30 | 50028.3358 | 0
Devonshire Building | 2017-03-27 03:45 | 50028.3408 | 20.016
Devonshire Building | 2017-03-27 04:00 | 50028.3408 | 0
Devonshire Building | 2017-03-27 04:15 | 50028.3458 | 20.016
Devonshire Building | 2017-03-27 04:30 | 50028.3458 | 0
Devonshire Building | 2017-03-27 04:45 | 50028.3508 | 20.016
Devonshire Building | 2017-03-27 05:00 | 50028.3508 | 0
Devonshire Building | 2017-03-27 05:15 | 50028.3558 | 20.016
Devonshire Building | 2017-03-27 05:30 | 50028.3608 | 20.016
Devonshire Building | 2017-03-27 05:45 | 50028.3658 | 20.016
Devonshire Building | 2017-03-27 06:00 | 50028.3658 | 0
Devonshire Building | 2017-03-27 06:15 | 50028.3708 | 20.016
Devonshire Building | 2017-03-27 06:30 | 50028.3808 | 39.996
Devonshire Building | 2017-03-27 06:45 | 50028.3858 | 20.016
Devonshire Building | 2017-03-27 07:00 | 50028.6308 | 979.992
Devonshire Building | 2017-03-27 07:15 | 50028.6558 | 100.008
Devonshire Building | 2017-03-27 07:30 | 50028.6708 | 60.012
Devonshire Building | 2017-03-27 07:45 | 50028.7008 | 119.988
Devonshire Building | 2017-03-27 08:00 | 50028.7258 | 100.008
Devonshire Building | 2017-03-27 08:15 | 50028.7608 | 140.004
Devonshire Building | 2017-03-27 08:30 | 50028.7858 | 100.008
Devonshire Building | 2017-03-27 08:45 | 50028.8158 | 119.988
Devonshire Building | 2017-03-27 09:00 | 50028.8408 | 100.008
Devonshire Building | 2017-03-27 09:15 | 50029.1658 | 1299.996
Devonshire Building | 2017-03-27 09:30 | 50029.1858 | 79.992
Devonshire Building | 2017-03-27 09:45 | 50029.2108 | 100.008
Devonshire Building | 2017-03-27 10:00 | 50029.2408 | 119.988
Devonshire Building | 2017-03-27 10:15 | 50029.2758 | 140.004
Devonshire Building | 2017-03-27 10:30 | 50029.4758 | 799.992
Devonshire Building | 2017-03-27 10:45 | 50029.6658 | 759.996
Devonshire Building | 2017-03-27 11:00 | 50029.7308 | 259.992
Devonshire Building | 2017-03-27 11:15 | 50029.7958 | 259.992
Devonshire Building | 2017-03-27 11:30 | 50029.8558 | 240.012
Devonshire Building | 2017-03-27 11:45 | 50029.9208 | 259.992
Devonshire Building | 2017-03-27 12:00 | 50030.1058 | 740.016
Devonshire Building | 2017-03-27 12:15 | 50030.3358 | 920.016
Devonshire Building | 2017-03-27 12:30 | 50030.3908 | 219.996
Devonshire Building | 2017-03-27 12:45 | 50030.4508 | 240.012
Devonshire Building | 2017-03-27 13:00 | 50030.5108 | 240.012
Devonshire Building | 2017-03-27 13:15 | 50030.5609 | 200.016
Devonshire Building | 2017-03-27 13:30 | 50030.6059 | 180
Devonshire Building | 2017-03-27 13:45 | 50030.6509 | 180
Devonshire Building | 2017-03-27 14:00 | 50030.9958 | 1379.988
Devonshire Building | 2017-03-27 14:15 | 50031.0209 | 100.008
Devonshire Building | 2017-03-27 14:30 | 50031.0508 | 119.988
Devonshire Building | 2017-03-27 14:45 | 50031.0808 | 119.988
Devonshire Building | 2017-03-27 15:00 | 50031.1108 | 119.988
Devonshire Building | 2017-03-27 15:15 | 50031.1358 | 100.008
Devonshire Building | 2017-03-27 15:30 | 50031.1608 | 100.008
Devonshire Building | 2017-03-27 15:45 | 50031.4658 | 1220.004
Devonshire Building | 2017-03-27 16:00 | 50031.4908 | 100.008
Devonshire Building | 2017-03-27 16:15 | 50031.5108 | 79.992
Devonshire Building | 2017-03-27 16:30 | 50031.5308 | 79.992
Devonshire Building | 2017-03-27 16:45 | 50031.5508 | 79.992
Devonshire Building | 2017-03-27 17:00 | 50031.5708 | 79.992
Devonshire Building | 2017-03-27 17:15 | 50031.5908 | 79.992
Devonshire Building | 2017-03-27 17:30 | 50031.6108 | 79.992
Devonshire Building | 2017-03-27 17:45 | 50031.6258 | 60.012
Devonshire Building | 2017-03-27 18:00 | 50031.6458 | 79.992
Devonshire Building | 2017-03-27 18:15 | 50031.6608 | 60.012
Devonshire Building | 2017-03-27 18:30 | 50031.6758 | 60.012
Devonshire Building | 2017-03-27 18:45 | 50031.6958 | 79.992
Devonshire Building | 2017-03-27 19:00 | 50031.7108 | 60.012
Devonshire Building | 2017-03-27 19:15 | 50031.7258 | 60.012
Devonshire Building | 2017-03-27 19:30 | 50031.7458 | 79.992
Devonshire Building | 2017-03-27 19:45 | 50031.7758 | 119.988
Devonshire Building | 2017-03-27 20:00 | 50031.8058 | 119.988
Devonshire Building | 2017-03-27 20:15 | 50031.8358 | 119.988
Devonshire Building | 2017-03-27 20:30 | 50031.8658 | 119.988
Devonshire Building | 2017-03-27 20:45 | 50031.8958 | 119.988
Devonshire Building | 2017-03-27 21:00 | 50031.9408 | 180
Devonshire Building | 2017-03-27 21:15 | 50031.9658 | 100.008
Devonshire Building | 2017-03-27 21:30 | 50031.9908 | 100.008
Devonshire Building | 2017-03-27 21:45 | 50032.0158 | 100.008
Devonshire Building | 2017-03-27 22:00 | 50032.0408 | 100.008
Devonshire Building | 2017-03-27 22:15 | 50032.0658 | 100.008
Devonshire Building | 2017-03-27 22:30 | 50032.0758 | 39.996
Devonshire Building | 2017-03-27 22:45 | 50032.0858 | 39.996
Devonshire Building | 2017-03-27 23:00 | 50032.0958 | 39.996
Devonshire Building | 2017-03-27 23:15 | 50032.1008 | 20.016
Devonshire Building | 2017-03-27 23:30 | 50032.1108 | 39.996
Devonshire Building | 2017-03-27 23:45 | 50032.1208 | 39.996 | 0
Devonshire Building | 2017-03-28 | 50032.125 | 20.016
Devonshire Building | 2017-03-28 00:15 | 50032.135 | 39.996
Devonshire Building | 2017-03-28 00:30 | 50032.33 | 780.012
Devonshire Building | 2017-03-28 00:45 | 50032.405 | 299.988
Devonshire Building | 2017-03-28 01:00 | 50032.405 | 0
Devonshire Building | 2017-03-28 01:15 | 50032.41 | 20.016
Devonshire Building | 2017-03-28 01:30 | 50032.415 | 20.016
Devonshire Building | 2017-03-28 01:45 | 50032.415 | 0
Devonshire Building | 2017-03-28 02:00 | 50032.42 | 20.016
Devonshire Building | 2017-03-28 02:15 | 50032.425 | 20.016
Devonshire Building | 2017-03-28 02:30 | 50032.425 | 0
Devonshire Building | 2017-03-28 02:45 | 50032.43 | 20.016
Devonshire Building | 2017-03-28 03:00 | 50032.435 | 20.016
Devonshire Building | 2017-03-28 03:15 | 50032.435 | 0
Devonshire Building | 2017-03-28 03:30 | 50032.44 | 20.016
Devonshire Building | 2017-03-28 03:45 | 50032.445 | 20.016
Devonshire Building | 2017-03-28 04:00 | 50032.445 | 0
Devonshire Building | 2017-03-28 04:15 | 50032.45 | 20.016
Devonshire Building | 2017-03-28 04:30 | 50032.455 | 20.016
Devonshire Building | 2017-03-28 04:45 | 50032.455 | 0
Devonshire Building | 2017-03-28 05:00 | 50032.46 | 20.016
Devonshire Building | 2017-03-28 05:15 | 50032.465 | 20.016
Devonshire Building | 2017-03-28 05:30 | 50032.465 | 0
Devonshire Building | 2017-03-28 05:45 | 50032.4701 | 20.016
Devonshire Building | 2017-03-28 06:00 | 50032.4751 | 20.016
Devonshire Building | 2017-03-28 06:15 | 50032.4801 | 20.016
Devonshire Building | 2017-03-28 06:30 | 50032.4851 | 20.016
Devonshire Building | 2017-03-28 06:45 | 50032.4901 | 20.016
Devonshire Building | 2017-03-28 07:00 | 50032.5001 | 39.996
Devonshire Building | 2017-03-28 07:15 | 50032.5101 | 39.996
Devonshire Building | 2017-03-28 07:30 | 50032.5151 | 20.016
Devonshire Building | 2017-03-28 07:45 | 50032.5301 | 60.012
Devonshire Building | 2017-03-28 08:00 | 50032.5501 | 79.992
Devonshire Building | 2017-03-28 08:15 | 50032.5651 | 60.012
Devonshire Building | 2017-03-28 08:30 | 50032.8501 | 1140.012
Devonshire Building | 2017-03-28 08:45 | 50032.8651 | 60.012
Devonshire Building | 2017-03-28 09:00 | 50032.8851 | 79.992
Devonshire Building | 2017-03-28 09:15 | 50032.9101 | 100.008
Devonshire Building | 2017-03-28 09:30 | 50032.9351 | 100.008
Devonshire Building | 2017-03-28 09:45 | 50032.9801 | 180
Devonshire Building | 2017-03-28 10:00 | 50033.3551 | 1500.012
Devonshire Building | 2017-03-28 10:15 | 50033.4451 | 360
Devonshire Building | 2017-03-28 10:30 | 50033.5251 | 320.004
Devonshire Building | 2017-03-28 10:45 | 50033.6001 | 299.988
Devonshire Building | 2017-03-28 11:00 | 50033.6651 | 259.992
Devonshire Building | 2017-03-28 11:15 | 50033.7251 | 240.012
Devonshire Building | 2017-03-28 11:30 | 50034.0701 | 1379.988
Devonshire Building | 2017-03-28 11:45 | 50034.1101 | 159.984
Devonshire Building | 2017-03-28 12:00 | 50034.1451 | 140.004
Devonshire Building | 2017-03-28 12:15 | 50034.1851 | 159.984
Devonshire Building | 2017-03-28 12:30 | 50034.2201 | 140.004
Devonshire Building | 2017-03-28 12:45 | 50034.2651 | 180
Devonshire Building | 2017-03-28 13:00 | 50034.3351 | 280.008
Devonshire Building | 2017-03-28 13:15 | 50034.6351 | 1199.988
Devonshire Building | 2017-03-28 13:30 | 50034.6801 | 180
Devonshire Building | 2017-03-28 13:45 | 50034.7351 | 219.996
Devonshire Building | 2017-03-28 14:00 | 50034.7901 | 219.996
Devonshire Building | 2017-03-28 14:15 | 50034.8401 | 200.016
Devonshire Building | 2017-03-28 14:30 | 50034.8901 | 200.016
Devonshire Building | 2017-03-28 14:45 | 50034.9401 | 200.016
Devonshire Building | 2017-03-28 15:00 | 50035.0651 | 500.004
Devonshire Building | 2017-03-28 15:15 | 50035.3301 | 1059.984
Devonshire Building | 2017-03-28 15:30 | 50035.3901 | 240.012
Devonshire Building | 2017-03-28 15:45 | 50035.4501 | 240.012
Devonshire Building | 2017-03-28 16:00 | 50035.5251 | 299.988
Devonshire Building | 2017-03-28 16:15 | 50035.6751 | 600.012
Devonshire Building | 2017-03-28 16:30 | 50035.9751 | 1199.988
Devonshire Building | 2017-03-28 16:45 | 50036.1451 | 680.004
Devonshire Building | 2017-03-28 17:00 | 50036.2401 | 380.016
Devonshire Building | 2017-03-28 17:15 | 50036.3751 | 540
Devonshire Building | 2017-03-28 17:30 | 50036.6001 | 900
Devonshire Building | 2017-03-28 17:45 | 50036.6251 | 100.008
Devonshire Building | 2017-03-28 18:00 | 50036.6501 | 100.008
Devonshire Building | 2017-03-28 18:15 | 50036.6751 | 100.008
Devonshire Building | 2017-03-28 18:30 | 50036.6951 | 79.992
Devonshire Building | 2017-03-28 18:45 | 50036.7201 | 100.008
Devonshire Building | 2017-03-28 19:00 | 50036.7401 | 79.992
Devonshire Building | 2017-03-28 19:15 | 50036.7601 | 79.992
Devonshire Building | 2017-03-28 19:30 | 50036.7801 | 79.992
Devonshire Building | 2017-03-28 19:45 | 50036.8001 | 79.992
Devonshire Building | 2017-03-28 20:00 | 50036.8201 | 79.992
Devonshire Building | 2017-03-28 20:15 | 50036.8401 | 79.992
Devonshire Building | 2017-03-28 20:30 | 50036.8601 | 79.992
Devonshire Building | 2017-03-28 20:45 | 50036.8801 | 79.992
Devonshire Building | 2017-03-28 21:00 | 50036.9001 | 79.992
Devonshire Building | 2017-03-28 21:15 | 50036.9151 | 60.012
Devonshire Building | 2017-03-28 21:30 | 50036.9301 | 60.012
Devonshire Building | 2017-03-28 21:45 | 50036.9451 | 60.012
Devonshire Building | 2017-03-28 22:00 | 50036.9651 | 79.992
Devonshire Building | 2017-03-28 22:15 | 50036.9801 | 60.012
Devonshire Building | 2017-03-28 22:30 | 50036.9951 | 60.012
Devonshire Building | 2017-03-28 22:45 | 50037.0101 | 60.012
Devonshire Building | 2017-03-28 23:00 | 50037.0201 | 39.996
Devonshire Building | 2017-03-28 23:15 | 50037.0351 | 60.012
Devonshire Building | 2017-03-28 23:30 | 50037.0451 | 39.996
Devonshire Building | 2017-03-28 23:45 | 50037.0601 | 60.012 | 0
Devonshire Building | 2017-03-29 | 50037.0703 | 39.996
Devonshire Building | 2017-03-29 00:15 | 50037.0803 | 39.996
Devonshire Building | 2017-03-29 00:30 | 50037.0903 | 39.996
Devonshire Building | 2017-03-29 00:45 | 50037.1053 | 60.012
Devonshire Building | 2017-03-29 01:00 | 50037.1153 | 39.996
Devonshire Building | 2017-03-29 01:15 | 50037.1253 | 39.996
Devonshire Building | 2017-03-29 01:30 | 50037.1303 | 20.016
Devonshire Building | 2017-03-29 01:45 | 50037.1403 | 39.996
Devonshire Building | 2017-03-29 02:00 | 50037.1503 | 39.996
Devonshire Building | 2017-03-29 02:15 | 50037.1553 | 20.016
Devonshire Building | 2017-03-29 02:30 | 50037.1653 | 39.996
Devonshire Building | 2017-03-29 02:45 | 50037.1753 | 39.996
Devonshire Building | 2017-03-29 03:00 | 50037.1803 | 20.016
Devonshire Building | 2017-03-29 03:15 | 50037.1903 | 39.996
Devonshire Building | 2017-03-29 03:30 | 50037.1953 | 20.016
Devonshire Building | 2017-03-29 03:45 | 50037.2053 | 39.996
Devonshire Building | 2017-03-29 04:00 | 50037.2103 | 20.016
Devonshire Building | 2017-03-29 04:15 | 50037.2153 | 20.016
Devonshire Building | 2017-03-29 04:30 | 50037.2253 | 39.996
Devonshire Building | 2017-03-29 04:45 | 50037.2303 | 20.016
Devonshire Building | 2017-03-29 05:00 | 50037.2353 | 20.016
Devonshire Building | 2017-03-29 05:15 | 50037.2403 | 20.016
Devonshire Building | 2017-03-29 05:30 | 50037.2503 | 39.996
Devonshire Building | 2017-03-29 05:45 | 50037.2553 | 20.016
Devonshire Building | 2017-03-29 06:00 | 50037.2603 | 20.016
Devonshire Building | 2017-03-29 06:15 | 50037.2703 | 39.996
Devonshire Building | 2017-03-29 06:30 | 50037.2753 | 20.016
Devonshire Building | 2017-03-29 06:45 | 50037.2853 | 39.996
Devonshire Building | 2017-03-29 07:00 | 50037.2904 | 20.016
Devonshire Building | 2017-03-29 07:15 | 50037.3003 | 39.996
Devonshire Building | 2017-03-29 07:30 | 50037.3054 | 20.016
Devonshire Building | 2017-03-29 07:45 | 50037.5304 | 900
Devonshire Building | 2017-03-29 08:00 | 50037.6104 | 320.004
Devonshire Building | 2017-03-29 08:15 | 50037.6154 | 20.016
Devonshire Building | 2017-03-29 08:30 | 50037.6304 | 60.012
Devonshire Building | 2017-03-29 08:45 | 50037.6554 | 100.008
Devonshire Building | 2017-03-29 09:00 | 50037.6754 | 79.992
Devonshire Building | 2017-03-29 09:15 | 50037.7004 | 100.008
Devonshire Building | 2017-03-29 09:30 | 50038.0254 | 1299.996
Devonshire Building | 2017-03-29 09:45 | 50038.0604 | 140.004
Devonshire Building | 2017-03-29 10:00 | 50038.1004 | 159.984
Devonshire Building | 2017-03-29 10:15 | 50038.1554 | 219.996
Devonshire Building | 2017-03-29 10:30 | 50038.5004 | 1379.988
Devonshire Building | 2017-03-29 10:45 | 50038.5954 | 380.016
Devonshire Building | 2017-03-29 11:00 | 50038.6754 | 320.004
Devonshire Building | 2017-03-29 11:15 | 50038.7554 | 320.004
Devonshire Building | 2017-03-29 11:30 | 50038.8304 | 299.988
Devonshire Building | 2017-03-29 11:45 | 50039.0404 | 839.988
Devonshire Building | 2017-03-29 12:00 | 50039.2604 | 879.984
Devonshire Building | 2017-03-29 12:15 | 50039.3304 | 280.008
Devonshire Building | 2017-03-29 12:30 | 50039.4054 | 299.988
Devonshire Building | 2017-03-29 12:45 | 50039.4654 | 240.012
Devonshire Building | 2017-03-29 13:00 | 50039.7054 | 960.012
Devonshire Building | 2017-03-29 13:15 | 50039.8554 | 600.012
Devonshire Building | 2017-03-29 13:30 | 50039.9104 | 219.996
Devonshire Building | 2017-03-29 13:45 | 50039.9754 | 259.992
Devonshire Building | 2017-03-29 14:00 | 50040.0304 | 219.996
Devonshire Building | 2017-03-29 14:15 | 50040.0804 | 200.016
Devonshire Building | 2017-03-29 14:30 | 50040.1254 | 180
Devonshire Building | 2017-03-29 14:45 | 50040.1654 | 159.984
Devonshire Building | 2017-03-29 15:00 | 50040.5004 | 1339.992
Devonshire Building | 2017-03-29 15:15 | 50040.5254 | 100.008
Devonshire Building | 2017-03-29 15:30 | 50040.5504 | 100.008
Devonshire Building | 2017-03-29 15:45 | 50040.5704 | 79.992
Devonshire Building | 2017-03-29 16:00 | 50040.6054 | 140.004
Devonshire Building | 2017-03-29 16:15 | 50040.6454 | 159.984
Devonshire Building | 2017-03-29 16:30 | 50040.7954 | 600.012
Devonshire Building | 2017-03-29 16:45 | 50041.0354 | 960.012
Devonshire Building | 2017-03-29 17:00 | 50041.1054 | 280.008
Devonshire Building | 2017-03-29 17:15 | 50041.1754 | 280.008
Devonshire Building | 2017-03-29 17:30 | 50041.2404 | 259.992
Devonshire Building | 2017-03-29 17:45 | 50041.3004 | 240.012
Devonshire Building | 2017-03-29 18:00 | 50041.3454 | 180
Devonshire Building | 2017-03-29 18:15 | 50041.3904 | 180
Devonshire Building | 2017-03-29 18:30 | 50041.4254 | 140.004
Devonshire Building | 2017-03-29 18:45 | 50041.4554 | 119.988
Devonshire Building | 2017-03-29 19:00 | 50041.4854 | 119.988
Devonshire Building | 2017-03-29 19:15 | 50041.5104 | 100.008
Devonshire Building | 2017-03-29 19:30 | 50041.5304 | 79.992
Devonshire Building | 2017-03-29 19:45 | 50041.5504 | 79.992
Devonshire Building | 2017-03-29 20:00 | 50041.5704 | 79.992
Devonshire Building | 2017-03-29 20:15 | 50041.5854 | 60.012
Devonshire Building | 2017-03-29 20:30 | 50041.6004 | 60.012
Devonshire Building | 2017-03-29 20:45 | 50041.6154 | 60.012
Devonshire Building | 2017-03-29 21:00 | 50041.6354 | 79.992
Devonshire Building | 2017-03-29 21:15 | 50041.6454 | 39.996
Devonshire Building | 2017-03-29 21:30 | 50041.6554 | 39.996
Devonshire Building | 2017-03-29 21:45 | 50041.6604 | 20.016
Devonshire Building | 2017-03-29 22:00 | 50041.6704 | 39.996
Devonshire Building | 2017-03-29 22:15 | 50041.6804 | 39.996
Devonshire Building | 2017-03-29 22:30 | 50041.6904 | 39.996
Devonshire Building | 2017-03-29 22:45 | 50041.7004 | 39.996
Devonshire Building | 2017-03-29 23:00 | 50041.7054 | 20.016
Devonshire Building | 2017-03-29 23:15 | 50041.7154 | 39.996
Devonshire Building | 2017-03-29 23:30 | 50041.7204 | 20.016
Devonshire Building | 2017-03-29 23:45 | 50041.7304 | 39.996 | 20.016
Devonshire Building | 2017-03-30 | 50041.7383 | 39.996
Devonshire Building | 2017-03-30 00:15 | 50041.7433 | 20.016
Devonshire Building | 2017-03-30 00:30 | 50041.7533 | 39.996
Devonshire Building | 2017-03-30 00:45 | 50041.7583 | 20.016
Devonshire Building | 2017-03-30 01:00 | 50041.7683 | 39.996
Devonshire Building | 2017-03-30 01:15 | 50041.7733 | 20.016
Devonshire Building | 2017-03-30 01:30 | 50041.7783 | 20.016
Devonshire Building | 2017-03-30 01:45 | 50041.7883 | 39.996
Devonshire Building | 2017-03-30 02:00 | 50041.7933 | 20.016
Devonshire Building | 2017-03-30 02:15 | 50041.7983 | 20.016
Devonshire Building | 2017-03-30 02:30 | 50041.8033 | 20.016
Devonshire Building | 2017-03-30 02:45 | 50041.8133 | 39.996
Devonshire Building | 2017-03-30 03:00 | 50041.8183 | 20.016
Devonshire Building | 2017-03-30 03:15 | 50041.8233 | 20.016
Devonshire Building | 2017-03-30 03:30 | 50041.8283 | 20.016
Devonshire Building | 2017-03-30 03:45 | 50041.8333 | 20.016
Devonshire Building | 2017-03-30 04:00 | 50041.8383 | 20.016
Devonshire Building | 2017-03-30 04:15 | 50041.8433 | 20.016
Devonshire Building | 2017-03-30 04:30 | 50041.8483 | 20.016
Devonshire Building | 2017-03-30 04:45 | 50041.8533 | 20.016
Devonshire Building | 2017-03-30 05:00 | 50041.8583 | 20.016
Devonshire Building | 2017-03-30 05:15 | 50041.8683 | 39.996
Devonshire Building | 2017-03-30 05:30 | 50041.8733 | 20.016
Devonshire Building | 2017-03-30 05:45 | 50041.8783 | 20.016
Devonshire Building | 2017-03-30 06:00 | 50041.8834 | 20.016
Devonshire Building | 2017-03-30 06:15 | 50041.8984 | 60.012
Devonshire Building | 2017-03-30 06:30 | 50041.9034 | 20.016
Devonshire Building | 2017-03-30 06:45 | 50041.9084 | 20.016
Devonshire Building | 2017-03-30 07:00 | 50041.9134 | 20.016
Devonshire Building | 2017-03-30 07:15 | 50041.9334 | 79.992
Devonshire Building | 2017-03-30 07:30 | 50042.2184 | 1140.012
Devonshire Building | 2017-03-30 07:45 | 50042.2334 | 60.012
Devonshire Building | 2017-03-30 08:00 | 50042.2684 | 140.004
Devonshire Building | 2017-03-30 08:15 | 50042.2984 | 119.988
Devonshire Building | 2017-03-30 08:30 | 50042.3184 | 79.992
Devonshire Building | 2017-03-30 08:45 | 50042.3434 | 100.008
Devonshire Building | 2017-03-30 09:00 | 50042.3634 | 79.992
Devonshire Building | 2017-03-30 09:15 | 50042.3884 | 100.008
Devonshire Building | 2017-03-30 09:30 | 50042.4134 | 100.008
Devonshire Building | 2017-03-30 09:45 | 50042.7434 | 1320.012
Devonshire Building | 2017-03-30 10:00 | 50042.7684 | 100.008
Devonshire Building | 2017-03-30 10:15 | 50042.7934 | 100.008
Devonshire Building | 2017-03-30 10:30 | 50042.8184 | 100.008
Devonshire Building | 2017-03-30 10:45 | 50042.8384 | 79.992
Devonshire Building | 2017-03-30 11:00 | 50042.8584 | 79.992
Devonshire Building | 2017-03-30 11:15 | 50043.1734 | 1260
Devonshire Building | 2017-03-30 11:30 | 50043.2184 | 180
Devonshire Building | 2017-03-30 11:45 | 50043.2784 | 240.012
Devonshire Building | 2017-03-30 12:00 | 50043.3384 | 240.012
Devonshire Building | 2017-03-30 12:15 | 50043.3984 | 240.012
Devonshire Building | 2017-03-30 12:30 | 50043.4584 | 240.012
Devonshire Building | 2017-03-30 12:45 | 50043.7984 | 1360.008
Devonshire Building | 2017-03-30 13:00 | 50043.8434 | 180
Devonshire Building | 2017-03-30 13:15 | 50043.8984 | 219.996
Devonshire Building | 2017-03-30 13:30 | 50043.9434 | 180
Devonshire Building | 2017-03-30 13:45 | 50043.9884 | 180
Devonshire Building | 2017-03-30 14:00 | 50044.0334 | 180
Devonshire Building | 2017-03-30 14:15 | 50044.0734 | 159.984
Devonshire Building | 2017-03-30 14:30 | 50044.4034 | 1320.012
Devonshire Building | 2017-03-30 14:45 | 50044.4284 | 100.008
Devonshire Building | 2017-03-30 15:00 | 50044.4484 | 79.992
Devonshire Building | 2017-03-30 15:15 | 50044.4734 | 100.008
Devonshire Building | 2017-03-30 15:30 | 50044.4984 | 100.008
Devonshire Building | 2017-03-30 15:45 | 50044.5234 | 100.008
Devonshire Building | 2017-03-30 16:00 | 50044.5484 | 100.008
Devonshire Building | 2017-03-30 16:15 | 50044.5684 | 79.992
Devonshire Building | 2017-03-30 16:30 | 50044.5884 | 79.992
Devonshire Building | 2017-03-30 16:45 | 50044.8784 | 1159.992
Devonshire Building | 2017-03-30 17:00 | 50044.9034 | 100.008
Devonshire Building | 2017-03-30 17:15 | 50044.9234 | 79.992
Devonshire Building | 2017-03-30 17:30 | 50044.9434 | 79.992
Devonshire Building | 2017-03-30 17:45 | 50044.9634 | 79.992
Devonshire Building | 2017-03-30 18:00 | 50044.9884 | 100.008
Devonshire Building | 2017-03-30 18:15 | 50045.0084 | 79.992
Devonshire Building | 2017-03-30 18:30 | 50045.0284 | 79.992
Devonshire Building | 2017-03-30 18:45 | 50045.0584 | 119.988
Devonshire Building | 2017-03-30 19:00 | 50045.0834 | 100.008
Devonshire Building | 2017-03-30 19:15 | 50045.1034 | 79.992
Devonshire Building | 2017-03-30 19:30 | 50045.1184 | 60.012
Devonshire Building | 2017-03-30 19:45 | 50045.1384 | 79.992
Devonshire Building | 2017-03-30 20:00 | 50045.1584 | 79.992
Devonshire Building | 2017-03-30 20:15 | 50045.1734 | 60.012
Devonshire Building | 2017-03-30 20:30 | 50045.1934 | 79.992
Devonshire Building | 2017-03-30 20:45 | 50045.2084 | 60.012
Devonshire Building | 2017-03-30 21:00 | 50045.2284 | 79.992
Devonshire Building | 2017-03-30 21:15 | 50045.2434 | 60.012
Devonshire Building | 2017-03-30 21:30 | 50045.2534 | 39.996
Devonshire Building | 2017-03-30 21:45 | 50045.2634 | 39.996
Devonshire Building | 2017-03-30 22:00 | 50045.2784 | 60.012
Devonshire Building | 2017-03-30 22:15 | 50045.2884 | 39.996
Devonshire Building | 2017-03-30 22:30 | 50045.2984 | 39.996
Devonshire Building | 2017-03-30 22:45 | 50045.3134 | 60.012
Devonshire Building | 2017-03-30 23:00 | 50045.3234 | 39.996
Devonshire Building | 2017-03-30 23:15 | 50045.3334 | 39.996
Devonshire Building | 2017-03-30 23:30 | 50045.3484 | 60.012
Devonshire Building | 2017-03-30 23:45 | 50045.3584 | 39.996 | 20.016
Devonshire Building | 2017-03-31 | 50045.3633 | 20.016
Devonshire Building | 2017-03-31 00:15 | 50045.3733 | 39.996
Devonshire Building | 2017-03-31 00:30 | 50045.3783 | 20.016
Devonshire Building | 2017-03-31 00:45 | 50045.3883 | 39.996
Devonshire Building | 2017-03-31 01:00 | 50045.3933 | 20.016
Devonshire Building | 2017-03-31 01:15 | 50045.4033 | 39.996
Devonshire Building | 2017-03-31 01:30 | 50045.4083 | 20.016
Devonshire Building | 2017-03-31 01:45 | 50045.4183 | 39.996
Devonshire Building | 2017-03-31 02:00 | 50045.4233 | 20.016
Devonshire Building | 2017-03-31 02:15 | 50045.4333 | 39.996
Devonshire Building | 2017-03-31 02:30 | 50045.4383 | 20.016
Devonshire Building | 2017-03-31 02:45 | 50045.4433 | 20.016
Devonshire Building | 2017-03-31 03:00 | 50045.4483 | 20.016
Devonshire Building | 2017-03-31 03:15 | 50045.4533 | 20.016
Devonshire Building | 2017-03-31 03:30 | 50045.4583 | 20.016
Devonshire Building | 2017-03-31 03:45 | 50045.4683 | 39.996
Devonshire Building | 2017-03-31 04:00 | 50045.4733 | 20.016
Devonshire Building | 2017-03-31 04:15 | 50045.4783 | 20.016
Devonshire Building | 2017-03-31 04:30 | 50045.4833 | 20.016
Devonshire Building | 2017-03-31 04:45 | 50045.4883 | 20.016
Devonshire Building | 2017-03-31 05:00 | 50045.4933 | 20.016
Devonshire Building | 2017-03-31 05:15 | 50045.4983 | 20.016
Devonshire Building | 2017-03-31 05:30 | 50045.5033 | 20.016
Devonshire Building | 2017-03-31 05:45 | 50045.5083 | 20.016
Devonshire Building | 2017-03-31 06:00 | 50045.5133 | 20.016
Devonshire Building | 2017-03-31 06:15 | 50045.5183 | 20.016
Devonshire Building | 2017-03-31 06:30 | 50045.5283 | 39.996
Devonshire Building | 2017-03-31 06:45 | 50045.5334 | 20.016
Devonshire Building | 2017-03-31 07:00 | 50045.5434 | 39.996
Devonshire Building | 2017-03-31 07:15 | 50045.6733 | 519.984
Devonshire Building | 2017-03-31 07:30 | 50045.8283 | 619.992
Devonshire Building | 2017-03-31 07:45 | 50045.8483 | 79.992
Devonshire Building | 2017-03-31 08:00 | 50045.8883 | 159.984
Devonshire Building | 2017-03-31 08:15 | 50045.9133 | 100.008
Devonshire Building | 2017-03-31 08:30 | 50045.9333 | 79.992
Devonshire Building | 2017-03-31 08:45 | 50045.9633 | 119.988
Devonshire Building | 2017-03-31 09:00 | 50045.9833 | 79.992
Devonshire Building | 2017-03-31 09:15 | 50046.0033 | 79.992
Devonshire Building | 2017-03-31 09:30 | 50046.3233 | 1280.016
Devonshire Building | 2017-03-31 09:45 | 50046.3483 | 100.008
Devonshire Building | 2017-03-31 10:00 | 50046.3733 | 100.008
Devonshire Building | 2017-03-31 10:15 | 50046.4133 | 159.984
Devonshire Building | 2017-03-31 10:30 | 50046.4683 | 219.996
Devonshire Building | 2017-03-31 10:45 | 50046.5383 | 280.008
Devonshire Building | 2017-03-31 11:00 | 50046.6033 | 259.992
Devonshire Building | 2017-03-31 11:15 | 50046.9533 | 1400.004
Devonshire Building | 2017-03-31 11:30 | 50047.0233 | 280.008
Devonshire Building | 2017-03-31 11:45 | 50047.2183 | 780.012
Devonshire Building | 2017-03-31 12:00 | 50047.5333 | 1260
Devonshire Building | 2017-03-31 12:15 | 50047.7033 | 680.004
Devonshire Building | 2017-03-31 12:30 | 50047.7933 | 360
Devonshire Building | 2017-03-31 12:45 | 50047.8583 | 259.992
Devonshire Building | 2017-03-31 13:00 | 50047.9383 | 320.004
Devonshire Building | 2017-03-31 13:15 | 50048.2183 | 1119.996
Devonshire Building | 2017-03-31 13:30 | 50048.2333 | 60.012
Devonshire Building | 2017-03-31 13:45 | 50048.2533 | 79.992
Devonshire Building | 2017-03-31 14:00 | 50048.2783 | 100.008
Devonshire Building | 2017-03-31 14:15 | 50048.3033 | 100.008
Devonshire Building | 2017-03-31 14:30 | 50048.3283 | 100.008
Devonshire Building | 2017-03-31 14:45 | 50048.3483 | 79.992
Devonshire Building | 2017-03-31 15:00 | 50048.3683 | 79.992
Devonshire Building | 2017-03-31 15:15 | 50048.6683 | 1199.988
Devonshire Building | 2017-03-31 15:30 | 50048.6883 | 79.992
Devonshire Building | 2017-03-31 15:45 | 50048.7083 | 79.992
Devonshire Building | 2017-03-31 16:00 | 50048.7233 | 60.012
Devonshire Building | 2017-03-31 16:15 | 50048.7433 | 79.992
Devonshire Building | 2017-03-31 16:30 | 50048.7633 | 79.992
Devonshire Building | 2017-03-31 16:45 | 50048.7833 | 79.992
Devonshire Building | 2017-03-31 17:00 | 50048.8033 | 79.992
Devonshire Building | 2017-03-31 17:15 | 50048.8233 | 79.992
Devonshire Building | 2017-03-31 17:30 | 50048.8383 | 60.012
Devonshire Building | 2017-03-31 17:45 | 50048.8583 | 79.992
Devonshire Building | 2017-03-31 18:00 | 50048.8783 | 79.992
Devonshire Building | 2017-03-31 18:15 | 50048.8983 | 79.992
Devonshire Building | 2017-03-31 18:30 | 50048.9133 | 60.012
Devonshire Building | 2017-03-31 18:45 | 50048.9333 | 79.992
Devonshire Building | 2017-03-31 19:00 | 50048.9483 | 60.012
Devonshire Building | 2017-03-31 19:15 | 50048.9683 | 79.992
Devonshire Building | 2017-03-31 19:30 | 50048.9833 | 60.012
Devonshire Building | 2017-03-31 19:45 | 50049.0033 | 79.992
Devonshire Building | 2017-03-31 20:00 | 50049.0183 | 60.012
Devonshire Building | 2017-03-31 20:15 | 50049.0333 | 60.012
Devonshire Building | 2017-03-31 20:30 | 50049.0483 | 60.012
Devonshire Building | 2017-03-31 20:45 | 50049.0633 | 60.012
Devonshire Building | 2017-03-31 21:00 | 50049.1083 | 180
Devonshire Building | 2017-03-31 21:15 | 50049.1333 | 100.008
Devonshire Building | 2017-03-31 21:30 | 50049.1583 | 100.008
Devonshire Building | 2017-03-31 21:45 | 50049.1783 | 79.992
Devonshire Building | 2017-03-31 22:00 | 50049.2033 | 100.008
Devonshire Building | 2017-03-31 22:15 | 50049.2283 | 100.008
Devonshire Building | 2017-03-31 22:30 | 50049.2533 | 100.008
Devonshire Building | 2017-03-31 22:45 | 50049.2784 | 100.008
Devonshire Building | 2017-03-31 23:00 | 50049.2983 | 79.992
Devonshire Building | 2017-03-31 23:15 | 50049.3234 | 100.008
Devonshire Building | 2017-03-31 23:30 | 50049.3434 | 79.992
Devonshire Building | 2017-03-31 23:45 | 50049.6233 | 1119.996 | 20.016
Devonshire Building | 2017-04-01 | 50049.6406 | 60.012
Devonshire Building | 2017-04-01 00:15 | 50049.6606 | 79.992
Devonshire Building | 2017-04-01 00:30 | 50049.6756 | 60.012
Devonshire Building | 2017-04-01 00:45 | 50049.6906 | 60.012
Devonshire Building | 2017-04-01 01:00 | 50049.7106 | 79.992
Devonshire Building | 2017-04-01 01:15 | 50049.7306 | 79.992
Devonshire Building | 2017-04-01 01:30 | 50049.7506 | 79.992
Devonshire Building | 2017-04-01 01:45 | 50049.7706 | 79.992
Devonshire Building | 2017-04-01 02:00 | 50049.7906 | 79.992
Devonshire Building | 2017-04-01 02:15 | 50049.8106 | 79.992
Devonshire Building | 2017-04-01 02:30 | 50049.8306 | 79.992
Devonshire Building | 2017-04-01 02:45 | 50049.8506 | 79.992
Devonshire Building | 2017-04-01 03:00 | 50049.8656 | 60.012
Devonshire Building | 2017-04-01 03:15 | 50049.8806 | 60.012
Devonshire Building | 2017-04-01 03:30 | 50049.9006 | 79.992
Devonshire Building | 2017-04-01 03:45 | 50049.9156 | 60.012
Devonshire Building | 2017-04-01 04:00 | 50049.9306 | 60.012
Devonshire Building | 2017-04-01 04:15 | 50049.9406 | 39.996
Devonshire Building | 2017-04-01 04:30 | 50049.9556 | 60.012
Devonshire Building | 2017-04-01 04:45 | 50049.9656 | 39.996
Devonshire Building | 2017-04-01 05:00 | 50049.9806 | 60.012
Devonshire Building | 2017-04-01 05:15 | 50049.9906 | 39.996
Devonshire Building | 2017-04-01 05:30 | 50050.0056 | 60.012
Devonshire Building | 2017-04-01 05:45 | 50050.0156 | 39.996
Devonshire Building | 2017-04-01 06:00 | 50050.0256 | 39.996
Devonshire Building | 2017-04-01 06:15 | 50050.0356 | 39.996
Devonshire Building | 2017-04-01 06:30 | 50050.0456 | 39.996
Devonshire Building | 2017-04-01 06:45 | 50050.0556 | 39.996
Devonshire Building | 2017-04-01 07:00 | 50050.0656 | 39.996
Devonshire Building | 2017-04-01 07:15 | 50050.0756 | 39.996
Devonshire Building | 2017-04-01 07:30 | 50050.0856 | 39.996
Devonshire Building | 2017-04-01 07:45 | 50050.1106 | 100.008
Devonshire Building | 2017-04-01 08:00 | 50050.1356 | 100.008
Devonshire Building | 2017-04-01 08:15 | 50050.1606 | 100.008
Devonshire Building | 2017-04-01 08:30 | 50050.1856 | 100.008
Devonshire Building | 2017-04-01 08:45 | 50050.2106 | 100.008
Devonshire Building | 2017-04-01 09:00 | 50050.2306 | 79.992
Devonshire Building | 2017-04-01 09:15 | 50050.2556 | 100.008
Devonshire Building | 2017-04-01 09:30 | 50050.2806 | 100.008
Devonshire Building | 2017-04-01 09:45 | 50050.3056 | 100.008
Devonshire Building | 2017-04-01 10:00 | 50050.3306 | 100.008
Devonshire Building | 2017-04-01 10:15 | 50050.3506 | 79.992
Devonshire Building | 2017-04-01 10:30 | 50050.3756 | 100.008
Devonshire Building | 2017-04-01 10:45 | 50050.3856 | 39.996
Devonshire Building | 2017-04-01 11:00 | 50050.3906 | 20.016
Devonshire Building | 2017-04-01 11:15 | 50050.4006 | 39.996
Devonshire Building | 2017-04-01 11:30 | 50050.4106 | 39.996
Devonshire Building | 2017-04-01 11:45 | 50050.4156 | 20.016
Devonshire Building | 2017-04-01 12:00 | 50050.4256 | 39.996
Devonshire Building | 2017-04-01 12:15 | 50050.4307 | 20.016
Devonshire Building | 2017-04-01 12:30 | 50050.4406 | 39.996
Devonshire Building | 2017-04-01 12:45 | 50050.4506 | 39.996
Devonshire Building | 2017-04-01 13:00 | 50050.4557 | 20.016
Devonshire Building | 2017-04-01 13:15 | 50050.4657 | 39.996
Devonshire Building | 2017-04-01 13:30 | 50050.4707 | 20.016
Devonshire Building | 2017-04-01 13:45 | 50050.4807 | 39.996
Devonshire Building | 2017-04-01 14:00 | 50050.4857 | 20.016
Devonshire Building | 2017-04-01 14:15 | 50050.4957 | 39.996
Devonshire Building | 2017-04-01 14:30 | 50050.5007 | 20.016
Devonshire Building | 2017-04-01 14:45 | 50050.5107 | 39.996
Devonshire Building | 2017-04-01 15:00 | 50050.5157 | 20.016
Devonshire Building | 2017-04-01 15:15 | 50050.5257 | 39.996
Devonshire Building | 2017-04-01 15:30 | 50050.5307 | 20.016
Devonshire Building | 2017-04-01 15:45 | 50050.5407 | 39.996
Devonshire Building | 2017-04-01 16:00 | 50050.5457 | 20.016
Devonshire Building | 2017-04-01 16:15 | 50050.5557 | 39.996
Devonshire Building | 2017-04-01 16:30 | 50050.5607 | 20.016
Devonshire Building | 2017-04-01 16:45 | 50050.5707 | 39.996
Devonshire Building | 2017-04-01 17:00 | 50050.5757 | 20.016
Devonshire Building | 2017-04-01 17:15 | 50050.5857 | 39.996
Devonshire Building | 2017-04-01 17:30 | 50050.5907 | 20.016
Devonshire Building | 2017-04-01 17:45 | 50050.6007 | 39.996
Devonshire Building | 2017-04-01 18:00 | 50050.6057 | 20.016
Devonshire Building | 2017-04-01 18:15 | 50050.6157 | 39.996
Devonshire Building | 2017-04-01 18:30 | 50050.6207 | 20.016
Devonshire Building | 2017-04-01 18:45 | 50050.6307 | 39.996
Devonshire Building | 2017-04-01 19:00 | 50050.6357 | 20.016
Devonshire Building | 2017-04-01 19:15 | 50050.6457 | 39.996
Devonshire Building | 2017-04-01 19:30 | 50050.6557 | 39.996
Devonshire Building | 2017-04-01 19:45 | 50050.6607 | 20.016
Devonshire Building | 2017-04-01 20:00 | 50050.6707 | 39.996
Devonshire Building | 2017-04-01 20:15 | 50050.6757 | 20.016
Devonshire Building | 2017-04-01 20:30 | 50050.6807 | 20.016
Devonshire Building | 2017-04-01 20:45 | 50050.6907 | 39.996
Devonshire Building | 2017-04-01 21:00 | 50050.7207 | 119.988
Devonshire Building | 2017-04-01 21:15 | 50050.7257 | 20.016
Devonshire Building | 2017-04-01 21:30 | 50050.7307 | 20.016
Devonshire Building | 2017-04-01 21:45 | 50050.7357 | 20.016
Devonshire Building | 2017-04-01 22:00 | 50050.7407 | 20.016
Devonshire Building | 2017-04-01 22:15 | 50050.7457 | 20.016
Devonshire Building | 2017-04-01 22:30 | 50050.7507 | 20.016
Devonshire Building | 2017-04-01 22:45 | 50050.7557 | 20.016
Devonshire Building | 2017-04-01 23:00 | 50050.7607 | 20.016
Devonshire Building | 2017-04-01 23:15 | 50050.7657 | 20.016
Devonshire Building | 2017-04-01 23:30 | 50050.7707 | 20.016
Devonshire Building | 2017-04-01 23:45 | 50050.7757 | 20.016 | 20.016
Devonshire Building | 2017-04-02 | 50050.7852 | 39.996
Devonshire Building | 2017-04-02 00:15 | 50050.7902 | 20.016
Devonshire Building | 2017-04-02 00:30 | 50050.7952 | 20.016
Devonshire Building | 2017-04-02 00:45 | 50050.8002 | 20.016
Devonshire Building | 2017-04-02 01:00 | 50050.8052 | 20.016
Devonshire Building | 2017-04-02 01:15 | 50050.8102 | 20.016
Devonshire Building | 2017-04-02 01:30 | 50050.8152 | 20.016
Devonshire Building | 2017-04-02 01:45 | 50050.8202 | 20.016
Devonshire Building | 2017-04-02 02:00 | 50050.8252 | 20.016
Devonshire Building | 2017-04-02 02:15 | 50050.8302 | 20.016
Devonshire Building | 2017-04-02 02:30 | 50050.8352 | 20.016
Devonshire Building | 2017-04-02 02:45 | 50050.8402 | 20.016
Devonshire Building | 2017-04-02 03:00 | 50050.8452 | 20.016
Devonshire Building | 2017-04-02 03:15 | 50050.8502 | 20.016
Devonshire Building | 2017-04-02 03:30 | 50050.8552 | 20.016
Devonshire Building | 2017-04-02 03:45 | 50050.8602 | 20.016
Devonshire Building | 2017-04-02 04:00 | 50051.1002 | 960.012
Devonshire Building | 2017-04-02 04:15 | 50051.1252 | 100.008
Devonshire Building | 2017-04-02 04:30 | 50051.1302 | 20.016
Devonshire Building | 2017-04-02 04:45 | 50051.1352 | 20.016
Devonshire Building | 2017-04-02 05:00 | 50051.1402 | 20.016
Devonshire Building | 2017-04-02 05:15 | 50051.1452 | 20.016
Devonshire Building | 2017-04-02 05:30 | 50051.1502 | 20.016
Devonshire Building | 2017-04-02 05:45 | 50051.1552 | 20.016
Devonshire Building | 2017-04-02 06:00 | 50051.1603 | 20.016
Devonshire Building | 2017-04-02 06:15 | 50051.1653 | 20.016
Devonshire Building | 2017-04-02 06:30 | 50051.1703 | 20.016
Devonshire Building | 2017-04-02 06:45 | 50051.1753 | 20.016
Devonshire Building | 2017-04-02 07:00 | 50051.1803 | 20.016
Devonshire Building | 2017-04-02 07:15 | 50051.1853 | 20.016
Devonshire Building | 2017-04-02 07:30 | 50051.1903 | 20.016
Devonshire Building | 2017-04-02 07:45 | 50051.2053 | 60.012
Devonshire Building | 2017-04-02 08:00 | 50051.2303 | 100.008
Devonshire Building | 2017-04-02 08:15 | 50051.2503 | 79.992
Devonshire Building | 2017-04-02 08:30 | 50051.2753 | 100.008
Devonshire Building | 2017-04-02 08:45 | 50051.3003 | 100.008
Devonshire Building | 2017-04-02 09:00 | 50051.3203 | 79.992
Devonshire Building | 2017-04-02 09:15 | 50051.3453 | 100.008
Devonshire Building | 2017-04-02 09:30 | 50051.3703 | 100.008
Devonshire Building | 2017-04-02 09:45 | 50051.3903 | 79.992
Devonshire Building | 2017-04-02 10:00 | 50051.4153 | 100.008
Devonshire Building | 2017-04-02 10:15 | 50051.4403 | 100.008
Devonshire Building | 2017-04-02 10:30 | 50051.4503 | 39.996
Devonshire Building | 2017-04-02 10:45 | 50051.4553 | 20.016
Devonshire Building | 2017-04-02 11:00 | 50051.4653 | 39.996
Devonshire Building | 2017-04-02 11:15 | 50051.4703 | 20.016
Devonshire Building | 2017-04-02 11:30 | 50051.4753 | 20.016
Devonshire Building | 2017-04-02 11:45 | 50051.4853 | 39.996
Devonshire Building | 2017-04-02 12:00 | 50051.4903 | 20.016
Devonshire Building | 2017-04-02 12:15 | 50051.4953 | 20.016
Devonshire Building | 2017-04-02 12:30 | 50051.5053 | 39.996
Devonshire Building | 2017-04-02 12:45 | 50051.5103 | 20.016
Devonshire Building | 2017-04-02 13:00 | 50051.5153 | 20.016
Devonshire Building | 2017-04-02 13:15 | 50051.5203 | 20.016
Devonshire Building | 2017-04-02 13:30 | 50051.5303 | 39.996
Devonshire Building | 2017-04-02 13:45 | 50051.5353 | 20.016
Devonshire Building | 2017-04-02 14:00 | 50051.5403 | 20.016
Devonshire Building | 2017-04-02 14:15 | 50051.5503 | 39.996
Devonshire Building | 2017-04-02 14:30 | 50051.5553 | 20.016
Devonshire Building | 2017-04-02 14:45 | 50051.5603 | 20.016
Devonshire Building | 2017-04-02 15:00 | 50051.5653 | 20.016
Devonshire Building | 2017-04-02 15:15 | 50051.5703 | 20.016
Devonshire Building | 2017-04-02 15:30 | 50051.5753 | 20.016
Devonshire Building | 2017-04-02 15:45 | 50051.5853 | 39.996
Devonshire Building | 2017-04-02 16:00 | 50051.5903 | 20.016
Devonshire Building | 2017-04-02 16:15 | 50051.5953 | 20.016
Devonshire Building | 2017-04-02 16:30 | 50051.6004 | 20.016
Devonshire Building | 2017-04-02 16:45 | 50051.6054 | 20.016
Devonshire Building | 2017-04-02 17:00 | 50051.6104 | 20.016
Devonshire Building | 2017-04-02 17:15 | 50051.6154 | 20.016
Devonshire Building | 2017-04-02 17:30 | 50051.6204 | 20.016
Devonshire Building | 2017-04-02 17:45 | 50051.6254 | 20.016
Devonshire Building | 2017-04-02 18:00 | 50051.6304 | 20.016
Devonshire Building | 2017-04-02 18:15 | 50051.6354 | 20.016
Devonshire Building | 2017-04-02 18:30 | 50051.6404 | 20.016
Devonshire Building | 2017-04-02 18:45 | 50051.6454 | 20.016
Devonshire Building | 2017-04-02 19:00 | 50051.6504 | 20.016
Devonshire Building | 2017-04-02 19:15 | 50051.6554 | 20.016
Devonshire Building | 2017-04-02 19:30 | 50051.6604 | 20.016
Devonshire Building | 2017-04-02 19:45 | 50051.6654 | 20.016
Devonshire Building | 2017-04-02 20:00 | 50051.6704 | 20.016
Devonshire Building | 2017-04-02 20:15 | 50051.6754 | 20.016
Devonshire Building | 2017-04-02 20:30 | 50051.6804 | 20.016
Devonshire Building | 2017-04-02 20:45 | 50051.6904 | 39.996
Devonshire Building | 2017-04-02 21:00 | 50051.7154 | 100.008
Devonshire Building | 2017-04-02 21:15 | 50051.7204 | 20.016
Devonshire Building | 2017-04-02 21:30 | 50051.7254 | 20.016
Devonshire Building | 2017-04-02 21:45 | 50051.7304 | 20.016
Devonshire Building | 2017-04-02 22:00 | 50051.7354 | 20.016
Devonshire Building | 2017-04-02 22:15 | 50051.7404 | 20.016
Devonshire Building | 2017-04-02 22:30 | 50051.7454 | 20.016
Devonshire Building | 2017-04-02 22:45 | 50051.7454 | 0
Devonshire Building | 2017-04-02 23:00 | 50051.7504 | 20.016
Devonshire Building | 2017-04-02 23:15 | 50051.7554 | 20.016
Devonshire Building | 2017-04-02 23:30 | 50051.7605 | 20.016
Devonshire Building | 2017-04-02 23:45 | 50051.7655 | 20.016 | 0
Devonshire Building | 2017-04-03 | 50051.7695 | 20.016
Devonshire Building | 2017-04-03 00:15 | 50051.7745 | 20.016
Devonshire Building | 2017-04-03 00:30 | 50051.7795 | 20.016
Devonshire Building | 2017-04-03 00:45 | 50051.7845 | 20.016
Devonshire Building | 2017-04-03 01:00 | 50051.7845 | 0
Devonshire Building | 2017-04-03 01:15 | 50051.7895 | 20.016
Devonshire Building | 2017-04-03 01:30 | 50051.7945 | 20.016
Devonshire Building | 2017-04-03 01:45 | 50051.7996 | 20.016
Devonshire Building | 2017-04-03 02:00 | 50051.8046 | 20.016
Devonshire Building | 2017-04-03 02:15 | 50051.8096 | 20.016
Devonshire Building | 2017-04-03 02:30 | 50051.8146 | 20.016
Devonshire Building | 2017-04-03 02:45 | 50051.8146 | 0
Devonshire Building | 2017-04-03 03:00 | 50051.8196 | 20.016
Devonshire Building | 2017-04-03 03:15 | 50051.8246 | 20.016
Devonshire Building | 2017-04-03 03:30 | 50051.8296 | 20.016
Devonshire Building | 2017-04-03 03:45 | 50051.8346 | 20.016
Devonshire Building | 2017-04-03 04:00 | 50051.8396 | 20.016
Devonshire Building | 2017-04-03 04:15 | 50051.8446 | 20.016
Devonshire Building | 2017-04-03 04:30 | 50051.8446 | 0
Devonshire Building | 2017-04-03 04:45 | 50051.8496 | 20.016
Devonshire Building | 2017-04-03 05:00 | 50051.8546 | 20.016
Devonshire Building | 2017-04-03 05:15 | 50051.8596 | 20.016
Devonshire Building | 2017-04-03 05:30 | 50051.8646 | 20.016
Devonshire Building | 2017-04-03 05:45 | 50051.8696 | 20.016
Devonshire Building | 2017-04-03 06:00 | 50051.8746 | 20.016
Devonshire Building | 2017-04-03 06:15 | 50051.8796 | 20.016
Devonshire Building | 2017-04-03 06:30 | 50051.8846 | 20.016
Devonshire Building | 2017-04-03 06:45 | 50052.1546 | 1080
Devonshire Building | 2017-04-03 07:00 | 50052.1846 | 119.988
Devonshire Building | 2017-04-03 07:15 | 50052.2046 | 79.992
Devonshire Building | 2017-04-03 07:30 | 50052.2096 | 20.016
Devonshire Building | 2017-04-03 07:45 | 50052.2396 | 119.988
Devonshire Building | 2017-04-03 08:00 | 50052.2696 | 119.988
Devonshire Building | 2017-04-03 08:15 | 50052.3196 | 200.016
Devonshire Building | 2017-04-03 08:30 | 50052.3846 | 259.992
Devonshire Building | 2017-04-03 08:45 | 50052.4546 | 280.008
Devonshire Building | 2017-04-03 09:00 | 50052.8196 | 1460.016
Devonshire Building | 2017-04-03 09:15 | 50052.9046 | 339.984
Devonshire Building | 2017-04-03 09:30 | 50052.9846 | 320.004
Devonshire Building | 2017-04-03 09:45 | 50053.0596 | 299.988
Devonshire Building | 2017-04-03 10:00 | 50053.4296 | 1479.996
Devonshire Building | 2017-04-03 10:15 | 50053.4996 | 280.008
Devonshire Building | 2017-04-03 10:30 | 50053.5696 | 280.008
Devonshire Building | 2017-04-03 10:45 | 50053.6346 | 259.992
Devonshire Building | 2017-04-03 11:00 | 50053.6996 | 259.992
Devonshire Building | 2017-04-03 11:15 | 50054.0596 | 1440
Devonshire Building | 2017-04-03 11:30 | 50054.1296 | 280.008
Devonshire Building | 2017-04-03 11:45 | 50054.2096 | 320.004
Devonshire Building | 2017-04-03 12:00 | 50054.2846 | 299.988
Devonshire Building | 2017-04-03 12:15 | 50054.3496 | 259.992
Devonshire Building | 2017-04-03 12:30 | 50054.4096 | 240.012
Devonshire Building | 2017-04-03 12:45 | 50054.7596 | 1400.004
Devonshire Building | 2017-04-03 13:00 | 50054.8046 | 180
Devonshire Building | 2017-04-03 13:15 | 50054.8496 | 180
Devonshire Building | 2017-04-03 13:30 | 50054.8946 | 180
Devonshire Building | 2017-04-03 13:45 | 50054.9396 | 180
Devonshire Building | 2017-04-03 14:00 | 50054.9796 | 159.984
Devonshire Building | 2017-04-03 14:15 | 50055.2996 | 1280.016
Devonshire Building | 2017-04-03 14:30 | 50055.3246 | 100.008
Devonshire Building | 2017-04-03 14:45 | 50055.3596 | 140.004
Devonshire Building | 2017-04-03 15:00 | 50055.3896 | 119.988
Devonshire Building | 2017-04-03 15:15 | 50055.4146 | 100.008
Devonshire Building | 2017-04-03 15:30 | 50055.4396 | 100.008
Devonshire Building | 2017-04-03 15:45 | 50055.7696 | 1320.012
Devonshire Building | 2017-04-03 16:00 | 50055.8046 | 140.004
Devonshire Building | 2017-04-03 16:15 | 50055.8346 | 119.988
Devonshire Building | 2017-04-03 16:30 | 50055.8746 | 159.984
Devonshire Building | 2017-04-03 16:45 | 50055.9096 | 140.004
Devonshire Building | 2017-04-03 17:00 | 50055.9446 | 140.004
Devonshire Building | 2017-04-03 17:15 | 50055.9796 | 140.004
Devonshire Building | 2017-04-03 17:30 | 50056.0196 | 159.984
Devonshire Building | 2017-04-03 17:45 | 50056.0496 | 119.988
Devonshire Building | 2017-04-03 18:00 | 50056.0846 | 140.004
Devonshire Building | 2017-04-03 18:15 | 50056.1096 | 100.008
Devonshire Building | 2017-04-03 18:30 | 50056.1396 | 119.988
Devonshire Building | 2017-04-03 18:45 | 50056.1646 | 100.008
Devonshire Building | 2017-04-03 19:00 | 50056.1946 | 119.988
Devonshire Building | 2017-04-03 19:15 | 50056.2196 | 100.008
Devonshire Building | 2017-04-03 19:30 | 50056.2496 | 119.988
Devonshire Building | 2017-04-03 19:45 | 50056.2846 | 140.004
Devonshire Building | 2017-04-03 20:00 | 50056.3246 | 159.984
Devonshire Building | 2017-04-03 20:15 | 50056.3646 | 159.984
Devonshire Building | 2017-04-03 20:30 | 50056.3996 | 140.004
Devonshire Building | 2017-04-03 20:45 | 50056.4396 | 159.984
Devonshire Building | 2017-04-03 21:00 | 50056.4946 | 219.996
Devonshire Building | 2017-04-03 21:15 | 50056.5246 | 119.988
Devonshire Building | 2017-04-03 21:30 | 50056.5546 | 119.988
Devonshire Building | 2017-04-03 21:45 | 50056.5846 | 119.988
Devonshire Building | 2017-04-03 22:00 | 50056.6146 | 119.988
Devonshire Building | 2017-04-03 22:15 | 50056.6296 | 60.012
Devonshire Building | 2017-04-03 22:30 | 50056.6446 | 60.012
Devonshire Building | 2017-04-03 22:45 | 50056.6596 | 60.012
Devonshire Building | 2017-04-03 23:00 | 50056.6746 | 60.012
Devonshire Building | 2017-04-03 23:15 | 50056.6896 | 60.012
Devonshire Building | 2017-04-03 23:30 | 50056.7046 | 60.012
Devonshire Building | 2017-04-03 23:45 | 50056.7146 | 39.996 | 0
Devonshire Building | 2017-04-04 | 50056.7305 | 60.012
Devonshire Building | 2017-04-04 00:15 | 50056.7455 | 60.012
Devonshire Building | 2017-04-04 00:30 | 50056.7605 | 60.012
Devonshire Building | 2017-04-04 00:45 | 50056.7705 | 39.996
Devonshire Building | 2017-04-04 01:00 | 50056.7855 | 60.012
Devonshire Building | 2017-04-04 01:15 | 50056.8005 | 60.012
Devonshire Building | 2017-04-04 01:30 | 50056.8105 | 39.996
Devonshire Building | 2017-04-04 01:45 | 50056.8255 | 60.012
Devonshire Building | 2017-04-04 02:00 | 50056.8405 | 60.012
Devonshire Building | 2017-04-04 02:15 | 50056.8505 | 39.996
Devonshire Building | 2017-04-04 02:30 | 50057.1205 | 1080
Devonshire Building | 2017-04-04 02:45 | 50057.1305 | 39.996
Devonshire Building | 2017-04-04 03:00 | 50057.1355 | 20.016
Devonshire Building | 2017-04-04 03:15 | 50057.1455 | 39.996
Devonshire Building | 2017-04-04 03:30 | 50057.1505 | 20.016
Devonshire Building | 2017-04-04 03:45 | 50057.1605 | 39.996
Devonshire Building | 2017-04-04 04:00 | 50057.1655 | 20.016
Devonshire Building | 2017-04-04 04:15 | 50057.1705 | 20.016
Devonshire Building | 2017-04-04 04:30 | 50057.1805 | 39.996
Devonshire Building | 2017-04-04 04:45 | 50057.1855 | 20.016
Devonshire Building | 2017-04-04 05:00 | 50057.1955 | 39.996
Devonshire Building | 2017-04-04 05:15 | 50057.2005 | 20.016
Devonshire Building | 2017-04-04 05:30 | 50057.2105 | 39.996
Devonshire Building | 2017-04-04 05:45 | 50057.2205 | 39.996
Devonshire Building | 2017-04-04 06:00 | 50057.2305 | 39.996
Devonshire Building | 2017-04-04 06:15 | 50057.2505 | 79.992
Devonshire Building | 2017-04-04 06:30 | 50057.2605 | 39.996
Devonshire Building | 2017-04-04 06:45 | 50057.2755 | 60.012
Devonshire Building | 2017-04-04 07:00 | 50057.2855 | 39.996
Devonshire Building | 2017-04-04 07:15 | 50057.2955 | 39.996
Devonshire Building | 2017-04-04 07:30 | 50057.3105 | 60.012
Devonshire Building | 2017-04-04 07:45 | 50057.3305 | 79.992
Devonshire Building | 2017-04-04 08:00 | 50057.3655 | 140.004
Devonshire Building | 2017-04-04 08:15 | 50057.3955 | 119.988
Devonshire Building | 2017-04-04 08:30 | 50057.4255 | 119.988
Devonshire Building | 2017-04-04 08:45 | 50057.7255 | 1199.988
Devonshire Building | 2017-04-04 09:00 | 50057.7655 | 159.984
Devonshire Building | 2017-04-04 09:15 | 50057.8105 | 180
Devonshire Building | 2017-04-04 09:30 | 50057.8605 | 200.016
Devonshire Building | 2017-04-04 09:45 | 50058.2355 | 1500.012
Devonshire Building | 2017-04-04 10:00 | 50058.2805 | 180
Devonshire Building | 2017-04-04 10:15 | 50058.3255 | 180
Devonshire Building | 2017-04-04 10:30 | 50058.3705 | 180
Devonshire Building | 2017-04-04 10:45 | 50058.4205 | 200.016
Devonshire Building | 2017-04-04 11:00 | 50058.4655 | 180
Devonshire Building | 2017-04-04 11:15 | 50058.6755 | 839.988
Devonshire Building | 2017-04-04 11:30 | 50058.8355 | 640.008
Devonshire Building | 2017-04-04 11:45 | 50058.8705 | 140.004
Devonshire Building | 2017-04-04 12:00 | 50058.9005 | 119.988
Devonshire Building | 2017-04-04 12:15 | 50058.9405 | 159.984
Devonshire Building | 2017-04-04 12:30 | 50058.9705 | 119.988
Devonshire Building | 2017-04-04 12:45 | 50059.0055 | 140.004
Devonshire Building | 2017-04-04 13:00 | 50059.3205 | 1260
Devonshire Building | 2017-04-04 13:15 | 50059.3555 | 140.004
Devonshire Building | 2017-04-04 13:30 | 50059.3905 | 140.004
Devonshire Building | 2017-04-04 13:45 | 50059.4405 | 200.016
Devonshire Building | 2017-04-04 14:00 | 50059.4955 | 219.996
Devonshire Building | 2017-04-04 14:15 | 50059.5505 | 219.996
Devonshire Building | 2017-04-04 14:30 | 50059.6155 | 259.992
Devonshire Building | 2017-04-04 14:45 | 50059.9805 | 1460.016
Devonshire Building | 2017-04-04 15:00 | 50060.0455 | 259.992
Devonshire Building | 2017-04-04 15:15 | 50060.1205 | 299.988
Devonshire Building | 2017-04-04 15:30 | 50060.2405 | 479.988
Devonshire Building | 2017-04-04 15:45 | 50060.3655 | 500.004
Devonshire Building | 2017-04-04 16:00 | 50060.4755 | 439.992
Devonshire Building | 2017-04-04 16:15 | 50060.5555 | 320.004
Devonshire Building | 2017-04-04 16:30 | 50060.6155 | 240.012
Devonshire Building | 2017-04-04 16:45 | 50060.7455 | 519.984
Devonshire Building | 2017-04-04 17:00 | 50060.9555 | 839.988
Devonshire Building | 2017-04-04 17:15 | 50060.9755 | 79.992
Devonshire Building | 2017-04-04 17:30 | 50061.0005 | 100.008
Devonshire Building | 2017-04-04 17:45 | 50061.0205 | 79.992
Devonshire Building | 2017-04-04 18:00 | 50061.0455 | 100.008
Devonshire Building | 2017-04-04 18:15 | 50061.0655 | 79.992
Devonshire Building | 2017-04-04 18:30 | 50061.0955 | 119.988
Devonshire Building | 2017-04-04 18:45 | 50061.1155 | 79.992
Devonshire Building | 2017-04-04 19:00 | 50061.1355 | 79.992
Devonshire Building | 2017-04-04 19:15 | 50061.1555 | 79.992
Devonshire Building | 2017-04-04 19:30 | 50061.1755 | 79.992
Devonshire Building | 2017-04-04 19:45 | 50061.1905 | 60.012
Devonshire Building | 2017-04-04 20:00 | 50061.2105 | 79.992
Devonshire Building | 2017-04-04 20:15 | 50061.2255 | 60.012
Devonshire Building | 2017-04-04 20:30 | 50061.2405 | 60.012
Devonshire Building | 2017-04-04 20:45 | 50061.2555 | 60.012
Devonshire Building | 2017-04-04 21:00 | 50061.2705 | 60.012
Devonshire Building | 2017-04-04 21:15 | 50061.2805 | 39.996
Devonshire Building | 2017-04-04 21:30 | 50061.2905 | 39.996
Devonshire Building | 2017-04-04 21:45 | 50061.3005 | 39.996
Devonshire Building | 2017-04-04 22:00 | 50061.3105 | 39.996
Devonshire Building | 2017-04-04 22:15 | 50061.3255 | 60.012
Devonshire Building | 2017-04-04 22:30 | 50061.3355 | 39.996
Devonshire Building | 2017-04-04 22:45 | 50061.3455 | 39.996
Devonshire Building | 2017-04-04 23:00 | 50061.3555 | 39.996
Devonshire Building | 2017-04-04 23:15 | 50061.3655 | 39.996
Devonshire Building | 2017-04-04 23:30 | 50061.3755 | 39.996
Devonshire Building | 2017-04-04 23:45 | 50061.3855 | 39.996 | 20.016
Devonshire Building | 2017-04-05 | 50061.3945 | 39.996
Devonshire Building | 2017-04-05 00:15 | 50061.4045 | 39.996
Devonshire Building | 2017-04-05 00:30 | 50061.4145 | 39.996
Devonshire Building | 2017-04-05 00:45 | 50061.4195 | 20.016
Devonshire Building | 2017-04-05 01:00 | 50061.4295 | 39.996
Devonshire Building | 2017-04-05 01:15 | 50061.4395 | 39.996
Devonshire Building | 2017-04-05 01:30 | 50061.4495 | 39.996
Devonshire Building | 2017-04-05 01:45 | 50061.4595 | 39.996
Devonshire Building | 2017-04-05 02:00 | 50061.4645 | 20.016
Devonshire Building | 2017-04-05 02:15 | 50061.4745 | 39.996
Devonshire Building | 2017-04-05 02:30 | 50061.4845 | 39.996
Devonshire Building | 2017-04-05 02:45 | 50061.4945 | 39.996
Devonshire Building | 2017-04-05 03:00 | 50061.4995 | 20.016
Devonshire Building | 2017-04-05 03:15 | 50061.5095 | 39.996
Devonshire Building | 2017-04-05 03:30 | 50061.5195 | 39.996
Devonshire Building | 2017-04-05 03:45 | 50061.5245 | 20.016
Devonshire Building | 2017-04-05 04:00 | 50061.5345 | 39.996
Devonshire Building | 2017-04-05 04:15 | 50061.5445 | 39.996
Devonshire Building | 2017-04-05 04:30 | 50061.5495 | 20.016
Devonshire Building | 2017-04-05 04:45 | 50061.5595 | 39.996
Devonshire Building | 2017-04-05 05:00 | 50061.5645 | 20.016
Devonshire Building | 2017-04-05 05:15 | 50061.5745 | 39.996
Devonshire Building | 2017-04-05 05:30 | 50061.5845 | 39.996
Devonshire Building | 2017-04-05 05:45 | 50061.5945 | 39.996
Devonshire Building | 2017-04-05 06:00 | 50061.5995 | 20.016
Devonshire Building | 2017-04-05 06:15 | 50061.6095 | 39.996
Devonshire Building | 2017-04-05 06:30 | 50061.6245 | 60.012
Devonshire Building | 2017-04-05 06:45 | 50061.6345 | 39.996
Devonshire Building | 2017-04-05 07:00 | 50061.6395 | 20.016
Devonshire Building | 2017-04-05 07:15 | 50061.6495 | 39.996
Devonshire Building | 2017-04-05 07:30 | 50061.6595 | 39.996
Devonshire Building | 2017-04-05 07:45 | 50061.6695 | 39.996
Devonshire Building | 2017-04-05 08:00 | 50061.9245 | 1019.988
Devonshire Building | 2017-04-05 08:15 | 50061.9895 | 259.992
Devonshire Building | 2017-04-05 08:30 | 50061.9995 | 39.996
Devonshire Building | 2017-04-05 08:45 | 50062.0095 | 39.996
Devonshire Building | 2017-04-05 09:00 | 50062.0245 | 60.012
Devonshire Building | 2017-04-05 09:15 | 50062.0345 | 39.996
Devonshire Building | 2017-04-05 09:30 | 50062.0595 | 100.008
Devonshire Building | 2017-04-05 09:45 | 50062.3695 | 1239.984
Devonshire Building | 2017-04-05 10:00 | 50062.4145 | 180
Devonshire Building | 2017-04-05 10:15 | 50062.4745 | 240.012
Devonshire Building | 2017-04-05 10:30 | 50062.5395 | 259.992
Devonshire Building | 2017-04-05 10:45 | 50062.6045 | 259.992
Devonshire Building | 2017-04-05 11:00 | 50062.6695 | 259.992
Devonshire Building | 2017-04-05 11:15 | 50062.7295 | 240.012
Devonshire Building | 2017-04-05 11:30 | 50063.0895 | 1440
Devonshire Building | 2017-04-05 11:45 | 50063.1445 | 219.996
Devonshire Building | 2017-04-05 12:00 | 50063.1995 | 219.996
Devonshire Building | 2017-04-05 12:15 | 50063.2545 | 219.996
Devonshire Building | 2017-04-05 12:30 | 50063.3145 | 240.012
Devonshire Building | 2017-04-05 12:45 | 50063.3595 | 180
Devonshire Building | 2017-04-05 13:00 | 50063.3945 | 140.004
Devonshire Building | 2017-04-05 13:15 | 50063.4345 | 159.984
Devonshire Building | 2017-04-05 13:30 | 50063.7545 | 1280.016
Devonshire Building | 2017-04-05 13:45 | 50063.7845 | 119.988
Devonshire Building | 2017-04-05 14:00 | 50063.8195 | 140.004
Devonshire Building | 2017-04-05 14:15 | 50063.8495 | 119.988
Devonshire Building | 2017-04-05 14:30 | 50063.8845 | 140.004
Devonshire Building | 2017-04-05 14:45 | 50063.9195 | 140.004
Devonshire Building | 2017-04-05 15:00 | 50063.9545 | 140.004
Devonshire Building | 2017-04-05 15:15 | 50063.9895 | 140.004
Devonshire Building | 2017-04-05 15:30 | 50064.0195 | 119.988
Devonshire Building | 2017-04-05 15:45 | 50064.3295 | 1239.984
Devonshire Building | 2017-04-05 16:00 | 50064.3545 | 100.008
Devonshire Building | 2017-04-05 16:15 | 50064.3795 | 100.008
Devonshire Building | 2017-04-05 16:30 | 50064.4045 | 100.008
Devonshire Building | 2017-04-05 16:45 | 50064.4345 | 119.988
Devonshire Building | 2017-04-05 17:00 | 50064.4595 | 100.008
Devonshire Building | 2017-04-05 17:15 | 50064.4845 | 100.008
Devonshire Building | 2017-04-05 17:30 | 50064.5095 | 100.008
Devonshire Building | 2017-04-05 17:45 | 50064.5345 | 100.008
Devonshire Building | 2017-04-05 18:00 | 50064.5595 | 100.008
Devonshire Building | 2017-04-05 18:15 | 50064.5845 | 100.008
Devonshire Building | 2017-04-05 18:30 | 50064.6045 | 79.992
Devonshire Building | 2017-04-05 18:45 | 50064.6295 | 100.008
Devonshire Building | 2017-04-05 19:00 | 50064.6495 | 79.992
Devonshire Building | 2017-04-05 19:15 | 50064.6695 | 79.992
Devonshire Building | 2017-04-05 19:30 | 50064.6845 | 60.012
Devonshire Building | 2017-04-05 19:45 | 50064.7045 | 79.992
Devonshire Building | 2017-04-05 20:00 | 50064.7245 | 79.992
Devonshire Building | 2017-04-05 20:15 | 50064.7395 | 60.012
Devonshire Building | 2017-04-05 20:30 | 50064.7595 | 79.992
Devonshire Building | 2017-04-05 20:45 | 50064.7745 | 60.012
Devonshire Building | 2017-04-05 21:00 | 50065.0495 | 1100.016
Devonshire Building | 2017-04-05 21:15 | 50065.0595 | 39.996
Devonshire Building | 2017-04-05 21:30 | 50065.0646 | 20.016
Devonshire Building | 2017-04-05 21:45 | 50065.0745 | 39.996
Devonshire Building | 2017-04-05 22:00 | 50065.0845 | 39.996
Devonshire Building | 2017-04-05 22:15 | 50065.0896 | 20.016
Devonshire Building | 2017-04-05 22:30 | 50065.0996 | 39.996
Devonshire Building | 2017-04-05 22:45 | 50065.1096 | 39.996
Devonshire Building | 2017-04-05 23:00 | 50065.1146 | 20.016
Devonshire Building | 2017-04-05 23:15 | 50065.1246 | 39.996
Devonshire Building | 2017-04-05 23:30 | 50065.1346 | 39.996
Devonshire Building | 2017-04-05 23:45 | 50065.1446 | 39.996 | 20.016
Devonshire Building | 2017-04-06 | 50065.1562 | 39.996
Devonshire Building | 2017-04-06 00:15 | 50065.1662 | 39.996
Devonshire Building | 2017-04-06 00:30 | 50065.1762 | 39.996
Devonshire Building | 2017-04-06 00:45 | 50065.1862 | 39.996
Devonshire Building | 2017-04-06 01:00 | 50065.1962 | 39.996
Devonshire Building | 2017-04-06 01:15 | 50065.2062 | 39.996
Devonshire Building | 2017-04-06 01:30 | 50065.2162 | 39.996
Devonshire Building | 2017-04-06 01:45 | 50065.2212 | 20.016
Devonshire Building | 2017-04-06 02:00 | 50065.2312 | 39.996
Devonshire Building | 2017-04-06 02:15 | 50065.2412 | 39.996
Devonshire Building | 2017-04-06 02:30 | 50065.2512 | 39.996
Devonshire Building | 2017-04-06 02:45 | 50065.2562 | 20.016
Devonshire Building | 2017-04-06 03:00 | 50065.2662 | 39.996
Devonshire Building | 2017-04-06 03:15 | 50065.2713 | 20.016
Devonshire Building | 2017-04-06 03:30 | 50065.2813 | 39.996
Devonshire Building | 2017-04-06 03:45 | 50065.2863 | 20.016
Devonshire Building | 2017-04-06 04:00 | 50065.2963 | 39.996
Devonshire Building | 2017-04-06 04:15 | 50065.3013 | 20.016
Devonshire Building | 2017-04-06 04:30 | 50065.3113 | 39.996
Devonshire Building | 2017-04-06 04:45 | 50065.3163 | 20.016
Devonshire Building | 2017-04-06 05:00 | 50065.3263 | 39.996
Devonshire Building | 2017-04-06 05:15 | 50065.3313 | 20.016
Devonshire Building | 2017-04-06 05:30 | 50065.3413 | 39.996
Devonshire Building | 2017-04-06 05:45 | 50065.3513 | 39.996
Devonshire Building | 2017-04-06 06:00 | 50065.3563 | 20.016
Devonshire Building | 2017-04-06 06:15 | 50065.3613 | 20.016
Devonshire Building | 2017-04-06 06:30 | 50065.3713 | 39.996
Devonshire Building | 2017-04-06 06:45 | 50065.3763 | 20.016
Devonshire Building | 2017-04-06 07:00 | 50065.3863 | 39.996
Devonshire Building | 2017-04-06 07:15 | 50065.4063 | 79.992
Devonshire Building | 2017-04-06 07:30 | 50065.4163 | 39.996
Devonshire Building | 2017-04-06 07:45 | 50065.4363 | 79.992
Devonshire Building | 2017-04-06 08:00 | 50065.4663 | 119.988
Devonshire Building | 2017-04-06 08:15 | 50065.7863 | 1280.016
Devonshire Building | 2017-04-06 08:30 | 50065.8163 | 119.988
Devonshire Building | 2017-04-06 08:45 | 50065.8463 | 119.988
Devonshire Building | 2017-04-06 09:00 | 50065.8713 | 100.008
Devonshire Building | 2017-04-06 09:15 | 50065.9063 | 140.004
Devonshire Building | 2017-04-06 09:30 | 50065.9413 | 140.004
Devonshire Building | 2017-04-06 09:45 | 50066.0463 | 420.012
Devonshire Building | 2017-04-06 10:00 | 50066.3213 | 1100.016
Devonshire Building | 2017-04-06 10:15 | 50066.3963 | 299.988
Devonshire Building | 2017-04-06 10:30 | 50066.4613 | 259.992
Devonshire Building | 2017-04-06 10:45 | 50066.5213 | 240.012
Devonshire Building | 2017-04-06 11:00 | 50066.5763 | 219.996
Devonshire Building | 2017-04-06 11:15 | 50066.9263 | 1400.004
Devonshire Building | 2017-04-06 11:30 | 50066.9613 | 140.004
Devonshire Building | 2017-04-06 11:45 | 50067.0013 | 159.984
Devonshire Building | 2017-04-06 12:00 | 50067.0463 | 180
Devonshire Building | 2017-04-06 12:15 | 50067.0863 | 159.984
Devonshire Building | 2017-04-06 12:30 | 50067.1263 | 159.984
Devonshire Building | 2017-04-06 12:45 | 50067.4563 | 1320.012
Devonshire Building | 2017-04-06 13:00 | 50067.4913 | 140.004
Devonshire Building | 2017-04-06 13:15 | 50067.5213 | 119.988
Devonshire Building | 2017-04-06 13:30 | 50067.5563 | 140.004
Devonshire Building | 2017-04-06 13:45 | 50067.5863 | 119.988
Devonshire Building | 2017-04-06 14:00 | 50067.7063 | 479.988
Devonshire Building | 2017-04-06 14:15 | 50067.9513 | 979.992
Devonshire Building | 2017-04-06 14:30 | 50067.9912 | 159.984
Devonshire Building | 2017-04-06 14:45 | 50068.0263 | 140.004
Devonshire Building | 2017-04-06 15:00 | 50068.0613 | 140.004
Devonshire Building | 2017-04-06 15:15 | 50068.0963 | 140.004
Devonshire Building | 2017-04-06 15:30 | 50068.1263 | 119.988
Devonshire Building | 2017-04-06 15:45 | 50068.3313 | 820.008
Devonshire Building | 2017-04-06 16:00 | 50068.5213 | 759.996
Devonshire Building | 2017-04-06 16:15 | 50068.5813 | 240.012
Devonshire Building | 2017-04-06 16:30 | 50068.6413 | 240.012
Devonshire Building | 2017-04-06 16:45 | 50068.7063 | 259.992
Devonshire Building | 2017-04-06 17:00 | 50068.7663 | 240.012
Devonshire Building | 2017-04-06 17:15 | 50068.8263 | 240.012
Devonshire Building | 2017-04-06 17:30 | 50068.8763 | 200.016
Devonshire Building | 2017-04-06 17:45 | 50068.9263 | 200.016
Devonshire Building | 2017-04-06 18:00 | 50068.9663 | 159.984
Devonshire Building | 2017-04-06 18:15 | 50069.0063 | 159.984
Devonshire Building | 2017-04-06 18:30 | 50069.0363 | 119.988
Devonshire Building | 2017-04-06 18:45 | 50069.0663 | 119.988
Devonshire Building | 2017-04-06 19:00 | 50069.0913 | 100.008
Devonshire Building | 2017-04-06 19:15 | 50069.1163 | 100.008
Devonshire Building | 2017-04-06 19:30 | 50069.1363 | 79.992
Devonshire Building | 2017-04-06 19:45 | 50069.1613 | 100.008
Devonshire Building | 2017-04-06 20:00 | 50069.1813 | 79.992
Devonshire Building | 2017-04-06 20:15 | 50069.1963 | 60.012
Devonshire Building | 2017-04-06 20:30 | 50069.2113 | 60.012
Devonshire Building | 2017-04-06 20:45 | 50069.2263 | 60.012
Devonshire Building | 2017-04-06 21:00 | 50069.2563 | 119.988
Devonshire Building | 2017-04-06 21:15 | 50069.2663 | 39.996
Devonshire Building | 2017-04-06 21:30 | 50069.2713 | 20.016
Devonshire Building | 2017-04-06 21:45 | 50069.2813 | 39.996
Devonshire Building | 2017-04-06 22:00 | 50069.2863 | 20.016
Devonshire Building | 2017-04-06 22:15 | 50069.2913 | 20.016
Devonshire Building | 2017-04-06 22:30 | 50069.2963 | 20.016
Devonshire Building | 2017-04-06 22:45 | 50069.3063 | 39.996
Devonshire Building | 2017-04-06 23:00 | 50069.3113 | 20.016
Devonshire Building | 2017-04-06 23:15 | 50069.3163 | 20.016
Devonshire Building | 2017-04-06 23:30 | 50069.3213 | 20.016
Devonshire Building | 2017-04-06 23:45 | 50069.3313 | 39.996 | 20.016
Devonshire Building | 2017-04-07 | 50069.3359 | 20.016
Devonshire Building | 2017-04-07 00:15 | 50069.3409 | 20.016
Devonshire Building | 2017-04-07 00:30 | 50069.3459 | 20.016
Devonshire Building | 2017-04-07 00:45 | 50069.351 | 20.016
Devonshire Building | 2017-04-07 01:00 | 50069.361 | 39.996
Devonshire Building | 2017-04-07 01:15 | 50069.366 | 20.016
Devonshire Building | 2017-04-07 01:30 | 50069.371 | 20.016
Devonshire Building | 2017-04-07 01:45 | 50069.376 | 20.016
Devonshire Building | 2017-04-07 02:00 | 50069.381 | 20.016
Devonshire Building | 2017-04-07 02:15 | 50069.386 | 20.016
Devonshire Building | 2017-04-07 02:30 | 50069.391 | 20.016
Devonshire Building | 2017-04-07 02:45 | 50069.396 | 20.016
Devonshire Building | 2017-04-07 03:00 | 50069.401 | 20.016
Devonshire Building | 2017-04-07 03:15 | 50069.406 | 20.016
Devonshire Building | 2017-04-07 03:30 | 50069.411 | 20.016
Devonshire Building | 2017-04-07 03:45 | 50069.416 | 20.016
Devonshire Building | 2017-04-07 04:00 | 50069.421 | 20.016
Devonshire Building | 2017-04-07 04:15 | 50069.426 | 20.016
Devonshire Building | 2017-04-07 04:30 | 50069.696 | 1080
Devonshire Building | 2017-04-07 04:45 | 50069.701 | 20.016
Devonshire Building | 2017-04-07 05:00 | 50069.706 | 20.016
Devonshire Building | 2017-04-07 05:15 | 50069.711 | 20.016
Devonshire Building | 2017-04-07 05:30 | 50069.716 | 20.016
Devonshire Building | 2017-04-07 05:45 | 50069.721 | 20.016
Devonshire Building | 2017-04-07 06:00 | 50069.726 | 20.016
Devonshire Building | 2017-04-07 06:15 | 50069.736 | 39.996
Devonshire Building | 2017-04-07 06:30 | 50069.741 | 20.016
Devonshire Building | 2017-04-07 06:45 | 50069.746 | 20.016
Devonshire Building | 2017-04-07 07:00 | 50069.751 | 20.016
Devonshire Building | 2017-04-07 07:15 | 50069.766 | 60.012
Devonshire Building | 2017-04-07 07:30 | 50069.786 | 79.992
Devonshire Building | 2017-04-07 07:45 | 50069.821 | 140.004
Devonshire Building | 2017-04-07 08:00 | 50069.891 | 280.008
Devonshire Building | 2017-04-07 08:15 | 50069.971 | 320.004
Devonshire Building | 2017-04-07 08:30 | 50070.046 | 299.988
Devonshire Building | 2017-04-07 08:45 | 50070.121 | 299.988
Devonshire Building | 2017-04-07 09:00 | 50070.536 | 1659.996
Devonshire Building | 2017-04-07 09:15 | 50070.631 | 380.016
Devonshire Building | 2017-04-07 09:30 | 50070.706 | 299.988
Devonshire Building | 2017-04-07 09:45 | 50070.791 | 339.984
Devonshire Building | 2017-04-07 10:00 | 50070.891 | 399.996
Devonshire Building | 2017-04-07 10:15 | 50070.976 | 339.984
Devonshire Building | 2017-04-07 10:30 | 50071.126 | 600.012
Devonshire Building | 2017-04-07 10:45 | 50071.671 | 2180.016
Devonshire Building | 2017-04-07 11:00 | 50071.726 | 219.996
Devonshire Building | 2017-04-07 11:15 | 50071.781 | 219.996
Devonshire Building | 2017-04-07 11:30 | 50071.831 | 200.016
Devonshire Building | 2017-04-07 11:45 | 50071.876 | 180
Devonshire Building | 2017-04-07 12:00 | 50072.391 | 2059.992
Devonshire Building | 2017-04-07 12:15 | 50072.476 | 339.984
Devonshire Building | 2017-04-07 12:30 | 50072.501 | 100.008
Devonshire Building | 2017-04-07 12:45 | 50072.521 | 79.992
Devonshire Building | 2017-04-07 13:00 | 50072.546 | 100.008
Devonshire Building | 2017-04-07 13:15 | 50072.576 | 119.988
Devonshire Building | 2017-04-07 13:30 | 50072.601 | 100.008
Devonshire Building | 2017-04-07 13:45 | 50072.626 | 100.008
Devonshire Building | 2017-04-07 14:00 | 50072.916 | 1159.992
Devonshire Building | 2017-04-07 14:15 | 50073.226 | 1239.984
Devonshire Building | 2017-04-07 14:30 | 50073.256 | 119.988
Devonshire Building | 2017-04-07 14:45 | 50073.281 | 100.008
Devonshire Building | 2017-04-07 15:00 | 50073.311 | 119.988
Devonshire Building | 2017-04-07 15:15 | 50073.336 | 100.008
Devonshire Building | 2017-04-07 15:30 | 50073.366 | 119.988
Devonshire Building | 2017-04-07 15:45 | 50073.391 | 100.008
Devonshire Building | 2017-04-07 16:00 | 50073.931 | 2160
Devonshire Building | 2017-04-07 16:15 | 50073.981 | 200.016
Devonshire Building | 2017-04-07 16:30 | 50074.011 | 119.988
Devonshire Building | 2017-04-07 16:45 | 50074.036 | 100.008
Devonshire Building | 2017-04-07 17:00 | 50074.066 | 119.988
Devonshire Building | 2017-04-07 17:15 | 50074.096 | 119.988
Devonshire Building | 2017-04-07 17:30 | 50074.126 | 119.988
Devonshire Building | 2017-04-07 17:45 | 50074.151 | 100.008
Devonshire Building | 2017-04-07 18:00 | 50074.176 | 100.008
Devonshire Building | 2017-04-07 18:15 | 50074.206 | 119.988
Devonshire Building | 2017-04-07 18:30 | 50074.231 | 100.008
Devonshire Building | 2017-04-07 18:45 | 50074.256 | 100.008
Devonshire Building | 2017-04-07 19:00 | 50074.276 | 79.992
Devonshire Building | 2017-04-07 19:15 | 50074.301 | 100.008
Devonshire Building | 2017-04-07 19:30 | 50074.321 | 79.992
Devonshire Building | 2017-04-07 19:45 | 50074.341 | 79.992
Devonshire Building | 2017-04-07 20:00 | 50074.361 | 79.992
Devonshire Building | 2017-04-07 20:15 | 50074.381 | 79.992
Devonshire Building | 2017-04-07 20:30 | 50074.401 | 79.992
Devonshire Building | 2017-04-07 20:45 | 50074.421 | 79.992
Devonshire Building | 2017-04-07 21:00 | 50074.461 | 159.984
Devonshire Building | 2017-04-07 21:15 | 50074.471 | 39.996
Devonshire Building | 2017-04-07 21:30 | 50074.486 | 60.012
Devonshire Building | 2017-04-07 21:45 | 50074.501 | 60.012
Devonshire Building | 2017-04-07 22:00 | 50074.516 | 60.012
Devonshire Building | 2017-04-07 22:15 | 50074.531 | 60.012
Devonshire Building | 2017-04-07 22:30 | 50074.541 | 39.996
Devonshire Building | 2017-04-07 22:45 | 50074.556 | 60.012
Devonshire Building | 2017-04-07 23:00 | 50074.566 | 39.996
Devonshire Building | 2017-04-07 23:15 | 50074.581 | 60.012
Devonshire Building | 2017-04-07 23:30 | 50074.591 | 39.996
Devonshire Building | 2017-04-07 23:45 | 50074.606 | 60.012 | 20.016
Devonshire Building | 2017-04-08 | 50074.6133 | 39.996
Devonshire Building | 2017-04-08 00:15 | 50074.6233 | 39.996
Devonshire Building | 2017-04-08 00:30 | 50074.6383 | 60.012
Devonshire Building | 2017-04-08 00:45 | 50074.6483 | 39.996
Devonshire Building | 2017-04-08 01:00 | 50074.6583 | 39.996
Devonshire Building | 2017-04-08 01:15 | 50074.6683 | 39.996
Devonshire Building | 2017-04-08 01:30 | 50074.6783 | 39.996
Devonshire Building | 2017-04-08 01:45 | 50074.6883 | 39.996
Devonshire Building | 2017-04-08 02:00 | 50074.6983 | 39.996
Devonshire Building | 2017-04-08 02:15 | 50074.7083 | 39.996
Devonshire Building | 2017-04-08 02:30 | 50074.7183 | 39.996
Devonshire Building | 2017-04-08 02:45 | 50074.7283 | 39.996
Devonshire Building | 2017-04-08 03:00 | 50074.7383 | 39.996
Devonshire Building | 2017-04-08 03:15 | 50074.7483 | 39.996
Devonshire Building | 2017-04-08 03:30 | 50074.7533 | 20.016
Devonshire Building | 2017-04-08 03:45 | 50074.7633 | 39.996
Devonshire Building | 2017-04-08 04:00 | 50074.7733 | 39.996
Devonshire Building | 2017-04-08 04:15 | 50074.7783 | 20.016
Devonshire Building | 2017-04-08 04:30 | 50074.7883 | 39.996
Devonshire Building | 2017-04-08 04:45 | 50074.7983 | 39.996
Devonshire Building | 2017-04-08 05:00 | 50074.8033 | 20.016
Devonshire Building | 2017-04-08 05:15 | 50074.8133 | 39.996
Devonshire Building | 2017-04-08 05:30 | 50074.8233 | 39.996
Devonshire Building | 2017-04-08 05:45 | 50074.8283 | 20.016
Devonshire Building | 2017-04-08 06:00 | 50074.8383 | 39.996
Devonshire Building | 2017-04-08 06:15 | 50074.8433 | 20.016
Devonshire Building | 2017-04-08 06:30 | 50074.8483 | 20.016
Devonshire Building | 2017-04-08 06:45 | 50075.3783 | 2120.004
Devonshire Building | 2017-04-08 07:00 | 50075.3833 | 20.016
Devonshire Building | 2017-04-08 07:15 | 50075.3833 | 0
Devonshire Building | 2017-04-08 07:30 | 50075.3883 | 20.016
Devonshire Building | 2017-04-08 07:45 | 50075.4083 | 79.992
Devonshire Building | 2017-04-08 08:00 | 50075.4283 | 79.992
Devonshire Building | 2017-04-08 08:15 | 50075.4583 | 119.988
Devonshire Building | 2017-04-08 08:30 | 50075.4883 | 119.988
Devonshire Building | 2017-04-08 08:45 | 50075.5083 | 79.992
Devonshire Building | 2017-04-08 09:00 | 50075.5233 | 60.012
Devonshire Building | 2017-04-08 09:15 | 50075.5433 | 79.992
Devonshire Building | 2017-04-08 09:30 | 50075.5633 | 79.992
Devonshire Building | 2017-04-08 09:45 | 50075.5833 | 79.992
Devonshire Building | 2017-04-08 10:00 | 50075.6033 | 79.992
Devonshire Building | 2017-04-08 10:15 | 50075.6233 | 79.992
Devonshire Building | 2017-04-08 10:30 | 50075.6433 | 79.992
Devonshire Building | 2017-04-08 10:45 | 50075.6483 | 20.016
Devonshire Building | 2017-04-08 11:00 | 50075.6533 | 20.016
Devonshire Building | 2017-04-08 11:15 | 50075.6583 | 20.016
Devonshire Building | 2017-04-08 11:30 | 50075.6633 | 20.016
Devonshire Building | 2017-04-08 11:45 | 50075.6683 | 20.016
Devonshire Building | 2017-04-08 12:00 | 50075.6733 | 20.016
Devonshire Building | 2017-04-08 12:15 | 50075.6783 | 20.016
Devonshire Building | 2017-04-08 12:30 | 50075.6833 | 20.016
Devonshire Building | 2017-04-08 12:45 | 50075.6883 | 20.016
Devonshire Building | 2017-04-08 13:00 | 50075.6933 | 20.016
Devonshire Building | 2017-04-08 13:15 | 50075.6983 | 20.016
Devonshire Building | 2017-04-08 13:30 | 50075.7033 | 20.016
Devonshire Building | 2017-04-08 13:45 | 50075.7083 | 20.016
Devonshire Building | 2017-04-08 14:00 | 50075.7133 | 20.016
Devonshire Building | 2017-04-08 14:15 | 50075.7183 | 20.016
Devonshire Building | 2017-04-08 14:30 | 50075.7183 | 0
Devonshire Building | 2017-04-08 14:45 | 50075.7233 | 20.016
Devonshire Building | 2017-04-08 15:00 | 50075.7283 | 20.016
Devonshire Building | 2017-04-08 15:15 | 50075.7333 | 20.016
Devonshire Building | 2017-04-08 15:30 | 50075.7384 | 20.016
Devonshire Building | 2017-04-08 15:45 | 50075.7384 | 0
Devonshire Building | 2017-04-08 16:00 | 50075.7434 | 20.016
Devonshire Building | 2017-04-08 16:15 | 50075.7484 | 20.016
Devonshire Building | 2017-04-08 16:30 | 50075.7534 | 20.016
Devonshire Building | 2017-04-08 16:45 | 50075.7584 | 20.016
Devonshire Building | 2017-04-08 17:00 | 50075.7584 | 0
Devonshire Building | 2017-04-08 17:15 | 50075.7634 | 20.016
Devonshire Building | 2017-04-08 17:30 | 50075.7684 | 20.016
Devonshire Building | 2017-04-08 17:45 | 50075.7734 | 20.016
Devonshire Building | 2017-04-08 18:00 | 50075.7734 | 0
Devonshire Building | 2017-04-08 18:15 | 50075.7784 | 20.016
Devonshire Building | 2017-04-08 18:30 | 50075.7834 | 20.016
Devonshire Building | 2017-04-08 18:45 | 50075.7884 | 20.016
Devonshire Building | 2017-04-08 19:00 | 50075.7884 | 0
Devonshire Building | 2017-04-08 19:15 | 50075.7934 | 20.016
Devonshire Building | 2017-04-08 19:30 | 50075.7984 | 20.016
Devonshire Building | 2017-04-08 19:45 | 50075.8034 | 20.016
Devonshire Building | 2017-04-08 20:00 | 50075.8034 | 0
Devonshire Building | 2017-04-08 20:15 | 50075.8084 | 20.016
Devonshire Building | 2017-04-08 20:30 | 50075.8134 | 20.016
Devonshire Building | 2017-04-08 20:45 | 50075.8184 | 20.016
Devonshire Building | 2017-04-08 21:00 | 50075.8434 | 100.008
Devonshire Building | 2017-04-08 21:15 | 50075.8484 | 20.016
Devonshire Building | 2017-04-08 21:30 | 50075.8534 | 20.016
Devonshire Building | 2017-04-08 21:45 | 50075.8584 | 20.016
Devonshire Building | 2017-04-08 22:00 | 50075.8634 | 20.016
Devonshire Building | 2017-04-08 22:15 | 50075.8684 | 20.016
Devonshire Building | 2017-04-08 22:30 | 50075.8734 | 20.016
Devonshire Building | 2017-04-08 22:45 | 50075.8784 | 20.016
Devonshire Building | 2017-04-08 23:00 | 50075.8835 | 20.016
Devonshire Building | 2017-04-08 23:15 | 50075.8885 | 20.016
Devonshire Building | 2017-04-08 23:30 | 50075.8935 | 20.016
Devonshire Building | 2017-04-08 23:45 | 50075.8985 | 20.016 | 0
Devonshire Building | 2017-04-09 | 50075.9062 | 20.016
Devonshire Building | 2017-04-09 00:15 | 50075.9113 | 20.016
Devonshire Building | 2017-04-09 00:30 | 50075.9163 | 20.016
Devonshire Building | 2017-04-09 00:45 | 50075.9213 | 20.016
Devonshire Building | 2017-04-09 01:00 | 50075.9263 | 20.016
Devonshire Building | 2017-04-09 01:15 | 50075.9313 | 20.016
Devonshire Building | 2017-04-09 01:30 | 50075.9363 | 20.016
Devonshire Building | 2017-04-09 01:45 | 50075.9413 | 20.016
Devonshire Building | 2017-04-09 02:00 | 50075.9463 | 20.016
Devonshire Building | 2017-04-09 02:15 | 50075.9513 | 20.016
Devonshire Building | 2017-04-09 02:30 | 50075.9563 | 20.016
Devonshire Building | 2017-04-09 02:45 | 50075.9613 | 20.016
Devonshire Building | 2017-04-09 03:00 | 50075.9663 | 20.016
Devonshire Building | 2017-04-09 03:15 | 50075.9713 | 20.016
Devonshire Building | 2017-04-09 03:30 | 50075.9763 | 20.016
Devonshire Building | 2017-04-09 03:45 | 50075.9763 | 0
Devonshire Building | 2017-04-09 04:00 | 50075.9813 | 20.016
Devonshire Building | 2017-04-09 04:15 | 50075.9863 | 20.016
Devonshire Building | 2017-04-09 04:30 | 50075.9913 | 20.016
Devonshire Building | 2017-04-09 04:45 | 50075.9963 | 20.016
Devonshire Building | 2017-04-09 05:00 | 50076.0013 | 20.016
Devonshire Building | 2017-04-09 05:15 | 50076.3363 | 1339.992
Devonshire Building | 2017-04-09 05:30 | 50076.5213 | 740.016
Devonshire Building | 2017-04-09 05:45 | 50076.5263 | 20.016
Devonshire Building | 2017-04-09 06:00 | 50076.5313 | 20.016
Devonshire Building | 2017-04-09 06:15 | 50076.5363 | 20.016
Devonshire Building | 2017-04-09 06:30 | 50076.5413 | 20.016
Devonshire Building | 2017-04-09 06:45 | 50076.5413 | 0
Devonshire Building | 2017-04-09 07:00 | 50076.5463 | 20.016
Devonshire Building | 2017-04-09 07:15 | 50076.5514 | 20.016
Devonshire Building | 2017-04-09 07:30 | 50076.5564 | 20.016
Devonshire Building | 2017-04-09 07:45 | 50076.5714 | 60.012
Devonshire Building | 2017-04-09 08:00 | 50076.5914 | 79.992
Devonshire Building | 2017-04-09 08:15 | 50076.6114 | 79.992
Devonshire Building | 2017-04-09 08:30 | 50076.6364 | 100.008
Devonshire Building | 2017-04-09 08:45 | 50076.6564 | 79.992
Devonshire Building | 2017-04-09 09:00 | 50076.6764 | 79.992
Devonshire Building | 2017-04-09 09:15 | 50076.6964 | 79.992
Devonshire Building | 2017-04-09 09:30 | 50076.7163 | 79.992
Devonshire Building | 2017-04-09 09:45 | 50076.7414 | 100.008
Devonshire Building | 2017-04-09 10:00 | 50076.7613 | 79.992
Devonshire Building | 2017-04-09 10:15 | 50076.7813 | 79.992
Devonshire Building | 2017-04-09 10:30 | 50076.7963 | 60.012
Devonshire Building | 2017-04-09 10:45 | 50076.8063 | 39.996
Devonshire Building | 2017-04-09 11:00 | 50076.8114 | 20.016
Devonshire Building | 2017-04-09 11:15 | 50076.8164 | 20.016
Devonshire Building | 2017-04-09 11:30 | 50076.8214 | 20.016
Devonshire Building | 2017-04-09 11:45 | 50076.8314 | 39.996
Devonshire Building | 2017-04-09 12:00 | 50076.8364 | 20.016
Devonshire Building | 2017-04-09 12:15 | 50076.8414 | 20.016
Devonshire Building | 2017-04-09 12:30 | 50076.8464 | 20.016
Devonshire Building | 2017-04-09 12:45 | 50076.8514 | 20.016
Devonshire Building | 2017-04-09 13:00 | 50076.8614 | 39.996
Devonshire Building | 2017-04-09 13:15 | 50076.8664 | 20.016
Devonshire Building | 2017-04-09 13:30 | 50076.8714 | 20.016
Devonshire Building | 2017-04-09 13:45 | 50076.8764 | 20.016
Devonshire Building | 2017-04-09 14:00 | 50076.8814 | 20.016
Devonshire Building | 2017-04-09 14:15 | 50076.8864 | 20.016
Devonshire Building | 2017-04-09 14:30 | 50076.8914 | 20.016
Devonshire Building | 2017-04-09 14:45 | 50076.8964 | 20.016
Devonshire Building | 2017-04-09 15:00 | 50076.9014 | 20.016
Devonshire Building | 2017-04-09 15:15 | 50076.9064 | 20.016
Devonshire Building | 2017-04-09 15:30 | 50076.9114 | 20.016
Devonshire Building | 2017-04-09 15:45 | 50076.9164 | 20.016
Devonshire Building | 2017-04-09 16:00 | 50076.9214 | 20.016
Devonshire Building | 2017-04-09 16:15 | 50076.9264 | 20.016
Devonshire Building | 2017-04-09 16:30 | 50076.9314 | 20.016
Devonshire Building | 2017-04-09 16:45 | 50076.9364 | 20.016
Devonshire Building | 2017-04-09 17:00 | 50076.9364 | 0
Devonshire Building | 2017-04-09 17:15 | 50076.9414 | 20.016
Devonshire Building | 2017-04-09 17:30 | 50076.9464 | 20.016
Devonshire Building | 2017-04-09 17:45 | 50076.9514 | 20.016
Devonshire Building | 2017-04-09 18:00 | 50076.9565 | 20.016
Devonshire Building | 2017-04-09 18:15 | 50076.9615 | 20.016
Devonshire Building | 2017-04-09 18:30 | 50076.9615 | 0
Devonshire Building | 2017-04-09 18:45 | 50076.9665 | 20.016
Devonshire Building | 2017-04-09 19:00 | 50076.9715 | 20.016
Devonshire Building | 2017-04-09 19:15 | 50076.9765 | 20.016
Devonshire Building | 2017-04-09 19:30 | 50076.9765 | 0
Devonshire Building | 2017-04-09 19:45 | 50076.9815 | 20.016
Devonshire Building | 2017-04-09 20:00 | 50076.9865 | 20.016
Devonshire Building | 2017-04-09 20:15 | 50076.9915 | 20.016
Devonshire Building | 2017-04-09 20:30 | 50076.9915 | 0
Devonshire Building | 2017-04-09 20:45 | 50076.9965 | 20.016
Devonshire Building | 2017-04-09 21:00 | 50077.0215 | 100.008
Devonshire Building | 2017-04-09 21:15 | 50077.0265 | 20.016
Devonshire Building | 2017-04-09 21:30 | 50077.0265 | 0
Devonshire Building | 2017-04-09 21:45 | 50077.0315 | 20.016
Devonshire Building | 2017-04-09 22:00 | 50077.0365 | 20.016
Devonshire Building | 2017-04-09 22:15 | 50077.0365 | 0
Devonshire Building | 2017-04-09 22:30 | 50077.0415 | 20.016
Devonshire Building | 2017-04-09 22:45 | 50077.0415 | 0
Devonshire Building | 2017-04-09 23:00 | 50077.0465 | 20.016
Devonshire Building | 2017-04-09 23:15 | 50077.0515 | 20.016
Devonshire Building | 2017-04-09 23:30 | 50077.0515 | 0
Devonshire Building | 2017-04-09 23:45 | 50077.0565 | 20.016 | 0
Devonshire Building | 2017-04-10 | 50077.0547 | 0
Devonshire Building | 2017-04-10 00:15 | 50077.0597 | 20.016
Devonshire Building | 2017-04-10 00:30 | 50077.0647 | 20.016
Devonshire Building | 2017-04-10 00:45 | 50077.0647 | 0
Devonshire Building | 2017-04-10 01:00 | 50077.0697 | 20.016
Devonshire Building | 2017-04-10 01:15 | 50077.0747 | 20.016
Devonshire Building | 2017-04-10 01:30 | 50077.0747 | 0
Devonshire Building | 2017-04-10 01:45 | 50077.0797 | 20.016
Devonshire Building | 2017-04-10 02:00 | 50077.0797 | 0
Devonshire Building | 2017-04-10 02:15 | 50077.0847 | 20.016
Devonshire Building | 2017-04-10 02:30 | 50077.0847 | 0
Devonshire Building | 2017-04-10 02:45 | 50077.0897 | 20.016
Devonshire Building | 2017-04-10 03:00 | 50077.0947 | 20.016
Devonshire Building | 2017-04-10 03:15 | 50077.0947 | 0
Devonshire Building | 2017-04-10 03:30 | 50077.0997 | 20.016
Devonshire Building | 2017-04-10 03:45 | 50077.0997 | 0
Devonshire Building | 2017-04-10 04:00 | 50077.2097 | 439.992
Devonshire Building | 2017-04-10 04:15 | 50077.6147 | 1620
Devonshire Building | 2017-04-10 04:30 | 50077.6147 | 0
Devonshire Building | 2017-04-10 04:45 | 50077.6197 | 20.016
Devonshire Building | 2017-04-10 05:00 | 50077.6197 | 0
Devonshire Building | 2017-04-10 05:15 | 50077.6247 | 20.016
Devonshire Building | 2017-04-10 05:30 | 50077.6297 | 20.016
Devonshire Building | 2017-04-10 05:45 | 50077.6397 | 39.996
Devonshire Building | 2017-04-10 06:00 | 50077.6447 | 20.016
Devonshire Building | 2017-04-10 06:15 | 50077.6447 | 0
Devonshire Building | 2017-04-10 06:30 | 50077.6497 | 20.016
Devonshire Building | 2017-04-10 06:45 | 50077.6597 | 39.996
Devonshire Building | 2017-04-10 07:00 | 50077.6697 | 39.996
Devonshire Building | 2017-04-10 07:15 | 50077.6747 | 20.016
Devonshire Building | 2017-04-10 07:30 | 50077.6797 | 20.016
Devonshire Building | 2017-04-10 07:45 | 50077.7197 | 159.984
Devonshire Building | 2017-04-10 08:00 | 50077.7647 | 180
Devonshire Building | 2017-04-10 08:15 | 50077.8197 | 219.996
Devonshire Building | 2017-04-10 08:30 | 50077.8847 | 259.992
Devonshire Building | 2017-04-10 08:45 | 50077.9497 | 259.992
Devonshire Building | 2017-04-10 09:00 | 50078.5847 | 2540.016
Devonshire Building | 2017-04-10 09:15 | 50078.6497 | 259.992
Devonshire Building | 2017-04-10 09:30 | 50078.7247 | 299.988
Devonshire Building | 2017-04-10 09:45 | 50078.7997 | 299.988
Devonshire Building | 2017-04-10 10:00 | 50078.8747 | 299.988
Devonshire Building | 2017-04-10 10:15 | 50079.5097 | 2540.016
Devonshire Building | 2017-04-10 10:30 | 50079.5797 | 280.008
Devonshire Building | 2017-04-10 10:45 | 50079.6347 | 219.996
Devonshire Building | 2017-04-10 11:00 | 50079.6897 | 219.996
Devonshire Building | 2017-04-10 11:15 | 50079.7397 | 200.016
Devonshire Building | 2017-04-10 11:30 | 50079.7847 | 180
Devonshire Building | 2017-04-10 11:45 | 50080.1947 | 1640.016
Devonshire Building | 2017-04-10 12:00 | 50080.4347 | 960.012
Devonshire Building | 2017-04-10 12:15 | 50080.4797 | 180
Devonshire Building | 2017-04-10 12:30 | 50080.5298 | 200.016
Devonshire Building | 2017-04-10 12:45 | 50080.5798 | 200.016
Devonshire Building | 2017-04-10 13:00 | 50080.6348 | 219.996
Devonshire Building | 2017-04-10 13:15 | 50080.6798 | 180
Devonshire Building | 2017-04-10 13:30 | 50080.7548 | 299.988
Devonshire Building | 2017-04-10 13:45 | 50081.3198 | 2260.008
Devonshire Building | 2017-04-10 14:00 | 50081.3648 | 180
Devonshire Building | 2017-04-10 14:15 | 50081.4198 | 219.996
Devonshire Building | 2017-04-10 14:30 | 50081.4648 | 180
Devonshire Building | 2017-04-10 14:45 | 50081.5098 | 180
Devonshire Building | 2017-04-10 15:00 | 50081.5548 | 180
Devonshire Building | 2017-04-10 15:15 | 50082.1298 | 2300.004
Devonshire Building | 2017-04-10 15:30 | 50082.1598 | 119.988
Devonshire Building | 2017-04-10 15:45 | 50082.1897 | 119.988
Devonshire Building | 2017-04-10 16:00 | 50082.2247 | 140.004
Devonshire Building | 2017-04-10 16:15 | 50082.2547 | 119.988
Devonshire Building | 2017-04-10 16:30 | 50082.2847 | 119.988
Devonshire Building | 2017-04-10 16:45 | 50082.3097 | 100.008
Devonshire Building | 2017-04-10 17:00 | 50082.3397 | 119.988
Devonshire Building | 2017-04-10 17:15 | 50082.3647 | 100.008
Devonshire Building | 2017-04-10 17:30 | 50082.3897 | 100.008
Devonshire Building | 2017-04-10 17:45 | 50082.4147 | 100.008
Devonshire Building | 2017-04-10 18:00 | 50082.4547 | 159.984
Devonshire Building | 2017-04-10 18:15 | 50082.4997 | 180
Devonshire Building | 2017-04-10 18:30 | 50082.6547 | 619.992
Devonshire Building | 2017-04-10 18:45 | 50083.1197 | 1860.012
Devonshire Building | 2017-04-10 19:00 | 50083.1647 | 180
Devonshire Building | 2017-04-10 19:15 | 50083.2097 | 180
Devonshire Building | 2017-04-10 19:30 | 50083.2647 | 219.996
Devonshire Building | 2017-04-10 19:45 | 50083.3097 | 180
Devonshire Building | 2017-04-10 20:00 | 50083.3547 | 180
Devonshire Building | 2017-04-10 20:15 | 50083.3997 | 180
Devonshire Building | 2017-04-10 20:30 | 50083.4397 | 159.984
Devonshire Building | 2017-04-10 20:45 | 50083.4797 | 159.984
Devonshire Building | 2017-04-10 21:00 | 50083.5147 | 140.004
Devonshire Building | 2017-04-10 21:15 | 50083.5497 | 140.004
Devonshire Building | 2017-04-10 21:30 | 50083.5797 | 119.988
Devonshire Building | 2017-04-10 21:45 | 50083.6097 | 119.988
Devonshire Building | 2017-04-10 22:00 | 50083.6247 | 60.012
Devonshire Building | 2017-04-10 22:15 | 50083.6397 | 60.012
Devonshire Building | 2017-04-10 22:30 | 50083.6547 | 60.012
Devonshire Building | 2017-04-10 22:45 | 50083.6647 | 39.996
Devonshire Building | 2017-04-10 23:00 | 50083.6747 | 39.996
Devonshire Building | 2017-04-10 23:15 | 50083.6897 | 60.012
Devonshire Building | 2017-04-10 23:30 | 50083.6997 | 39.996
Devonshire Building | 2017-04-10 23:45 | 50083.7097 | 39.996
Devonshire Building | 2017-04-11 | 50083.7188 | 39.996
Devonshire Building | 2017-04-11 00:15 | 50083.7287 | 39.996
Devonshire Building | 2017-04-11 00:30 | 50083.7338 | 20.016
Devonshire Building | 2017-04-11 00:45 | 50083.7438 | 39.996
Devonshire Building | 2017-04-11 01:00 | 50083.7538 | 39.996
Devonshire Building | 2017-04-11 01:15 | 50083.7588 | 20.016
Devonshire Building | 2017-04-11 01:30 | 50083.7688 | 39.996
Devonshire Building | 2017-04-11 01:45 | 50083.7738 | 20.016
Devonshire Building | 2017-04-11 02:00 | 50083.7838 | 39.996
Devonshire Building | 2017-04-11 02:15 | 50083.7888 | 20.016
Devonshire Building | 2017-04-11 02:30 | 50083.7988 | 39.996
Devonshire Building | 2017-04-11 02:45 | 50083.8038 | 20.016
Devonshire Building | 2017-04-11 03:00 | 50083.8088 | 20.016
Devonshire Building | 2017-04-11 03:15 | 50083.8188 | 39.996
Devonshire Building | 2017-04-11 03:30 | 50083.8238 | 20.016
Devonshire Building | 2017-04-11 03:45 | 50083.8288 | 20.016
Devonshire Building | 2017-04-11 04:00 | 50083.8338 | 20.016
Devonshire Building | 2017-04-11 04:15 | 50083.8438 | 39.996
Devonshire Building | 2017-04-11 04:30 | 50083.8488 | 20.016
Devonshire Building | 2017-04-11 04:45 | 50083.8538 | 20.016
Devonshire Building | 2017-04-11 05:00 | 50083.8588 | 20.016
Devonshire Building | 2017-04-11 05:15 | 50083.8638 | 20.016
Devonshire Building | 2017-04-11 05:30 | 50083.8738 | 39.996
Devonshire Building | 2017-04-11 05:45 | 50083.8788 | 20.016
Devonshire Building | 2017-04-11 06:00 | 50083.8838 | 20.016
Devonshire Building | 2017-04-11 06:15 | 50083.9038 | 79.992
Devonshire Building | 2017-04-11 06:30 | 50083.9138 | 39.996
Devonshire Building | 2017-04-11 06:45 | 50083.9188 | 20.016
Devonshire Building | 2017-04-11 07:00 | 50083.9288 | 39.996
Devonshire Building | 2017-04-11 07:15 | 50083.9388 | 39.996
Devonshire Building | 2017-04-11 07:30 | 50083.9488 | 39.996
Devonshire Building | 2017-04-11 07:45 | 50083.9538 | 20.016
Devonshire Building | 2017-04-11 08:00 | 50083.9938 | 159.984
Devonshire Building | 2017-04-11 08:15 | 50084.5188 | 2099.988
Devonshire Building | 2017-04-11 08:30 | 50084.5438 | 100.008
Devonshire Building | 2017-04-11 08:45 | 50084.5488 | 20.016
Devonshire Building | 2017-04-11 09:00 | 50084.5788 | 119.988
Devonshire Building | 2017-04-11 09:15 | 50084.6338 | 219.996
Devonshire Building | 2017-04-11 09:30 | 50085.1488 | 2059.992
Devonshire Building | 2017-04-11 09:45 | 50085.3588 | 839.988
Devonshire Building | 2017-04-11 10:00 | 50085.4538 | 380.016
Devonshire Building | 2017-04-11 10:15 | 50085.5288 | 299.988
Devonshire Building | 2017-04-11 10:30 | 50085.5888 | 240.012
Devonshire Building | 2017-04-11 10:45 | 50085.6438 | 219.996
Devonshire Building | 2017-04-11 11:00 | 50086.0288 | 1540.008
Devonshire Building | 2017-04-11 11:15 | 50086.3038 | 1100.016
Devonshire Building | 2017-04-11 11:30 | 50086.3438 | 159.984
Devonshire Building | 2017-04-11 11:45 | 50086.3788 | 140.004
Devonshire Building | 2017-04-11 12:00 | 50086.4188 | 159.984
Devonshire Building | 2017-04-11 12:15 | 50086.4488 | 119.988
Devonshire Building | 2017-04-11 12:30 | 50086.4888 | 159.984
Devonshire Building | 2017-04-11 12:45 | 50087.0188 | 2120.004
Devonshire Building | 2017-04-11 13:00 | 50087.0988 | 320.004
Devonshire Building | 2017-04-11 13:15 | 50087.1288 | 119.988
Devonshire Building | 2017-04-11 13:30 | 50087.1588 | 119.988
Devonshire Building | 2017-04-11 13:45 | 50087.1988 | 159.984
Devonshire Building | 2017-04-11 14:00 | 50087.2438 | 180
Devonshire Building | 2017-04-11 14:15 | 50087.2938 | 200.016
Devonshire Building | 2017-04-11 14:30 | 50087.3388 | 180
Devonshire Building | 2017-04-11 14:45 | 50087.3838 | 180
Devonshire Building | 2017-04-11 15:00 | 50087.7738 | 1559.988
Devonshire Building | 2017-04-11 15:15 | 50088.0238 | 1000.008
Devonshire Building | 2017-04-11 15:30 | 50088.1038 | 320.004
Devonshire Building | 2017-04-11 15:45 | 50088.2388 | 540
Devonshire Building | 2017-04-11 16:00 | 50088.4238 | 740.016
Devonshire Building | 2017-04-11 16:15 | 50088.5638 | 560.016
Devonshire Building | 2017-04-11 16:30 | 50088.6638 | 399.996
Devonshire Building | 2017-04-11 16:45 | 50088.7438 | 320.004
Devonshire Building | 2017-04-11 17:00 | 50088.8088 | 259.992
Devonshire Building | 2017-04-11 17:15 | 50089.1338 | 1299.996
Devonshire Building | 2017-04-11 17:30 | 50089.4238 | 1159.992
Devonshire Building | 2017-04-11 17:45 | 50089.4538 | 119.988
Devonshire Building | 2017-04-11 18:00 | 50089.4738 | 79.992
Devonshire Building | 2017-04-11 18:15 | 50089.4838 | 39.996
Devonshire Building | 2017-04-11 18:30 | 50089.4988 | 60.012
Devonshire Building | 2017-04-11 18:45 | 50089.5088 | 39.996
Devonshire Building | 2017-04-11 19:00 | 50089.5238 | 60.012
Devonshire Building | 2017-04-11 19:15 | 50089.5388 | 60.012
Devonshire Building | 2017-04-11 19:30 | 50089.5488 | 39.996
Devonshire Building | 2017-04-11 19:45 | 50089.5638 | 60.012
Devonshire Building | 2017-04-11 20:00 | 50089.5738 | 39.996
Devonshire Building | 2017-04-11 20:15 | 50089.5888 | 60.012
Devonshire Building | 2017-04-11 20:30 | 50089.5988 | 39.996
Devonshire Building | 2017-04-11 20:45 | 50089.6088 | 39.996
Devonshire Building | 2017-04-11 21:00 | 50089.6238 | 60.012
Devonshire Building | 2017-04-11 21:15 | 50089.6338 | 39.996
Devonshire Building | 2017-04-11 21:30 | 50089.6438 | 39.996
Devonshire Building | 2017-04-11 21:45 | 50089.6538 | 39.996
Devonshire Building | 2017-04-11 22:00 | 50089.6588 | 20.016
Devonshire Building | 2017-04-11 22:15 | 50089.6688 | 39.996
Devonshire Building | 2017-04-11 22:30 | 50089.6788 | 39.996
Devonshire Building | 2017-04-11 22:45 | 50089.6888 | 39.996
Devonshire Building | 2017-04-11 23:00 | 50089.6938 | 20.016
Devonshire Building | 2017-04-11 23:15 | 50089.7038 | 39.996
Devonshire Building | 2017-04-11 23:30 | 50089.7088 | 20.016
Devonshire Building | 2017-04-11 23:45 | 50089.7188 | 39.996
Devonshire Building | 2017-04-12 | 50089.7305 | 39.996
Devonshire Building | 2017-04-12 00:15 | 50089.7355 | 20.016
Devonshire Building | 2017-04-12 00:30 | 50089.7455 | 39.996
Devonshire Building | 2017-04-12 00:45 | 50089.7505 | 20.016
Devonshire Building | 2017-04-12 01:00 | 50089.7555 | 20.016
Devonshire Building | 2017-04-12 01:15 | 50089.7655 | 39.996
Devonshire Building | 2017-04-12 01:30 | 50089.7705 | 20.016
Devonshire Building | 2017-04-12 01:45 | 50089.7755 | 20.016
Devonshire Building | 2017-04-12 02:00 | 50089.7855 | 39.996
Devonshire Building | 2017-04-12 02:15 | 50089.7905 | 20.016
Devonshire Building | 2017-04-12 02:30 | 50089.7955 | 20.016
Devonshire Building | 2017-04-12 02:45 | 50089.8005 | 20.016
Devonshire Building | 2017-04-12 03:00 | 50089.8105 | 39.996
Devonshire Building | 2017-04-12 03:15 | 50089.8155 | 20.016
Devonshire Building | 2017-04-12 03:30 | 50089.8205 | 20.016
Devonshire Building | 2017-04-12 03:45 | 50089.8255 | 20.016
Devonshire Building | 2017-04-12 04:00 | 50089.8305 | 20.016
Devonshire Building | 2017-04-12 04:15 | 50089.8355 | 20.016
Devonshire Building | 2017-04-12 04:30 | 50089.8405 | 20.016
Devonshire Building | 2017-04-12 04:45 | 50089.8505 | 39.996
Devonshire Building | 2017-04-12 05:00 | 50089.8555 | 20.016
Devonshire Building | 2017-04-12 05:15 | 50089.8605 | 20.016
Devonshire Building | 2017-04-12 05:30 | 50089.8655 | 20.016
Devonshire Building | 2017-04-12 05:45 | 50089.8705 | 20.016
Devonshire Building | 2017-04-12 06:00 | 50089.8805 | 39.996
Devonshire Building | 2017-04-12 06:15 | 50089.8855 | 20.016
Devonshire Building | 2017-04-12 06:30 | 50089.8905 | 20.016
Devonshire Building | 2017-04-12 06:45 | 50089.8955 | 20.016
Devonshire Building | 2017-04-12 07:00 | 50089.9006 | 20.016
Devonshire Building | 2017-04-12 07:15 | 50089.9156 | 60.012
Devonshire Building | 2017-04-12 07:30 | 50090.4206 | 2019.996
Devonshire Building | 2017-04-12 07:45 | 50090.4506 | 119.988
Devonshire Building | 2017-04-12 08:00 | 50090.4805 | 119.988
Devonshire Building | 2017-04-12 08:15 | 50090.5056 | 100.008
Devonshire Building | 2017-04-12 08:30 | 50090.5355 | 119.988
Devonshire Building | 2017-04-12 08:45 | 50090.5655 | 119.988
Devonshire Building | 2017-04-12 09:00 | 50090.8005 | 939.996
Devonshire Building | 2017-04-12 09:15 | 50091.2055 | 1620
Devonshire Building | 2017-04-12 09:30 | 50091.2655 | 240.012
Devonshire Building | 2017-04-12 09:45 | 50091.3305 | 259.992
Devonshire Building | 2017-04-12 10:00 | 50091.4005 | 280.008
Devonshire Building | 2017-04-12 10:15 | 50092.0105 | 2440.008
Devonshire Building | 2017-04-12 10:30 | 50092.0706 | 240.012
Devonshire Building | 2017-04-12 10:45 | 50092.1206 | 200.016
Devonshire Building | 2017-04-12 11:00 | 50092.1606 | 159.984
Devonshire Building | 2017-04-12 11:15 | 50092.2705 | 439.992
Devonshire Building | 2017-04-12 11:30 | 50092.8305 | 2239.992
Devonshire Building | 2017-04-12 11:45 | 50092.8705 | 159.984
Devonshire Building | 2017-04-12 12:00 | 50092.9105 | 159.984
Devonshire Building | 2017-04-12 12:15 | 50092.9505 | 159.984
Devonshire Building | 2017-04-12 12:30 | 50092.9905 | 159.984
Devonshire Building | 2017-04-12 12:45 | 50093.0505 | 240.012
Devonshire Building | 2017-04-12 13:00 | 50093.1205 | 280.008
Devonshire Building | 2017-04-12 13:15 | 50093.3655 | 979.992
Devonshire Building | 2017-04-12 13:30 | 50093.9105 | 2180.016
Devonshire Building | 2017-04-12 13:45 | 50094.0405 | 519.984
Devonshire Building | 2017-04-12 14:00 | 50094.1305 | 360
Devonshire Building | 2017-04-12 14:15 | 50094.2005 | 280.008
Devonshire Building | 2017-04-12 14:30 | 50094.2605 | 240.012
Devonshire Building | 2017-04-12 14:45 | 50094.3155 | 219.996
Devonshire Building | 2017-04-12 15:00 | 50094.3705 | 219.996
Devonshire Building | 2017-04-12 15:15 | 50094.7255 | 1419.984
Devonshire Building | 2017-04-12 15:30 | 50095.0005 | 1100.016
Devonshire Building | 2017-04-12 15:45 | 50095.0355 | 140.004
Devonshire Building | 2017-04-12 16:00 | 50095.0755 | 159.984
Devonshire Building | 2017-04-12 16:15 | 50095.1155 | 159.984
Devonshire Building | 2017-04-12 16:30 | 50095.1455 | 119.988
Devonshire Building | 2017-04-12 16:45 | 50095.1805 | 140.004
Devonshire Building | 2017-04-12 17:00 | 50095.2155 | 140.004
Devonshire Building | 2017-04-12 17:15 | 50095.2555 | 159.984
Devonshire Building | 2017-04-12 17:30 | 50095.3055 | 200.016
Devonshire Building | 2017-04-12 17:45 | 50095.3555 | 200.016
Devonshire Building | 2017-04-12 18:00 | 50095.9155 | 2239.992
Devonshire Building | 2017-04-12 18:15 | 50095.9655 | 200.016
Devonshire Building | 2017-04-12 18:30 | 50096.0155 | 200.016
Devonshire Building | 2017-04-12 18:45 | 50096.0605 | 180
Devonshire Building | 2017-04-12 19:00 | 50096.1005 | 159.984
Devonshire Building | 2017-04-12 19:15 | 50096.1405 | 159.984
Devonshire Building | 2017-04-12 19:30 | 50096.1705 | 119.988
Devonshire Building | 2017-04-12 19:45 | 50096.2005 | 119.988
Devonshire Building | 2017-04-12 20:00 | 50096.2255 | 100.008
Devonshire Building | 2017-04-12 20:15 | 50096.2455 | 79.992
Devonshire Building | 2017-04-12 20:30 | 50096.2655 | 79.992
Devonshire Building | 2017-04-12 20:45 | 50096.2855 | 79.992
Devonshire Building | 2017-04-12 21:00 | 50096.3005 | 60.012
Devonshire Building | 2017-04-12 21:15 | 50096.3155 | 60.012
Devonshire Building | 2017-04-12 21:30 | 50096.3255 | 39.996
Devonshire Building | 2017-04-12 21:45 | 50096.3355 | 39.996
Devonshire Building | 2017-04-12 22:00 | 50096.3505 | 60.012
Devonshire Building | 2017-04-12 22:15 | 50096.3605 | 39.996
Devonshire Building | 2017-04-12 22:30 | 50096.3755 | 60.012
Devonshire Building | 2017-04-12 22:45 | 50096.3855 | 39.996
Devonshire Building | 2017-04-12 23:00 | 50096.3955 | 39.996
Devonshire Building | 2017-04-12 23:15 | 50096.4055 | 39.996
Devonshire Building | 2017-04-12 23:30 | 50096.4205 | 60.012
Devonshire Building | 2017-04-12 23:45 | 50096.4305 | 39.996
Devonshire Building | 2017-04-13 | 50096.4375 | 39.996
Devonshire Building | 2017-04-13 00:15 | 50096.4475 | 39.996
Devonshire Building | 2017-04-13 00:30 | 50096.4575 | 39.996
Devonshire Building | 2017-04-13 00:45 | 50096.4675 | 39.996
Devonshire Building | 2017-04-13 01:00 | 50096.4775 | 39.996
Devonshire Building | 2017-04-13 01:15 | 50096.4875 | 39.996
Devonshire Building | 2017-04-13 01:30 | 50096.4975 | 39.996
Devonshire Building | 2017-04-13 01:45 | 50096.5175 | 79.992
Devonshire Building | 2017-04-13 02:00 | 50096.5425 | 100.008
Devonshire Building | 2017-04-13 02:15 | 50096.5675 | 100.008
Devonshire Building | 2017-04-13 02:30 | 50096.5925 | 100.008
Devonshire Building | 2017-04-13 02:45 | 50096.6175 | 100.008
Devonshire Building | 2017-04-13 03:00 | 50096.6425 | 100.008
Devonshire Building | 2017-04-13 03:15 | 50096.6625 | 79.992
Devonshire Building | 2017-04-13 03:30 | 50096.6875 | 100.008
Devonshire Building | 2017-04-13 03:45 | 50096.7125 | 100.008
Devonshire Building | 2017-04-13 04:00 | 50096.7325 | 79.992
Devonshire Building | 2017-04-13 04:15 | 50096.7375 | 20.016
Devonshire Building | 2017-04-13 04:30 | 50096.7475 | 39.996
Devonshire Building | 2017-04-13 04:45 | 50096.7525 | 20.016
Devonshire Building | 2017-04-13 05:00 | 50096.7625 | 39.996
Devonshire Building | 2017-04-13 05:15 | 50096.7675 | 20.016
Devonshire Building | 2017-04-13 05:30 | 50096.7775 | 39.996
Devonshire Building | 2017-04-13 05:45 | 50096.7825 | 20.016
Devonshire Building | 2017-04-13 06:00 | 50096.7925 | 39.996
Devonshire Building | 2017-04-13 06:15 | 50096.7975 | 20.016
Devonshire Building | 2017-04-13 06:30 | 50096.8075 | 39.996
Devonshire Building | 2017-04-13 06:45 | 50096.8125 | 20.016
Devonshire Building | 2017-04-13 07:00 | 50096.8225 | 39.996
Devonshire Building | 2017-04-13 07:15 | 50096.8275 | 20.016
Devonshire Building | 2017-04-13 07:30 | 50096.8325 | 20.016
Devonshire Building | 2017-04-13 07:45 | 50096.8475 | 60.012
Devonshire Building | 2017-04-13 08:00 | 50097.4125 | 2260.008
Devonshire Building | 2017-04-13 08:15 | 50097.4275 | 60.012
Devonshire Building | 2017-04-13 08:30 | 50097.4375 | 39.996
Devonshire Building | 2017-04-13 08:45 | 50097.4525 | 60.012
Devonshire Building | 2017-04-13 09:00 | 50097.4675 | 60.012
Devonshire Building | 2017-04-13 09:15 | 50097.4825 | 60.012
Devonshire Building | 2017-04-13 09:30 | 50097.5025 | 79.992
Devonshire Building | 2017-04-13 09:45 | 50098.0825 | 2319.984
Devonshire Building | 2017-04-13 10:00 | 50098.1325 | 200.016
Devonshire Building | 2017-04-13 10:15 | 50098.1875 | 219.996
Devonshire Building | 2017-04-13 10:30 | 50098.2425 | 219.996
Devonshire Building | 2017-04-13 10:45 | 50098.2975 | 219.996
Devonshire Building | 2017-04-13 11:00 | 50098.3525 | 219.996
Devonshire Building | 2017-04-13 11:15 | 50098.4525 | 399.996
Devonshire Building | 2017-04-13 11:30 | 50098.9675 | 2059.992
Devonshire Building | 2017-04-13 11:45 | 50099.0375 | 280.008
Devonshire Building | 2017-04-13 12:00 | 50099.2275 | 759.996
Devonshire Building | 2017-04-13 12:15 | 50099.3825 | 619.992
Devonshire Building | 2017-04-13 12:30 | 50099.4875 | 420.012
Devonshire Building | 2017-04-13 12:45 | 50099.5575 | 280.008
Devonshire Building | 2017-04-13 13:00 | 50099.6125 | 219.996
Devonshire Building | 2017-04-13 13:15 | 50099.6625 | 200.016
Devonshire Building | 2017-04-13 13:30 | 50100.2425 | 2319.984
Devonshire Building | 2017-04-13 13:45 | 50100.2575 | 60.012
Devonshire Building | 2017-04-13 14:00 | 50100.2725 | 60.012
Devonshire Building | 2017-04-13 14:15 | 50100.2925 | 79.992
Devonshire Building | 2017-04-13 14:30 | 50100.3075 | 60.012
Devonshire Building | 2017-04-13 14:45 | 50100.3225 | 60.012
Devonshire Building | 2017-04-13 15:00 | 50100.3376 | 60.012
Devonshire Building | 2017-04-13 15:15 | 50100.5426 | 820.008
Devonshire Building | 2017-04-13 15:30 | 50100.9476 | 1620
Devonshire Building | 2017-04-13 15:45 | 50101.0126 | 259.992
Devonshire Building | 2017-04-13 16:00 | 50101.0975 | 339.984
Devonshire Building | 2017-04-13 16:15 | 50101.1775 | 320.004
Devonshire Building | 2017-04-13 16:30 | 50101.2476 | 280.008
Devonshire Building | 2017-04-13 16:45 | 50101.3076 | 240.012
Devonshire Building | 2017-04-13 17:00 | 50101.3676 | 240.012
Devonshire Building | 2017-04-13 17:15 | 50101.4126 | 180
Devonshire Building | 2017-04-13 17:30 | 50101.4476 | 140.004
Devonshire Building | 2017-04-13 17:45 | 50101.4826 | 140.004
Devonshire Building | 2017-04-13 18:00 | 50101.5076 | 100.008
Devonshire Building | 2017-04-13 18:15 | 50101.5326 | 100.008
Devonshire Building | 2017-04-13 18:30 | 50101.5576 | 100.008
Devonshire Building | 2017-04-13 18:45 | 50101.5776 | 79.992
Devonshire Building | 2017-04-13 19:00 | 50101.5976 | 79.992
Devonshire Building | 2017-04-13 19:15 | 50101.6126 | 60.012
Devonshire Building | 2017-04-13 19:30 | 50101.6276 | 60.012
Devonshire Building | 2017-04-13 19:45 | 50101.6576 | 119.988
Devonshire Building | 2017-04-13 20:00 | 50101.6876 | 119.988
Devonshire Building | 2017-04-13 20:15 | 50101.7176 | 119.988
Devonshire Building | 2017-04-13 20:30 | 50101.7426 | 100.008
Devonshire Building | 2017-04-13 20:45 | 50101.7726 | 119.988
Devonshire Building | 2017-04-13 21:00 | 50101.8176 | 180
Devonshire Building | 2017-04-13 21:15 | 50101.8376 | 79.992
Devonshire Building | 2017-04-13 21:30 | 50101.8576 | 79.992
Devonshire Building | 2017-04-13 21:45 | 50101.8775 | 79.992
Devonshire Building | 2017-04-13 22:00 | 50101.8926 | 60.012
Devonshire Building | 2017-04-13 22:15 | 50101.8976 | 20.016
Devonshire Building | 2017-04-13 22:30 | 50101.9026 | 20.016
Devonshire Building | 2017-04-13 22:45 | 50101.9076 | 20.016
Devonshire Building | 2017-04-13 23:00 | 50101.9076 | 0
Devonshire Building | 2017-04-13 23:15 | 50101.9126 | 20.016
Devonshire Building | 2017-04-13 23:30 | 50101.9176 | 20.016
Devonshire Building | 2017-04-13 23:45 | 50102.4326 | 2059.992
Devonshire Building | 2017-04-14 | 50102.4375 | 20.016
Devonshire Building | 2017-04-14 00:15 | 50102.4425 | 20.016
Devonshire Building | 2017-04-14 00:30 | 50102.4475 | 20.016
Devonshire Building | 2017-04-14 00:45 | 50102.4475 | 0
Devonshire Building | 2017-04-14 01:00 | 50102.4525 | 20.016
Devonshire Building | 2017-04-14 01:15 | 50102.4575 | 20.016
Devonshire Building | 2017-04-14 01:30 | 50102.4575 | 0
Devonshire Building | 2017-04-14 01:45 | 50102.4625 | 20.016
Devonshire Building | 2017-04-14 02:00 | 50102.4675 | 20.016
Devonshire Building | 2017-04-14 02:15 | 50102.4675 | 0
Devonshire Building | 2017-04-14 02:30 | 50102.4725 | 20.016
Devonshire Building | 2017-04-14 02:45 | 50102.4775 | 20.016
Devonshire Building | 2017-04-14 03:00 | 50102.4775 | 0
Devonshire Building | 2017-04-14 03:15 | 50102.4825 | 20.016
Devonshire Building | 2017-04-14 03:30 | 50102.4875 | 20.016
Devonshire Building | 2017-04-14 03:45 | 50102.4875 | 0
Devonshire Building | 2017-04-14 04:00 | 50102.4925 | 20.016
Devonshire Building | 2017-04-14 04:15 | 50102.4975 | 20.016
Devonshire Building | 2017-04-14 04:30 | 50102.4975 | 0
Devonshire Building | 2017-04-14 04:45 | 50102.5026 | 20.016
Devonshire Building | 2017-04-14 05:00 | 50102.5076 | 20.016
Devonshire Building | 2017-04-14 05:15 | 50102.5076 | 0
Devonshire Building | 2017-04-14 05:30 | 50102.5126 | 20.016
Devonshire Building | 2017-04-14 05:45 | 50102.5176 | 20.016
Devonshire Building | 2017-04-14 06:00 | 50102.5176 | 0
Devonshire Building | 2017-04-14 06:15 | 50102.5226 | 20.016
Devonshire Building | 2017-04-14 06:30 | 50102.5276 | 20.016
Devonshire Building | 2017-04-14 06:45 | 50102.5326 | 20.016
Devonshire Building | 2017-04-14 07:00 | 50102.5326 | 0
Devonshire Building | 2017-04-14 07:15 | 50102.5376 | 20.016
Devonshire Building | 2017-04-14 07:30 | 50102.5426 | 20.016
Devonshire Building | 2017-04-14 07:45 | 50102.5426 | 0
Devonshire Building | 2017-04-14 08:00 | 50102.5476 | 20.016
Devonshire Building | 2017-04-14 08:15 | 50102.5526 | 20.016
Devonshire Building | 2017-04-14 08:30 | 50102.5526 | 0
Devonshire Building | 2017-04-14 08:45 | 50102.5576 | 20.016
Devonshire Building | 2017-04-14 09:00 | 50102.5626 | 20.016
Devonshire Building | 2017-04-14 09:15 | 50102.5676 | 20.016
Devonshire Building | 2017-04-14 09:30 | 50102.5676 | 0
Devonshire Building | 2017-04-14 09:45 | 50102.5726 | 20.016
Devonshire Building | 2017-04-14 10:00 | 50102.5776 | 20.016
Devonshire Building | 2017-04-14 10:15 | 50102.5776 | 0
Devonshire Building | 2017-04-14 10:30 | 50102.5826 | 20.016
Devonshire Building | 2017-04-14 10:45 | 50102.5876 | 20.016
Devonshire Building | 2017-04-14 11:00 | 50102.5876 | 0
Devonshire Building | 2017-04-14 11:15 | 50102.5926 | 20.016
Devonshire Building | 2017-04-14 11:30 | 50102.5976 | 20.016
Devonshire Building | 2017-04-14 11:45 | 50102.5976 | 0
Devonshire Building | 2017-04-14 12:00 | 50102.6026 | 20.016
Devonshire Building | 2017-04-14 12:15 | 50102.6076 | 20.016
Devonshire Building | 2017-04-14 12:30 | 50102.6126 | 20.016
Devonshire Building | 2017-04-14 12:45 | 50102.6126 | 0
Devonshire Building | 2017-04-14 13:00 | 50102.6176 | 20.016
Devonshire Building | 2017-04-14 13:15 | 50102.6226 | 20.016
Devonshire Building | 2017-04-14 13:30 | 50102.6226 | 0
Devonshire Building | 2017-04-14 13:45 | 50102.6277 | 20.016
Devonshire Building | 2017-04-14 14:00 | 50102.6327 | 20.016
Devonshire Building | 2017-04-14 14:15 | 50102.6327 | 0
Devonshire Building | 2017-04-14 14:30 | 50102.6427 | 39.996
Devonshire Building | 2017-04-14 14:45 | 50102.6477 | 20.016
Devonshire Building | 2017-04-14 15:00 | 50102.6477 | 0
Devonshire Building | 2017-04-14 15:15 | 50102.6527 | 20.016
Devonshire Building | 2017-04-14 15:30 | 50102.6577 | 20.016
Devonshire Building | 2017-04-14 15:45 | 50102.6577 | 0
Devonshire Building | 2017-04-14 16:00 | 50102.6627 | 20.016
Devonshire Building | 2017-04-14 16:15 | 50102.6677 | 20.016
Devonshire Building | 2017-04-14 16:30 | 50102.6727 | 20.016
Devonshire Building | 2017-04-14 16:45 | 50102.6727 | 0
Devonshire Building | 2017-04-14 17:00 | 50102.6827 | 39.996
Devonshire Building | 2017-04-14 17:15 | 50102.6877 | 20.016
Devonshire Building | 2017-04-14 17:30 | 50102.6927 | 20.016
Devonshire Building | 2017-04-14 17:45 | 50102.6977 | 20.016
Devonshire Building | 2017-04-14 18:00 | 50103.2227 | 2099.988
Devonshire Building | 2017-04-14 18:15 | 50103.2277 | 20.016
Devonshire Building | 2017-04-14 18:30 | 50103.2327 | 20.016
Devonshire Building | 2017-04-14 18:45 | 50103.2377 | 20.016
Devonshire Building | 2017-04-14 19:00 | 50103.2427 | 20.016
Devonshire Building | 2017-04-14 19:15 | 50103.2477 | 20.016
Devonshire Building | 2017-04-14 19:30 | 50103.2627 | 60.012
Devonshire Building | 2017-04-14 19:45 | 50103.2827 | 79.992
Devonshire Building | 2017-04-14 20:00 | 50103.3027 | 79.992
Devonshire Building | 2017-04-14 20:15 | 50103.3227 | 79.992
Devonshire Building | 2017-04-14 20:30 | 50103.3427 | 79.992
Devonshire Building | 2017-04-14 20:45 | 50103.3627 | 79.992
Devonshire Building | 2017-04-14 21:00 | 50103.3877 | 100.008
Devonshire Building | 2017-04-14 21:15 | 50103.4077 | 79.992
Devonshire Building | 2017-04-14 21:30 | 50103.4327 | 100.008
Devonshire Building | 2017-04-14 21:45 | 50103.4527 | 79.992
Devonshire Building | 2017-04-14 22:00 | 50103.4727 | 79.992
Devonshire Building | 2017-04-14 22:15 | 50103.4927 | 79.992
Devonshire Building | 2017-04-14 22:30 | 50103.4977 | 20.016
Devonshire Building | 2017-04-14 22:45 | 50103.5077 | 39.996
Devonshire Building | 2017-04-14 23:00 | 50103.5127 | 20.016
Devonshire Building | 2017-04-14 23:15 | 50103.5227 | 39.996
Devonshire Building | 2017-04-14 23:30 | 50103.5327 | 39.996
Devonshire Building | 2017-04-14 23:45 | 50103.5377 | 20.016
Devonshire Building | 2017-04-15 | 50103.5508 | 39.996
Devonshire Building | 2017-04-15 00:15 | 50103.5558 | 20.016
Devonshire Building | 2017-04-15 00:30 | 50103.5658 | 39.996
Devonshire Building | 2017-04-15 00:45 | 50103.5708 | 20.016
Devonshire Building | 2017-04-15 01:00 | 50103.5808 | 39.996
Devonshire Building | 2017-04-15 01:15 | 50103.5858 | 20.016
Devonshire Building | 2017-04-15 01:30 | 50103.5908 | 20.016
Devonshire Building | 2017-04-15 01:45 | 50103.5958 | 20.016
Devonshire Building | 2017-04-15 02:00 | 50103.6058 | 39.996
Devonshire Building | 2017-04-15 02:15 | 50103.6108 | 20.016
Devonshire Building | 2017-04-15 02:30 | 50103.6158 | 20.016
Devonshire Building | 2017-04-15 02:45 | 50103.6208 | 20.016
Devonshire Building | 2017-04-15 03:00 | 50103.6308 | 39.996
Devonshire Building | 2017-04-15 03:15 | 50103.6358 | 20.016
Devonshire Building | 2017-04-15 03:30 | 50103.6408 | 20.016
Devonshire Building | 2017-04-15 03:45 | 50103.6458 | 20.016
Devonshire Building | 2017-04-15 04:00 | 50103.6508 | 20.016
Devonshire Building | 2017-04-15 04:15 | 50103.6558 | 20.016
Devonshire Building | 2017-04-15 04:30 | 50103.6608 | 20.016
Devonshire Building | 2017-04-15 04:45 | 50103.6658 | 20.016
Devonshire Building | 2017-04-15 05:00 | 50103.6708 | 20.016
Devonshire Building | 2017-04-15 05:15 | 50103.6758 | 20.016
Devonshire Building | 2017-04-15 05:30 | 50103.6808 | 20.016
Devonshire Building | 2017-04-15 05:45 | 50103.6859 | 20.016
Devonshire Building | 2017-04-15 06:00 | 50103.6909 | 20.016
Devonshire Building | 2017-04-15 06:15 | 50103.6959 | 20.016
Devonshire Building | 2017-04-15 06:30 | 50103.7009 | 20.016
Devonshire Building | 2017-04-15 06:45 | 50103.7059 | 20.016
Devonshire Building | 2017-04-15 07:00 | 50103.7109 | 20.016
Devonshire Building | 2017-04-15 07:15 | 50103.7159 | 20.016
Devonshire Building | 2017-04-15 07:30 | 50103.7209 | 20.016
Devonshire Building | 2017-04-15 07:45 | 50103.7209 | 0
Devonshire Building | 2017-04-15 08:00 | 50103.7259 | 20.016
Devonshire Building | 2017-04-15 08:15 | 50103.7309 | 20.016
Devonshire Building | 2017-04-15 08:30 | 50103.7359 | 20.016
Devonshire Building | 2017-04-15 08:45 | 50103.7409 | 20.016
Devonshire Building | 2017-04-15 09:00 | 50103.7459 | 20.016
Devonshire Building | 2017-04-15 09:15 | 50103.7459 | 0
Devonshire Building | 2017-04-15 09:30 | 50103.7509 | 20.016
Devonshire Building | 2017-04-15 09:45 | 50103.7559 | 20.016
Devonshire Building | 2017-04-15 10:00 | 50103.7609 | 20.016
Devonshire Building | 2017-04-15 10:15 | 50103.7609 | 0
Devonshire Building | 2017-04-15 10:30 | 50103.7659 | 20.016
Devonshire Building | 2017-04-15 10:45 | 50103.7709 | 20.016
Devonshire Building | 2017-04-15 11:00 | 50103.7759 | 20.016
Devonshire Building | 2017-04-15 11:15 | 50103.7809 | 20.016
Devonshire Building | 2017-04-15 11:30 | 50103.7809 | 0
Devonshire Building | 2017-04-15 11:45 | 50103.7859 | 20.016
Devonshire Building | 2017-04-15 12:00 | 50103.7909 | 20.016
Devonshire Building | 2017-04-15 12:15 | 50103.7959 | 20.016
Devonshire Building | 2017-04-15 12:30 | 50103.7959 | 0
Devonshire Building | 2017-04-15 12:45 | 50103.8009 | 20.016
Devonshire Building | 2017-04-15 13:00 | 50103.8059 | 20.016
Devonshire Building | 2017-04-15 13:15 | 50103.811 | 20.016
Devonshire Building | 2017-04-15 13:30 | 50103.811 | 0
Devonshire Building | 2017-04-15 13:45 | 50103.826 | 60.012
Devonshire Building | 2017-04-15 14:00 | 50103.846 | 79.992
Devonshire Building | 2017-04-15 14:15 | 50103.866 | 79.992
Devonshire Building | 2017-04-15 14:30 | 50103.8859 | 79.992
Devonshire Building | 2017-04-15 14:45 | 50103.9059 | 79.992
Devonshire Building | 2017-04-15 15:00 | 50103.9259 | 79.992
Devonshire Building | 2017-04-15 15:15 | 50103.9459 | 79.992
Devonshire Building | 2017-04-15 15:30 | 50103.9659 | 79.992
Devonshire Building | 2017-04-15 15:45 | 50103.9809 | 60.012
Devonshire Building | 2017-04-15 16:00 | 50103.9859 | 20.016
Devonshire Building | 2017-04-15 16:15 | 50103.9859 | 0
Devonshire Building | 2017-04-15 16:30 | 50103.991 | 20.016
Devonshire Building | 2017-04-15 16:45 | 50103.996 | 20.016
Devonshire Building | 2017-04-15 17:00 | 50104.001 | 20.016
Devonshire Building | 2017-04-15 17:15 | 50104.001 | 0
Devonshire Building | 2017-04-15 17:30 | 50104.006 | 20.016
Devonshire Building | 2017-04-15 17:45 | 50104.011 | 20.016
Devonshire Building | 2017-04-15 18:00 | 50104.536 | 2099.988
Devonshire Building | 2017-04-15 18:15 | 50104.541 | 20.016
Devonshire Building | 2017-04-15 18:30 | 50104.541 | 0
Devonshire Building | 2017-04-15 18:45 | 50104.546 | 20.016
Devonshire Building | 2017-04-15 19:00 | 50104.551 | 20.016
Devonshire Building | 2017-04-15 19:15 | 50104.551 | 0
Devonshire Building | 2017-04-15 19:30 | 50104.556 | 20.016
Devonshire Building | 2017-04-15 19:45 | 50104.561 | 20.016
Devonshire Building | 2017-04-15 20:00 | 50104.561 | 0
Devonshire Building | 2017-04-15 20:15 | 50104.566 | 20.016
Devonshire Building | 2017-04-15 20:30 | 50104.566 | 0
Devonshire Building | 2017-04-15 20:45 | 50104.571 | 20.016
Devonshire Building | 2017-04-15 21:00 | 50104.576 | 20.016
Devonshire Building | 2017-04-15 21:15 | 50104.581 | 20.016
Devonshire Building | 2017-04-15 21:30 | 50104.581 | 0
Devonshire Building | 2017-04-15 21:45 | 50104.586 | 20.016
Devonshire Building | 2017-04-15 22:00 | 50104.591 | 20.016
Devonshire Building | 2017-04-15 22:15 | 50104.591 | 0
Devonshire Building | 2017-04-15 22:30 | 50104.596 | 20.016
Devonshire Building | 2017-04-15 22:45 | 50104.596 | 0
Devonshire Building | 2017-04-15 23:00 | 50104.601 | 20.016
Devonshire Building | 2017-04-15 23:15 | 50104.606 | 20.016
Devonshire Building | 2017-04-15 23:30 | 50104.606 | 0
Devonshire Building | 2017-04-15 23:45 | 50104.611 | 20.016
Devonshire Building | 2017-04-16 | 50104.6094 | 0
Devonshire Building | 2017-04-16 00:15 | 50104.6144 | 20.016
Devonshire Building | 2017-04-16 00:30 | 50104.6194 | 20.016
Devonshire Building | 2017-04-16 00:45 | 50104.6194 | 0
Devonshire Building | 2017-04-16 01:00 | 50104.6244 | 20.016
Devonshire Building | 2017-04-16 01:15 | 50104.6244 | 0
Devonshire Building | 2017-04-16 01:30 | 50104.6294 | 20.016
Devonshire Building | 2017-04-16 01:45 | 50104.6344 | 20.016
Devonshire Building | 2017-04-16 02:00 | 50104.6344 | 0
Devonshire Building | 2017-04-16 02:15 | 50104.6394 | 20.016
Devonshire Building | 2017-04-16 02:30 | 50104.6394 | 0
Devonshire Building | 2017-04-16 02:45 | 50104.6444 | 20.016
Devonshire Building | 2017-04-16 03:00 | 50104.6494 | 20.016
Devonshire Building | 2017-04-16 03:15 | 50104.6494 | 0
Devonshire Building | 2017-04-16 03:30 | 50104.6544 | 20.016
Devonshire Building | 2017-04-16 03:45 | 50104.6594 | 20.016
Devonshire Building | 2017-04-16 04:00 | 50104.6594 | 0
Devonshire Building | 2017-04-16 04:15 | 50104.6644 | 20.016
Devonshire Building | 2017-04-16 04:30 | 50104.6644 | 0
Devonshire Building | 2017-04-16 04:45 | 50104.6694 | 20.016
Devonshire Building | 2017-04-16 05:00 | 50104.6744 | 20.016
Devonshire Building | 2017-04-16 05:15 | 50104.6744 | 0
Devonshire Building | 2017-04-16 05:30 | 50104.6794 | 20.016
Devonshire Building | 2017-04-16 05:45 | 50104.6794 | 0
Devonshire Building | 2017-04-16 06:00 | 50104.6844 | 20.016
Devonshire Building | 2017-04-16 06:15 | 50104.6894 | 20.016
Devonshire Building | 2017-04-16 06:30 | 50104.6894 | 0
Devonshire Building | 2017-04-16 06:45 | 50104.6944 | 20.016
Devonshire Building | 2017-04-16 07:00 | 50104.6944 | 0
Devonshire Building | 2017-04-16 07:15 | 50104.6995 | 20.016
Devonshire Building | 2017-04-16 07:30 | 50104.7045 | 20.016
Devonshire Building | 2017-04-16 07:45 | 50104.7045 | 0
Devonshire Building | 2017-04-16 08:00 | 50104.7195 | 60.012
Devonshire Building | 2017-04-16 08:15 | 50104.7395 | 79.992
Devonshire Building | 2017-04-16 08:30 | 50104.7545 | 60.012
Devonshire Building | 2017-04-16 08:45 | 50104.7745 | 79.992
Devonshire Building | 2017-04-16 09:00 | 50104.7945 | 79.992
Devonshire Building | 2017-04-16 09:15 | 50104.8145 | 79.992
Devonshire Building | 2017-04-16 09:30 | 50104.8345 | 79.992
Devonshire Building | 2017-04-16 09:45 | 50104.8544 | 79.992
Devonshire Building | 2017-04-16 10:00 | 50104.8644 | 39.996
Devonshire Building | 2017-04-16 10:15 | 50104.8695 | 20.016
Devonshire Building | 2017-04-16 10:30 | 50104.8695 | 0
Devonshire Building | 2017-04-16 10:45 | 50104.8745 | 20.016
Devonshire Building | 2017-04-16 11:00 | 50104.8795 | 20.016
Devonshire Building | 2017-04-16 11:15 | 50104.8795 | 0
Devonshire Building | 2017-04-16 11:30 | 50104.8845 | 20.016
Devonshire Building | 2017-04-16 11:45 | 50104.8895 | 20.016
Devonshire Building | 2017-04-16 12:00 | 50104.8945 | 20.016
Devonshire Building | 2017-04-16 12:15 | 50104.8995 | 20.016
Devonshire Building | 2017-04-16 12:30 | 50104.8995 | 0
Devonshire Building | 2017-04-16 12:45 | 50104.9045 | 20.016
Devonshire Building | 2017-04-16 13:00 | 50104.9095 | 20.016
Devonshire Building | 2017-04-16 13:15 | 50105.4395 | 2120.004
Devonshire Building | 2017-04-16 13:30 | 50105.4395 | 0
Devonshire Building | 2017-04-16 13:45 | 50105.4445 | 20.016
Devonshire Building | 2017-04-16 14:00 | 50105.4495 | 20.016
Devonshire Building | 2017-04-16 14:15 | 50105.4495 | 0
Devonshire Building | 2017-04-16 14:30 | 50105.4545 | 20.016
Devonshire Building | 2017-04-16 14:45 | 50105.4595 | 20.016
Devonshire Building | 2017-04-16 15:00 | 50105.4645 | 20.016
Devonshire Building | 2017-04-16 15:15 | 50105.4645 | 0
Devonshire Building | 2017-04-16 15:30 | 50105.4695 | 20.016
Devonshire Building | 2017-04-16 15:45 | 50105.4695 | 0
Devonshire Building | 2017-04-16 16:00 | 50105.4745 | 20.016
Devonshire Building | 2017-04-16 16:15 | 50105.4795 | 20.016
Devonshire Building | 2017-04-16 16:30 | 50105.4795 | 0
Devonshire Building | 2017-04-16 16:45 | 50105.4845 | 20.016
Devonshire Building | 2017-04-16 17:00 | 50105.4895 | 20.016
Devonshire Building | 2017-04-16 17:15 | 50105.4895 | 0
Devonshire Building | 2017-04-16 17:30 | 50105.4945 | 20.016
Devonshire Building | 2017-04-16 17:45 | 50105.4995 | 20.016
Devonshire Building | 2017-04-16 18:00 | 50105.4995 | 0
Devonshire Building | 2017-04-16 18:15 | 50105.5045 | 20.016
Devonshire Building | 2017-04-16 18:30 | 50105.5045 | 0
Devonshire Building | 2017-04-16 18:45 | 50105.5095 | 20.016
Devonshire Building | 2017-04-16 19:00 | 50105.5095 | 0
Devonshire Building | 2017-04-16 19:15 | 50105.5145 | 20.016
Devonshire Building | 2017-04-16 19:30 | 50105.5195 | 20.016
Devonshire Building | 2017-04-16 19:45 | 50105.5195 | 0
Devonshire Building | 2017-04-16 20:00 | 50105.5246 | 20.016
Devonshire Building | 2017-04-16 20:15 | 50105.5246 | 0
Devonshire Building | 2017-04-16 20:30 | 50105.5296 | 20.016
Devonshire Building | 2017-04-16 20:45 | 50105.5346 | 20.016
Devonshire Building | 2017-04-16 21:00 | 50105.5396 | 20.016
Devonshire Building | 2017-04-16 21:15 | 50105.5446 | 20.016
Devonshire Building | 2017-04-16 21:30 | 50105.5446 | 0
Devonshire Building | 2017-04-16 21:45 | 50105.5496 | 20.016
Devonshire Building | 2017-04-16 22:00 | 50105.5546 | 20.016
Devonshire Building | 2017-04-16 22:15 | 50105.5546 | 0
Devonshire Building | 2017-04-16 22:30 | 50105.5596 | 20.016
Devonshire Building | 2017-04-16 22:45 | 50105.5596 | 0
Devonshire Building | 2017-04-16 23:00 | 50105.5646 | 20.016
Devonshire Building | 2017-04-16 23:15 | 50105.5696 | 20.016
Devonshire Building | 2017-04-16 23:30 | 50105.5696 | 0
Devonshire Building | 2017-04-16 23:45 | 50105.5746 | 20.016
Devonshire Building | 2017-04-17 | 50105.5742 | 0
Devonshire Building | 2017-04-17 00:15 | 50105.5792 | 20.016
Devonshire Building | 2017-04-17 00:30 | 50105.5792 | 0
Devonshire Building | 2017-04-17 00:45 | 50105.5842 | 20.016
Devonshire Building | 2017-04-17 01:00 | 50105.5892 | 20.016
Devonshire Building | 2017-04-17 01:15 | 50105.5892 | 0
Devonshire Building | 2017-04-17 01:30 | 50105.5942 | 20.016
Devonshire Building | 2017-04-17 01:45 | 50105.5942 | 0
Devonshire Building | 2017-04-17 02:00 | 50105.5992 | 20.016
Devonshire Building | 2017-04-17 02:15 | 50105.5992 | 0
Devonshire Building | 2017-04-17 02:30 | 50105.6042 | 20.016
Devonshire Building | 2017-04-17 02:45 | 50105.6092 | 20.016
Devonshire Building | 2017-04-17 03:00 | 50105.6092 | 0
Devonshire Building | 2017-04-17 03:15 | 50105.6143 | 20.016
Devonshire Building | 2017-04-17 03:30 | 50105.6143 | 0
Devonshire Building | 2017-04-17 03:45 | 50105.6193 | 20.016
Devonshire Building | 2017-04-17 04:00 | 50105.6193 | 0
Devonshire Building | 2017-04-17 04:15 | 50105.6243 | 20.016
Devonshire Building | 2017-04-17 04:30 | 50105.6243 | 0
Devonshire Building | 2017-04-17 04:45 | 50105.6293 | 20.016
Devonshire Building | 2017-04-17 05:00 | 50105.6343 | 20.016
Devonshire Building | 2017-04-17 05:15 | 50105.6343 | 0
Devonshire Building | 2017-04-17 05:30 | 50105.6393 | 20.016
Devonshire Building | 2017-04-17 05:45 | 50105.6393 | 0
Devonshire Building | 2017-04-17 06:00 | 50105.6443 | 20.016
Devonshire Building | 2017-04-17 06:15 | 50105.6443 | 0
Devonshire Building | 2017-04-17 06:30 | 50105.6493 | 20.016
Devonshire Building | 2017-04-17 06:45 | 50105.6493 | 0
Devonshire Building | 2017-04-17 07:00 | 50105.6543 | 20.016
Devonshire Building | 2017-04-17 07:15 | 50105.6593 | 20.016
Devonshire Building | 2017-04-17 07:30 | 50105.6593 | 0
Devonshire Building | 2017-04-17 07:45 | 50105.6793 | 79.992
Devonshire Building | 2017-04-17 08:00 | 50105.6993 | 79.992
Devonshire Building | 2017-04-17 08:15 | 50105.7143 | 60.012
Devonshire Building | 2017-04-17 08:30 | 50105.7343 | 79.992
Devonshire Building | 2017-04-17 08:45 | 50105.7543 | 79.992
Devonshire Building | 2017-04-17 09:00 | 50105.7743 | 79.992
Devonshire Building | 2017-04-17 09:15 | 50105.7943 | 79.992
Devonshire Building | 2017-04-17 09:30 | 50105.8143 | 79.992
Devonshire Building | 2017-04-17 09:45 | 50105.8293 | 60.012
Devonshire Building | 2017-04-17 10:00 | 50105.8493 | 79.992
Devonshire Building | 2017-04-17 10:15 | 50105.8693 | 79.992
Devonshire Building | 2017-04-17 10:30 | 50105.8693 | 0
Devonshire Building | 2017-04-17 10:45 | 50105.8743 | 20.016
Devonshire Building | 2017-04-17 11:00 | 50105.8793 | 20.016
Devonshire Building | 2017-04-17 11:15 | 50105.8793 | 0
Devonshire Building | 2017-04-17 11:30 | 50105.8843 | 20.016
Devonshire Building | 2017-04-17 11:45 | 50105.8843 | 0
Devonshire Building | 2017-04-17 12:00 | 50105.8893 | 20.016
Devonshire Building | 2017-04-17 12:15 | 50106.1593 | 1080
Devonshire Building | 2017-04-17 12:30 | 50106.1643 | 20.016
Devonshire Building | 2017-04-17 12:45 | 50106.1693 | 20.016
Devonshire Building | 2017-04-17 13:00 | 50106.1693 | 0
Devonshire Building | 2017-04-17 13:15 | 50106.1743 | 20.016
Devonshire Building | 2017-04-17 13:30 | 50106.1793 | 20.016
Devonshire Building | 2017-04-17 13:45 | 50106.1793 | 0
Devonshire Building | 2017-04-17 14:00 | 50106.1843 | 20.016
Devonshire Building | 2017-04-17 14:15 | 50106.1893 | 20.016
Devonshire Building | 2017-04-17 14:30 | 50106.1893 | 0
Devonshire Building | 2017-04-17 14:45 | 50106.1943 | 20.016
Devonshire Building | 2017-04-17 15:00 | 50106.1993 | 20.016
Devonshire Building | 2017-04-17 15:15 | 50106.1993 | 0
Devonshire Building | 2017-04-17 15:30 | 50106.2043 | 20.016
Devonshire Building | 2017-04-17 15:45 | 50106.2093 | 20.016
Devonshire Building | 2017-04-17 16:00 | 50106.2143 | 20.016
Devonshire Building | 2017-04-17 16:15 | 50106.2193 | 20.016
Devonshire Building | 2017-04-17 16:30 | 50106.2193 | 0
Devonshire Building | 2017-04-17 16:45 | 50106.2243 | 20.016
Devonshire Building | 2017-04-17 17:00 | 50106.2293 | 20.016
Devonshire Building | 2017-04-17 17:15 | 50106.2293 | 0
Devonshire Building | 2017-04-17 17:30 | 50106.2344 | 20.016
Devonshire Building | 2017-04-17 17:45 | 50106.2394 | 20.016
Devonshire Building | 2017-04-17 18:00 | 50106.2394 | 0
Devonshire Building | 2017-04-17 18:15 | 50106.2444 | 20.016
Devonshire Building | 2017-04-17 18:30 | 50106.2444 | 0
Devonshire Building | 2017-04-17 18:45 | 50106.2494 | 20.016
Devonshire Building | 2017-04-17 19:00 | 50106.2494 | 0
Devonshire Building | 2017-04-17 19:15 | 50106.2544 | 20.016
Devonshire Building | 2017-04-17 19:30 | 50106.2594 | 20.016
Devonshire Building | 2017-04-17 19:45 | 50106.2594 | 0
Devonshire Building | 2017-04-17 20:00 | 50106.2644 | 20.016
Devonshire Building | 2017-04-17 20:15 | 50106.2644 | 0
Devonshire Building | 2017-04-17 20:30 | 50106.2694 | 20.016
Devonshire Building | 2017-04-17 20:45 | 50106.2744 | 20.016
Devonshire Building | 2017-04-17 21:00 | 50106.2994 | 100.008
Devonshire Building | 2017-04-17 21:15 | 50106.2994 | 0
Devonshire Building | 2017-04-17 21:30 | 50106.3044 | 20.016
Devonshire Building | 2017-04-17 21:45 | 50106.3044 | 0
Devonshire Building | 2017-04-17 22:00 | 50106.3094 | 20.016
Devonshire Building | 2017-04-17 22:15 | 50106.3144 | 20.016
Devonshire Building | 2017-04-17 22:30 | 50106.3144 | 0
Devonshire Building | 2017-04-17 22:45 | 50106.3194 | 20.016
Devonshire Building | 2017-04-17 23:00 | 50106.3194 | 0
Devonshire Building | 2017-04-17 23:15 | 50106.3244 | 20.016
Devonshire Building | 2017-04-17 23:30 | 50106.3294 | 20.016
Devonshire Building | 2017-04-17 23:45 | 50106.3294 | 0
Devonshire Building | 2017-04-18 | 50106.3359 | 20.016
Devonshire Building | 2017-04-18 00:15 | 50106.3359 | 0
Devonshire Building | 2017-04-18 00:30 | 50106.3409 | 20.016
Devonshire Building | 2017-04-18 00:45 | 50106.3409 | 0
Devonshire Building | 2017-04-18 01:00 | 50106.3459 | 20.016
Devonshire Building | 2017-04-18 01:15 | 50106.351 | 20.016
Devonshire Building | 2017-04-18 01:30 | 50106.351 | 0
Devonshire Building | 2017-04-18 01:45 | 50106.356 | 20.016
Devonshire Building | 2017-04-18 02:00 | 50106.356 | 0
Devonshire Building | 2017-04-18 02:15 | 50106.361 | 20.016
Devonshire Building | 2017-04-18 02:30 | 50106.361 | 0
Devonshire Building | 2017-04-18 02:45 | 50106.366 | 20.016
Devonshire Building | 2017-04-18 03:00 | 50106.366 | 0
Devonshire Building | 2017-04-18 03:15 | 50106.371 | 20.016
Devonshire Building | 2017-04-18 03:30 | 50106.376 | 20.016
Devonshire Building | 2017-04-18 03:45 | 50106.376 | 0
Devonshire Building | 2017-04-18 04:00 | 50106.381 | 20.016
Devonshire Building | 2017-04-18 04:15 | 50106.381 | 0
Devonshire Building | 2017-04-18 04:30 | 50106.386 | 20.016
Devonshire Building | 2017-04-18 04:45 | 50106.391 | 20.016
Devonshire Building | 2017-04-18 05:00 | 50106.391 | 0
Devonshire Building | 2017-04-18 05:15 | 50106.396 | 20.016
Devonshire Building | 2017-04-18 05:30 | 50106.401 | 20.016
Devonshire Building | 2017-04-18 05:45 | 50106.406 | 20.016
Devonshire Building | 2017-04-18 06:00 | 50106.411 | 20.016
Devonshire Building | 2017-04-18 06:15 | 50106.681 | 1080
Devonshire Building | 2017-04-18 06:30 | 50106.686 | 20.016
Devonshire Building | 2017-04-18 06:45 | 50106.691 | 20.016
Devonshire Building | 2017-04-18 07:00 | 50106.696 | 20.016
Devonshire Building | 2017-04-18 07:15 | 50106.701 | 20.016
Devonshire Building | 2017-04-18 07:30 | 50106.721 | 79.992
Devonshire Building | 2017-04-18 07:45 | 50106.761 | 159.984
Devonshire Building | 2017-04-18 08:00 | 50106.856 | 380.016
Devonshire Building | 2017-04-18 08:15 | 50106.881 | 100.008
Devonshire Building | 2017-04-18 08:30 | 50106.906 | 100.008
Devonshire Building | 2017-04-18 08:45 | 50106.926 | 79.992
Devonshire Building | 2017-04-18 09:00 | 50107.071 | 579.996
Devonshire Building | 2017-04-18 09:15 | 50107.271 | 799.992
Devonshire Building | 2017-04-18 09:30 | 50107.306 | 140.004
Devonshire Building | 2017-04-18 09:45 | 50107.346 | 159.984
Devonshire Building | 2017-04-18 10:00 | 50107.401 | 219.996
Devonshire Building | 2017-04-18 10:15 | 50107.746 | 1379.988
Devonshire Building | 2017-04-18 10:30 | 50107.821 | 299.988
Devonshire Building | 2017-04-18 10:45 | 50107.886 | 259.992
Devonshire Building | 2017-04-18 11:00 | 50107.956 | 280.008
Devonshire Building | 2017-04-18 11:15 | 50108.006 | 200.016
Devonshire Building | 2017-04-18 11:30 | 50108.046 | 159.984
Devonshire Building | 2017-04-18 11:45 | 50108.096 | 200.016
Devonshire Building | 2017-04-18 12:00 | 50108.421 | 1299.996
Devonshire Building | 2017-04-18 12:15 | 50108.461 | 159.984
Devonshire Building | 2017-04-18 12:30 | 50108.496 | 140.004
Devonshire Building | 2017-04-18 12:45 | 50108.536 | 159.984
Devonshire Building | 2017-04-18 13:00 | 50108.571 | 140.004
Devonshire Building | 2017-04-18 13:15 | 50108.611 | 159.984
Devonshire Building | 2017-04-18 13:30 | 50108.646 | 140.004
Devonshire Building | 2017-04-18 13:45 | 50108.681 | 140.004
Devonshire Building | 2017-04-18 14:00 | 50108.716 | 140.004
Devonshire Building | 2017-04-18 14:15 | 50109.051 | 1339.992
Devonshire Building | 2017-04-18 14:30 | 50109.076 | 100.008
Devonshire Building | 2017-04-18 14:45 | 50109.101 | 100.008
Devonshire Building | 2017-04-18 15:00 | 50109.121 | 79.992
Devonshire Building | 2017-04-18 15:15 | 50109.151 | 119.988
Devonshire Building | 2017-04-18 15:30 | 50109.176 | 100.008
Devonshire Building | 2017-04-18 15:45 | 50109.201 | 100.008
Devonshire Building | 2017-04-18 16:00 | 50109.226 | 100.008
Devonshire Building | 2017-04-18 16:15 | 50109.256 | 119.988
Devonshire Building | 2017-04-18 16:30 | 50109.561 | 1220.004
Devonshire Building | 2017-04-18 16:45 | 50109.581 | 79.992
Devonshire Building | 2017-04-18 17:00 | 50109.601 | 79.992
Devonshire Building | 2017-04-18 17:15 | 50109.621 | 79.992
Devonshire Building | 2017-04-18 17:30 | 50109.641 | 79.992
Devonshire Building | 2017-04-18 17:45 | 50109.666 | 100.008
Devonshire Building | 2017-04-18 18:00 | 50109.686 | 79.992
Devonshire Building | 2017-04-18 18:15 | 50109.706 | 79.992
Devonshire Building | 2017-04-18 18:30 | 50109.726 | 79.992
Devonshire Building | 2017-04-18 18:45 | 50109.741 | 60.012
Devonshire Building | 2017-04-18 19:00 | 50109.761 | 79.992
Devonshire Building | 2017-04-18 19:15 | 50109.776 | 60.012
Devonshire Building | 2017-04-18 19:30 | 50109.796 | 79.992
Devonshire Building | 2017-04-18 19:45 | 50109.826 | 119.988
Devonshire Building | 2017-04-18 20:00 | 50109.856 | 119.988
Devonshire Building | 2017-04-18 20:15 | 50109.891 | 140.004
Devonshire Building | 2017-04-18 20:30 | 50109.916 | 100.008
Devonshire Building | 2017-04-18 20:45 | 50109.946 | 119.988
Devonshire Building | 2017-04-18 21:00 | 50109.976 | 119.988
Devonshire Building | 2017-04-18 21:15 | 50110.001 | 100.008
Devonshire Building | 2017-04-18 21:30 | 50110.026 | 100.008
Devonshire Building | 2017-04-18 21:45 | 50110.051 | 100.008
Devonshire Building | 2017-04-18 22:00 | 50110.076 | 100.008
Devonshire Building | 2017-04-18 22:15 | 50110.101 | 100.008
Devonshire Building | 2017-04-18 22:30 | 50110.111 | 39.996
Devonshire Building | 2017-04-18 22:45 | 50110.116 | 20.016
Devonshire Building | 2017-04-18 23:00 | 50110.126 | 39.996
Devonshire Building | 2017-04-18 23:15 | 50110.136 | 39.996
Devonshire Building | 2017-04-18 23:30 | 50110.141 | 20.016
Devonshire Building | 2017-04-18 23:45 | 50110.151 | 39.996
Devonshire Building | 2017-04-19 | 50110.1562 | 20.016
Devonshire Building | 2017-04-19 00:15 | 50110.1662 | 39.996
Devonshire Building | 2017-04-19 00:30 | 50110.1713 | 20.016
Devonshire Building | 2017-04-19 00:45 | 50110.1813 | 39.996
Devonshire Building | 2017-04-19 01:00 | 50110.1863 | 20.016
Devonshire Building | 2017-04-19 01:15 | 50110.1963 | 39.996
Devonshire Building | 2017-04-19 01:30 | 50110.2013 | 20.016
Devonshire Building | 2017-04-19 01:45 | 50110.2063 | 20.016
Devonshire Building | 2017-04-19 02:00 | 50110.2163 | 39.996
Devonshire Building | 2017-04-19 02:15 | 50110.2213 | 20.016
Devonshire Building | 2017-04-19 02:30 | 50110.2263 | 20.016
Devonshire Building | 2017-04-19 02:45 | 50110.2313 | 20.016
Devonshire Building | 2017-04-19 03:00 | 50110.2363 | 20.016
Devonshire Building | 2017-04-19 03:15 | 50110.2413 | 20.016
Devonshire Building | 2017-04-19 03:30 | 50110.2513 | 39.996
Devonshire Building | 2017-04-19 03:45 | 50110.2563 | 20.016
Devonshire Building | 2017-04-19 04:00 | 50110.2613 | 20.016
Devonshire Building | 2017-04-19 04:15 | 50110.2663 | 20.016
Devonshire Building | 2017-04-19 04:30 | 50110.2713 | 20.016
Devonshire Building | 2017-04-19 04:45 | 50110.2763 | 20.016
Devonshire Building | 2017-04-19 05:00 | 50110.2863 | 39.996
Devonshire Building | 2017-04-19 05:15 | 50110.2913 | 20.016
Devonshire Building | 2017-04-19 05:30 | 50110.2963 | 20.016
Devonshire Building | 2017-04-19 05:45 | 50110.3063 | 39.996
Devonshire Building | 2017-04-19 06:00 | 50110.3113 | 20.016
Devonshire Building | 2017-04-19 06:15 | 50110.3213 | 39.996
Devonshire Building | 2017-04-19 06:30 | 50110.3263 | 20.016
Devonshire Building | 2017-04-19 06:45 | 50110.3363 | 39.996
Devonshire Building | 2017-04-19 07:00 | 50110.3413 | 20.016
Devonshire Building | 2017-04-19 07:15 | 50110.3513 | 39.996
Devonshire Building | 2017-04-19 07:30 | 50110.3663 | 60.012
Devonshire Building | 2017-04-19 07:45 | 50110.6213 | 1019.988
Devonshire Building | 2017-04-19 08:00 | 50110.6663 | 180
Devonshire Building | 2017-04-19 08:15 | 50110.6813 | 60.012
Devonshire Building | 2017-04-19 08:30 | 50110.6863 | 20.016
Devonshire Building | 2017-04-19 08:45 | 50110.6963 | 39.996
Devonshire Building | 2017-04-19 09:00 | 50110.7013 | 20.016
Devonshire Building | 2017-04-19 09:15 | 50110.7163 | 60.012
Devonshire Building | 2017-04-19 09:30 | 50110.7413 | 100.008
Devonshire Building | 2017-04-19 09:45 | 50111.0913 | 1400.004
Devonshire Building | 2017-04-19 10:00 | 50111.1513 | 240.012
Devonshire Building | 2017-04-19 10:15 | 50111.2163 | 259.992
Devonshire Building | 2017-04-19 10:30 | 50111.2813 | 259.992
Devonshire Building | 2017-04-19 10:45 | 50111.3363 | 219.996
Devonshire Building | 2017-04-19 11:00 | 50111.3813 | 180
Devonshire Building | 2017-04-19 11:15 | 50111.5313 | 600.012
Devonshire Building | 2017-04-19 11:30 | 50111.7463 | 860.004
Devonshire Building | 2017-04-19 11:45 | 50111.7763 | 119.988
Devonshire Building | 2017-04-19 12:00 | 50111.8063 | 119.988
Devonshire Building | 2017-04-19 12:15 | 50111.8413 | 140.004
Devonshire Building | 2017-04-19 12:30 | 50111.8763 | 140.004
Devonshire Building | 2017-04-19 12:45 | 50111.9113 | 140.004
Devonshire Building | 2017-04-19 13:00 | 50111.9463 | 140.004
Devonshire Building | 2017-04-19 13:15 | 50111.9863 | 159.984
Devonshire Building | 2017-04-19 13:30 | 50112.3213 | 1339.992
Devonshire Building | 2017-04-19 13:45 | 50112.3763 | 219.996
Devonshire Building | 2017-04-19 14:00 | 50112.4363 | 240.012
Devonshire Building | 2017-04-19 14:15 | 50112.4963 | 240.012
Devonshire Building | 2017-04-19 14:30 | 50112.5563 | 240.012
Devonshire Building | 2017-04-19 14:45 | 50112.6163 | 240.012
Devonshire Building | 2017-04-19 15:00 | 50112.6713 | 219.996
Devonshire Building | 2017-04-19 15:15 | 50112.7563 | 339.984
Devonshire Building | 2017-04-19 15:30 | 50113.3163 | 2239.992
Devonshire Building | 2017-04-19 15:45 | 50113.4313 | 460.008
Devonshire Building | 2017-04-19 16:00 | 50113.6063 | 699.984
Devonshire Building | 2017-04-19 16:15 | 50113.7363 | 519.984
Devonshire Building | 2017-04-19 16:30 | 50113.8263 | 360
Devonshire Building | 2017-04-19 16:45 | 50113.8863 | 240.012
Devonshire Building | 2017-04-19 17:00 | 50113.9413 | 219.996
Devonshire Building | 2017-04-19 17:15 | 50113.9813 | 159.984
Devonshire Building | 2017-04-19 17:30 | 50114.0163 | 140.004
Devonshire Building | 2017-04-19 17:45 | 50114.0463 | 119.988
Devonshire Building | 2017-04-19 18:00 | 50114.0713 | 100.008
Devonshire Building | 2017-04-19 18:15 | 50114.0963 | 100.008
Devonshire Building | 2017-04-19 18:30 | 50114.1163 | 79.992
Devonshire Building | 2017-04-19 18:45 | 50114.1363 | 79.992
Devonshire Building | 2017-04-19 19:00 | 50114.1563 | 79.992
Devonshire Building | 2017-04-19 19:15 | 50114.1713 | 60.012
Devonshire Building | 2017-04-19 19:30 | 50114.1863 | 60.012
Devonshire Building | 2017-04-19 19:45 | 50114.2013 | 60.012
Devonshire Building | 2017-04-19 20:00 | 50114.2113 | 39.996
Devonshire Building | 2017-04-19 20:15 | 50114.2263 | 60.012
Devonshire Building | 2017-04-19 20:30 | 50114.2363 | 39.996
Devonshire Building | 2017-04-19 20:45 | 50114.2513 | 60.012
Devonshire Building | 2017-04-19 21:00 | 50114.2763 | 100.008
Devonshire Building | 2017-04-19 21:15 | 50114.2813 | 20.016
Devonshire Building | 2017-04-19 21:30 | 50114.2863 | 20.016
Devonshire Building | 2017-04-19 21:45 | 50114.8063 | 2080.008
Devonshire Building | 2017-04-19 22:00 | 50114.8063 | 0
Devonshire Building | 2017-04-19 22:15 | 50114.8113 | 20.016
Devonshire Building | 2017-04-19 22:30 | 50114.8164 | 20.016
Devonshire Building | 2017-04-19 22:45 | 50114.8164 | 0
Devonshire Building | 2017-04-19 23:00 | 50114.8214 | 20.016
Devonshire Building | 2017-04-19 23:15 | 50114.8264 | 20.016
Devonshire Building | 2017-04-19 23:30 | 50114.8264 | 0
Devonshire Building | 2017-04-19 23:45 | 50114.8314 | 20.016
Devonshire Building | 2017-04-20 | 50114.8281 | 0
Devonshire Building | 2017-04-20 00:15 | 50114.8331 | 20.016
Devonshire Building | 2017-04-20 00:30 | 50114.8381 | 20.016
Devonshire Building | 2017-04-20 00:45 | 50114.8381 | 0
Devonshire Building | 2017-04-20 01:00 | 50114.8431 | 20.016
Devonshire Building | 2017-04-20 01:15 | 50114.8481 | 20.016
Devonshire Building | 2017-04-20 01:30 | 50114.8481 | 0
Devonshire Building | 2017-04-20 01:45 | 50114.8532 | 20.016
Devonshire Building | 2017-04-20 02:00 | 50114.8532 | 0
Devonshire Building | 2017-04-20 02:15 | 50114.8582 | 20.016
Devonshire Building | 2017-04-20 02:30 | 50114.8632 | 20.016
Devonshire Building | 2017-04-20 02:45 | 50114.8632 | 0
Devonshire Building | 2017-04-20 03:00 | 50114.8682 | 20.016
Devonshire Building | 2017-04-20 03:15 | 50114.8682 | 0
Devonshire Building | 2017-04-20 03:30 | 50114.8732 | 20.016
Devonshire Building | 2017-04-20 03:45 | 50114.8782 | 20.016
Devonshire Building | 2017-04-20 04:00 | 50114.8782 | 0
Devonshire Building | 2017-04-20 04:15 | 50114.8832 | 20.016
Devonshire Building | 2017-04-20 04:30 | 50114.8832 | 0
Devonshire Building | 2017-04-20 04:45 | 50114.8882 | 20.016
Devonshire Building | 2017-04-20 05:00 | 50114.8932 | 20.016
Devonshire Building | 2017-04-20 05:15 | 50114.8982 | 20.016
Devonshire Building | 2017-04-20 05:30 | 50114.8982 | 0
Devonshire Building | 2017-04-20 05:45 | 50114.9082 | 39.996
Devonshire Building | 2017-04-20 06:00 | 50114.9082 | 0
Devonshire Building | 2017-04-20 06:15 | 50114.9232 | 60.012
Devonshire Building | 2017-04-20 06:30 | 50114.9482 | 100.008
Devonshire Building | 2017-04-20 06:45 | 50114.9532 | 20.016
Devonshire Building | 2017-04-20 07:00 | 50114.9582 | 20.016
Devonshire Building | 2017-04-20 07:15 | 50114.9632 | 20.016
Devonshire Building | 2017-04-20 07:30 | 50114.9782 | 60.012
Devonshire Building | 2017-04-20 07:45 | 50114.9832 | 20.016
Devonshire Building | 2017-04-20 08:00 | 50115.0132 | 119.988
Devonshire Building | 2017-04-20 08:15 | 50115.0282 | 60.012
Devonshire Building | 2017-04-20 08:30 | 50115.0482 | 79.992
Devonshire Building | 2017-04-20 08:45 | 50115.5982 | 2199.996
Devonshire Building | 2017-04-20 09:00 | 50115.6382 | 159.984
Devonshire Building | 2017-04-20 09:15 | 50115.6832 | 180
Devonshire Building | 2017-04-20 09:30 | 50115.7332 | 200.016
Devonshire Building | 2017-04-20 09:45 | 50115.8132 | 320.004
Devonshire Building | 2017-04-20 10:00 | 50116.4382 | 2499.984
Devonshire Building | 2017-04-20 10:15 | 50116.5182 | 320.004
Devonshire Building | 2017-04-20 10:30 | 50116.5882 | 280.008
Devonshire Building | 2017-04-20 10:45 | 50116.6632 | 299.988
Devonshire Building | 2017-04-20 11:00 | 50116.7332 | 280.008
Devonshire Building | 2017-04-20 11:15 | 50117.3232 | 2360.016
Devonshire Building | 2017-04-20 11:30 | 50117.4282 | 420.012
Devonshire Building | 2017-04-20 11:45 | 50117.5732 | 579.996
Devonshire Building | 2017-04-20 12:00 | 50117.6932 | 479.988
Devonshire Building | 2017-04-20 12:15 | 50117.7882 | 380.016
Devonshire Building | 2017-04-20 12:30 | 50117.8682 | 320.004
Devonshire Building | 2017-04-20 12:45 | 50118.4232 | 2220.012
Devonshire Building | 2017-04-20 13:00 | 50118.5132 | 360
Devonshire Building | 2017-04-20 13:15 | 50118.5582 | 180
Devonshire Building | 2017-04-20 13:30 | 50118.5982 | 159.984
Devonshire Building | 2017-04-20 13:45 | 50118.6332 | 140.004
Devonshire Building | 2017-04-20 14:00 | 50118.6732 | 159.984
Devonshire Building | 2017-04-20 14:15 | 50118.7082 | 140.004
Devonshire Building | 2017-04-20 14:30 | 50119.3182 | 2440.008
Devonshire Building | 2017-04-20 14:45 | 50119.3632 | 180
Devonshire Building | 2017-04-20 15:00 | 50119.3982 | 140.004
Devonshire Building | 2017-04-20 15:15 | 50119.4382 | 159.984
Devonshire Building | 2017-04-20 15:30 | 50119.4782 | 159.984
Devonshire Building | 2017-04-20 15:45 | 50119.5182 | 159.984
Devonshire Building | 2017-04-20 16:00 | 50119.6332 | 460.008
Devonshire Building | 2017-04-20 16:15 | 50120.1432 | 2040.012
Devonshire Building | 2017-04-20 16:30 | 50120.1782 | 140.004
Devonshire Building | 2017-04-20 16:45 | 50120.2132 | 140.004
Devonshire Building | 2017-04-20 17:00 | 50120.2532 | 159.984
Devonshire Building | 2017-04-20 17:15 | 50120.2882 | 140.004
Devonshire Building | 2017-04-20 17:30 | 50120.3232 | 140.004
Devonshire Building | 2017-04-20 17:45 | 50120.3532 | 119.988
Devonshire Building | 2017-04-20 18:00 | 50120.3882 | 140.004
Devonshire Building | 2017-04-20 18:15 | 50120.4182 | 119.988
Devonshire Building | 2017-04-20 18:30 | 50120.4532 | 140.004
Devonshire Building | 2017-04-20 18:45 | 50120.4832 | 119.988
Devonshire Building | 2017-04-20 19:00 | 50120.5132 | 119.988
Devonshire Building | 2017-04-20 19:15 | 50120.5432 | 119.988
Devonshire Building | 2017-04-20 19:30 | 50120.5732 | 119.988
Devonshire Building | 2017-04-20 19:45 | 50120.6032 | 119.988
Devonshire Building | 2017-04-20 20:00 | 50120.6332 | 119.988
Devonshire Building | 2017-04-20 20:15 | 50120.6632 | 119.988
Devonshire Building | 2017-04-20 20:30 | 50120.6932 | 119.988
Devonshire Building | 2017-04-20 20:45 | 50120.7182 | 100.008
Devonshire Building | 2017-04-20 21:00 | 50120.7582 | 159.984
Devonshire Building | 2017-04-20 21:15 | 50120.7782 | 79.992
Devonshire Building | 2017-04-20 21:30 | 50120.7932 | 60.012
Devonshire Building | 2017-04-20 21:45 | 50120.8132 | 79.992
Devonshire Building | 2017-04-20 22:00 | 50120.8282 | 60.012
Devonshire Building | 2017-04-20 22:15 | 50120.8432 | 60.012
Devonshire Building | 2017-04-20 22:30 | 50120.8632 | 79.992
Devonshire Building | 2017-04-20 22:45 | 50120.8782 | 60.012
Devonshire Building | 2017-04-20 23:00 | 50120.8932 | 60.012
Devonshire Building | 2017-04-20 23:15 | 50120.9032 | 39.996
Devonshire Building | 2017-04-20 23:30 | 50120.9182 | 60.012
Devonshire Building | 2017-04-20 23:45 | 50120.9332 | 60.012
Devonshire Building | 2017-04-21 | 50120.9453 | 39.996
Devonshire Building | 2017-04-21 00:15 | 50120.9603 | 60.012
Devonshire Building | 2017-04-21 00:30 | 50120.9703 | 39.996
Devonshire Building | 2017-04-21 00:45 | 50120.9803 | 39.996
Devonshire Building | 2017-04-21 01:00 | 50120.9953 | 60.012
Devonshire Building | 2017-04-21 01:15 | 50121.0053 | 39.996
Devonshire Building | 2017-04-21 01:30 | 50121.0153 | 39.996
Devonshire Building | 2017-04-21 01:45 | 50121.0253 | 39.996
Devonshire Building | 2017-04-21 02:00 | 50121.0303 | 20.016
Devonshire Building | 2017-04-21 02:15 | 50121.0403 | 39.996
Devonshire Building | 2017-04-21 02:30 | 50121.0503 | 39.996
Devonshire Building | 2017-04-21 02:45 | 50121.0603 | 39.996
Devonshire Building | 2017-04-21 03:00 | 50121.0653 | 20.016
Devonshire Building | 2017-04-21 03:15 | 50121.0753 | 39.996
Devonshire Building | 2017-04-21 03:30 | 50121.0803 | 20.016
Devonshire Building | 2017-04-21 03:45 | 50121.0903 | 39.996
Devonshire Building | 2017-04-21 04:00 | 50121.0953 | 20.016
Devonshire Building | 2017-04-21 04:15 | 50121.1053 | 39.996
Devonshire Building | 2017-04-21 04:30 | 50121.1103 | 20.016
Devonshire Building | 2017-04-21 04:45 | 50121.1153 | 20.016
Devonshire Building | 2017-04-21 05:00 | 50121.1253 | 39.996
Devonshire Building | 2017-04-21 05:15 | 50121.1303 | 20.016
Devonshire Building | 2017-04-21 05:30 | 50121.1353 | 20.016
Devonshire Building | 2017-04-21 05:45 | 50121.1453 | 39.996
Devonshire Building | 2017-04-21 06:00 | 50121.1503 | 20.016
Devonshire Building | 2017-04-21 06:15 | 50121.1553 | 20.016
Devonshire Building | 2017-04-21 06:30 | 50121.1653 | 39.996
Devonshire Building | 2017-04-21 06:45 | 50121.4353 | 1080
Devonshire Building | 2017-04-21 07:00 | 50121.7203 | 1140.012
Devonshire Building | 2017-04-21 07:15 | 50121.7253 | 20.016
Devonshire Building | 2017-04-21 07:30 | 50121.7353 | 39.996
Devonshire Building | 2017-04-21 07:45 | 50121.7553 | 79.992
Devonshire Building | 2017-04-21 08:00 | 50121.7953 | 159.984
Devonshire Building | 2017-04-21 08:15 | 50121.8153 | 79.992
Devonshire Building | 2017-04-21 08:30 | 50121.8403 | 100.008
Devonshire Building | 2017-04-21 08:45 | 50121.8653 | 100.008
Devonshire Building | 2017-04-21 09:00 | 50121.8903 | 100.008
Devonshire Building | 2017-04-21 09:15 | 50121.9253 | 140.004
Devonshire Building | 2017-04-21 09:30 | 50122.3503 | 1699.992
Devonshire Building | 2017-04-21 09:45 | 50122.6053 | 1019.988
Devonshire Building | 2017-04-21 10:00 | 50122.7003 | 380.016
Devonshire Building | 2017-04-21 10:15 | 50122.7903 | 360
Devonshire Building | 2017-04-21 10:30 | 50122.8703 | 320.004
Devonshire Building | 2017-04-21 10:45 | 50122.9353 | 259.992
Devonshire Building | 2017-04-21 11:00 | 50122.9853 | 200.016
Devonshire Building | 2017-04-21 11:15 | 50123.0303 | 180
Devonshire Building | 2017-04-21 11:30 | 50123.0753 | 180
Devonshire Building | 2017-04-21 11:45 | 50123.6353 | 2239.992
Devonshire Building | 2017-04-21 12:00 | 50123.7153 | 320.004
Devonshire Building | 2017-04-21 12:15 | 50123.7503 | 140.004
Devonshire Building | 2017-04-21 12:30 | 50123.7903 | 159.984
Devonshire Building | 2017-04-21 12:45 | 50123.8253 | 140.004
Devonshire Building | 2017-04-21 13:00 | 50123.8553 | 119.988
Devonshire Building | 2017-04-21 13:15 | 50123.9053 | 200.016
Devonshire Building | 2017-04-21 13:30 | 50123.9453 | 159.984
Devonshire Building | 2017-04-21 13:45 | 50123.9803 | 140.004
Devonshire Building | 2017-04-21 14:00 | 50124.5353 | 2220.012
Devonshire Building | 2017-04-21 14:15 | 50124.6304 | 380.016
Devonshire Building | 2017-04-21 14:30 | 50124.6804 | 200.016
Devonshire Building | 2017-04-21 14:45 | 50124.7104 | 119.988
Devonshire Building | 2017-04-21 15:00 | 50124.7403 | 119.988
Devonshire Building | 2017-04-21 15:15 | 50124.7703 | 119.988
Devonshire Building | 2017-04-21 15:30 | 50124.8003 | 119.988
Devonshire Building | 2017-04-21 15:45 | 50124.8303 | 119.988
Devonshire Building | 2017-04-21 16:00 | 50124.8553 | 100.008
Devonshire Building | 2017-04-21 16:15 | 50125.4253 | 2279.988
Devonshire Building | 2017-04-21 16:30 | 50125.4403 | 60.012
Devonshire Building | 2017-04-21 16:45 | 50125.4553 | 60.012
Devonshire Building | 2017-04-21 17:00 | 50125.4653 | 39.996
Devonshire Building | 2017-04-21 17:15 | 50125.4803 | 60.012
Devonshire Building | 2017-04-21 17:30 | 50125.4953 | 60.012
Devonshire Building | 2017-04-21 17:45 | 50125.5053 | 39.996
Devonshire Building | 2017-04-21 18:00 | 50125.5204 | 60.012
Devonshire Building | 2017-04-21 18:15 | 50125.5404 | 79.992
Devonshire Building | 2017-04-21 18:30 | 50125.5554 | 60.012
Devonshire Building | 2017-04-21 18:45 | 50125.5654 | 39.996
Devonshire Building | 2017-04-21 19:00 | 50125.5804 | 60.012
Devonshire Building | 2017-04-21 19:15 | 50125.5954 | 60.012
Devonshire Building | 2017-04-21 19:30 | 50125.6104 | 60.012
Devonshire Building | 2017-04-21 19:45 | 50125.6204 | 39.996
Devonshire Building | 2017-04-21 20:00 | 50125.6354 | 60.012
Devonshire Building | 2017-04-21 20:15 | 50125.6454 | 39.996
Devonshire Building | 2017-04-21 20:30 | 50125.6554 | 39.996
Devonshire Building | 2017-04-21 20:45 | 50125.6704 | 60.012
Devonshire Building | 2017-04-21 21:00 | 50125.6904 | 79.992
Devonshire Building | 2017-04-21 21:15 | 50125.7004 | 39.996
Devonshire Building | 2017-04-21 21:30 | 50125.7104 | 39.996
Devonshire Building | 2017-04-21 21:45 | 50125.7154 | 20.016
Devonshire Building | 2017-04-21 22:00 | 50125.7254 | 39.996
Devonshire Building | 2017-04-21 22:15 | 50125.7354 | 39.996
Devonshire Building | 2017-04-21 22:30 | 50125.7454 | 39.996
Devonshire Building | 2017-04-21 22:45 | 50125.7554 | 39.996
Devonshire Building | 2017-04-21 23:00 | 50125.7604 | 20.016
Devonshire Building | 2017-04-21 23:15 | 50125.7704 | 39.996
Devonshire Building | 2017-04-21 23:30 | 50125.7804 | 39.996
Devonshire Building | 2017-04-21 23:45 | 50125.7854 | 20.016
Devonshire Building | 2017-04-22 | 50125.7969 | 39.996
Devonshire Building | 2017-04-22 00:15 | 50125.8019 | 20.016
Devonshire Building | 2017-04-22 00:30 | 50125.8119 | 39.996
Devonshire Building | 2017-04-22 00:45 | 50125.8219 | 39.996
Devonshire Building | 2017-04-22 01:00 | 50125.8269 | 20.016
Devonshire Building | 2017-04-22 01:15 | 50125.8369 | 39.996
Devonshire Building | 2017-04-22 01:30 | 50125.8419 | 20.016
Devonshire Building | 2017-04-22 01:45 | 50125.8519 | 39.996
Devonshire Building | 2017-04-22 02:00 | 50125.8569 | 20.016
Devonshire Building | 2017-04-22 02:15 | 50125.8669 | 39.996
Devonshire Building | 2017-04-22 02:30 | 50125.8719 | 20.016
Devonshire Building | 2017-04-22 02:45 | 50125.8819 | 39.996
Devonshire Building | 2017-04-22 03:00 | 50125.8869 | 20.016
Devonshire Building | 2017-04-22 03:15 | 50125.8919 | 20.016
Devonshire Building | 2017-04-22 03:30 | 50125.9019 | 39.996
Devonshire Building | 2017-04-22 03:45 | 50125.9069 | 20.016
Devonshire Building | 2017-04-22 04:00 | 50125.9169 | 39.996
Devonshire Building | 2017-04-22 04:15 | 50125.9219 | 20.016
Devonshire Building | 2017-04-22 04:30 | 50125.9319 | 39.996
Devonshire Building | 2017-04-22 04:45 | 50125.9369 | 20.016
Devonshire Building | 2017-04-22 05:00 | 50125.9419 | 20.016
Devonshire Building | 2017-04-22 05:15 | 50125.9519 | 39.996
Devonshire Building | 2017-04-22 05:30 | 50125.9569 | 20.016
Devonshire Building | 2017-04-22 05:45 | 50125.9619 | 20.016
Devonshire Building | 2017-04-22 06:00 | 50125.9719 | 39.996
Devonshire Building | 2017-04-22 06:15 | 50125.9769 | 20.016
Devonshire Building | 2017-04-22 06:30 | 50125.9819 | 20.016
Devonshire Building | 2017-04-22 06:45 | 50125.9919 | 39.996
Devonshire Building | 2017-04-22 07:00 | 50125.9969 | 20.016
Devonshire Building | 2017-04-22 07:15 | 50126.0069 | 39.996
Devonshire Building | 2017-04-22 07:30 | 50126.0119 | 20.016
Devonshire Building | 2017-04-22 07:45 | 50126.0269 | 60.012
Devonshire Building | 2017-04-22 08:00 | 50126.0519 | 100.008
Devonshire Building | 2017-04-22 08:15 | 50126.0719 | 79.992
Devonshire Building | 2017-04-22 08:30 | 50126.0919 | 79.992
Devonshire Building | 2017-04-22 08:45 | 50126.1169 | 100.008
Devonshire Building | 2017-04-22 09:00 | 50126.1369 | 79.992
Devonshire Building | 2017-04-22 09:15 | 50126.1619 | 100.008
Devonshire Building | 2017-04-22 09:30 | 50126.1819 | 79.992
Devonshire Building | 2017-04-22 09:45 | 50126.2069 | 100.008
Devonshire Building | 2017-04-22 10:00 | 50126.2269 | 79.992
Devonshire Building | 2017-04-22 10:15 | 50126.2469 | 79.992
Devonshire Building | 2017-04-22 10:30 | 50126.2569 | 39.996
Devonshire Building | 2017-04-22 10:45 | 50126.2619 | 20.016
Devonshire Building | 2017-04-22 11:00 | 50126.2719 | 39.996
Devonshire Building | 2017-04-22 11:15 | 50126.2769 | 20.016
Devonshire Building | 2017-04-22 11:30 | 50126.2819 | 20.016
Devonshire Building | 2017-04-22 11:45 | 50126.5619 | 1119.996
Devonshire Building | 2017-04-22 12:00 | 50126.5619 | 0
Devonshire Building | 2017-04-22 12:15 | 50126.5669 | 20.016
Devonshire Building | 2017-04-22 12:30 | 50126.572 | 20.016
Devonshire Building | 2017-04-22 12:45 | 50126.572 | 0
Devonshire Building | 2017-04-22 13:00 | 50126.577 | 20.016
Devonshire Building | 2017-04-22 13:15 | 50126.582 | 20.016
Devonshire Building | 2017-04-22 13:30 | 50126.587 | 20.016
Devonshire Building | 2017-04-22 13:45 | 50126.587 | 0
Devonshire Building | 2017-04-22 14:00 | 50126.592 | 20.016
Devonshire Building | 2017-04-22 14:15 | 50126.597 | 20.016
Devonshire Building | 2017-04-22 14:30 | 50126.602 | 20.016
Devonshire Building | 2017-04-22 14:45 | 50126.607 | 20.016
Devonshire Building | 2017-04-22 15:00 | 50126.612 | 20.016
Devonshire Building | 2017-04-22 15:15 | 50126.612 | 0
Devonshire Building | 2017-04-22 15:30 | 50126.617 | 20.016
Devonshire Building | 2017-04-22 15:45 | 50126.622 | 20.016
Devonshire Building | 2017-04-22 16:00 | 50126.627 | 20.016
Devonshire Building | 2017-04-22 16:15 | 50126.627 | 0
Devonshire Building | 2017-04-22 16:30 | 50126.632 | 20.016
Devonshire Building | 2017-04-22 16:45 | 50126.637 | 20.016
Devonshire Building | 2017-04-22 17:00 | 50126.642 | 20.016
Devonshire Building | 2017-04-22 17:15 | 50126.647 | 20.016
Devonshire Building | 2017-04-22 17:30 | 50126.652 | 20.016
Devonshire Building | 2017-04-22 17:45 | 50126.652 | 0
Devonshire Building | 2017-04-22 18:00 | 50126.657 | 20.016
Devonshire Building | 2017-04-22 18:15 | 50126.662 | 20.016
Devonshire Building | 2017-04-22 18:30 | 50126.667 | 20.016
Devonshire Building | 2017-04-22 18:45 | 50126.672 | 20.016
Devonshire Building | 2017-04-22 19:00 | 50126.677 | 20.016
Devonshire Building | 2017-04-22 19:15 | 50126.682 | 20.016
Devonshire Building | 2017-04-22 19:30 | 50126.687 | 20.016
Devonshire Building | 2017-04-22 19:45 | 50126.692 | 20.016
Devonshire Building | 2017-04-22 20:00 | 50126.692 | 0
Devonshire Building | 2017-04-22 20:15 | 50126.6971 | 20.016
Devonshire Building | 2017-04-22 20:30 | 50126.7021 | 20.016
Devonshire Building | 2017-04-22 20:45 | 50126.7071 | 20.016
Devonshire Building | 2017-04-22 21:00 | 50126.7171 | 39.996
Devonshire Building | 2017-04-22 21:15 | 50126.7221 | 20.016
Devonshire Building | 2017-04-22 21:30 | 50126.7271 | 20.016
Devonshire Building | 2017-04-22 21:45 | 50126.7321 | 20.016
Devonshire Building | 2017-04-22 22:00 | 50126.7371 | 20.016
Devonshire Building | 2017-04-22 22:15 | 50126.7371 | 0
Devonshire Building | 2017-04-22 22:30 | 50126.7421 | 20.016
Devonshire Building | 2017-04-22 22:45 | 50126.7471 | 20.016
Devonshire Building | 2017-04-22 23:00 | 50126.7521 | 20.016
Devonshire Building | 2017-04-22 23:15 | 50126.7571 | 20.016
Devonshire Building | 2017-04-22 23:30 | 50126.7571 | 0
Devonshire Building | 2017-04-22 23:45 | 50126.7621 | 20.016
Devonshire Building | 2017-04-23 | 50126.7656 | 20.016
Devonshire Building | 2017-04-23 00:15 | 50126.7706 | 20.016
Devonshire Building | 2017-04-23 00:30 | 50126.7706 | 0
Devonshire Building | 2017-04-23 00:45 | 50126.7756 | 20.016
Devonshire Building | 2017-04-23 01:00 | 50126.7806 | 20.016
Devonshire Building | 2017-04-23 01:15 | 50126.7806 | 0
Devonshire Building | 2017-04-23 01:30 | 50126.7856 | 20.016
Devonshire Building | 2017-04-23 01:45 | 50126.7907 | 20.016
Devonshire Building | 2017-04-23 02:00 | 50126.7957 | 20.016
Devonshire Building | 2017-04-23 02:15 | 50126.7957 | 0
Devonshire Building | 2017-04-23 02:30 | 50126.8007 | 20.016
Devonshire Building | 2017-04-23 02:45 | 50126.8057 | 20.016
Devonshire Building | 2017-04-23 03:00 | 50126.8057 | 0
Devonshire Building | 2017-04-23 03:15 | 50126.8107 | 20.016
Devonshire Building | 2017-04-23 03:30 | 50126.8157 | 20.016
Devonshire Building | 2017-04-23 03:45 | 50126.8207 | 20.016
Devonshire Building | 2017-04-23 04:00 | 50126.8207 | 0
Devonshire Building | 2017-04-23 04:15 | 50126.8257 | 20.016
Devonshire Building | 2017-04-23 04:30 | 50126.8307 | 20.016
Devonshire Building | 2017-04-23 04:45 | 50126.8307 | 0
Devonshire Building | 2017-04-23 05:00 | 50126.8357 | 20.016
Devonshire Building | 2017-04-23 05:15 | 50126.8407 | 20.016
Devonshire Building | 2017-04-23 05:30 | 50126.8407 | 0
Devonshire Building | 2017-04-23 05:45 | 50126.8457 | 20.016
Devonshire Building | 2017-04-23 06:00 | 50126.8507 | 20.016
Devonshire Building | 2017-04-23 06:15 | 50126.8507 | 0
Devonshire Building | 2017-04-23 06:30 | 50126.8557 | 20.016
Devonshire Building | 2017-04-23 06:45 | 50126.8607 | 20.016
Devonshire Building | 2017-04-23 07:00 | 50126.8607 | 0
Devonshire Building | 2017-04-23 07:15 | 50126.8657 | 20.016
Devonshire Building | 2017-04-23 07:30 | 50126.8657 | 0
Devonshire Building | 2017-04-23 07:45 | 50126.8807 | 60.012
Devonshire Building | 2017-04-23 08:00 | 50126.9007 | 79.992
Devonshire Building | 2017-04-23 08:15 | 50126.9207 | 79.992
Devonshire Building | 2017-04-23 08:30 | 50126.9407 | 79.992
Devonshire Building | 2017-04-23 08:45 | 50126.9607 | 79.992
Devonshire Building | 2017-04-23 09:00 | 50126.9757 | 60.012
Devonshire Building | 2017-04-23 09:15 | 50126.9957 | 79.992
Devonshire Building | 2017-04-23 09:30 | 50127.0157 | 79.992
Devonshire Building | 2017-04-23 09:45 | 50127.0357 | 79.992
Devonshire Building | 2017-04-23 10:00 | 50127.0557 | 79.992
Devonshire Building | 2017-04-23 10:15 | 50127.0657 | 39.996
Devonshire Building | 2017-04-23 10:30 | 50127.0707 | 20.016
Devonshire Building | 2017-04-23 10:45 | 50127.0707 | 0
Devonshire Building | 2017-04-23 11:00 | 50127.0757 | 20.016
Devonshire Building | 2017-04-23 11:15 | 50127.0757 | 0
Devonshire Building | 2017-04-23 11:30 | 50127.0807 | 20.016
Devonshire Building | 2017-04-23 11:45 | 50127.0857 | 20.016
Devonshire Building | 2017-04-23 12:00 | 50127.0857 | 0
Devonshire Building | 2017-04-23 12:15 | 50127.0907 | 20.016
Devonshire Building | 2017-04-23 12:30 | 50127.0957 | 20.016
Devonshire Building | 2017-04-23 12:45 | 50127.3607 | 1059.984
Devonshire Building | 2017-04-23 13:00 | 50127.3657 | 20.016
Devonshire Building | 2017-04-23 13:15 | 50127.3657 | 0
Devonshire Building | 2017-04-23 13:30 | 50127.3707 | 20.016
Devonshire Building | 2017-04-23 13:45 | 50127.3807 | 39.996
Devonshire Building | 2017-04-23 14:00 | 50127.3857 | 20.016
Devonshire Building | 2017-04-23 14:15 | 50127.3857 | 0
Devonshire Building | 2017-04-23 14:30 | 50127.3957 | 39.996
Devonshire Building | 2017-04-23 14:45 | 50127.3957 | 0
Devonshire Building | 2017-04-23 15:00 | 50127.4007 | 20.016
Devonshire Building | 2017-04-23 15:15 | 50127.4057 | 20.016
Devonshire Building | 2017-04-23 15:30 | 50127.4057 | 0
Devonshire Building | 2017-04-23 15:45 | 50127.4107 | 20.016
Devonshire Building | 2017-04-23 16:00 | 50127.4157 | 20.016
Devonshire Building | 2017-04-23 16:15 | 50127.4207 | 20.016
Devonshire Building | 2017-04-23 16:30 | 50127.4258 | 20.016
Devonshire Building | 2017-04-23 16:45 | 50127.4258 | 0
Devonshire Building | 2017-04-23 17:00 | 50127.4308 | 20.016
Devonshire Building | 2017-04-23 17:15 | 50127.4358 | 20.016
Devonshire Building | 2017-04-23 17:30 | 50127.4408 | 20.016
Devonshire Building | 2017-04-23 17:45 | 50127.4408 | 0
Devonshire Building | 2017-04-23 18:00 | 50127.4458 | 20.016
Devonshire Building | 2017-04-23 18:15 | 50127.4508 | 20.016
Devonshire Building | 2017-04-23 18:30 | 50127.4558 | 20.016
Devonshire Building | 2017-04-23 18:45 | 50127.4608 | 20.016
Devonshire Building | 2017-04-23 19:00 | 50127.4658 | 20.016
Devonshire Building | 2017-04-23 19:15 | 50127.4708 | 20.016
Devonshire Building | 2017-04-23 19:30 | 50127.4708 | 0
Devonshire Building | 2017-04-23 19:45 | 50127.4758 | 20.016
Devonshire Building | 2017-04-23 20:00 | 50127.4808 | 20.016
Devonshire Building | 2017-04-23 20:15 | 50127.4858 | 20.016
Devonshire Building | 2017-04-23 20:30 | 50127.4908 | 20.016
Devonshire Building | 2017-04-23 20:45 | 50127.4958 | 20.016
Devonshire Building | 2017-04-23 21:00 | 50127.5058 | 39.996
Devonshire Building | 2017-04-23 21:15 | 50127.5058 | 0
Devonshire Building | 2017-04-23 21:30 | 50127.5108 | 20.016
Devonshire Building | 2017-04-23 21:45 | 50127.5158 | 20.016
Devonshire Building | 2017-04-23 22:00 | 50127.5208 | 20.016
Devonshire Building | 2017-04-23 22:15 | 50127.5258 | 20.016
Devonshire Building | 2017-04-23 22:30 | 50127.5258 | 0
Devonshire Building | 2017-04-23 22:45 | 50127.5308 | 20.016
Devonshire Building | 2017-04-23 23:00 | 50127.5358 | 20.016
Devonshire Building | 2017-04-23 23:15 | 50127.5408 | 20.016
Devonshire Building | 2017-04-23 23:30 | 50127.5458 | 20.016
Devonshire Building | 2017-04-23 23:45 | 50127.5458 | 0
Devonshire Building | 2017-04-24 | 50127.5508 | 20.016
Devonshire Building | 2017-04-24 00:15 | 50127.5558 | 20.016
Devonshire Building | 2017-04-24 00:30 | 50127.5608 | 20.016
Devonshire Building | 2017-04-24 00:45 | 50127.5608 | 0
Devonshire Building | 2017-04-24 01:00 | 50127.5658 | 20.016
Devonshire Building | 2017-04-24 01:15 | 50127.5708 | 20.016
Devonshire Building | 2017-04-24 01:30 | 50127.5708 | 0
Devonshire Building | 2017-04-24 01:45 | 50127.5758 | 20.016
Devonshire Building | 2017-04-24 02:00 | 50127.5808 | 20.016
Devonshire Building | 2017-04-24 02:15 | 50127.5858 | 20.016
Devonshire Building | 2017-04-24 02:30 | 50127.5858 | 0
Devonshire Building | 2017-04-24 02:45 | 50127.5908 | 20.016
Devonshire Building | 2017-04-24 03:00 | 50127.5958 | 20.016
Devonshire Building | 2017-04-24 03:15 | 50127.5958 | 0
Devonshire Building | 2017-04-24 03:30 | 50127.6008 | 20.016
Devonshire Building | 2017-04-24 03:45 | 50127.6058 | 20.016
Devonshire Building | 2017-04-24 04:00 | 50127.6108 | 20.016
Devonshire Building | 2017-04-24 04:15 | 50127.6108 | 0
Devonshire Building | 2017-04-24 04:30 | 50127.6158 | 20.016
Devonshire Building | 2017-04-24 04:45 | 50127.6208 | 20.016
Devonshire Building | 2017-04-24 05:00 | 50127.6208 | 0
Devonshire Building | 2017-04-24 05:15 | 50127.6258 | 20.016
Devonshire Building | 2017-04-24 05:30 | 50127.6308 | 20.016
Devonshire Building | 2017-04-24 05:45 | 50127.6358 | 20.016
Devonshire Building | 2017-04-24 06:00 | 50127.6409 | 20.016
Devonshire Building | 2017-04-24 06:15 | 50127.6459 | 20.016
Devonshire Building | 2017-04-24 06:30 | 50127.6509 | 20.016
Devonshire Building | 2017-04-24 06:45 | 50127.6609 | 39.996
Devonshire Building | 2017-04-24 07:00 | 50127.6659 | 20.016
Devonshire Building | 2017-04-24 07:15 | 50127.6759 | 39.996
Devonshire Building | 2017-04-24 07:30 | 50127.9559 | 1119.996
Devonshire Building | 2017-04-24 07:45 | 50127.9759 | 79.992
Devonshire Building | 2017-04-24 08:00 | 50128.0109 | 140.004
Devonshire Building | 2017-04-24 08:15 | 50128.0359 | 100.008
Devonshire Building | 2017-04-24 08:30 | 50128.0609 | 100.008
Devonshire Building | 2017-04-24 08:45 | 50128.0809 | 79.992
Devonshire Building | 2017-04-24 09:00 | 50128.1959 | 460.008
Devonshire Building | 2017-04-24 09:15 | 50128.4459 | 1000.008
Devonshire Building | 2017-04-24 09:30 | 50128.4909 | 180
Devonshire Building | 2017-04-24 09:45 | 50128.5759 | 339.984
Devonshire Building | 2017-04-24 10:00 | 50128.7759 | 799.992
Devonshire Building | 2017-04-24 10:15 | 50129.2809 | 2019.996
Devonshire Building | 2017-04-24 10:30 | 50129.4759 | 780.012
Devonshire Building | 2017-04-24 10:45 | 50129.6309 | 619.992
Devonshire Building | 2017-04-24 11:00 | 50129.7609 | 519.984
Devonshire Building | 2017-04-24 11:15 | 50130.1559 | 1580.004
Devonshire Building | 2017-04-24 11:30 | 50130.2559 | 399.996
Devonshire Building | 2017-04-24 11:45 | 50130.3459 | 360
Devonshire Building | 2017-04-24 12:00 | 50130.4209 | 299.988
Devonshire Building | 2017-04-24 12:15 | 50130.4909 | 280.008
Devonshire Building | 2017-04-24 12:30 | 50130.5609 | 280.008
Devonshire Building | 2017-04-24 12:45 | 50130.7359 | 699.984
Devonshire Building | 2017-04-24 13:00 | 50130.9359 | 799.992
Devonshire Building | 2017-04-24 13:15 | 50130.9709 | 140.004
Devonshire Building | 2017-04-24 13:30 | 50131.0059 | 140.004
Devonshire Building | 2017-04-24 13:45 | 50131.0409 | 140.004
Devonshire Building | 2017-04-24 14:00 | 50131.0759 | 140.004
Devonshire Building | 2017-04-24 14:15 | 50131.1059 | 119.988
Devonshire Building | 2017-04-24 14:30 | 50131.4408 | 1339.992
Devonshire Building | 2017-04-24 14:45 | 50131.4909 | 200.016
Devonshire Building | 2017-04-24 15:00 | 50131.5459 | 219.996
Devonshire Building | 2017-04-24 15:15 | 50131.6059 | 240.012
Devonshire Building | 2017-04-24 15:30 | 50131.6659 | 240.012
Devonshire Building | 2017-04-24 15:45 | 50131.7209 | 219.996
Devonshire Building | 2017-04-24 16:00 | 50131.7709 | 200.016
Devonshire Building | 2017-04-24 16:15 | 50131.8409 | 280.008
Devonshire Building | 2017-04-24 16:30 | 50132.1609 | 1280.016
Devonshire Building | 2017-04-24 16:45 | 50132.2159 | 219.996
Devonshire Building | 2017-04-24 17:00 | 50132.2709 | 219.996
Devonshire Building | 2017-04-24 17:15 | 50132.3259 | 219.996
Devonshire Building | 2017-04-24 17:30 | 50132.3759 | 200.016
Devonshire Building | 2017-04-24 17:45 | 50132.4209 | 180
Devonshire Building | 2017-04-24 18:00 | 50132.4659 | 180
Devonshire Building | 2017-04-24 18:15 | 50132.5109 | 180
Devonshire Building | 2017-04-24 18:30 | 50132.5509 | 159.984
Devonshire Building | 2017-04-24 18:45 | 50132.5909 | 159.984
Devonshire Building | 2017-04-24 19:00 | 50132.6259 | 140.004
Devonshire Building | 2017-04-24 19:15 | 50132.6609 | 140.004
Devonshire Building | 2017-04-24 19:30 | 50132.6759 | 60.012
Devonshire Building | 2017-04-24 19:45 | 50132.6909 | 60.012
Devonshire Building | 2017-04-24 20:00 | 50132.7059 | 60.012
Devonshire Building | 2017-04-24 20:15 | 50132.7209 | 60.012
Devonshire Building | 2017-04-24 20:30 | 50132.7309 | 39.996
Devonshire Building | 2017-04-24 20:45 | 50132.7459 | 60.012
Devonshire Building | 2017-04-24 21:00 | 50132.7709 | 100.008
Devonshire Building | 2017-04-24 21:15 | 50132.7709 | 0
Devonshire Building | 2017-04-24 21:30 | 50132.7759 | 20.016
Devonshire Building | 2017-04-24 21:45 | 50132.7809 | 20.016
Devonshire Building | 2017-04-24 22:00 | 50132.7859 | 20.016
Devonshire Building | 2017-04-24 22:15 | 50132.7909 | 20.016
Devonshire Building | 2017-04-24 22:30 | 50132.7909 | 0
Devonshire Building | 2017-04-24 22:45 | 50132.7959 | 20.016
Devonshire Building | 2017-04-24 23:00 | 50132.8009 | 20.016
Devonshire Building | 2017-04-24 23:15 | 50132.8059 | 20.016
Devonshire Building | 2017-04-24 23:30 | 50132.8109 | 20.016
Devonshire Building | 2017-04-24 23:45 | 50132.8109 | 0
Devonshire Building | 2017-04-25 | 50132.8125 | 20.016
Devonshire Building | 2017-04-25 00:15 | 50132.8175 | 20.016
Devonshire Building | 2017-04-25 00:30 | 50132.8225 | 20.016
Devonshire Building | 2017-04-25 00:45 | 50132.8275 | 20.016
Devonshire Building | 2017-04-25 01:00 | 50132.8275 | 0
Devonshire Building | 2017-04-25 01:15 | 50132.8325 | 20.016
Devonshire Building | 2017-04-25 01:30 | 50132.8375 | 20.016
Devonshire Building | 2017-04-25 01:45 | 50132.8425 | 20.016
Devonshire Building | 2017-04-25 02:00 | 50132.8425 | 0
Devonshire Building | 2017-04-25 02:15 | 50132.8475 | 20.016
Devonshire Building | 2017-04-25 02:30 | 50132.8525 | 20.016
Devonshire Building | 2017-04-25 02:45 | 50132.8575 | 20.016
Devonshire Building | 2017-04-25 03:00 | 50132.8625 | 20.016
Devonshire Building | 2017-04-25 03:15 | 50132.8625 | 0
Devonshire Building | 2017-04-25 03:30 | 50132.8675 | 20.016
Devonshire Building | 2017-04-25 03:45 | 50132.8725 | 20.016
Devonshire Building | 2017-04-25 04:00 | 50132.8776 | 20.016
Devonshire Building | 2017-04-25 04:15 | 50132.8776 | 0
Devonshire Building | 2017-04-25 04:30 | 50132.8826 | 20.016
Devonshire Building | 2017-04-25 04:45 | 50132.8876 | 20.016
Devonshire Building | 2017-04-25 05:00 | 50132.8876 | 0
Devonshire Building | 2017-04-25 05:15 | 50132.8926 | 20.016
Devonshire Building | 2017-04-25 05:30 | 50132.8976 | 20.016
Devonshire Building | 2017-04-25 05:45 | 50132.9026 | 20.016
Devonshire Building | 2017-04-25 06:00 | 50132.9076 | 20.016
Devonshire Building | 2017-04-25 06:15 | 50132.9126 | 20.016
Devonshire Building | 2017-04-25 06:30 | 50132.9226 | 39.996
Devonshire Building | 2017-04-25 06:45 | 50132.9276 | 20.016
Devonshire Building | 2017-04-25 07:00 | 50133.0826 | 619.992
Devonshire Building | 2017-04-25 07:15 | 50133.2076 | 500.004
Devonshire Building | 2017-04-25 07:30 | 50133.2226 | 60.012
Devonshire Building | 2017-04-25 07:45 | 50133.2276 | 20.016
Devonshire Building | 2017-04-25 08:00 | 50133.2376 | 39.996
Devonshire Building | 2017-04-25 08:15 | 50133.2476 | 39.996
Devonshire Building | 2017-04-25 08:30 | 50133.2626 | 60.012
Devonshire Building | 2017-04-25 08:45 | 50133.2726 | 39.996
Devonshire Building | 2017-04-25 09:00 | 50133.2826 | 39.996
Devonshire Building | 2017-04-25 09:15 | 50133.6226 | 1360.008
Devonshire Building | 2017-04-25 09:30 | 50133.7376 | 460.008
Devonshire Building | 2017-04-25 09:45 | 50133.8076 | 280.008
Devonshire Building | 2017-04-25 10:00 | 50133.8826 | 299.988
Devonshire Building | 2017-04-25 10:15 | 50133.9576 | 299.988
Devonshire Building | 2017-04-25 10:30 | 50134.5976 | 2559.996
Devonshire Building | 2017-04-25 10:45 | 50134.6576 | 240.012
Devonshire Building | 2017-04-25 11:00 | 50134.7226 | 259.992
Devonshire Building | 2017-04-25 11:15 | 50134.7926 | 280.008
Devonshire Building | 2017-04-25 11:30 | 50134.8576 | 259.992
Devonshire Building | 2017-04-25 11:45 | 50134.9826 | 500.004
Devonshire Building | 2017-04-25 12:00 | 50135.5076 | 2099.988
Devonshire Building | 2017-04-25 12:15 | 50135.5676 | 240.012
Devonshire Building | 2017-04-25 12:30 | 50135.6276 | 240.012
Devonshire Building | 2017-04-25 12:45 | 50135.6926 | 259.992
Devonshire Building | 2017-04-25 13:00 | 50135.7676 | 299.988
Devonshire Building | 2017-04-25 13:15 | 50135.9676 | 799.992
Devonshire Building | 2017-04-25 13:30 | 50136.5576 | 2360.016
Devonshire Building | 2017-04-25 13:45 | 50136.7526 | 780.012
Devonshire Building | 2017-04-25 14:00 | 50136.9076 | 619.992
Devonshire Building | 2017-04-25 14:15 | 50137.0226 | 460.008
Devonshire Building | 2017-04-25 14:30 | 50137.1126 | 360
Devonshire Building | 2017-04-25 14:45 | 50137.1876 | 299.988
Devonshire Building | 2017-04-25 15:00 | 50137.3976 | 839.988
Devonshire Building | 2017-04-25 15:15 | 50137.7926 | 1580.004
Devonshire Building | 2017-04-25 15:30 | 50137.8176 | 100.008
Devonshire Building | 2017-04-25 15:45 | 50137.8476 | 119.988
Devonshire Building | 2017-04-25 16:00 | 50137.8776 | 119.988
Devonshire Building | 2017-04-25 16:15 | 50137.9026 | 100.008
Devonshire Building | 2017-04-25 16:30 | 50138.3176 | 1659.996
Devonshire Building | 2017-04-25 16:45 | 50138.5326 | 860.004
Devonshire Building | 2017-04-25 17:00 | 50138.5626 | 119.988
Devonshire Building | 2017-04-25 17:15 | 50138.5976 | 140.004
Devonshire Building | 2017-04-25 17:30 | 50138.6276 | 119.988
Devonshire Building | 2017-04-25 17:45 | 50138.6576 | 119.988
Devonshire Building | 2017-04-25 18:00 | 50138.6926 | 140.004
Devonshire Building | 2017-04-25 18:15 | 50138.7226 | 119.988
Devonshire Building | 2017-04-25 18:30 | 50138.7476 | 100.008
Devonshire Building | 2017-04-25 18:45 | 50138.7776 | 119.988
Devonshire Building | 2017-04-25 19:00 | 50138.8026 | 100.008
Devonshire Building | 2017-04-25 19:15 | 50138.8276 | 100.008
Devonshire Building | 2017-04-25 19:30 | 50138.8526 | 100.008
Devonshire Building | 2017-04-25 19:45 | 50138.8726 | 79.992
Devonshire Building | 2017-04-25 20:00 | 50138.8976 | 100.008
Devonshire Building | 2017-04-25 20:15 | 50138.9176 | 79.992
Devonshire Building | 2017-04-25 20:30 | 50138.9426 | 100.008
Devonshire Building | 2017-04-25 20:45 | 50138.9626 | 79.992
Devonshire Building | 2017-04-25 21:00 | 50138.9876 | 100.008
Devonshire Building | 2017-04-25 21:15 | 50139.0026 | 60.012
Devonshire Building | 2017-04-25 21:30 | 50139.0176 | 60.012
Devonshire Building | 2017-04-25 21:45 | 50139.0326 | 60.012
Devonshire Building | 2017-04-25 22:00 | 50139.0476 | 60.012
Devonshire Building | 2017-04-25 22:15 | 50139.0626 | 60.012
Devonshire Building | 2017-04-25 22:30 | 50139.0726 | 39.996
Devonshire Building | 2017-04-25 22:45 | 50139.0876 | 60.012
Devonshire Building | 2017-04-25 23:00 | 50139.1026 | 60.012
Devonshire Building | 2017-04-25 23:15 | 50139.1176 | 60.012
Devonshire Building | 2017-04-25 23:30 | 50139.1326 | 60.012
Devonshire Building | 2017-04-25 23:45 | 50139.1426 | 39.996
Devonshire Building | 2017-04-26 | 50139.1602 | 60.012
Devonshire Building | 2017-04-26 00:15 | 50139.1752 | 60.012
Devonshire Building | 2017-04-26 00:30 | 50139.1852 | 39.996
Devonshire Building | 2017-04-26 00:45 | 50139.2002 | 60.012
Devonshire Building | 2017-04-26 01:00 | 50139.2152 | 60.012
Devonshire Building | 2017-04-26 01:15 | 50139.2252 | 39.996
Devonshire Building | 2017-04-26 01:30 | 50139.2402 | 60.012
Devonshire Building | 2017-04-26 01:45 | 50139.2502 | 39.996
Devonshire Building | 2017-04-26 02:00 | 50139.2652 | 60.012
Devonshire Building | 2017-04-26 02:15 | 50139.2752 | 39.996
Devonshire Building | 2017-04-26 02:30 | 50139.2852 | 39.996
Devonshire Building | 2017-04-26 02:45 | 50139.3002 | 60.012
Devonshire Building | 2017-04-26 03:00 | 50139.3102 | 39.996
Devonshire Building | 2017-04-26 03:15 | 50139.3202 | 39.996
Devonshire Building | 2017-04-26 03:30 | 50139.3352 | 60.012
Devonshire Building | 2017-04-26 03:45 | 50139.3452 | 39.996
Devonshire Building | 2017-04-26 04:00 | 50139.3552 | 39.996
Devonshire Building | 2017-04-26 04:15 | 50139.3702 | 60.012
Devonshire Building | 2017-04-26 04:30 | 50139.3802 | 39.996
Devonshire Building | 2017-04-26 04:45 | 50139.3902 | 39.996
Devonshire Building | 2017-04-26 05:00 | 50139.4002 | 39.996
Devonshire Building | 2017-04-26 05:15 | 50139.4152 | 60.012
Devonshire Building | 2017-04-26 05:30 | 50139.4252 | 39.996
Devonshire Building | 2017-04-26 05:45 | 50139.4352 | 39.996
Devonshire Building | 2017-04-26 06:00 | 50139.4452 | 39.996
Devonshire Building | 2017-04-26 06:15 | 50139.4552 | 39.996
Devonshire Building | 2017-04-26 06:30 | 50139.4752 | 79.992
Devonshire Building | 2017-04-26 06:45 | 50139.4852 | 39.996
Devonshire Building | 2017-04-26 07:00 | 50139.7702 | 1140.012
Devonshire Building | 2017-04-26 07:15 | 50139.7802 | 39.996
Devonshire Building | 2017-04-26 07:30 | 50139.7902 | 39.996
Devonshire Building | 2017-04-26 07:45 | 50139.7952 | 20.016
Devonshire Building | 2017-04-26 08:00 | 50139.8102 | 60.012
Devonshire Building | 2017-04-26 08:15 | 50139.8252 | 60.012
Devonshire Building | 2017-04-26 08:30 | 50139.8402 | 60.012
Devonshire Building | 2017-04-26 08:45 | 50139.8552 | 60.012
Devonshire Building | 2017-04-26 09:00 | 50139.8852 | 119.988
Devonshire Building | 2017-04-26 09:15 | 50140.2152 | 1320.012
Devonshire Building | 2017-04-26 09:30 | 50140.2602 | 180
Devonshire Building | 2017-04-26 09:45 | 50140.3302 | 280.008
Devonshire Building | 2017-04-26 10:00 | 50140.4002 | 280.008
Devonshire Building | 2017-04-26 10:15 | 50140.4702 | 280.008
Devonshire Building | 2017-04-26 10:30 | 50140.7602 | 1159.992
Devonshire Building | 2017-04-26 10:45 | 50140.9402 | 720
Devonshire Building | 2017-04-26 11:00 | 50141.0502 | 439.992
Devonshire Building | 2017-04-26 11:15 | 50141.1452 | 380.016
Devonshire Building | 2017-04-26 11:30 | 50141.2252 | 320.004
Devonshire Building | 2017-04-26 11:45 | 50141.2952 | 280.008
Devonshire Building | 2017-04-26 12:00 | 50141.6002 | 1220.004
Devonshire Building | 2017-04-26 12:15 | 50141.6952 | 380.016
Devonshire Building | 2017-04-26 12:30 | 50141.7302 | 140.004
Devonshire Building | 2017-04-26 12:45 | 50141.7652 | 140.004
Devonshire Building | 2017-04-26 13:00 | 50141.8052 | 159.984
Devonshire Building | 2017-04-26 13:15 | 50141.8552 | 200.016
Devonshire Building | 2017-04-26 13:30 | 50141.9052 | 200.016
Devonshire Building | 2017-04-26 13:45 | 50142.2452 | 1360.008
Devonshire Building | 2017-04-26 14:00 | 50142.3152 | 280.008
Devonshire Building | 2017-04-26 14:15 | 50142.4002 | 339.984
Devonshire Building | 2017-04-26 14:30 | 50142.4802 | 320.004
Devonshire Building | 2017-04-26 14:45 | 50142.5552 | 299.988
Devonshire Building | 2017-04-26 15:00 | 50142.6202 | 259.992
Devonshire Building | 2017-04-26 15:15 | 50142.9702 | 1400.004
Devonshire Building | 2017-04-26 15:30 | 50143.0202 | 200.016
Devonshire Building | 2017-04-26 15:45 | 50143.0702 | 200.016
Devonshire Building | 2017-04-26 16:00 | 50143.1202 | 200.016
Devonshire Building | 2017-04-26 16:15 | 50143.1602 | 159.984
Devonshire Building | 2017-04-26 16:30 | 50143.2002 | 159.984
Devonshire Building | 2017-04-26 16:45 | 50143.2352 | 140.004
Devonshire Building | 2017-04-26 17:00 | 50143.2652 | 119.988
Devonshire Building | 2017-04-26 17:15 | 50143.2952 | 119.988
Devonshire Building | 2017-04-26 17:30 | 50143.3152 | 79.992
Devonshire Building | 2017-04-26 17:45 | 50143.3402 | 100.008
Devonshire Building | 2017-04-26 18:00 | 50143.3602 | 79.992
Devonshire Building | 2017-04-26 18:15 | 50143.3802 | 79.992
Devonshire Building | 2017-04-26 18:30 | 50143.4002 | 79.992
Devonshire Building | 2017-04-26 18:45 | 50143.4202 | 79.992
Devonshire Building | 2017-04-26 19:00 | 50143.4302 | 39.996
Devonshire Building | 2017-04-26 19:15 | 50143.4452 | 60.012
Devonshire Building | 2017-04-26 19:30 | 50143.4602 | 60.012
Devonshire Building | 2017-04-26 19:45 | 50143.4702 | 39.996
Devonshire Building | 2017-04-26 20:00 | 50143.4852 | 60.012
Devonshire Building | 2017-04-26 20:15 | 50143.4952 | 39.996
Devonshire Building | 2017-04-26 20:30 | 50143.5102 | 60.012
Devonshire Building | 2017-04-26 20:45 | 50143.5202 | 39.996
Devonshire Building | 2017-04-26 21:00 | 50143.5502 | 119.988
Devonshire Building | 2017-04-26 21:15 | 50143.5552 | 20.016
Devonshire Building | 2017-04-26 21:30 | 50143.5602 | 20.016
Devonshire Building | 2017-04-26 21:45 | 50143.5602 | 0
Devonshire Building | 2017-04-26 22:00 | 50143.5652 | 20.016
Devonshire Building | 2017-04-26 22:15 | 50143.5702 | 20.016
Devonshire Building | 2017-04-26 22:30 | 50143.5752 | 20.016
Devonshire Building | 2017-04-26 22:45 | 50143.5802 | 20.016
Devonshire Building | 2017-04-26 23:00 | 50143.5852 | 20.016
Devonshire Building | 2017-04-26 23:15 | 50143.5852 | 0
Devonshire Building | 2017-04-26 23:30 | 50143.5902 | 20.016
Devonshire Building | 2017-04-26 23:45 | 50143.5952 | 20.016
Devonshire Building | 2017-04-27 | 50143.6016 | 20.016
Devonshire Building | 2017-04-27 00:15 | 50143.6066 | 20.016
Devonshire Building | 2017-04-27 00:30 | 50143.6116 | 20.016
Devonshire Building | 2017-04-27 00:45 | 50143.6116 | 0
Devonshire Building | 2017-04-27 01:00 | 50143.6166 | 20.016
Devonshire Building | 2017-04-27 01:15 | 50143.6216 | 20.016
Devonshire Building | 2017-04-27 01:30 | 50143.6266 | 20.016
Devonshire Building | 2017-04-27 01:45 | 50143.6316 | 20.016
Devonshire Building | 2017-04-27 02:00 | 50143.6366 | 20.016
Devonshire Building | 2017-04-27 02:15 | 50143.6366 | 0
Devonshire Building | 2017-04-27 02:30 | 50143.6416 | 20.016
Devonshire Building | 2017-04-27 02:45 | 50143.6466 | 20.016
Devonshire Building | 2017-04-27 03:00 | 50143.6516 | 20.016
Devonshire Building | 2017-04-27 03:15 | 50143.6516 | 0
Devonshire Building | 2017-04-27 03:30 | 50143.9216 | 1080
Devonshire Building | 2017-04-27 03:45 | 50143.9216 | 0
Devonshire Building | 2017-04-27 04:00 | 50143.9266 | 20.016
Devonshire Building | 2017-04-27 04:15 | 50143.9316 | 20.016
Devonshire Building | 2017-04-27 04:30 | 50143.9366 | 20.016
Devonshire Building | 2017-04-27 04:45 | 50143.9366 | 0
Devonshire Building | 2017-04-27 05:00 | 50143.9416 | 20.016
Devonshire Building | 2017-04-27 05:15 | 50143.9466 | 20.016
Devonshire Building | 2017-04-27 05:30 | 50143.9516 | 20.016
Devonshire Building | 2017-04-27 05:45 | 50143.9566 | 20.016
Devonshire Building | 2017-04-27 06:00 | 50143.9616 | 20.016
Devonshire Building | 2017-04-27 06:15 | 50143.9666 | 20.016
Devonshire Building | 2017-04-27 06:30 | 50143.9716 | 20.016
Devonshire Building | 2017-04-27 06:45 | 50143.9766 | 20.016
Devonshire Building | 2017-04-27 07:00 | 50143.9866 | 39.996
Devonshire Building | 2017-04-27 07:15 | 50143.9916 | 20.016
Devonshire Building | 2017-04-27 07:30 | 50144.0016 | 39.996
Devonshire Building | 2017-04-27 07:45 | 50144.0067 | 20.016
Devonshire Building | 2017-04-27 08:00 | 50144.0317 | 100.008
Devonshire Building | 2017-04-27 08:15 | 50144.0417 | 39.996
Devonshire Building | 2017-04-27 08:30 | 50144.1567 | 460.008
Devonshire Building | 2017-04-27 08:45 | 50144.3417 | 740.016
Devonshire Building | 2017-04-27 09:00 | 50144.4417 | 399.996
Devonshire Building | 2017-04-27 09:15 | 50144.5867 | 579.996
Devonshire Building | 2017-04-27 09:30 | 50144.7017 | 460.008
Devonshire Building | 2017-04-27 09:45 | 50144.7967 | 380.016
Devonshire Building | 2017-04-27 10:00 | 50145.1467 | 1400.004
Devonshire Building | 2017-04-27 10:15 | 50145.2067 | 240.012
Devonshire Building | 2017-04-27 10:30 | 50145.2717 | 259.992
Devonshire Building | 2017-04-27 10:45 | 50145.3367 | 259.992
Devonshire Building | 2017-04-27 11:00 | 50145.4117 | 299.988
Devonshire Building | 2017-04-27 11:15 | 50145.5817 | 680.004
Devonshire Building | 2017-04-27 11:30 | 50145.8267 | 979.992
Devonshire Building | 2017-04-27 11:45 | 50145.8867 | 240.012
Devonshire Building | 2017-04-27 12:00 | 50145.9417 | 219.996
Devonshire Building | 2017-04-27 12:15 | 50145.9967 | 219.996
Devonshire Building | 2017-04-27 12:30 | 50146.0567 | 240.012
Devonshire Building | 2017-04-27 12:45 | 50146.4117 | 1419.984
Devonshire Building | 2017-04-27 13:00 | 50146.4667 | 219.996
Devonshire Building | 2017-04-27 13:15 | 50146.5117 | 180
Devonshire Building | 2017-04-27 13:30 | 50146.5517 | 159.984
Devonshire Building | 2017-04-27 13:45 | 50146.6017 | 200.016
Devonshire Building | 2017-04-27 14:00 | 50146.6467 | 180
Devonshire Building | 2017-04-27 14:15 | 50146.6867 | 159.984
Devonshire Building | 2017-04-27 14:30 | 50146.9817 | 1180.008
Devonshire Building | 2017-04-27 14:45 | 50147.0067 | 100.008
Devonshire Building | 2017-04-27 15:00 | 50147.0367 | 119.988
Devonshire Building | 2017-04-27 15:15 | 50147.0917 | 219.996
Devonshire Building | 2017-04-27 15:30 | 50147.1566 | 259.992
Devonshire Building | 2017-04-27 15:45 | 50147.2167 | 240.012
Devonshire Building | 2017-04-27 16:00 | 50147.2767 | 240.012
Devonshire Building | 2017-04-27 16:15 | 50147.6267 | 1400.004
Devonshire Building | 2017-04-27 16:30 | 50147.6767 | 200.016
Devonshire Building | 2017-04-27 16:45 | 50147.7267 | 200.016
Devonshire Building | 2017-04-27 17:00 | 50147.7817 | 219.996
Devonshire Building | 2017-04-27 17:15 | 50147.8317 | 200.016
Devonshire Building | 2017-04-27 17:30 | 50147.8817 | 200.016
Devonshire Building | 2017-04-27 17:45 | 50147.9267 | 180
Devonshire Building | 2017-04-27 18:00 | 50147.9767 | 200.016
Devonshire Building | 2017-04-27 18:15 | 50148.0167 | 159.984
Devonshire Building | 2017-04-27 18:30 | 50148.0567 | 159.984
Devonshire Building | 2017-04-27 18:45 | 50148.0917 | 140.004
Devonshire Building | 2017-04-27 19:00 | 50148.1267 | 140.004
Devonshire Building | 2017-04-27 19:15 | 50148.1567 | 119.988
Devonshire Building | 2017-04-27 19:30 | 50148.1817 | 100.008
Devonshire Building | 2017-04-27 19:45 | 50148.2017 | 79.992
Devonshire Building | 2017-04-27 20:00 | 50148.2267 | 100.008
Devonshire Building | 2017-04-27 20:15 | 50148.2417 | 60.012
Devonshire Building | 2017-04-27 20:30 | 50148.2617 | 79.992
Devonshire Building | 2017-04-27 20:45 | 50148.2767 | 60.012
Devonshire Building | 2017-04-27 21:00 | 50148.3067 | 119.988
Devonshire Building | 2017-04-27 21:15 | 50148.3117 | 20.016
Devonshire Building | 2017-04-27 21:30 | 50148.3217 | 39.996
Devonshire Building | 2017-04-27 21:45 | 50148.3267 | 20.016
Devonshire Building | 2017-04-27 22:00 | 50148.3317 | 20.016
Devonshire Building | 2017-04-27 22:15 | 50148.3367 | 20.016
Devonshire Building | 2017-04-27 22:30 | 50148.3417 | 20.016
Devonshire Building | 2017-04-27 22:45 | 50148.3467 | 20.016
Devonshire Building | 2017-04-27 23:00 | 50148.3567 | 39.996
Devonshire Building | 2017-04-27 23:15 | 50148.3617 | 20.016
Devonshire Building | 2017-04-27 23:30 | 50148.3667 | 20.016
Devonshire Building | 2017-04-27 23:45 | 50148.3717 | 20.016
Devonshire Building | 2017-04-28 | 50148.375 | 20.016
Devonshire Building | 2017-04-28 00:15 | 50148.38 | 20.016
Devonshire Building | 2017-04-28 00:30 | 50148.385 | 20.016
Devonshire Building | 2017-04-28 00:45 | 50148.39 | 20.016
Devonshire Building | 2017-04-28 01:00 | 50148.395 | 20.016
Devonshire Building | 2017-04-28 01:15 | 50148.405 | 39.996
Devonshire Building | 2017-04-28 01:30 | 50148.41 | 20.016
Devonshire Building | 2017-04-28 01:45 | 50148.415 | 20.016
Devonshire Building | 2017-04-28 02:00 | 50148.42 | 20.016
Devonshire Building | 2017-04-28 02:15 | 50148.425 | 20.016
Devonshire Building | 2017-04-28 02:30 | 50148.43 | 20.016
Devonshire Building | 2017-04-28 02:45 | 50148.435 | 20.016
Devonshire Building | 2017-04-28 03:00 | 50148.44 | 20.016
Devonshire Building | 2017-04-28 03:15 | 50148.44 | 0
Devonshire Building | 2017-04-28 03:30 | 50148.445 | 20.016
Devonshire Building | 2017-04-28 03:45 | 50148.4501 | 20.016
Devonshire Building | 2017-04-28 04:00 | 50148.4551 | 20.016
Devonshire Building | 2017-04-28 04:15 | 50148.4601 | 20.016
Devonshire Building | 2017-04-28 04:30 | 50148.4651 | 20.016
Devonshire Building | 2017-04-28 04:45 | 50148.4701 | 20.016
Devonshire Building | 2017-04-28 05:00 | 50148.4751 | 20.016
Devonshire Building | 2017-04-28 05:15 | 50148.4801 | 20.016
Devonshire Building | 2017-04-28 05:30 | 50148.4851 | 20.016
Devonshire Building | 2017-04-28 05:45 | 50148.4901 | 20.016
Devonshire Building | 2017-04-28 06:00 | 50148.4951 | 20.016
Devonshire Building | 2017-04-28 06:15 | 50148.5001 | 20.016
Devonshire Building | 2017-04-28 06:30 | 50148.7801 | 1119.996
Devonshire Building | 2017-04-28 06:45 | 50148.7901 | 39.996
Devonshire Building | 2017-04-28 07:00 | 50148.7951 | 20.016
Devonshire Building | 2017-04-28 07:15 | 50148.8051 | 39.996
Devonshire Building | 2017-04-28 07:30 | 50148.8101 | 20.016
Devonshire Building | 2017-04-28 07:45 | 50148.8251 | 60.012
Devonshire Building | 2017-04-28 08:00 | 50148.8401 | 60.012
Devonshire Building | 2017-04-28 08:15 | 50148.8551 | 60.012
Devonshire Building | 2017-04-28 08:30 | 50148.8801 | 100.008
Devonshire Building | 2017-04-28 08:45 | 50148.9101 | 119.988
Devonshire Building | 2017-04-28 09:00 | 50148.9451 | 140.004
Devonshire Building | 2017-04-28 09:15 | 50149.2951 | 1400.004
Devonshire Building | 2017-04-28 09:30 | 50149.3501 | 219.996
Devonshire Building | 2017-04-28 09:45 | 50149.4501 | 399.996
Devonshire Building | 2017-04-28 10:00 | 50149.5201 | 280.008
Devonshire Building | 2017-04-28 10:15 | 50149.5901 | 280.008
Devonshire Building | 2017-04-28 10:30 | 50149.9451 | 1419.984
Devonshire Building | 2017-04-28 10:45 | 50150.0101 | 259.992
Devonshire Building | 2017-04-28 11:00 | 50150.0751 | 259.992
Devonshire Building | 2017-04-28 11:15 | 50150.1301 | 219.996
Devonshire Building | 2017-04-28 11:30 | 50150.1801 | 200.016
Devonshire Building | 2017-04-28 11:45 | 50150.4901 | 1239.984
Devonshire Building | 2017-04-28 12:00 | 50150.5451 | 219.996
Devonshire Building | 2017-04-28 12:15 | 50150.5851 | 159.984
Devonshire Building | 2017-04-28 12:30 | 50150.6251 | 159.984
Devonshire Building | 2017-04-28 12:45 | 50150.6651 | 159.984
Devonshire Building | 2017-04-28 13:00 | 50150.7051 | 159.984
Devonshire Building | 2017-04-28 13:15 | 50150.7451 | 159.984
Devonshire Building | 2017-04-28 13:30 | 50151.0651 | 1280.016
Devonshire Building | 2017-04-28 13:45 | 50151.1301 | 259.992
Devonshire Building | 2017-04-28 14:00 | 50151.1951 | 259.992
Devonshire Building | 2017-04-28 14:15 | 50151.2551 | 240.012
Devonshire Building | 2017-04-28 14:30 | 50151.3251 | 280.008
Devonshire Building | 2017-04-28 14:45 | 50151.4051 | 320.004
Devonshire Building | 2017-04-28 15:00 | 50151.4901 | 339.984
Devonshire Building | 2017-04-28 15:15 | 50151.5751 | 339.984
Devonshire Building | 2017-04-28 15:30 | 50151.9701 | 1580.004
Devonshire Building | 2017-04-28 15:45 | 50152.0551 | 339.984
Devonshire Building | 2017-04-28 16:00 | 50152.1351 | 320.004
Devonshire Building | 2017-04-28 16:15 | 50152.2151 | 320.004
Devonshire Building | 2017-04-28 16:30 | 50152.2701 | 219.996
Devonshire Building | 2017-04-28 16:45 | 50152.3201 | 200.016
Devonshire Building | 2017-04-28 17:00 | 50152.3701 | 200.016
Devonshire Building | 2017-04-28 17:15 | 50152.4151 | 180
Devonshire Building | 2017-04-28 17:30 | 50152.4551 | 159.984
Devonshire Building | 2017-04-28 17:45 | 50152.4951 | 159.984
Devonshire Building | 2017-04-28 18:00 | 50152.5301 | 140.004
Devonshire Building | 2017-04-28 18:15 | 50152.5701 | 159.984
Devonshire Building | 2017-04-28 18:30 | 50152.6051 | 140.004
Devonshire Building | 2017-04-28 18:45 | 50152.6401 | 140.004
Devonshire Building | 2017-04-28 19:00 | 50152.6751 | 140.004
Devonshire Building | 2017-04-28 19:15 | 50152.7051 | 119.988
Devonshire Building | 2017-04-28 19:30 | 50152.7301 | 100.008
Devonshire Building | 2017-04-28 19:45 | 50152.7551 | 100.008
Devonshire Building | 2017-04-28 20:00 | 50152.7751 | 79.992
Devonshire Building | 2017-04-28 20:15 | 50152.7951 | 79.992
Devonshire Building | 2017-04-28 20:30 | 50152.8151 | 79.992
Devonshire Building | 2017-04-28 20:45 | 50152.8301 | 60.012
Devonshire Building | 2017-04-28 21:00 | 50152.8601 | 119.988
Devonshire Building | 2017-04-28 21:15 | 50152.8651 | 20.016
Devonshire Building | 2017-04-28 21:30 | 50152.8701 | 20.016
Devonshire Building | 2017-04-28 21:45 | 50152.8801 | 39.996
Devonshire Building | 2017-04-28 22:00 | 50152.8851 | 20.016
Devonshire Building | 2017-04-28 22:15 | 50152.8901 | 20.016
Devonshire Building | 2017-04-28 22:30 | 50152.9001 | 39.996
Devonshire Building | 2017-04-28 22:45 | 50152.9051 | 20.016
Devonshire Building | 2017-04-28 23:00 | 50152.9101 | 20.016
Devonshire Building | 2017-04-28 23:15 | 50152.9151 | 20.016
Devonshire Building | 2017-04-28 23:30 | 50152.9251 | 39.996
Devonshire Building | 2017-04-28 23:45 | 50152.9301 | 20.016
Devonshire Building | 2017-04-29 | 50153.2031 | 1100.016
Devonshire Building | 2017-04-29 00:15 | 50153.2081 | 20.016
Devonshire Building | 2017-04-29 00:30 | 50153.2131 | 20.016
Devonshire Building | 2017-04-29 00:45 | 50153.2181 | 20.016
Devonshire Building | 2017-04-29 01:00 | 50153.2231 | 20.016
Devonshire Building | 2017-04-29 01:15 | 50153.2282 | 20.016
Devonshire Building | 2017-04-29 01:30 | 50153.2332 | 20.016
Devonshire Building | 2017-04-29 01:45 | 50153.2382 | 20.016
Devonshire Building | 2017-04-29 02:00 | 50153.2382 | 0
Devonshire Building | 2017-04-29 02:15 | 50153.2432 | 20.016
Devonshire Building | 2017-04-29 02:30 | 50153.2482 | 20.016
Devonshire Building | 2017-04-29 02:45 | 50153.2532 | 20.016
Devonshire Building | 2017-04-29 03:00 | 50153.2582 | 20.016
Devonshire Building | 2017-04-29 03:15 | 50153.2632 | 20.016
Devonshire Building | 2017-04-29 03:30 | 50153.2632 | 0
Devonshire Building | 2017-04-29 03:45 | 50153.2682 | 20.016
Devonshire Building | 2017-04-29 04:00 | 50153.2732 | 20.016
Devonshire Building | 2017-04-29 04:15 | 50153.2782 | 20.016
Devonshire Building | 2017-04-29 04:30 | 50153.2832 | 20.016
Devonshire Building | 2017-04-29 04:45 | 50153.2882 | 20.016
Devonshire Building | 2017-04-29 05:00 | 50153.2932 | 20.016
Devonshire Building | 2017-04-29 05:15 | 50153.2982 | 20.016
Devonshire Building | 2017-04-29 05:30 | 50153.3032 | 20.016
Devonshire Building | 2017-04-29 05:45 | 50153.3082 | 20.016
Devonshire Building | 2017-04-29 06:00 | 50153.3132 | 20.016
Devonshire Building | 2017-04-29 06:15 | 50153.3182 | 20.016
Devonshire Building | 2017-04-29 06:30 | 50153.3182 | 0
Devonshire Building | 2017-04-29 06:45 | 50153.3232 | 20.016
Devonshire Building | 2017-04-29 07:00 | 50153.3282 | 20.016
Devonshire Building | 2017-04-29 07:15 | 50153.3332 | 20.016
Devonshire Building | 2017-04-29 07:30 | 50153.3382 | 20.016
Devonshire Building | 2017-04-29 07:45 | 50153.3432 | 20.016
Devonshire Building | 2017-04-29 08:00 | 50153.3532 | 39.996
Devonshire Building | 2017-04-29 08:15 | 50153.3732 | 79.992
Devonshire Building | 2017-04-29 08:30 | 50153.3932 | 79.992
Devonshire Building | 2017-04-29 08:45 | 50153.4132 | 79.992
Devonshire Building | 2017-04-29 09:00 | 50153.4332 | 79.992
Devonshire Building | 2017-04-29 09:15 | 50153.4532 | 79.992
Devonshire Building | 2017-04-29 09:30 | 50153.4732 | 79.992
Devonshire Building | 2017-04-29 09:45 | 50153.4932 | 79.992
Devonshire Building | 2017-04-29 10:00 | 50153.5132 | 79.992
Devonshire Building | 2017-04-29 10:15 | 50153.5182 | 20.016
Devonshire Building | 2017-04-29 10:30 | 50153.5182 | 0
Devonshire Building | 2017-04-29 10:45 | 50153.5232 | 20.016
Devonshire Building | 2017-04-29 11:00 | 50153.5282 | 20.016
Devonshire Building | 2017-04-29 11:15 | 50153.5332 | 20.016
Devonshire Building | 2017-04-29 11:30 | 50153.5332 | 0
Devonshire Building | 2017-04-29 11:45 | 50153.5382 | 20.016
Devonshire Building | 2017-04-29 12:00 | 50153.5432 | 20.016
Devonshire Building | 2017-04-29 12:15 | 50153.5483 | 20.016
Devonshire Building | 2017-04-29 12:30 | 50153.5483 | 0
Devonshire Building | 2017-04-29 12:45 | 50153.5533 | 20.016
Devonshire Building | 2017-04-29 13:00 | 50153.5583 | 20.016
Devonshire Building | 2017-04-29 13:15 | 50153.5633 | 20.016
Devonshire Building | 2017-04-29 13:30 | 50153.5683 | 20.016
Devonshire Building | 2017-04-29 13:45 | 50153.5683 | 0
Devonshire Building | 2017-04-29 14:00 | 50153.5733 | 20.016
Devonshire Building | 2017-04-29 14:15 | 50153.5783 | 20.016
Devonshire Building | 2017-04-29 14:30 | 50153.5783 | 0
Devonshire Building | 2017-04-29 14:45 | 50153.5833 | 20.016
Devonshire Building | 2017-04-29 15:00 | 50153.5883 | 20.016
Devonshire Building | 2017-04-29 15:15 | 50153.5883 | 0
Devonshire Building | 2017-04-29 15:30 | 50153.5933 | 20.016
Devonshire Building | 2017-04-29 15:45 | 50153.5983 | 20.016
Devonshire Building | 2017-04-29 16:00 | 50153.5983 | 0
Devonshire Building | 2017-04-29 16:15 | 50153.6033 | 20.016
Devonshire Building | 2017-04-29 16:30 | 50153.6083 | 20.016
Devonshire Building | 2017-04-29 16:45 | 50153.6083 | 0
Devonshire Building | 2017-04-29 17:00 | 50153.6133 | 20.016
Devonshire Building | 2017-04-29 17:15 | 50153.6183 | 20.016
Devonshire Building | 2017-04-29 17:30 | 50153.6233 | 20.016
Devonshire Building | 2017-04-29 17:45 | 50153.6233 | 0
Devonshire Building | 2017-04-29 18:00 | 50153.8883 | 1059.984
Devonshire Building | 2017-04-29 18:15 | 50153.8933 | 20.016
Devonshire Building | 2017-04-29 18:30 | 50153.8983 | 20.016
Devonshire Building | 2017-04-29 18:45 | 50153.8983 | 0
Devonshire Building | 2017-04-29 19:00 | 50153.9033 | 20.016
Devonshire Building | 2017-04-29 19:15 | 50153.9083 | 20.016
Devonshire Building | 2017-04-29 19:30 | 50153.9133 | 20.016
Devonshire Building | 2017-04-29 19:45 | 50153.9133 | 0
Devonshire Building | 2017-04-29 20:00 | 50153.9183 | 20.016
Devonshire Building | 2017-04-29 20:15 | 50153.9233 | 20.016
Devonshire Building | 2017-04-29 20:30 | 50153.9233 | 0
Devonshire Building | 2017-04-29 20:45 | 50153.9283 | 20.016
Devonshire Building | 2017-04-29 21:00 | 50153.9383 | 39.996
Devonshire Building | 2017-04-29 21:15 | 50153.9433 | 20.016
Devonshire Building | 2017-04-29 21:30 | 50153.9433 | 0
Devonshire Building | 2017-04-29 21:45 | 50153.9483 | 20.016
Devonshire Building | 2017-04-29 22:00 | 50153.9534 | 20.016
Devonshire Building | 2017-04-29 22:15 | 50153.9584 | 20.016
Devonshire Building | 2017-04-29 22:30 | 50153.9584 | 0
Devonshire Building | 2017-04-29 22:45 | 50153.9634 | 20.016
Devonshire Building | 2017-04-29 23:00 | 50153.9684 | 20.016
Devonshire Building | 2017-04-29 23:15 | 50153.9734 | 20.016
Devonshire Building | 2017-04-29 23:30 | 50153.9784 | 20.016
Devonshire Building | 2017-04-29 23:45 | 50153.9834 | 20.016
Devonshire Building | 2017-04-30 | 50153.9844 | 0
Devonshire Building | 2017-04-30 00:15 | 50153.9894 | 20.016
Devonshire Building | 2017-04-30 00:30 | 50153.9944 | 20.016
Devonshire Building | 2017-04-30 00:45 | 50153.9994 | 20.016
Devonshire Building | 2017-04-30 01:00 | 50154.0044 | 20.016
Devonshire Building | 2017-04-30 01:15 | 50154.0094 | 20.016
Devonshire Building | 2017-04-30 01:30 | 50154.0144 | 20.016
Devonshire Building | 2017-04-30 01:45 | 50154.0194 | 20.016
Devonshire Building | 2017-04-30 02:00 | 50154.0244 | 20.016
Devonshire Building | 2017-04-30 02:15 | 50154.0294 | 20.016
Devonshire Building | 2017-04-30 02:30 | 50154.0344 | 20.016
Devonshire Building | 2017-04-30 02:45 | 50154.0344 | 0
Devonshire Building | 2017-04-30 03:00 | 50154.0394 | 20.016
Devonshire Building | 2017-04-30 03:15 | 50154.0444 | 20.016
Devonshire Building | 2017-04-30 03:30 | 50154.0494 | 20.016
Devonshire Building | 2017-04-30 03:45 | 50154.0544 | 20.016
Devonshire Building | 2017-04-30 04:00 | 50154.0594 | 20.016
Devonshire Building | 2017-04-30 04:15 | 50154.0644 | 20.016
Devonshire Building | 2017-04-30 04:30 | 50154.0694 | 20.016
Devonshire Building | 2017-04-30 04:45 | 50154.0745 | 20.016
Devonshire Building | 2017-04-30 05:00 | 50154.0745 | 0
Devonshire Building | 2017-04-30 05:15 | 50154.0795 | 20.016
Devonshire Building | 2017-04-30 05:30 | 50154.0845 | 20.016
Devonshire Building | 2017-04-30 05:45 | 50154.0895 | 20.016
Devonshire Building | 2017-04-30 06:00 | 50154.0945 | 20.016
Devonshire Building | 2017-04-30 06:15 | 50154.0945 | 0
Devonshire Building | 2017-04-30 06:30 | 50154.0995 | 20.016
Devonshire Building | 2017-04-30 06:45 | 50154.1045 | 20.016
Devonshire Building | 2017-04-30 07:00 | 50154.1095 | 20.016
Devonshire Building | 2017-04-30 07:15 | 50154.1145 | 20.016
Devonshire Building | 2017-04-30 07:30 | 50154.1145 | 0
Devonshire Building | 2017-04-30 07:45 | 50154.1345 | 79.992
Devonshire Building | 2017-04-30 08:00 | 50154.1545 | 79.992
Devonshire Building | 2017-04-30 08:15 | 50154.1745 | 79.992
Devonshire Building | 2017-04-30 08:30 | 50154.1945 | 79.992
Devonshire Building | 2017-04-30 08:45 | 50154.2145 | 79.992
Devonshire Building | 2017-04-30 09:00 | 50154.2345 | 79.992
Devonshire Building | 2017-04-30 09:15 | 50154.2545 | 79.992
Devonshire Building | 2017-04-30 09:30 | 50154.2745 | 79.992
Devonshire Building | 2017-04-30 09:45 | 50154.2945 | 79.992
Devonshire Building | 2017-04-30 10:00 | 50154.3145 | 79.992
Devonshire Building | 2017-04-30 10:15 | 50154.3295 | 60.012
Devonshire Building | 2017-04-30 10:30 | 50154.3345 | 20.016
Devonshire Building | 2017-04-30 10:45 | 50154.3345 | 0
Devonshire Building | 2017-04-30 11:00 | 50154.3395 | 20.016
Devonshire Building | 2017-04-30 11:15 | 50154.3445 | 20.016
Devonshire Building | 2017-04-30 11:30 | 50154.3495 | 20.016
Devonshire Building | 2017-04-30 11:45 | 50154.3545 | 20.016
Devonshire Building | 2017-04-30 12:00 | 50154.3545 | 0
Devonshire Building | 2017-04-30 12:15 | 50154.3595 | 20.016
Devonshire Building | 2017-04-30 12:30 | 50154.3645 | 20.016
Devonshire Building | 2017-04-30 12:45 | 50154.3695 | 20.016
Devonshire Building | 2017-04-30 13:00 | 50154.3745 | 20.016
Devonshire Building | 2017-04-30 13:15 | 50154.3795 | 20.016
Devonshire Building | 2017-04-30 13:30 | 50154.3795 | 0
Devonshire Building | 2017-04-30 13:45 | 50154.3845 | 20.016
Devonshire Building | 2017-04-30 14:00 | 50154.3895 | 20.016
Devonshire Building | 2017-04-30 14:15 | 50154.3945 | 20.016
Devonshire Building | 2017-04-30 14:30 | 50154.3945 | 0
Devonshire Building | 2017-04-30 14:45 | 50154.3995 | 20.016
Devonshire Building | 2017-04-30 15:00 | 50154.4045 | 20.016
Devonshire Building | 2017-04-30 15:15 | 50154.4045 | 0
Devonshire Building | 2017-04-30 15:30 | 50154.4095 | 20.016
Devonshire Building | 2017-04-30 15:45 | 50154.4145 | 20.016
Devonshire Building | 2017-04-30 16:00 | 50154.4195 | 20.016
Devonshire Building | 2017-04-30 16:15 | 50154.4245 | 20.016
Devonshire Building | 2017-04-30 16:30 | 50154.4295 | 20.016
Devonshire Building | 2017-04-30 16:45 | 50154.5845 | 619.992
Devonshire Building | 2017-04-30 17:00 | 50154.7045 | 479.988
Devonshire Building | 2017-04-30 17:15 | 50154.7095 | 20.016
Devonshire Building | 2017-04-30 17:30 | 50154.7095 | 0
Devonshire Building | 2017-04-30 17:45 | 50154.7145 | 20.016
Devonshire Building | 2017-04-30 18:00 | 50154.7196 | 20.016
Devonshire Building | 2017-04-30 18:15 | 50154.7196 | 0
Devonshire Building | 2017-04-30 18:30 | 50154.7246 | 20.016
Devonshire Building | 2017-04-30 18:45 | 50154.7296 | 20.016
Devonshire Building | 2017-04-30 19:00 | 50154.7296 | 0
Devonshire Building | 2017-04-30 19:15 | 50154.7346 | 20.016
Devonshire Building | 2017-04-30 19:30 | 50154.7396 | 20.016
Devonshire Building | 2017-04-30 19:45 | 50154.7396 | 0
Devonshire Building | 2017-04-30 20:00 | 50154.7446 | 20.016
Devonshire Building | 2017-04-30 20:15 | 50154.7496 | 20.016
Devonshire Building | 2017-04-30 20:30 | 50154.7546 | 20.016
Devonshire Building | 2017-04-30 20:45 | 50154.7546 | 0
Devonshire Building | 2017-04-30 21:00 | 50154.7646 | 39.996
Devonshire Building | 2017-04-30 21:15 | 50154.7696 | 20.016
Devonshire Building | 2017-04-30 21:30 | 50154.7696 | 0
Devonshire Building | 2017-04-30 21:45 | 50154.7746 | 20.016
Devonshire Building | 2017-04-30 22:00 | 50154.7796 | 20.016
Devonshire Building | 2017-04-30 22:15 | 50154.7846 | 20.016
Devonshire Building | 2017-04-30 22:30 | 50154.7846 | 0
Devonshire Building | 2017-04-30 22:45 | 50154.7896 | 20.016
Devonshire Building | 2017-04-30 23:00 | 50154.7946 | 20.016
Devonshire Building | 2017-04-30 23:15 | 50154.7996 | 20.016
Devonshire Building | 2017-04-30 23:30 | 50154.8046 | 20.016
Devonshire Building | 2017-04-30 23:45 | 50154.8046 | 0
Devonshire Building | 2017-05-01 | 50154.8086 | 20.016
Devonshire Building | 2017-05-01 00:15 | 50154.8136 | 20.016
Devonshire Building | 2017-05-01 00:30 | 50154.8186 | 20.016
Devonshire Building | 2017-05-01 00:45 | 50154.8236 | 20.016
Devonshire Building | 2017-05-01 01:00 | 50154.8286 | 20.016
Devonshire Building | 2017-05-01 01:15 | 50154.8336 | 20.016
Devonshire Building | 2017-05-01 01:30 | 50154.8336 | 0
Devonshire Building | 2017-05-01 01:45 | 50154.8386 | 20.016
Devonshire Building | 2017-05-01 02:00 | 50154.8436 | 20.016
Devonshire Building | 2017-05-01 02:15 | 50154.8486 | 20.016
Devonshire Building | 2017-05-01 02:30 | 50154.8536 | 20.016
Devonshire Building | 2017-05-01 02:45 | 50154.8536 | 0
Devonshire Building | 2017-05-01 03:00 | 50154.8586 | 20.016
Devonshire Building | 2017-05-01 03:15 | 50154.8636 | 20.016
Devonshire Building | 2017-05-01 03:30 | 50154.8686 | 20.016
Devonshire Building | 2017-05-01 03:45 | 50154.8736 | 20.016
Devonshire Building | 2017-05-01 04:00 | 50154.8736 | 0
Devonshire Building | 2017-05-01 04:15 | 50154.8786 | 20.016
Devonshire Building | 2017-05-01 04:30 | 50154.8837 | 20.016
Devonshire Building | 2017-05-01 04:45 | 50154.8887 | 20.016
Devonshire Building | 2017-05-01 05:00 | 50154.8887 | 0
Devonshire Building | 2017-05-01 05:15 | 50154.8937 | 20.016
Devonshire Building | 2017-05-01 05:30 | 50154.8987 | 20.016
Devonshire Building | 2017-05-01 05:45 | 50154.9037 | 20.016
Devonshire Building | 2017-05-01 06:00 | 50154.9037 | 0
Devonshire Building | 2017-05-01 06:15 | 50154.9087 | 20.016
Devonshire Building | 2017-05-01 06:30 | 50154.9137 | 20.016
Devonshire Building | 2017-05-01 06:45 | 50154.9137 | 0
Devonshire Building | 2017-05-01 07:00 | 50154.9187 | 20.016
Devonshire Building | 2017-05-01 07:15 | 50154.9237 | 20.016
Devonshire Building | 2017-05-01 07:30 | 50154.9237 | 0
Devonshire Building | 2017-05-01 07:45 | 50154.9387 | 60.012
Devonshire Building | 2017-05-01 08:00 | 50154.9587 | 79.992
Devonshire Building | 2017-05-01 08:15 | 50154.9787 | 79.992
Devonshire Building | 2017-05-01 08:30 | 50154.9987 | 79.992
Devonshire Building | 2017-05-01 08:45 | 50155.0187 | 79.992
Devonshire Building | 2017-05-01 09:00 | 50155.0387 | 79.992
Devonshire Building | 2017-05-01 09:15 | 50155.0587 | 79.992
Devonshire Building | 2017-05-01 09:30 | 50155.0787 | 79.992
Devonshire Building | 2017-05-01 09:45 | 50155.0987 | 79.992
Devonshire Building | 2017-05-01 10:00 | 50155.1187 | 79.992
Devonshire Building | 2017-05-01 10:15 | 50155.1237 | 20.016
Devonshire Building | 2017-05-01 10:30 | 50155.1237 | 0
Devonshire Building | 2017-05-01 10:45 | 50155.1287 | 20.016
Devonshire Building | 2017-05-01 11:00 | 50155.1337 | 20.016
Devonshire Building | 2017-05-01 11:15 | 50155.1387 | 20.016
Devonshire Building | 2017-05-01 11:30 | 50155.1387 | 0
Devonshire Building | 2017-05-01 11:45 | 50155.1437 | 20.016
Devonshire Building | 2017-05-01 12:00 | 50155.1487 | 20.016
Devonshire Building | 2017-05-01 12:15 | 50155.1487 | 0
Devonshire Building | 2017-05-01 12:30 | 50155.1537 | 20.016
Devonshire Building | 2017-05-01 12:45 | 50155.1587 | 20.016
Devonshire Building | 2017-05-01 13:00 | 50155.1637 | 20.016
Devonshire Building | 2017-05-01 13:15 | 50155.1637 | 0
Devonshire Building | 2017-05-01 13:30 | 50155.1687 | 20.016
Devonshire Building | 2017-05-01 13:45 | 50155.1687 | 0
Devonshire Building | 2017-05-01 14:00 | 50155.1737 | 20.016
Devonshire Building | 2017-05-01 14:15 | 50155.1787 | 20.016
Devonshire Building | 2017-05-01 14:30 | 50155.1837 | 20.016
Devonshire Building | 2017-05-01 14:45 | 50155.1887 | 20.016
Devonshire Building | 2017-05-01 15:00 | 50155.4537 | 1059.984
Devonshire Building | 2017-05-01 15:15 | 50155.4537 | 0
Devonshire Building | 2017-05-01 15:30 | 50155.4587 | 20.016
Devonshire Building | 2017-05-01 15:45 | 50155.4637 | 20.016
Devonshire Building | 2017-05-01 16:00 | 50155.4637 | 0
Devonshire Building | 2017-05-01 16:15 | 50155.4687 | 20.016
Devonshire Building | 2017-05-01 16:30 | 50155.4737 | 20.016
Devonshire Building | 2017-05-01 16:45 | 50155.4737 | 0
Devonshire Building | 2017-05-01 17:00 | 50155.4787 | 20.016
Devonshire Building | 2017-05-01 17:15 | 50155.4787 | 0
Devonshire Building | 2017-05-01 17:30 | 50155.4837 | 20.016
Devonshire Building | 2017-05-01 17:45 | 50155.4887 | 20.016
Devonshire Building | 2017-05-01 18:00 | 50155.4887 | 0
Devonshire Building | 2017-05-01 18:15 | 50155.4938 | 20.016
Devonshire Building | 2017-05-01 18:30 | 50155.4938 | 0
Devonshire Building | 2017-05-01 18:45 | 50155.4988 | 20.016
Devonshire Building | 2017-05-01 19:00 | 50155.5038 | 20.016
Devonshire Building | 2017-05-01 19:15 | 50155.5038 | 0
Devonshire Building | 2017-05-01 19:30 | 50155.5088 | 20.016
Devonshire Building | 2017-05-01 19:45 | 50155.5088 | 0
Devonshire Building | 2017-05-01 20:00 | 50155.5138 | 20.016
Devonshire Building | 2017-05-01 20:15 | 50155.5138 | 0
Devonshire Building | 2017-05-01 20:30 | 50155.5188 | 20.016
Devonshire Building | 2017-05-01 20:45 | 50155.5238 | 20.016
Devonshire Building | 2017-05-01 21:00 | 50155.5288 | 20.016
Devonshire Building | 2017-05-01 21:15 | 50155.5338 | 20.016
Devonshire Building | 2017-05-01 21:30 | 50155.5388 | 20.016
Devonshire Building | 2017-05-01 21:45 | 50155.5388 | 0
Devonshire Building | 2017-05-01 22:00 | 50155.5438 | 20.016
Devonshire Building | 2017-05-01 22:15 | 50155.5438 | 0
Devonshire Building | 2017-05-01 22:30 | 50155.5488 | 20.016
Devonshire Building | 2017-05-01 22:45 | 50155.5538 | 20.016
Devonshire Building | 2017-05-01 23:00 | 50155.5538 | 0
Devonshire Building | 2017-05-01 23:15 | 50155.5588 | 20.016
Devonshire Building | 2017-05-01 23:30 | 50155.5588 | 0
Devonshire Building | 2017-05-01 23:45 | 50155.5638 | 20.016
Devonshire Building | 2017-05-02 | 50155.5625 | 0
Devonshire Building | 2017-05-02 00:15 | 50155.5675 | 20.016
Devonshire Building | 2017-05-02 00:30 | 50155.5725 | 20.016
Devonshire Building | 2017-05-02 00:45 | 50155.5725 | 0
Devonshire Building | 2017-05-02 01:00 | 50155.5775 | 20.016
Devonshire Building | 2017-05-02 01:15 | 50155.5775 | 0
Devonshire Building | 2017-05-02 01:30 | 50155.5825 | 20.016
Devonshire Building | 2017-05-02 01:45 | 50155.5875 | 20.016
Devonshire Building | 2017-05-02 02:00 | 50155.5875 | 0
Devonshire Building | 2017-05-02 02:15 | 50155.5925 | 20.016
Devonshire Building | 2017-05-02 02:30 | 50155.5925 | 0
Devonshire Building | 2017-05-02 02:45 | 50155.5975 | 20.016
Devonshire Building | 2017-05-02 03:00 | 50155.5975 | 0
Devonshire Building | 2017-05-02 03:15 | 50155.6025 | 20.016
Devonshire Building | 2017-05-02 03:30 | 50155.6075 | 20.016
Devonshire Building | 2017-05-02 03:45 | 50155.6075 | 0
Devonshire Building | 2017-05-02 04:00 | 50155.6125 | 20.016
Devonshire Building | 2017-05-02 04:15 | 50155.6125 | 0
Devonshire Building | 2017-05-02 04:30 | 50155.6175 | 20.016
Devonshire Building | 2017-05-02 04:45 | 50155.6175 | 0
Devonshire Building | 2017-05-02 05:00 | 50155.6225 | 20.016
Devonshire Building | 2017-05-02 05:15 | 50155.6276 | 20.016
Devonshire Building | 2017-05-02 05:30 | 50155.6326 | 20.016
Devonshire Building | 2017-05-02 05:45 | 50155.6326 | 0
Devonshire Building | 2017-05-02 06:00 | 50155.6426 | 39.996
Devonshire Building | 2017-05-02 06:15 | 50155.6476 | 20.016
Devonshire Building | 2017-05-02 06:30 | 50155.6526 | 20.016
Devonshire Building | 2017-05-02 06:45 | 50155.6576 | 20.016
Devonshire Building | 2017-05-02 07:00 | 50155.6626 | 20.016
Devonshire Building | 2017-05-02 07:15 | 50155.6726 | 39.996
Devonshire Building | 2017-05-02 07:30 | 50155.9576 | 1140.012
Devonshire Building | 2017-05-02 07:45 | 50155.9926 | 140.004
Devonshire Building | 2017-05-02 08:00 | 50156.0176 | 100.008
Devonshire Building | 2017-05-02 08:15 | 50156.0426 | 100.008
Devonshire Building | 2017-05-02 08:30 | 50156.0676 | 100.008
Devonshire Building | 2017-05-02 08:45 | 50156.0976 | 119.988
Devonshire Building | 2017-05-02 09:00 | 50156.1226 | 100.008
Devonshire Building | 2017-05-02 09:15 | 50156.6726 | 2199.996
Devonshire Building | 2017-05-02 09:30 | 50156.6976 | 100.008
Devonshire Building | 2017-05-02 09:45 | 50156.7226 | 100.008
Devonshire Building | 2017-05-02 10:00 | 50156.7626 | 159.984
Devonshire Building | 2017-05-02 10:15 | 50156.7976 | 140.004
Devonshire Building | 2017-05-02 10:30 | 50157.4176 | 2480.004
Devonshire Building | 2017-05-02 10:45 | 50157.5176 | 399.996
Devonshire Building | 2017-05-02 11:00 | 50157.5976 | 320.004
Devonshire Building | 2017-05-02 11:15 | 50157.6676 | 280.008
Devonshire Building | 2017-05-02 11:30 | 50157.7326 | 259.992
Devonshire Building | 2017-05-02 11:45 | 50157.8026 | 280.008
Devonshire Building | 2017-05-02 12:00 | 50158.3926 | 2360.016
Devonshire Building | 2017-05-02 12:15 | 50158.4426 | 200.016
Devonshire Building | 2017-05-02 12:30 | 50158.4876 | 180
Devonshire Building | 2017-05-02 12:45 | 50158.5326 | 180
Devonshire Building | 2017-05-02 13:00 | 50158.5676 | 140.004
Devonshire Building | 2017-05-02 13:15 | 50159.1526 | 2340
Devonshire Building | 2017-05-02 13:30 | 50159.1776 | 100.008
Devonshire Building | 2017-05-02 13:45 | 50159.2026 | 100.008
Devonshire Building | 2017-05-02 14:00 | 50159.2276 | 100.008
Devonshire Building | 2017-05-02 14:15 | 50159.2576 | 119.988
Devonshire Building | 2017-05-02 14:30 | 50159.2876 | 119.988
Devonshire Building | 2017-05-02 14:45 | 50159.3176 | 119.988
Devonshire Building | 2017-05-02 15:00 | 50159.9176 | 2400.012
Devonshire Building | 2017-05-02 15:15 | 50159.9576 | 159.984
Devonshire Building | 2017-05-02 15:30 | 50160.0176 | 240.012
Devonshire Building | 2017-05-02 15:45 | 50160.0676 | 200.016
Devonshire Building | 2017-05-02 16:00 | 50160.1126 | 180
Devonshire Building | 2017-05-02 16:15 | 50160.1526 | 159.984
Devonshire Building | 2017-05-02 16:30 | 50160.1926 | 159.984
Devonshire Building | 2017-05-02 16:45 | 50160.5726 | 1519.992
Devonshire Building | 2017-05-02 17:00 | 50160.8026 | 920.016
Devonshire Building | 2017-05-02 17:15 | 50160.8326 | 119.988
Devonshire Building | 2017-05-02 17:30 | 50160.8626 | 119.988
Devonshire Building | 2017-05-02 17:45 | 50160.8976 | 140.004
Devonshire Building | 2017-05-02 18:00 | 50160.9226 | 100.008
Devonshire Building | 2017-05-02 18:15 | 50160.9476 | 100.008
Devonshire Building | 2017-05-02 18:30 | 50160.9726 | 100.008
Devonshire Building | 2017-05-02 18:45 | 50160.9976 | 100.008
Devonshire Building | 2017-05-02 19:00 | 50161.0176 | 79.992
Devonshire Building | 2017-05-02 19:15 | 50161.0376 | 79.992
Devonshire Building | 2017-05-02 19:30 | 50161.0526 | 60.012
Devonshire Building | 2017-05-02 19:45 | 50161.0726 | 79.992
Devonshire Building | 2017-05-02 20:00 | 50161.0826 | 39.996
Devonshire Building | 2017-05-02 20:15 | 50161.0976 | 60.012
Devonshire Building | 2017-05-02 20:30 | 50161.1126 | 60.012
Devonshire Building | 2017-05-02 20:45 | 50161.1226 | 39.996
Devonshire Building | 2017-05-02 21:00 | 50161.1476 | 100.008
Devonshire Building | 2017-05-02 21:15 | 50161.1526 | 20.016
Devonshire Building | 2017-05-02 21:30 | 50161.1676 | 60.012
Devonshire Building | 2017-05-02 21:45 | 50161.1726 | 20.016
Devonshire Building | 2017-05-02 22:00 | 50161.1776 | 20.016
Devonshire Building | 2017-05-02 22:15 | 50161.1826 | 20.016
Devonshire Building | 2017-05-02 22:30 | 50161.1876 | 20.016
Devonshire Building | 2017-05-02 22:45 | 50161.1926 | 20.016
Devonshire Building | 2017-05-02 23:00 | 50161.1976 | 20.016
Devonshire Building | 2017-05-02 23:15 | 50161.1976 | 0
Devonshire Building | 2017-05-02 23:30 | 50161.2026 | 20.016
Devonshire Building | 2017-05-02 23:45 | 50161.2126 | 39.996
Devonshire Building | 2017-05-03 | 50161.2148 | 0
Devonshire Building | 2017-05-03 00:15 | 50161.2198 | 20.016
Devonshire Building | 2017-05-03 00:30 | 50161.2248 | 20.016
Devonshire Building | 2017-05-03 00:45 | 50161.2299 | 20.016
Devonshire Building | 2017-05-03 01:00 | 50161.2349 | 20.016
Devonshire Building | 2017-05-03 01:15 | 50161.2349 | 0
Devonshire Building | 2017-05-03 01:30 | 50161.2399 | 20.016
Devonshire Building | 2017-05-03 01:45 | 50161.2449 | 20.016
Devonshire Building | 2017-05-03 02:00 | 50161.2499 | 20.016
Devonshire Building | 2017-05-03 02:15 | 50161.2549 | 20.016
Devonshire Building | 2017-05-03 02:30 | 50161.2599 | 20.016
Devonshire Building | 2017-05-03 02:45 | 50161.2599 | 0
Devonshire Building | 2017-05-03 03:00 | 50161.2649 | 20.016
Devonshire Building | 2017-05-03 03:15 | 50161.2699 | 20.016
Devonshire Building | 2017-05-03 03:30 | 50161.2749 | 20.016
Devonshire Building | 2017-05-03 03:45 | 50161.2749 | 0
Devonshire Building | 2017-05-03 04:00 | 50161.2799 | 20.016
Devonshire Building | 2017-05-03 04:15 | 50161.2849 | 20.016
Devonshire Building | 2017-05-03 04:30 | 50161.2849 | 0
Devonshire Building | 2017-05-03 04:45 | 50161.2899 | 20.016
Devonshire Building | 2017-05-03 05:00 | 50161.2949 | 20.016
Devonshire Building | 2017-05-03 05:15 | 50161.2999 | 20.016
Devonshire Building | 2017-05-03 05:30 | 50161.3049 | 20.016
Devonshire Building | 2017-05-03 05:45 | 50161.3099 | 20.016
Devonshire Building | 2017-05-03 06:00 | 50161.3149 | 20.016
Devonshire Building | 2017-05-03 06:15 | 50161.3149 | 0
Devonshire Building | 2017-05-03 06:30 | 50161.5099 | 780.012
Devonshire Building | 2017-05-03 06:45 | 50161.8599 | 1400.004
Devonshire Building | 2017-05-03 07:00 | 50161.8649 | 20.016
Devonshire Building | 2017-05-03 07:15 | 50161.8749 | 39.996
Devonshire Building | 2017-05-03 07:30 | 50161.8849 | 39.996
Devonshire Building | 2017-05-03 07:45 | 50161.8999 | 60.012
Devonshire Building | 2017-05-03 08:00 | 50161.9349 | 140.004
Devonshire Building | 2017-05-03 08:15 | 50161.9599 | 100.008
Devonshire Building | 2017-05-03 08:30 | 50161.9899 | 119.988
Devonshire Building | 2017-05-03 08:45 | 50162.0149 | 100.008
Devonshire Building | 2017-05-03 09:00 | 50162.6099 | 2379.996
Devonshire Building | 2017-05-03 09:15 | 50162.6549 | 180
Devonshire Building | 2017-05-03 09:30 | 50162.7249 | 280.008
Devonshire Building | 2017-05-03 09:45 | 50162.8449 | 479.988
Devonshire Building | 2017-05-03 10:00 | 50162.9649 | 479.988
Devonshire Building | 2017-05-03 10:15 | 50163.6149 | 2599.992
Devonshire Building | 2017-05-03 10:30 | 50163.7299 | 460.008
Devonshire Building | 2017-05-03 10:45 | 50163.8249 | 380.016
Devonshire Building | 2017-05-03 11:00 | 50163.9049 | 320.004
Devonshire Building | 2017-05-03 11:15 | 50163.9749 | 280.008
Devonshire Building | 2017-05-03 11:30 | 50164.0449 | 280.008
Devonshire Building | 2017-05-03 11:45 | 50164.6549 | 2440.008
Devonshire Building | 2017-05-03 12:00 | 50164.7099 | 219.996
Devonshire Building | 2017-05-03 12:15 | 50164.7649 | 219.996
Devonshire Building | 2017-05-03 12:30 | 50164.8199 | 219.996
Devonshire Building | 2017-05-03 12:45 | 50164.8749 | 219.996
Devonshire Building | 2017-05-03 13:00 | 50164.9249 | 200.016
Devonshire Building | 2017-05-03 13:15 | 50165.4949 | 2279.988
Devonshire Building | 2017-05-03 13:30 | 50165.5349 | 159.984
Devonshire Building | 2017-05-03 13:45 | 50165.5849 | 200.016
Devonshire Building | 2017-05-03 14:00 | 50165.6349 | 200.016
Devonshire Building | 2017-05-03 14:15 | 50165.6849 | 200.016
Devonshire Building | 2017-05-03 14:30 | 50165.7299 | 180
Devonshire Building | 2017-05-03 14:45 | 50165.7699 | 159.984
Devonshire Building | 2017-05-03 15:00 | 50166.0999 | 1320.012
Devonshire Building | 2017-05-03 15:15 | 50166.4099 | 1239.984
Devonshire Building | 2017-05-03 15:30 | 50166.4599 | 200.016
Devonshire Building | 2017-05-03 15:45 | 50166.4999 | 159.984
Devonshire Building | 2017-05-03 16:00 | 50166.5449 | 180
Devonshire Building | 2017-05-03 16:15 | 50166.5899 | 180
Devonshire Building | 2017-05-03 16:30 | 50166.6249 | 140.004
Devonshire Building | 2017-05-03 16:45 | 50167.1799 | 2220.012
Devonshire Building | 2017-05-03 17:00 | 50167.2099 | 119.988
Devonshire Building | 2017-05-03 17:15 | 50167.2449 | 140.004
Devonshire Building | 2017-05-03 17:30 | 50167.2799 | 140.004
Devonshire Building | 2017-05-03 17:45 | 50167.3149 | 140.004
Devonshire Building | 2017-05-03 18:00 | 50167.3499 | 140.004
Devonshire Building | 2017-05-03 18:15 | 50167.3799 | 119.988
Devonshire Building | 2017-05-03 18:30 | 50167.4099 | 119.988
Devonshire Building | 2017-05-03 18:45 | 50167.4349 | 100.008
Devonshire Building | 2017-05-03 19:00 | 50167.4599 | 100.008
Devonshire Building | 2017-05-03 19:15 | 50167.4899 | 119.988
Devonshire Building | 2017-05-03 19:30 | 50167.5099 | 79.992
Devonshire Building | 2017-05-03 19:45 | 50167.5249 | 60.012
Devonshire Building | 2017-05-03 20:00 | 50167.5449 | 79.992
Devonshire Building | 2017-05-03 20:15 | 50167.5599 | 60.012
Devonshire Building | 2017-05-03 20:30 | 50167.5749 | 60.012
Devonshire Building | 2017-05-03 20:45 | 50167.5899 | 60.012
Devonshire Building | 2017-05-03 21:00 | 50167.6199 | 119.988
Devonshire Building | 2017-05-03 21:15 | 50167.6249 | 20.016
Devonshire Building | 2017-05-03 21:30 | 50167.63 | 20.016
Devonshire Building | 2017-05-03 21:45 | 50167.635 | 20.016
Devonshire Building | 2017-05-03 22:00 | 50167.64 | 20.016
Devonshire Building | 2017-05-03 22:15 | 50167.645 | 20.016
Devonshire Building | 2017-05-03 22:30 | 50167.65 | 20.016
Devonshire Building | 2017-05-03 22:45 | 50167.655 | 20.016
Devonshire Building | 2017-05-03 23:00 | 50167.665 | 39.996
Devonshire Building | 2017-05-03 23:15 | 50167.67 | 20.016
Devonshire Building | 2017-05-03 23:30 | 50167.675 | 20.016
Devonshire Building | 2017-05-03 23:45 | 50167.68 | 20.016
Devonshire Building | 2017-05-04 | 50167.6836 | 20.016
Devonshire Building | 2017-05-04 00:15 | 50167.6886 | 20.016
Devonshire Building | 2017-05-04 00:30 | 50167.6936 | 20.016
Devonshire Building | 2017-05-04 00:45 | 50167.6986 | 20.016
Devonshire Building | 2017-05-04 01:00 | 50167.7036 | 20.016
Devonshire Building | 2017-05-04 01:15 | 50167.7086 | 20.016
Devonshire Building | 2017-05-04 01:30 | 50167.7136 | 20.016
Devonshire Building | 2017-05-04 01:45 | 50167.7186 | 20.016
Devonshire Building | 2017-05-04 02:00 | 50167.7236 | 20.016
Devonshire Building | 2017-05-04 02:15 | 50167.7286 | 20.016
Devonshire Building | 2017-05-04 02:30 | 50167.7336 | 20.016
Devonshire Building | 2017-05-04 02:45 | 50167.7386 | 20.016
Devonshire Building | 2017-05-04 03:00 | 50167.7436 | 20.016
Devonshire Building | 2017-05-04 03:15 | 50167.7486 | 20.016
Devonshire Building | 2017-05-04 03:30 | 50167.7536 | 20.016
Devonshire Building | 2017-05-04 03:45 | 50167.7587 | 20.016
Devonshire Building | 2017-05-04 04:00 | 50167.7637 | 20.016
Devonshire Building | 2017-05-04 04:15 | 50167.7687 | 20.016
Devonshire Building | 2017-05-04 04:30 | 50167.7737 | 20.016
Devonshire Building | 2017-05-04 04:45 | 50167.7787 | 20.016
Devonshire Building | 2017-05-04 05:00 | 50167.7837 | 20.016
Devonshire Building | 2017-05-04 05:15 | 50167.7887 | 20.016
Devonshire Building | 2017-05-04 05:30 | 50167.7937 | 20.016
Devonshire Building | 2017-05-04 05:45 | 50167.7987 | 20.016
Devonshire Building | 2017-05-04 06:00 | 50167.8037 | 20.016
Devonshire Building | 2017-05-04 06:15 | 50167.8087 | 20.016
Devonshire Building | 2017-05-04 06:30 | 50167.8137 | 20.016
Devonshire Building | 2017-05-04 06:45 | 50168.3337 | 2080.008
Devonshire Building | 2017-05-04 07:00 | 50168.3587 | 100.008
Devonshire Building | 2017-05-04 07:15 | 50168.3637 | 20.016
Devonshire Building | 2017-05-04 07:30 | 50168.3737 | 39.996
Devonshire Building | 2017-05-04 07:45 | 50168.3937 | 79.992
Devonshire Building | 2017-05-04 08:00 | 50168.4437 | 200.016
Devonshire Building | 2017-05-04 08:15 | 50168.4687 | 100.008
Devonshire Building | 2017-05-04 08:30 | 50168.5087 | 159.984
Devonshire Building | 2017-05-04 08:45 | 50168.5587 | 200.016
Devonshire Building | 2017-05-04 09:00 | 50168.6337 | 299.988
Devonshire Building | 2017-05-04 09:15 | 50169.2887 | 2620.008
Devonshire Building | 2017-05-04 09:30 | 50169.3787 | 360
Devonshire Building | 2017-05-04 09:45 | 50169.4737 | 380.016
Devonshire Building | 2017-05-04 10:00 | 50169.5537 | 320.004
Devonshire Building | 2017-05-04 10:15 | 50169.6237 | 280.008
Devonshire Building | 2017-05-04 10:30 | 50170.1537 | 2120.004
Devonshire Building | 2017-05-04 10:45 | 50170.2787 | 500.004
Devonshire Building | 2017-05-04 11:00 | 50170.3237 | 180
Devonshire Building | 2017-05-04 11:15 | 50170.4087 | 339.984
Devonshire Building | 2017-05-04 11:30 | 50170.4837 | 299.988
Devonshire Building | 2017-05-04 11:45 | 50170.5587 | 299.988
Devonshire Building | 2017-05-04 12:00 | 50170.6287 | 280.008
Devonshire Building | 2017-05-04 12:15 | 50170.6887 | 240.012
Devonshire Building | 2017-05-04 12:30 | 50171.2787 | 2360.016
Devonshire Building | 2017-05-04 12:45 | 50171.3237 | 180
Devonshire Building | 2017-05-04 13:00 | 50171.3637 | 159.984
Devonshire Building | 2017-05-04 13:15 | 50171.4087 | 180
Devonshire Building | 2017-05-04 13:30 | 50171.4537 | 180
Devonshire Building | 2017-05-04 13:45 | 50171.5037 | 200.016
Devonshire Building | 2017-05-04 14:00 | 50172.1187 | 2459.988
Devonshire Building | 2017-05-04 14:15 | 50172.1737 | 219.996
Devonshire Building | 2017-05-04 14:30 | 50172.2237 | 200.016
Devonshire Building | 2017-05-04 14:45 | 50172.2787 | 219.996
Devonshire Building | 2017-05-04 15:00 | 50172.3337 | 219.996
Devonshire Building | 2017-05-04 15:15 | 50172.3987 | 259.992
Devonshire Building | 2017-05-04 15:30 | 50172.4637 | 259.992
Devonshire Building | 2017-05-04 15:45 | 50172.5387 | 299.988
Devonshire Building | 2017-05-04 16:00 | 50173.1737 | 2540.016
Devonshire Building | 2017-05-04 16:15 | 50173.2387 | 259.992
Devonshire Building | 2017-05-04 16:30 | 50173.2937 | 219.996
Devonshire Building | 2017-05-04 16:45 | 50173.3487 | 219.996
Devonshire Building | 2017-05-04 17:00 | 50173.3987 | 200.016
Devonshire Building | 2017-05-04 17:15 | 50173.4437 | 180
Devonshire Building | 2017-05-04 17:30 | 50173.4937 | 200.016
Devonshire Building | 2017-05-04 17:45 | 50173.5337 | 159.984
Devonshire Building | 2017-05-04 18:00 | 50173.5737 | 159.984
Devonshire Building | 2017-05-04 18:15 | 50173.6137 | 159.984
Devonshire Building | 2017-05-04 18:30 | 50173.6537 | 159.984
Devonshire Building | 2017-05-04 18:45 | 50173.6937 | 159.984
Devonshire Building | 2017-05-04 19:00 | 50173.7337 | 159.984
Devonshire Building | 2017-05-04 19:15 | 50173.7637 | 119.988
Devonshire Building | 2017-05-04 19:30 | 50173.7937 | 119.988
Devonshire Building | 2017-05-04 19:45 | 50173.8137 | 79.992
Devonshire Building | 2017-05-04 20:00 | 50173.8387 | 100.008
Devonshire Building | 2017-05-04 20:15 | 50173.8587 | 79.992
Devonshire Building | 2017-05-04 20:30 | 50173.8737 | 60.012
Devonshire Building | 2017-05-04 20:45 | 50173.8887 | 60.012
Devonshire Building | 2017-05-04 21:00 | 50173.9187 | 119.988
Devonshire Building | 2017-05-04 21:15 | 50173.9287 | 39.996
Devonshire Building | 2017-05-04 21:30 | 50173.9337 | 20.016
Devonshire Building | 2017-05-04 21:45 | 50173.9437 | 39.996
Devonshire Building | 2017-05-04 22:00 | 50173.9487 | 20.016
Devonshire Building | 2017-05-04 22:15 | 50173.9537 | 20.016
Devonshire Building | 2017-05-04 22:30 | 50173.9637 | 39.996
Devonshire Building | 2017-05-04 22:45 | 50173.9687 | 20.016
Devonshire Building | 2017-05-04 23:00 | 50173.9737 | 20.016
Devonshire Building | 2017-05-04 23:15 | 50173.9837 | 39.996
Devonshire Building | 2017-05-04 23:30 | 50173.9887 | 20.016
Devonshire Building | 2017-05-04 23:45 | 50174.0487 | 240.012
Devonshire Building | 2017-05-05 | 50174.5156 | 1860.012
Devonshire Building | 2017-05-05 00:15 | 50174.5206 | 20.016
Devonshire Building | 2017-05-05 00:30 | 50174.5256 | 20.016
Devonshire Building | 2017-05-05 00:45 | 50174.5306 | 20.016
Devonshire Building | 2017-05-05 01:00 | 50174.5356 | 20.016
Devonshire Building | 2017-05-05 01:15 | 50174.5356 | 0
Devonshire Building | 2017-05-05 01:30 | 50174.5407 | 20.016
Devonshire Building | 2017-05-05 01:45 | 50174.5457 | 20.016
Devonshire Building | 2017-05-05 02:00 | 50174.5507 | 20.016
Devonshire Building | 2017-05-05 02:15 | 50174.5557 | 20.016
Devonshire Building | 2017-05-05 02:30 | 50174.5607 | 20.016
Devonshire Building | 2017-05-05 02:45 | 50174.5657 | 20.016
Devonshire Building | 2017-05-05 03:00 | 50174.5707 | 20.016
Devonshire Building | 2017-05-05 03:15 | 50174.5757 | 20.016
Devonshire Building | 2017-05-05 03:30 | 50174.5807 | 20.016
Devonshire Building | 2017-05-05 03:45 | 50174.5857 | 20.016
Devonshire Building | 2017-05-05 04:00 | 50174.5907 | 20.016
Devonshire Building | 2017-05-05 04:15 | 50174.5957 | 20.016
Devonshire Building | 2017-05-05 04:30 | 50174.6007 | 20.016
Devonshire Building | 2017-05-05 04:45 | 50174.6057 | 20.016
Devonshire Building | 2017-05-05 05:00 | 50174.6107 | 20.016
Devonshire Building | 2017-05-05 05:15 | 50174.6207 | 39.996
Devonshire Building | 2017-05-05 05:30 | 50174.6257 | 20.016
Devonshire Building | 2017-05-05 05:45 | 50174.6307 | 20.016
Devonshire Building | 2017-05-05 06:00 | 50174.6357 | 20.016
Devonshire Building | 2017-05-05 06:15 | 50174.6407 | 20.016
Devonshire Building | 2017-05-05 06:30 | 50174.6507 | 39.996
Devonshire Building | 2017-05-05 06:45 | 50174.6557 | 20.016
Devonshire Building | 2017-05-05 07:00 | 50174.6607 | 20.016
Devonshire Building | 2017-05-05 07:15 | 50174.6707 | 39.996
Devonshire Building | 2017-05-05 07:30 | 50174.6807 | 39.996
Devonshire Building | 2017-05-05 07:45 | 50174.7007 | 79.992
Devonshire Building | 2017-05-05 08:00 | 50174.7507 | 200.016
Devonshire Building | 2017-05-05 08:15 | 50174.8007 | 200.016
Devonshire Building | 2017-05-05 08:30 | 50174.9857 | 740.016
Devonshire Building | 2017-05-05 08:45 | 50175.4407 | 1820.016
Devonshire Building | 2017-05-05 09:00 | 50175.5007 | 240.012
Devonshire Building | 2017-05-05 09:15 | 50175.5757 | 299.988
Devonshire Building | 2017-05-05 09:30 | 50175.6557 | 320.004
Devonshire Building | 2017-05-05 09:45 | 50175.7307 | 299.988
Devonshire Building | 2017-05-05 10:00 | 50176.3607 | 2520
Devonshire Building | 2017-05-05 10:15 | 50176.4307 | 280.008
Devonshire Building | 2017-05-05 10:30 | 50176.4807 | 200.016
Devonshire Building | 2017-05-05 10:45 | 50176.5307 | 200.016
Devonshire Building | 2017-05-05 11:00 | 50176.5808 | 200.016
Devonshire Building | 2017-05-05 11:15 | 50177.1908 | 2440.008
Devonshire Building | 2017-05-05 11:30 | 50177.2608 | 280.008
Devonshire Building | 2017-05-05 11:45 | 50177.3308 | 280.008
Devonshire Building | 2017-05-05 12:00 | 50177.3958 | 259.992
Devonshire Building | 2017-05-05 12:15 | 50177.4658 | 280.008
Devonshire Building | 2017-05-05 12:30 | 50177.5308 | 259.992
Devonshire Building | 2017-05-05 12:45 | 50178.1158 | 2340
Devonshire Building | 2017-05-05 13:00 | 50178.1858 | 280.008
Devonshire Building | 2017-05-05 13:15 | 50178.2458 | 240.012
Devonshire Building | 2017-05-05 13:30 | 50178.3058 | 240.012
Devonshire Building | 2017-05-05 13:45 | 50178.3558 | 200.016
Devonshire Building | 2017-05-05 14:00 | 50178.4108 | 219.996
Devonshire Building | 2017-05-05 14:15 | 50178.9908 | 2319.984
Devonshire Building | 2017-05-05 14:30 | 50179.0358 | 180
Devonshire Building | 2017-05-05 14:45 | 50179.0758 | 159.984
Devonshire Building | 2017-05-05 15:00 | 50179.1208 | 180
Devonshire Building | 2017-05-05 15:15 | 50179.1608 | 159.984
Devonshire Building | 2017-05-05 15:30 | 50179.1958 | 140.004
Devonshire Building | 2017-05-05 15:45 | 50179.5808 | 1540.008
Devonshire Building | 2017-05-05 16:00 | 50179.8258 | 979.992
Devonshire Building | 2017-05-05 16:15 | 50179.8708 | 180
Devonshire Building | 2017-05-05 16:30 | 50179.9258 | 219.996
Devonshire Building | 2017-05-05 16:45 | 50179.9758 | 200.016
Devonshire Building | 2017-05-05 17:00 | 50180.0308 | 219.996
Devonshire Building | 2017-05-05 17:15 | 50180.0758 | 180
Devonshire Building | 2017-05-05 17:30 | 50180.1208 | 180
Devonshire Building | 2017-05-05 17:45 | 50180.1658 | 180
Devonshire Building | 2017-05-05 18:00 | 50180.2008 | 140.004
Devonshire Building | 2017-05-05 18:15 | 50180.2358 | 140.004
Devonshire Building | 2017-05-05 18:30 | 50180.2658 | 119.988
Devonshire Building | 2017-05-05 18:45 | 50180.2908 | 100.008
Devonshire Building | 2017-05-05 19:00 | 50180.3158 | 100.008
Devonshire Building | 2017-05-05 19:15 | 50180.3408 | 100.008
Devonshire Building | 2017-05-05 19:30 | 50180.3608 | 79.992
Devonshire Building | 2017-05-05 19:45 | 50180.3758 | 60.012
Devonshire Building | 2017-05-05 20:00 | 50180.3958 | 79.992
Devonshire Building | 2017-05-05 20:15 | 50180.4108 | 60.012
Devonshire Building | 2017-05-05 20:30 | 50180.4258 | 60.012
Devonshire Building | 2017-05-05 20:45 | 50180.4408 | 60.012
Devonshire Building | 2017-05-05 21:00 | 50180.4658 | 100.008
Devonshire Building | 2017-05-05 21:15 | 50180.4758 | 39.996
Devonshire Building | 2017-05-05 21:30 | 50180.4808 | 20.016
Devonshire Building | 2017-05-05 21:45 | 50180.4858 | 20.016
Devonshire Building | 2017-05-05 22:00 | 50180.4908 | 20.016
Devonshire Building | 2017-05-05 22:15 | 50180.4958 | 20.016
Devonshire Building | 2017-05-05 22:30 | 50180.5058 | 39.996
Devonshire Building | 2017-05-05 22:45 | 50180.5108 | 20.016
Devonshire Building | 2017-05-05 23:00 | 50180.5158 | 20.016
Devonshire Building | 2017-05-05 23:15 | 50180.5208 | 20.016
Devonshire Building | 2017-05-05 23:30 | 50180.5258 | 20.016
Devonshire Building | 2017-05-05 23:45 | 50180.5308 | 20.016
Devonshire Building | 2017-05-06 | 50180.5352 | 20.016
Devonshire Building | 2017-05-06 00:15 | 50180.5452 | 39.996
Devonshire Building | 2017-05-06 00:30 | 50180.5502 | 20.016
Devonshire Building | 2017-05-06 00:45 | 50180.5552 | 20.016
Devonshire Building | 2017-05-06 01:00 | 50180.5602 | 20.016
Devonshire Building | 2017-05-06 01:15 | 50180.5652 | 20.016
Devonshire Building | 2017-05-06 01:30 | 50180.5702 | 20.016
Devonshire Building | 2017-05-06 01:45 | 50180.5752 | 20.016
Devonshire Building | 2017-05-06 02:00 | 50180.5802 | 20.016
Devonshire Building | 2017-05-06 02:15 | 50180.5852 | 20.016
Devonshire Building | 2017-05-06 02:30 | 50180.5902 | 20.016
Devonshire Building | 2017-05-06 02:45 | 50180.5952 | 20.016
Devonshire Building | 2017-05-06 03:00 | 50180.6002 | 20.016
Devonshire Building | 2017-05-06 03:15 | 50180.6052 | 20.016
Devonshire Building | 2017-05-06 03:30 | 50180.6102 | 20.016
Devonshire Building | 2017-05-06 03:45 | 50180.6152 | 20.016
Devonshire Building | 2017-05-06 04:00 | 50180.6202 | 20.016
Devonshire Building | 2017-05-06 04:15 | 50180.6252 | 20.016
Devonshire Building | 2017-05-06 04:30 | 50180.6302 | 20.016
Devonshire Building | 2017-05-06 04:45 | 50180.6352 | 20.016
Devonshire Building | 2017-05-06 05:00 | 50180.6402 | 20.016
Devonshire Building | 2017-05-06 05:15 | 50180.6452 | 20.016
Devonshire Building | 2017-05-06 05:30 | 50180.6452 | 0
Devonshire Building | 2017-05-06 05:45 | 50180.8702 | 900
Devonshire Building | 2017-05-06 06:00 | 50181.1702 | 1199.988
Devonshire Building | 2017-05-06 06:15 | 50181.1752 | 20.016
Devonshire Building | 2017-05-06 06:30 | 50181.1802 | 20.016
Devonshire Building | 2017-05-06 06:45 | 50181.1852 | 20.016
Devonshire Building | 2017-05-06 07:00 | 50181.1903 | 20.016
Devonshire Building | 2017-05-06 07:15 | 50181.1953 | 20.016
Devonshire Building | 2017-05-06 07:30 | 50181.1953 | 0
Devonshire Building | 2017-05-06 07:45 | 50181.2103 | 60.012
Devonshire Building | 2017-05-06 08:00 | 50181.2303 | 79.992
Devonshire Building | 2017-05-06 08:15 | 50181.2503 | 79.992
Devonshire Building | 2017-05-06 08:30 | 50181.2703 | 79.992
Devonshire Building | 2017-05-06 08:45 | 50181.2953 | 100.008
Devonshire Building | 2017-05-06 09:00 | 50181.3203 | 100.008
Devonshire Building | 2017-05-06 09:15 | 50181.3403 | 79.992
Devonshire Building | 2017-05-06 09:30 | 50181.3603 | 79.992
Devonshire Building | 2017-05-06 09:45 | 50181.3853 | 100.008
Devonshire Building | 2017-05-06 10:00 | 50181.4053 | 79.992
Devonshire Building | 2017-05-06 10:15 | 50181.4203 | 60.012
Devonshire Building | 2017-05-06 10:30 | 50181.4253 | 20.016
Devonshire Building | 2017-05-06 10:45 | 50181.4353 | 39.996
Devonshire Building | 2017-05-06 11:00 | 50181.4403 | 20.016
Devonshire Building | 2017-05-06 11:15 | 50181.4453 | 20.016
Devonshire Building | 2017-05-06 11:30 | 50181.4503 | 20.016
Devonshire Building | 2017-05-06 11:45 | 50181.4553 | 20.016
Devonshire Building | 2017-05-06 12:00 | 50181.4653 | 39.996
Devonshire Building | 2017-05-06 12:15 | 50181.4703 | 20.016
Devonshire Building | 2017-05-06 12:30 | 50181.4753 | 20.016
Devonshire Building | 2017-05-06 12:45 | 50181.4853 | 39.996
Devonshire Building | 2017-05-06 13:00 | 50181.4903 | 20.016
Devonshire Building | 2017-05-06 13:15 | 50181.4953 | 20.016
Devonshire Building | 2017-05-06 13:30 | 50181.5003 | 20.016
Devonshire Building | 2017-05-06 13:45 | 50181.5053 | 20.016
Devonshire Building | 2017-05-06 14:00 | 50181.5103 | 20.016
Devonshire Building | 2017-05-06 14:15 | 50181.5153 | 20.016
Devonshire Building | 2017-05-06 14:30 | 50181.5203 | 20.016
Devonshire Building | 2017-05-06 14:45 | 50181.5253 | 20.016
Devonshire Building | 2017-05-06 15:00 | 50181.5303 | 20.016
Devonshire Building | 2017-05-06 15:15 | 50181.5353 | 20.016
Devonshire Building | 2017-05-06 15:30 | 50181.5403 | 20.016
Devonshire Building | 2017-05-06 15:45 | 50181.5453 | 20.016
Devonshire Building | 2017-05-06 16:00 | 50181.5503 | 20.016
Devonshire Building | 2017-05-06 16:15 | 50181.5553 | 20.016
Devonshire Building | 2017-05-06 16:30 | 50181.5603 | 20.016
Devonshire Building | 2017-05-06 16:45 | 50181.5653 | 20.016
Devonshire Building | 2017-05-06 17:00 | 50181.5703 | 20.016
Devonshire Building | 2017-05-06 17:15 | 50181.5754 | 20.016
Devonshire Building | 2017-05-06 17:30 | 50181.5804 | 20.016
Devonshire Building | 2017-05-06 17:45 | 50181.5854 | 20.016
Devonshire Building | 2017-05-06 18:00 | 50181.5904 | 20.016
Devonshire Building | 2017-05-06 18:15 | 50181.5954 | 20.016
Devonshire Building | 2017-05-06 18:30 | 50181.6004 | 20.016
Devonshire Building | 2017-05-06 18:45 | 50181.6004 | 0
Devonshire Building | 2017-05-06 19:00 | 50181.6104 | 39.996
Devonshire Building | 2017-05-06 19:15 | 50181.6154 | 20.016
Devonshire Building | 2017-05-06 19:30 | 50181.6204 | 20.016
Devonshire Building | 2017-05-06 19:45 | 50181.6204 | 0
Devonshire Building | 2017-05-06 20:00 | 50181.6254 | 20.016
Devonshire Building | 2017-05-06 20:15 | 50181.6304 | 20.016
Devonshire Building | 2017-05-06 20:30 | 50181.6354 | 20.016
Devonshire Building | 2017-05-06 20:45 | 50181.6404 | 20.016
Devonshire Building | 2017-05-06 21:00 | 50181.6704 | 119.988
Devonshire Building | 2017-05-06 21:15 | 50181.6754 | 20.016
Devonshire Building | 2017-05-06 21:30 | 50181.6804 | 20.016
Devonshire Building | 2017-05-06 21:45 | 50181.6854 | 20.016
Devonshire Building | 2017-05-06 22:00 | 50181.6904 | 20.016
Devonshire Building | 2017-05-06 22:15 | 50181.7004 | 39.996
Devonshire Building | 2017-05-06 22:30 | 50181.7054 | 20.016
Devonshire Building | 2017-05-06 22:45 | 50182.2204 | 2059.992
Devonshire Building | 2017-05-06 23:00 | 50182.2254 | 20.016
Devonshire Building | 2017-05-06 23:15 | 50182.2304 | 20.016
Devonshire Building | 2017-05-06 23:30 | 50182.2354 | 20.016
Devonshire Building | 2017-05-06 23:45 | 50182.2404 | 20.016
Devonshire Building | 2017-05-07 | 50182.2461 | 20.016
Devonshire Building | 2017-05-07 00:15 | 50182.2511 | 20.016
Devonshire Building | 2017-05-07 00:30 | 50182.2561 | 20.016
Devonshire Building | 2017-05-07 00:45 | 50182.2611 | 20.016
Devonshire Building | 2017-05-07 01:00 | 50182.2661 | 20.016
Devonshire Building | 2017-05-07 01:15 | 50182.2711 | 20.016
Devonshire Building | 2017-05-07 01:30 | 50182.2811 | 39.996
Devonshire Building | 2017-05-07 01:45 | 50182.2861 | 20.016
Devonshire Building | 2017-05-07 02:00 | 50182.2911 | 20.016
Devonshire Building | 2017-05-07 02:15 | 50182.3011 | 39.996
Devonshire Building | 2017-05-07 02:30 | 50182.3061 | 20.016
Devonshire Building | 2017-05-07 02:45 | 50182.3161 | 39.996
Devonshire Building | 2017-05-07 03:00 | 50182.3211 | 20.016
Devonshire Building | 2017-05-07 03:15 | 50182.3311 | 39.996
Devonshire Building | 2017-05-07 03:30 | 50182.3411 | 39.996
Devonshire Building | 2017-05-07 03:45 | 50182.3461 | 20.016
Devonshire Building | 2017-05-07 04:00 | 50182.3561 | 39.996
Devonshire Building | 2017-05-07 04:15 | 50182.3661 | 39.996
Devonshire Building | 2017-05-07 04:30 | 50182.3711 | 20.016
Devonshire Building | 2017-05-07 04:45 | 50182.3811 | 39.996
Devonshire Building | 2017-05-07 05:00 | 50182.3861 | 20.016
Devonshire Building | 2017-05-07 05:15 | 50182.3911 | 20.016
Devonshire Building | 2017-05-07 05:30 | 50182.4011 | 39.996
Devonshire Building | 2017-05-07 05:45 | 50182.4061 | 20.016
Devonshire Building | 2017-05-07 06:00 | 50182.4111 | 20.016
Devonshire Building | 2017-05-07 06:15 | 50182.4211 | 39.996
Devonshire Building | 2017-05-07 06:30 | 50182.4261 | 20.016
Devonshire Building | 2017-05-07 06:45 | 50182.4311 | 20.016
Devonshire Building | 2017-05-07 07:00 | 50182.4362 | 20.016
Devonshire Building | 2017-05-07 07:15 | 50182.4412 | 20.016
Devonshire Building | 2017-05-07 07:30 | 50182.4562 | 60.012
Devonshire Building | 2017-05-07 07:45 | 50182.4762 | 79.992
Devonshire Building | 2017-05-07 08:00 | 50182.4962 | 79.992
Devonshire Building | 2017-05-07 08:15 | 50182.5212 | 100.008
Devonshire Building | 2017-05-07 08:30 | 50182.5412 | 79.992
Devonshire Building | 2017-05-07 08:45 | 50182.5612 | 79.992
Devonshire Building | 2017-05-07 09:00 | 50182.5812 | 79.992
Devonshire Building | 2017-05-07 09:15 | 50182.6062 | 100.008
Devonshire Building | 2017-05-07 09:30 | 50182.6262 | 79.992
Devonshire Building | 2017-05-07 09:45 | 50182.6461 | 79.992
Devonshire Building | 2017-05-07 10:00 | 50182.6661 | 79.992
Devonshire Building | 2017-05-07 10:15 | 50182.6911 | 100.008
Devonshire Building | 2017-05-07 10:30 | 50182.7111 | 79.992
Devonshire Building | 2017-05-07 10:45 | 50182.7162 | 20.016
Devonshire Building | 2017-05-07 11:00 | 50182.7212 | 20.016
Devonshire Building | 2017-05-07 11:15 | 50182.7262 | 20.016
Devonshire Building | 2017-05-07 11:30 | 50182.7312 | 20.016
Devonshire Building | 2017-05-07 11:45 | 50182.7362 | 20.016
Devonshire Building | 2017-05-07 12:00 | 50182.7412 | 20.016
Devonshire Building | 2017-05-07 12:15 | 50182.7462 | 20.016
Devonshire Building | 2017-05-07 12:30 | 50182.7512 | 20.016
Devonshire Building | 2017-05-07 12:45 | 50182.7562 | 20.016
Devonshire Building | 2017-05-07 13:00 | 50182.7612 | 20.016
Devonshire Building | 2017-05-07 13:15 | 50182.7662 | 20.016
Devonshire Building | 2017-05-07 13:30 | 50182.7712 | 20.016
Devonshire Building | 2017-05-07 13:45 | 50182.7762 | 20.016
Devonshire Building | 2017-05-07 14:00 | 50182.7762 | 0
Devonshire Building | 2017-05-07 14:15 | 50182.7812 | 20.016
Devonshire Building | 2017-05-07 14:30 | 50182.7862 | 20.016
Devonshire Building | 2017-05-07 14:45 | 50182.7912 | 20.016
Devonshire Building | 2017-05-07 15:00 | 50182.7962 | 20.016
Devonshire Building | 2017-05-07 15:15 | 50182.8012 | 20.016
Devonshire Building | 2017-05-07 15:30 | 50182.8062 | 20.016
Devonshire Building | 2017-05-07 15:45 | 50182.8112 | 20.016
Devonshire Building | 2017-05-07 16:00 | 50182.8162 | 20.016
Devonshire Building | 2017-05-07 16:15 | 50182.8212 | 20.016
Devonshire Building | 2017-05-07 16:30 | 50182.8262 | 20.016
Devonshire Building | 2017-05-07 16:45 | 50182.8312 | 20.016
Devonshire Building | 2017-05-07 17:00 | 50182.8362 | 20.016
Devonshire Building | 2017-05-07 17:15 | 50182.8362 | 0
Devonshire Building | 2017-05-07 17:30 | 50182.8413 | 20.016
Devonshire Building | 2017-05-07 17:45 | 50182.8463 | 20.016
Devonshire Building | 2017-05-07 18:00 | 50182.8513 | 20.016
Devonshire Building | 2017-05-07 18:15 | 50182.8563 | 20.016
Devonshire Building | 2017-05-07 18:30 | 50182.8613 | 20.016
Devonshire Building | 2017-05-07 18:45 | 50182.8663 | 20.016
Devonshire Building | 2017-05-07 19:00 | 50182.8713 | 20.016
Devonshire Building | 2017-05-07 19:15 | 50182.8763 | 20.016
Devonshire Building | 2017-05-07 19:30 | 50182.8763 | 0
Devonshire Building | 2017-05-07 19:45 | 50182.8813 | 20.016
Devonshire Building | 2017-05-07 20:00 | 50182.8863 | 20.016
Devonshire Building | 2017-05-07 20:15 | 50182.8913 | 20.016
Devonshire Building | 2017-05-07 20:30 | 50182.8963 | 20.016
Devonshire Building | 2017-05-07 20:45 | 50182.9013 | 20.016
Devonshire Building | 2017-05-07 21:00 | 50182.9263 | 100.008
Devonshire Building | 2017-05-07 21:15 | 50182.9313 | 20.016
Devonshire Building | 2017-05-07 21:30 | 50182.9313 | 0
Devonshire Building | 2017-05-07 21:45 | 50182.9363 | 20.016
Devonshire Building | 2017-05-07 22:00 | 50182.9413 | 20.016
Devonshire Building | 2017-05-07 22:15 | 50182.9463 | 20.016
Devonshire Building | 2017-05-07 22:30 | 50182.9463 | 0
Devonshire Building | 2017-05-07 22:45 | 50182.9513 | 20.016
Devonshire Building | 2017-05-07 23:00 | 50182.9563 | 20.016
Devonshire Building | 2017-05-07 23:15 | 50182.9563 | 0
Devonshire Building | 2017-05-07 23:30 | 50182.9613 | 20.016
Devonshire Building | 2017-05-07 23:45 | 50183.4313 | 1879.992
Devonshire Building | 2017-05-08 | 50183.4766 | 180
Devonshire Building | 2017-05-08 00:15 | 50183.4816 | 20.016
Devonshire Building | 2017-05-08 00:30 | 50183.4816 | 0
Devonshire Building | 2017-05-08 00:45 | 50183.4866 | 20.016
Devonshire Building | 2017-05-08 01:00 | 50183.4916 | 20.016
Devonshire Building | 2017-05-08 01:15 | 50183.4916 | 0
Devonshire Building | 2017-05-08 01:30 | 50183.4966 | 20.016
Devonshire Building | 2017-05-08 01:45 | 50183.4966 | 0
Devonshire Building | 2017-05-08 02:00 | 50183.5016 | 20.016
Devonshire Building | 2017-05-08 02:15 | 50183.5066 | 20.016
Devonshire Building | 2017-05-08 02:30 | 50183.5066 | 0
Devonshire Building | 2017-05-08 02:45 | 50183.5116 | 20.016
Devonshire Building | 2017-05-08 03:00 | 50183.5116 | 0
Devonshire Building | 2017-05-08 03:15 | 50183.5166 | 20.016
Devonshire Building | 2017-05-08 03:30 | 50183.5216 | 20.016
Devonshire Building | 2017-05-08 03:45 | 50183.5216 | 0
Devonshire Building | 2017-05-08 04:00 | 50183.5266 | 20.016
Devonshire Building | 2017-05-08 04:15 | 50183.5316 | 20.016
Devonshire Building | 2017-05-08 04:30 | 50183.5316 | 0
Devonshire Building | 2017-05-08 04:45 | 50183.5366 | 20.016
Devonshire Building | 2017-05-08 05:00 | 50183.5366 | 0
Devonshire Building | 2017-05-08 05:15 | 50183.5416 | 20.016
Devonshire Building | 2017-05-08 05:30 | 50183.5466 | 20.016
Devonshire Building | 2017-05-08 05:45 | 50183.5516 | 20.016
Devonshire Building | 2017-05-08 06:00 | 50183.5566 | 20.016
Devonshire Building | 2017-05-08 06:15 | 50183.5616 | 20.016
Devonshire Building | 2017-05-08 06:30 | 50183.5716 | 39.996
Devonshire Building | 2017-05-08 06:45 | 50183.5766 | 20.016
Devonshire Building | 2017-05-08 07:00 | 50183.5816 | 20.016
Devonshire Building | 2017-05-08 07:15 | 50183.5916 | 39.996
Devonshire Building | 2017-05-08 07:30 | 50183.6016 | 39.996
Devonshire Building | 2017-05-08 07:45 | 50183.6266 | 100.008
Devonshire Building | 2017-05-08 08:00 | 50184.0366 | 1640.016
Devonshire Building | 2017-05-08 08:15 | 50184.2066 | 680.004
Devonshire Building | 2017-05-08 08:30 | 50184.2316 | 100.008
Devonshire Building | 2017-05-08 08:45 | 50184.2616 | 119.988
Devonshire Building | 2017-05-08 09:00 | 50184.2916 | 119.988
Devonshire Building | 2017-05-08 09:15 | 50184.9166 | 2499.984
Devonshire Building | 2017-05-08 09:30 | 50184.9616 | 180
Devonshire Building | 2017-05-08 09:45 | 50185.0116 | 200.016
Devonshire Building | 2017-05-08 10:00 | 50185.1216 | 439.992
Devonshire Building | 2017-05-08 10:15 | 50185.5666 | 1779.984
Devonshire Building | 2017-05-08 10:30 | 50186.1966 | 2520
Devonshire Building | 2017-05-08 10:45 | 50186.3466 | 600.012
Devonshire Building | 2017-05-08 11:00 | 50186.4466 | 399.996
Devonshire Building | 2017-05-08 11:15 | 50186.5216 | 299.988
Devonshire Building | 2017-05-08 11:30 | 50186.6016 | 320.004
Devonshire Building | 2017-05-08 11:45 | 50187.2216 | 2480.004
Devonshire Building | 2017-05-08 12:00 | 50187.2766 | 219.996
Devonshire Building | 2017-05-08 12:15 | 50187.3266 | 200.016
Devonshire Building | 2017-05-08 12:30 | 50187.3816 | 219.996
Devonshire Building | 2017-05-08 12:45 | 50187.4266 | 180
Devonshire Building | 2017-05-08 13:00 | 50187.7216 | 1180.008
Devonshire Building | 2017-05-08 13:15 | 50188.1116 | 1559.988
Devonshire Building | 2017-05-08 13:30 | 50188.1466 | 140.004
Devonshire Building | 2017-05-08 13:45 | 50188.1916 | 180
Devonshire Building | 2017-05-08 14:00 | 50188.2366 | 180
Devonshire Building | 2017-05-08 14:15 | 50188.2766 | 159.984
Devonshire Building | 2017-05-08 14:30 | 50188.8916 | 2459.988
Devonshire Building | 2017-05-08 14:45 | 50188.9516 | 240.012
Devonshire Building | 2017-05-08 15:00 | 50189.0216 | 280.008
Devonshire Building | 2017-05-08 15:15 | 50189.0966 | 299.988
Devonshire Building | 2017-05-08 15:30 | 50189.1816 | 339.984
Devonshire Building | 2017-05-08 15:45 | 50189.2816 | 399.996
Devonshire Building | 2017-05-08 16:00 | 50189.9166 | 2540.016
Devonshire Building | 2017-05-08 16:15 | 50190.0016 | 339.984
Devonshire Building | 2017-05-08 16:30 | 50190.0716 | 280.008
Devonshire Building | 2017-05-08 16:45 | 50190.1316 | 240.012
Devonshire Building | 2017-05-08 17:00 | 50190.1866 | 219.996
Devonshire Building | 2017-05-08 17:15 | 50190.2416 | 219.996
Devonshire Building | 2017-05-08 17:30 | 50190.2966 | 219.996
Devonshire Building | 2017-05-08 17:45 | 50190.3366 | 159.984
Devonshire Building | 2017-05-08 18:00 | 50190.3816 | 180
Devonshire Building | 2017-05-08 18:15 | 50190.4316 | 200.016
Devonshire Building | 2017-05-08 18:30 | 50190.4766 | 180
Devonshire Building | 2017-05-08 18:45 | 50190.5116 | 140.004
Devonshire Building | 2017-05-08 19:00 | 50190.5416 | 119.988
Devonshire Building | 2017-05-08 19:15 | 50190.5766 | 140.004
Devonshire Building | 2017-05-08 19:30 | 50190.6066 | 119.988
Devonshire Building | 2017-05-08 19:45 | 50190.6366 | 119.988
Devonshire Building | 2017-05-08 20:00 | 50190.6666 | 119.988
Devonshire Building | 2017-05-08 20:15 | 50190.6916 | 100.008
Devonshire Building | 2017-05-08 20:30 | 50190.7066 | 60.012
Devonshire Building | 2017-05-08 20:45 | 50190.7166 | 39.996
Devonshire Building | 2017-05-08 21:00 | 50190.7466 | 119.988
Devonshire Building | 2017-05-08 21:15 | 50190.7466 | 0
Devonshire Building | 2017-05-08 21:30 | 50190.7516 | 20.016
Devonshire Building | 2017-05-08 21:45 | 50190.7566 | 20.016
Devonshire Building | 2017-05-08 22:00 | 50190.7616 | 20.016
Devonshire Building | 2017-05-08 22:15 | 50190.7716 | 39.996
Devonshire Building | 2017-05-08 22:30 | 50190.7766 | 20.016
Devonshire Building | 2017-05-08 22:45 | 50190.7766 | 0
Devonshire Building | 2017-05-08 23:00 | 50190.7816 | 20.016
Devonshire Building | 2017-05-08 23:15 | 50190.7866 | 20.016
Devonshire Building | 2017-05-08 23:30 | 50190.7916 | 20.016
Devonshire Building | 2017-05-08 23:45 | 50190.7966 | 20.016
Devonshire Building | 2017-05-09 | 50190.793 | 0
Devonshire Building | 2017-05-09 00:15 | 50190.798 | 20.016
Devonshire Building | 2017-05-09 00:30 | 50190.803 | 20.016
Devonshire Building | 2017-05-09 00:45 | 50190.808 | 20.016
Devonshire Building | 2017-05-09 01:00 | 50190.808 | 0
Devonshire Building | 2017-05-09 01:15 | 50191.333 | 2099.988
Devonshire Building | 2017-05-09 01:30 | 50191.338 | 20.016
Devonshire Building | 2017-05-09 01:45 | 50191.343 | 20.016
Devonshire Building | 2017-05-09 02:00 | 50191.343 | 0
Devonshire Building | 2017-05-09 02:15 | 50191.348 | 20.016
Devonshire Building | 2017-05-09 02:30 | 50191.353 | 20.016
Devonshire Building | 2017-05-09 02:45 | 50191.358 | 20.016
Devonshire Building | 2017-05-09 03:00 | 50191.358 | 0
Devonshire Building | 2017-05-09 03:15 | 50191.363 | 20.016
Devonshire Building | 2017-05-09 03:30 | 50191.368 | 20.016
Devonshire Building | 2017-05-09 03:45 | 50191.373 | 20.016
Devonshire Building | 2017-05-09 04:00 | 50191.373 | 0
Devonshire Building | 2017-05-09 04:15 | 50191.378 | 20.016
Devonshire Building | 2017-05-09 04:30 | 50191.383 | 20.016
Devonshire Building | 2017-05-09 04:45 | 50191.388 | 20.016
Devonshire Building | 2017-05-09 05:00 | 50191.388 | 0
Devonshire Building | 2017-05-09 05:15 | 50191.393 | 20.016
Devonshire Building | 2017-05-09 05:30 | 50191.398 | 20.016
Devonshire Building | 2017-05-09 05:45 | 50191.403 | 20.016
Devonshire Building | 2017-05-09 06:00 | 50191.408 | 20.016
Devonshire Building | 2017-05-09 06:15 | 50191.413 | 20.016
Devonshire Building | 2017-05-09 06:30 | 50191.423 | 39.996
Devonshire Building | 2017-05-09 06:45 | 50191.428 | 20.016
Devonshire Building | 2017-05-09 07:00 | 50191.433 | 20.016
Devonshire Building | 2017-05-09 07:15 | 50191.4381 | 20.016
Devonshire Building | 2017-05-09 07:30 | 50191.4481 | 39.996
Devonshire Building | 2017-05-09 07:45 | 50191.4631 | 60.012
Devonshire Building | 2017-05-09 08:00 | 50191.4931 | 119.988
Devonshire Building | 2017-05-09 08:15 | 50191.5131 | 79.992
Devonshire Building | 2017-05-09 08:30 | 50192.073 | 2239.992
Devonshire Building | 2017-05-09 08:45 | 50192.113 | 159.984
Devonshire Building | 2017-05-09 09:00 | 50192.143 | 119.988
Devonshire Building | 2017-05-09 09:15 | 50192.183 | 159.984
Devonshire Building | 2017-05-09 09:30 | 50192.228 | 180
Devonshire Building | 2017-05-09 09:45 | 50192.893 | 2660.004
Devonshire Building | 2017-05-09 10:00 | 50192.978 | 339.984
Devonshire Building | 2017-05-09 10:15 | 50193.058 | 320.004
Devonshire Building | 2017-05-09 10:30 | 50193.133 | 299.988
Devonshire Building | 2017-05-09 10:45 | 50193.198 | 259.992
Devonshire Building | 2017-05-09 11:00 | 50193.833 | 2540.016
Devonshire Building | 2017-05-09 11:15 | 50193.928 | 380.016
Devonshire Building | 2017-05-09 11:30 | 50194.088 | 640.008
Devonshire Building | 2017-05-09 11:45 | 50194.278 | 759.996
Devonshire Building | 2017-05-09 12:00 | 50194.418 | 560.016
Devonshire Building | 2017-05-09 12:15 | 50195.093 | 2700
Devonshire Building | 2017-05-09 12:30 | 50195.198 | 420.012
Devonshire Building | 2017-05-09 12:45 | 50195.308 | 439.992
Devonshire Building | 2017-05-09 13:00 | 50195.398 | 360
Devonshire Building | 2017-05-09 13:15 | 50195.473 | 299.988
Devonshire Building | 2017-05-09 13:30 | 50195.538 | 259.992
Devonshire Building | 2017-05-09 13:45 | 50195.608 | 280.008
Devonshire Building | 2017-05-09 14:00 | 50196.213 | 2419.992
Devonshire Building | 2017-05-09 14:15 | 50196.248 | 140.004
Devonshire Building | 2017-05-09 14:30 | 50196.278 | 119.988
Devonshire Building | 2017-05-09 14:45 | 50196.308 | 119.988
Devonshire Building | 2017-05-09 15:00 | 50196.333 | 100.008
Devonshire Building | 2017-05-09 15:15 | 50196.373 | 159.984
Devonshire Building | 2017-05-09 15:30 | 50196.648 | 1100.016
Devonshire Building | 2017-05-09 15:45 | 50196.983 | 1339.992
Devonshire Building | 2017-05-09 16:00 | 50197.013 | 119.988
Devonshire Building | 2017-05-09 16:15 | 50197.033 | 79.992
Devonshire Building | 2017-05-09 16:30 | 50197.063 | 119.988
Devonshire Building | 2017-05-09 16:45 | 50197.083 | 79.992
Devonshire Building | 2017-05-09 17:00 | 50197.113 | 119.988
Devonshire Building | 2017-05-09 17:15 | 50197.133 | 79.992
Devonshire Building | 2017-05-09 17:30 | 50197.158 | 100.008
Devonshire Building | 2017-05-09 17:45 | 50197.698 | 2160
Devonshire Building | 2017-05-09 18:00 | 50197.718 | 79.992
Devonshire Building | 2017-05-09 18:15 | 50197.738 | 79.992
Devonshire Building | 2017-05-09 18:30 | 50197.763 | 100.008
Devonshire Building | 2017-05-09 18:45 | 50197.788 | 100.008
Devonshire Building | 2017-05-09 19:00 | 50197.813 | 100.008
Devonshire Building | 2017-05-09 19:15 | 50197.833 | 79.992
Devonshire Building | 2017-05-09 19:30 | 50197.858 | 100.008
Devonshire Building | 2017-05-09 19:45 | 50197.878 | 79.992
Devonshire Building | 2017-05-09 20:00 | 50197.898 | 79.992
Devonshire Building | 2017-05-09 20:15 | 50197.913 | 60.012
Devonshire Building | 2017-05-09 20:30 | 50197.933 | 79.992
Devonshire Building | 2017-05-09 20:45 | 50197.953 | 79.992
Devonshire Building | 2017-05-09 21:00 | 50197.973 | 79.992
Devonshire Building | 2017-05-09 21:15 | 50197.988 | 60.012
Devonshire Building | 2017-05-09 21:30 | 50198.003 | 60.012
Devonshire Building | 2017-05-09 21:45 | 50198.018 | 60.012
Devonshire Building | 2017-05-09 22:00 | 50198.028 | 39.996
Devonshire Building | 2017-05-09 22:15 | 50198.043 | 60.012
Devonshire Building | 2017-05-09 22:30 | 50198.058 | 60.012
Devonshire Building | 2017-05-09 22:45 | 50198.068 | 39.996
Devonshire Building | 2017-05-09 23:00 | 50198.083 | 60.012
Devonshire Building | 2017-05-09 23:15 | 50198.098 | 60.012
Devonshire Building | 2017-05-09 23:30 | 50198.108 | 39.996
Devonshire Building | 2017-05-09 23:45 | 50198.123 | 60.012
Devonshire Building | 2017-05-10 | 50198.1328 | 39.996
Devonshire Building | 2017-05-10 00:15 | 50198.1478 | 60.012
Devonshire Building | 2017-05-10 00:30 | 50198.1578 | 39.996
Devonshire Building | 2017-05-10 00:45 | 50198.1678 | 39.996
Devonshire Building | 2017-05-10 01:00 | 50198.1828 | 60.012
Devonshire Building | 2017-05-10 01:15 | 50198.1928 | 39.996
Devonshire Building | 2017-05-10 01:30 | 50198.2028 | 39.996
Devonshire Building | 2017-05-10 01:45 | 50198.2128 | 39.996
Devonshire Building | 2017-05-10 02:00 | 50198.2278 | 60.012
Devonshire Building | 2017-05-10 02:15 | 50198.2378 | 39.996
Devonshire Building | 2017-05-10 02:30 | 50198.2478 | 39.996
Devonshire Building | 2017-05-10 02:45 | 50198.2578 | 39.996
Devonshire Building | 2017-05-10 03:00 | 50198.2678 | 39.996
Devonshire Building | 2017-05-10 03:15 | 50198.2778 | 39.996
Devonshire Building | 2017-05-10 03:30 | 50198.2878 | 39.996
Devonshire Building | 2017-05-10 03:45 | 50198.2978 | 39.996
Devonshire Building | 2017-05-10 04:00 | 50198.3078 | 39.996
Devonshire Building | 2017-05-10 04:15 | 50198.3178 | 39.996
Devonshire Building | 2017-05-10 04:30 | 50198.3228 | 20.016
Devonshire Building | 2017-05-10 04:45 | 50198.3328 | 39.996
Devonshire Building | 2017-05-10 05:00 | 50198.3428 | 39.996
Devonshire Building | 2017-05-10 05:15 | 50198.3528 | 39.996
Devonshire Building | 2017-05-10 05:30 | 50198.3628 | 39.996
Devonshire Building | 2017-05-10 05:45 | 50198.3728 | 39.996
Devonshire Building | 2017-05-10 06:00 | 50198.3778 | 20.016
Devonshire Building | 2017-05-10 06:15 | 50198.3878 | 39.996
Devonshire Building | 2017-05-10 06:30 | 50198.3928 | 20.016
Devonshire Building | 2017-05-10 06:45 | 50198.4128 | 79.992
Devonshire Building | 2017-05-10 07:00 | 50198.4228 | 39.996
Devonshire Building | 2017-05-10 07:15 | 50198.4328 | 39.996
Devonshire Building | 2017-05-10 07:30 | 50198.4428 | 39.996
Devonshire Building | 2017-05-10 07:45 | 50198.7428 | 1199.988
Devonshire Building | 2017-05-10 08:00 | 50199.0278 | 1140.012
Devonshire Building | 2017-05-10 08:15 | 50199.0578 | 119.988
Devonshire Building | 2017-05-10 08:30 | 50199.0878 | 119.988
Devonshire Building | 2017-05-10 08:45 | 50199.1228 | 140.004
Devonshire Building | 2017-05-10 09:00 | 50199.1578 | 140.004
Devonshire Building | 2017-05-10 09:15 | 50199.7478 | 2360.016
Devonshire Building | 2017-05-10 09:30 | 50199.7978 | 200.016
Devonshire Building | 2017-05-10 09:45 | 50199.8528 | 219.996
Devonshire Building | 2017-05-10 10:00 | 50199.9178 | 259.992
Devonshire Building | 2017-05-10 10:15 | 50200.3078 | 1559.988
Devonshire Building | 2017-05-10 10:30 | 50200.5828 | 1100.016
Devonshire Building | 2017-05-10 10:45 | 50200.6378 | 219.996
Devonshire Building | 2017-05-10 11:00 | 50200.6878 | 200.016
Devonshire Building | 2017-05-10 11:15 | 50200.7478 | 240.012
Devonshire Building | 2017-05-10 11:30 | 50201.3228 | 2300.004
Devonshire Building | 2017-05-10 11:45 | 50201.4778 | 619.992
Devonshire Building | 2017-05-10 12:00 | 50201.5878 | 439.992
Devonshire Building | 2017-05-10 12:15 | 50201.6878 | 399.996
Devonshire Building | 2017-05-10 12:30 | 50201.8028 | 460.008
Devonshire Building | 2017-05-10 12:45 | 50201.9178 | 460.008
Devonshire Building | 2017-05-10 13:00 | 50202.5728 | 2620.008
Devonshire Building | 2017-05-10 13:15 | 50202.6578 | 339.984
Devonshire Building | 2017-05-10 13:30 | 50202.7428 | 339.984
Devonshire Building | 2017-05-10 13:45 | 50202.8128 | 280.008
Devonshire Building | 2017-05-10 14:00 | 50202.8728 | 240.012
Devonshire Building | 2017-05-10 14:15 | 50202.9178 | 180
Devonshire Building | 2017-05-10 14:30 | 50203.5028 | 2340
Devonshire Building | 2017-05-10 14:45 | 50203.5478 | 180
Devonshire Building | 2017-05-10 15:00 | 50203.5878 | 159.984
Devonshire Building | 2017-05-10 15:15 | 50203.6328 | 180
Devonshire Building | 2017-05-10 15:30 | 50203.6778 | 180
Devonshire Building | 2017-05-10 15:45 | 50204.2228 | 2180.016
Devonshire Building | 2017-05-10 16:00 | 50204.3978 | 699.984
Devonshire Building | 2017-05-10 16:15 | 50204.5478 | 600.012
Devonshire Building | 2017-05-10 16:30 | 50204.6628 | 460.008
Devonshire Building | 2017-05-10 16:45 | 50204.7478 | 339.984
Devonshire Building | 2017-05-10 17:00 | 50204.8128 | 259.992
Devonshire Building | 2017-05-10 17:15 | 50204.8628 | 200.016
Devonshire Building | 2017-05-10 17:30 | 50204.9028 | 159.984
Devonshire Building | 2017-05-10 17:45 | 50204.9378 | 140.004
Devonshire Building | 2017-05-10 18:00 | 50204.9678 | 119.988
Devonshire Building | 2017-05-10 18:15 | 50204.9928 | 100.008
Devonshire Building | 2017-05-10 18:30 | 50205.0128 | 79.992
Devonshire Building | 2017-05-10 18:45 | 50205.0378 | 100.008
Devonshire Building | 2017-05-10 19:00 | 50205.0528 | 60.012
Devonshire Building | 2017-05-10 19:15 | 50205.0728 | 79.992
Devonshire Building | 2017-05-10 19:30 | 50205.0878 | 60.012
Devonshire Building | 2017-05-10 19:45 | 50205.1028 | 60.012
Devonshire Building | 2017-05-10 20:00 | 50205.1228 | 79.992
Devonshire Building | 2017-05-10 20:15 | 50205.1328 | 39.996
Devonshire Building | 2017-05-10 20:30 | 50205.1478 | 60.012
Devonshire Building | 2017-05-10 20:45 | 50205.1628 | 60.012
Devonshire Building | 2017-05-10 21:00 | 50205.1878 | 100.008
Devonshire Building | 2017-05-10 21:15 | 50205.1928 | 20.016
Devonshire Building | 2017-05-10 21:30 | 50205.1978 | 20.016
Devonshire Building | 2017-05-10 21:45 | 50205.2028 | 20.016
Devonshire Building | 2017-05-10 22:00 | 50205.2078 | 20.016
Devonshire Building | 2017-05-10 22:15 | 50205.2128 | 20.016
Devonshire Building | 2017-05-10 22:30 | 50205.2178 | 20.016
Devonshire Building | 2017-05-10 22:45 | 50205.2178 | 0
Devonshire Building | 2017-05-10 23:00 | 50205.2228 | 20.016
Devonshire Building | 2017-05-10 23:15 | 50205.2279 | 20.016
Devonshire Building | 2017-05-10 23:30 | 50205.2329 | 20.016
Devonshire Building | 2017-05-10 23:45 | 50205.2379 | 20.016
Devonshire Building | 2017-05-11 | 50205.2461 | 20.016
Devonshire Building | 2017-05-11 00:15 | 50205.7611 | 2059.992
Devonshire Building | 2017-05-11 00:30 | 50205.7611 | 0
Devonshire Building | 2017-05-11 00:45 | 50205.7661 | 20.016
Devonshire Building | 2017-05-11 01:00 | 50205.7711 | 20.016
Devonshire Building | 2017-05-11 01:15 | 50205.7761 | 20.016
Devonshire Building | 2017-05-11 01:30 | 50205.7811 | 20.016
Devonshire Building | 2017-05-11 01:45 | 50205.7861 | 20.016
Devonshire Building | 2017-05-11 02:00 | 50205.7911 | 20.016
Devonshire Building | 2017-05-11 02:15 | 50205.7961 | 20.016
Devonshire Building | 2017-05-11 02:30 | 50205.8011 | 20.016
Devonshire Building | 2017-05-11 02:45 | 50205.8011 | 0
Devonshire Building | 2017-05-11 03:00 | 50205.8061 | 20.016
Devonshire Building | 2017-05-11 03:15 | 50205.8111 | 20.016
Devonshire Building | 2017-05-11 03:30 | 50205.8161 | 20.016
Devonshire Building | 2017-05-11 03:45 | 50205.8211 | 20.016
Devonshire Building | 2017-05-11 04:00 | 50205.8261 | 20.016
Devonshire Building | 2017-05-11 04:15 | 50205.8311 | 20.016
Devonshire Building | 2017-05-11 04:30 | 50205.8361 | 20.016
Devonshire Building | 2017-05-11 04:45 | 50205.8412 | 20.016
Devonshire Building | 2017-05-11 05:00 | 50205.8462 | 20.016
Devonshire Building | 2017-05-11 05:15 | 50205.8512 | 20.016
Devonshire Building | 2017-05-11 05:30 | 50205.8562 | 20.016
Devonshire Building | 2017-05-11 05:45 | 50205.8662 | 39.996
Devonshire Building | 2017-05-11 06:00 | 50205.8712 | 20.016
Devonshire Building | 2017-05-11 06:15 | 50205.8762 | 20.016
Devonshire Building | 2017-05-11 06:30 | 50205.8812 | 20.016
Devonshire Building | 2017-05-11 06:45 | 50205.8912 | 39.996
Devonshire Building | 2017-05-11 07:00 | 50205.8962 | 20.016
Devonshire Building | 2017-05-11 07:15 | 50205.9062 | 39.996
Devonshire Building | 2017-05-11 07:30 | 50205.9112 | 20.016
Devonshire Building | 2017-05-11 07:45 | 50205.9362 | 100.008
Devonshire Building | 2017-05-11 08:00 | 50205.9712 | 140.004
Devonshire Building | 2017-05-11 08:15 | 50206.2262 | 1019.988
Devonshire Building | 2017-05-11 08:30 | 50206.6062 | 1519.992
Devonshire Building | 2017-05-11 08:45 | 50206.6662 | 240.012
Devonshire Building | 2017-05-11 09:00 | 50206.7262 | 240.012
Devonshire Building | 2017-05-11 09:15 | 50206.7912 | 259.992
Devonshire Building | 2017-05-11 09:30 | 50207.4112 | 2480.004
Devonshire Building | 2017-05-11 09:45 | 50207.5012 | 360
Devonshire Building | 2017-05-11 10:00 | 50207.5962 | 380.016
Devonshire Building | 2017-05-11 10:15 | 50207.6712 | 299.988
Devonshire Building | 2017-05-11 10:30 | 50207.7312 | 240.012
Devonshire Building | 2017-05-11 10:45 | 50207.7812 | 200.016
Devonshire Building | 2017-05-11 11:00 | 50208.4012 | 2480.004
Devonshire Building | 2017-05-11 11:15 | 50208.4462 | 180
Devonshire Building | 2017-05-11 11:30 | 50208.5012 | 219.996
Devonshire Building | 2017-05-11 11:45 | 50208.5512 | 200.016
Devonshire Building | 2017-05-11 12:00 | 50208.6062 | 219.996
Devonshire Building | 2017-05-11 12:15 | 50209.2462 | 2559.996
Devonshire Building | 2017-05-11 12:30 | 50209.2962 | 200.016
Devonshire Building | 2017-05-11 12:45 | 50209.3462 | 200.016
Devonshire Building | 2017-05-11 13:00 | 50209.4062 | 240.012
Devonshire Building | 2017-05-11 13:15 | 50209.4562 | 200.016
Devonshire Building | 2017-05-11 13:30 | 50209.5012 | 180
Devonshire Building | 2017-05-11 13:45 | 50209.5662 | 259.992
Devonshire Building | 2017-05-11 14:00 | 50210.1662 | 2400.012
Devonshire Building | 2017-05-11 14:15 | 50210.2362 | 280.008
Devonshire Building | 2017-05-11 14:30 | 50210.3012 | 259.992
Devonshire Building | 2017-05-11 14:45 | 50210.3612 | 240.012
Devonshire Building | 2017-05-11 15:00 | 50210.4162 | 219.996
Devonshire Building | 2017-05-11 15:15 | 50210.4662 | 200.016
Devonshire Building | 2017-05-11 15:30 | 50210.5212 | 219.996
Devonshire Building | 2017-05-11 15:45 | 50211.1012 | 2319.984
Devonshire Building | 2017-05-11 16:00 | 50211.1562 | 219.996
Devonshire Building | 2017-05-11 16:15 | 50211.2162 | 240.012
Devonshire Building | 2017-05-11 16:30 | 50211.2712 | 219.996
Devonshire Building | 2017-05-11 16:45 | 50211.3212 | 200.016
Devonshire Building | 2017-05-11 17:00 | 50211.3612 | 159.984
Devonshire Building | 2017-05-11 17:15 | 50211.3962 | 140.004
Devonshire Building | 2017-05-11 17:30 | 50211.4312 | 140.004
Devonshire Building | 2017-05-11 17:45 | 50211.4662 | 140.004
Devonshire Building | 2017-05-11 18:00 | 50211.4862 | 79.992
Devonshire Building | 2017-05-11 18:15 | 50211.5112 | 100.008
Devonshire Building | 2017-05-11 18:30 | 50211.5312 | 79.992
Devonshire Building | 2017-05-11 18:45 | 50211.5512 | 79.992
Devonshire Building | 2017-05-11 19:00 | 50211.5662 | 60.012
Devonshire Building | 2017-05-11 19:15 | 50211.5812 | 60.012
Devonshire Building | 2017-05-11 19:30 | 50211.5962 | 60.012
Devonshire Building | 2017-05-11 19:45 | 50211.6112 | 60.012
Devonshire Building | 2017-05-11 20:00 | 50211.6262 | 60.012
Devonshire Building | 2017-05-11 20:15 | 50211.6412 | 60.012
Devonshire Building | 2017-05-11 20:30 | 50211.6512 | 39.996
Devonshire Building | 2017-05-11 20:45 | 50211.6662 | 60.012
Devonshire Building | 2017-05-11 21:00 | 50211.6962 | 119.988
Devonshire Building | 2017-05-11 21:15 | 50211.7012 | 20.016
Devonshire Building | 2017-05-11 21:30 | 50211.7062 | 20.016
Devonshire Building | 2017-05-11 21:45 | 50211.7112 | 20.016
Devonshire Building | 2017-05-11 22:00 | 50211.7162 | 20.016
Devonshire Building | 2017-05-11 22:15 | 50211.7212 | 20.016
Devonshire Building | 2017-05-11 22:30 | 50211.7263 | 20.016
Devonshire Building | 2017-05-11 22:45 | 50211.7313 | 20.016
Devonshire Building | 2017-05-11 23:00 | 50212.2513 | 2080.008
Devonshire Building | 2017-05-11 23:15 | 50212.2563 | 20.016
Devonshire Building | 2017-05-11 23:30 | 50212.2613 | 20.016
Devonshire Building | 2017-05-11 23:45 | 50212.2663 | 20.016
Devonshire Building | 2017-05-12 | 50212.2695 | 20.016
Devonshire Building | 2017-05-12 00:15 | 50212.2695 | 0
Devonshire Building | 2017-05-12 00:30 | 50212.2745 | 20.016
Devonshire Building | 2017-05-12 00:45 | 50212.2795 | 20.016
Devonshire Building | 2017-05-12 01:00 | 50212.2845 | 20.016
Devonshire Building | 2017-05-12 01:15 | 50212.2895 | 20.016
Devonshire Building | 2017-05-12 01:30 | 50212.2945 | 20.016
Devonshire Building | 2017-05-12 01:45 | 50212.2996 | 20.016
Devonshire Building | 2017-05-12 02:00 | 50212.3046 | 20.016
Devonshire Building | 2017-05-12 02:15 | 50212.3096 | 20.016
Devonshire Building | 2017-05-12 02:30 | 50212.3096 | 0
Devonshire Building | 2017-05-12 02:45 | 50212.3146 | 20.016
Devonshire Building | 2017-05-12 03:00 | 50212.3196 | 20.016
Devonshire Building | 2017-05-12 03:15 | 50212.3246 | 20.016
Devonshire Building | 2017-05-12 03:30 | 50212.3296 | 20.016
Devonshire Building | 2017-05-12 03:45 | 50212.3346 | 20.016
Devonshire Building | 2017-05-12 04:00 | 50212.3446 | 39.996
Devonshire Building | 2017-05-12 04:15 | 50212.3496 | 20.016
Devonshire Building | 2017-05-12 04:30 | 50212.3546 | 20.016
Devonshire Building | 2017-05-12 04:45 | 50212.3596 | 20.016
Devonshire Building | 2017-05-12 05:00 | 50212.3646 | 20.016
Devonshire Building | 2017-05-12 05:15 | 50212.3696 | 20.016
Devonshire Building | 2017-05-12 05:30 | 50212.3746 | 20.016
Devonshire Building | 2017-05-12 05:45 | 50212.3796 | 20.016
Devonshire Building | 2017-05-12 06:00 | 50212.3846 | 20.016
Devonshire Building | 2017-05-12 06:15 | 50212.3896 | 20.016
Devonshire Building | 2017-05-12 06:30 | 50212.3946 | 20.016
Devonshire Building | 2017-05-12 06:45 | 50212.4046 | 39.996
Devonshire Building | 2017-05-12 07:00 | 50212.4096 | 20.016
Devonshire Building | 2017-05-12 07:15 | 50212.4296 | 79.992
Devonshire Building | 2017-05-12 07:30 | 50212.4446 | 60.012
Devonshire Building | 2017-05-12 07:45 | 50212.4846 | 159.984
Devonshire Building | 2017-05-12 08:00 | 50212.5446 | 240.012
Devonshire Building | 2017-05-12 08:15 | 50212.8596 | 1260
Devonshire Building | 2017-05-12 08:30 | 50213.2346 | 1500.012
Devonshire Building | 2017-05-12 08:45 | 50213.3296 | 380.016
Devonshire Building | 2017-05-12 09:00 | 50213.4196 | 360
Devonshire Building | 2017-05-12 09:15 | 50213.5096 | 360
Devonshire Building | 2017-05-12 09:30 | 50213.5896 | 320.004
Devonshire Building | 2017-05-12 09:45 | 50213.6896 | 399.996
Devonshire Building | 2017-05-12 10:00 | 50214.3246 | 2540.016
Devonshire Building | 2017-05-12 10:15 | 50214.4246 | 399.996
Devonshire Building | 2017-05-12 10:30 | 50214.6246 | 799.992
Devonshire Building | 2017-05-12 10:45 | 50214.7846 | 640.008
Devonshire Building | 2017-05-12 11:00 | 50214.9196 | 540
Devonshire Building | 2017-05-12 11:15 | 50215.0196 | 399.996
Devonshire Building | 2017-05-12 11:30 | 50215.6246 | 2419.992
Devonshire Building | 2017-05-12 11:45 | 50215.6846 | 240.012
Devonshire Building | 2017-05-12 12:00 | 50215.7496 | 259.992
Devonshire Building | 2017-05-12 12:15 | 50215.8096 | 240.012
Devonshire Building | 2017-05-12 12:30 | 50215.8746 | 259.992
Devonshire Building | 2017-05-12 12:45 | 50215.9546 | 320.004
Devonshire Building | 2017-05-12 13:00 | 50216.0396 | 339.984
Devonshire Building | 2017-05-12 13:15 | 50216.1246 | 339.984
Devonshire Building | 2017-05-12 13:30 | 50216.7746 | 2599.992
Devonshire Building | 2017-05-12 13:45 | 50216.9196 | 579.996
Devonshire Building | 2017-05-12 14:00 | 50217.0546 | 540
Devonshire Building | 2017-05-12 14:15 | 50217.1746 | 479.988
Devonshire Building | 2017-05-12 14:30 | 50217.2696 | 380.016
Devonshire Building | 2017-05-12 14:45 | 50217.3396 | 280.008
Devonshire Building | 2017-05-12 15:00 | 50217.3996 | 240.012
Devonshire Building | 2017-05-12 15:15 | 50218.0346 | 2540.016
Devonshire Building | 2017-05-12 15:30 | 50218.1546 | 479.988
Devonshire Building | 2017-05-12 15:45 | 50218.2646 | 439.992
Devonshire Building | 2017-05-12 16:00 | 50218.3496 | 339.984
Devonshire Building | 2017-05-12 16:15 | 50218.4196 | 280.008
Devonshire Building | 2017-05-12 16:30 | 50218.4796 | 240.012
Devonshire Building | 2017-05-12 16:45 | 50218.5246 | 180
Devonshire Building | 2017-05-12 17:00 | 50218.5696 | 180
Devonshire Building | 2017-05-12 17:15 | 50218.6096 | 159.984
Devonshire Building | 2017-05-12 17:30 | 50218.6546 | 180
Devonshire Building | 2017-05-12 17:45 | 50218.6946 | 159.984
Devonshire Building | 2017-05-12 18:00 | 50218.7346 | 159.984
Devonshire Building | 2017-05-12 18:15 | 50218.7746 | 159.984
Devonshire Building | 2017-05-12 18:30 | 50218.8146 | 159.984
Devonshire Building | 2017-05-12 18:45 | 50218.8546 | 159.984
Devonshire Building | 2017-05-12 19:00 | 50218.8946 | 159.984
Devonshire Building | 2017-05-12 19:15 | 50218.9346 | 159.984
Devonshire Building | 2017-05-12 19:30 | 50218.9796 | 180
Devonshire Building | 2017-05-12 19:45 | 50219.0196 | 159.984
Devonshire Building | 2017-05-12 20:00 | 50219.5846 | 2260.008
Devonshire Building | 2017-05-12 20:15 | 50219.6346 | 200.016
Devonshire Building | 2017-05-12 20:30 | 50219.6946 | 240.012
Devonshire Building | 2017-05-12 20:45 | 50219.7496 | 219.996
Devonshire Building | 2017-05-12 21:00 | 50219.8046 | 219.996
Devonshire Building | 2017-05-12 21:15 | 50219.8596 | 219.996
Devonshire Building | 2017-05-12 21:30 | 50219.9096 | 200.016
Devonshire Building | 2017-05-12 21:45 | 50219.9596 | 200.016
Devonshire Building | 2017-05-12 22:00 | 50220.0046 | 180
Devonshire Building | 2017-05-12 22:15 | 50220.0496 | 180
Devonshire Building | 2017-05-12 22:30 | 50220.0996 | 200.016
Devonshire Building | 2017-05-12 22:45 | 50220.1496 | 200.016
Devonshire Building | 2017-05-12 23:00 | 50220.2296 | 320.004
Devonshire Building | 2017-05-12 23:15 | 50220.3096 | 320.004
Devonshire Building | 2017-05-12 23:30 | 50220.3796 | 280.008
Devonshire Building | 2017-05-12 23:45 | 50220.4596 | 320.004
Devonshire Building | 2017-05-13 | 50220.5352 | 299.988
Devonshire Building | 2017-05-13 00:15 | 50220.6102 | 299.988
Devonshire Building | 2017-05-13 00:30 | 50220.6852 | 299.988
Devonshire Building | 2017-05-13 00:45 | 50220.7602 | 299.988
Devonshire Building | 2017-05-13 01:00 | 50220.8351 | 299.988
Devonshire Building | 2017-05-13 01:15 | 50220.9101 | 299.988
Devonshire Building | 2017-05-13 01:30 | 50220.9851 | 299.988
Devonshire Building | 2017-05-13 01:45 | 50221.0551 | 280.008
Devonshire Building | 2017-05-13 02:00 | 50221.1301 | 299.988
Devonshire Building | 2017-05-13 02:15 | 50221.2051 | 299.988
Devonshire Building | 2017-05-13 02:30 | 50221.2801 | 299.988
Devonshire Building | 2017-05-13 02:45 | 50221.3501 | 280.008
Devonshire Building | 2017-05-13 03:00 | 50221.4201 | 280.008
Devonshire Building | 2017-05-13 03:15 | 50221.4951 | 299.988
Devonshire Building | 2017-05-13 03:30 | 50221.5601 | 259.992
Devonshire Building | 2017-05-13 03:45 | 50221.6351 | 299.988
Devonshire Building | 2017-05-13 04:00 | 50221.7051 | 280.008
Devonshire Building | 2017-05-13 04:15 | 50221.7751 | 280.008
Devonshire Building | 2017-05-13 04:30 | 50221.8451 | 280.008
Devonshire Building | 2017-05-13 04:45 | 50221.9151 | 280.008
Devonshire Building | 2017-05-13 05:00 | 50221.9801 | 259.992
Devonshire Building | 2017-05-13 05:15 | 50222.0501 | 280.008
Devonshire Building | 2017-05-13 05:30 | 50222.1201 | 280.008
Devonshire Building | 2017-05-13 05:45 | 50222.1901 | 280.008
Devonshire Building | 2017-05-13 06:00 | 50222.2601 | 280.008
Devonshire Building | 2017-05-13 06:15 | 50222.3301 | 280.008
Devonshire Building | 2017-05-13 06:30 | 50222.4001 | 280.008
Devonshire Building | 2017-05-13 06:45 | 50222.4651 | 259.992
Devonshire Building | 2017-05-13 07:00 | 50222.5301 | 259.992
Devonshire Building | 2017-05-13 07:15 | 50222.5951 | 259.992
Devonshire Building | 2017-05-13 07:30 | 50222.6701 | 299.988
Devonshire Building | 2017-05-13 07:45 | 50222.7501 | 320.004
Devonshire Building | 2017-05-13 08:00 | 50222.8301 | 320.004
Devonshire Building | 2017-05-13 08:15 | 50222.9101 | 320.004
Devonshire Building | 2017-05-13 08:30 | 50222.9951 | 339.984
Devonshire Building | 2017-05-13 08:45 | 50223.0751 | 320.004
Devonshire Building | 2017-05-13 09:00 | 50223.1551 | 320.004
Devonshire Building | 2017-05-13 09:15 | 50223.2351 | 320.004
Devonshire Building | 2017-05-13 09:30 | 50223.3151 | 320.004
Devonshire Building | 2017-05-13 09:45 | 50223.3951 | 320.004
Devonshire Building | 2017-05-13 10:00 | 50223.4751 | 320.004
Devonshire Building | 2017-05-13 10:15 | 50223.5551 | 320.004
Devonshire Building | 2017-05-13 10:30 | 50223.6351 | 320.004
Devonshire Building | 2017-05-13 10:45 | 50223.7051 | 280.008
Devonshire Building | 2017-05-13 11:00 | 50223.7701 | 259.992
Devonshire Building | 2017-05-13 11:15 | 50223.8351 | 259.992
Devonshire Building | 2017-05-13 11:30 | 50223.9001 | 259.992
Devonshire Building | 2017-05-13 11:45 | 50223.9651 | 259.992
Devonshire Building | 2017-05-13 12:00 | 50224.0301 | 259.992
Devonshire Building | 2017-05-13 12:15 | 50224.0951 | 259.992
Devonshire Building | 2017-05-13 12:30 | 50224.1601 | 259.992
Devonshire Building | 2017-05-13 12:45 | 50224.2251 | 259.992
Devonshire Building | 2017-05-13 13:00 | 50224.2901 | 259.992
Devonshire Building | 2017-05-13 13:15 | 50224.3551 | 259.992
Devonshire Building | 2017-05-13 13:30 | 50224.4201 | 259.992
Devonshire Building | 2017-05-13 13:45 | 50225.0001 | 2319.984
Devonshire Building | 2017-05-13 14:00 | 50225.0651 | 259.992
Devonshire Building | 2017-05-13 14:15 | 50225.1301 | 259.992
Devonshire Building | 2017-05-13 14:30 | 50225.1951 | 259.992
Devonshire Building | 2017-05-13 14:45 | 50225.2651 | 280.008
Devonshire Building | 2017-05-13 15:00 | 50225.3351 | 280.008
Devonshire Building | 2017-05-13 15:15 | 50225.4001 | 259.992
Devonshire Building | 2017-05-13 15:30 | 50225.4701 | 280.008
Devonshire Building | 2017-05-13 15:45 | 50225.5401 | 280.008
Devonshire Building | 2017-05-13 16:00 | 50225.6051 | 259.992
Devonshire Building | 2017-05-13 16:15 | 50225.6701 | 259.992
Devonshire Building | 2017-05-13 16:30 | 50225.7401 | 280.008
Devonshire Building | 2017-05-13 16:45 | 50225.8051 | 259.992
Devonshire Building | 2017-05-13 17:00 | 50225.8701 | 259.992
Devonshire Building | 2017-05-13 17:15 | 50225.9351 | 259.992
Devonshire Building | 2017-05-13 17:30 | 50226.0001 | 259.992
Devonshire Building | 2017-05-13 17:45 | 50226.0651 | 259.992
Devonshire Building | 2017-05-13 18:00 | 50226.1301 | 259.992
Devonshire Building | 2017-05-13 18:15 | 50226.1951 | 259.992
Devonshire Building | 2017-05-13 18:30 | 50226.2601 | 259.992
Devonshire Building | 2017-05-13 18:45 | 50226.3251 | 259.992
Devonshire Building | 2017-05-13 19:00 | 50226.3901 | 259.992
Devonshire Building | 2017-05-13 19:15 | 50226.4551 | 259.992
Devonshire Building | 2017-05-13 19:30 | 50226.5201 | 259.992
Devonshire Building | 2017-05-13 19:45 | 50226.5851 | 259.992
Devonshire Building | 2017-05-13 20:00 | 50226.6501 | 259.992
Devonshire Building | 2017-05-13 20:15 | 50226.7151 | 259.992
Devonshire Building | 2017-05-13 20:30 | 50226.7801 | 259.992
Devonshire Building | 2017-05-13 20:45 | 50226.8451 | 259.992
Devonshire Building | 2017-05-13 21:00 | 50226.9151 | 280.008
Devonshire Building | 2017-05-13 21:15 | 50226.9801 | 259.992
Devonshire Building | 2017-05-13 21:30 | 50227.0451 | 259.992
Devonshire Building | 2017-05-13 21:45 | 50227.1151 | 280.008
Devonshire Building | 2017-05-13 22:00 | 50227.1801 | 259.992
Devonshire Building | 2017-05-13 22:15 | 50227.2451 | 259.992
Devonshire Building | 2017-05-13 22:30 | 50227.3101 | 259.992
Devonshire Building | 2017-05-13 22:45 | 50227.3751 | 259.992
Devonshire Building | 2017-05-13 23:00 | 50227.4401 | 259.992
Devonshire Building | 2017-05-13 23:15 | 50227.5051 | 259.992
Devonshire Building | 2017-05-13 23:30 | 50227.5701 | 259.992
Devonshire Building | 2017-05-13 23:45 | 50227.6351 | 259.992
Devonshire Building | 2017-05-14 | 50227.6992 | 259.992
Devonshire Building | 2017-05-14 00:15 | 50227.7642 | 259.992
Devonshire Building | 2017-05-14 00:30 | 50227.8292 | 259.992
Devonshire Building | 2017-05-14 00:45 | 50227.8942 | 259.992
Devonshire Building | 2017-05-14 01:00 | 50227.9592 | 259.992
Devonshire Building | 2017-05-14 01:15 | 50228.0242 | 259.992
Devonshire Building | 2017-05-14 01:30 | 50228.0892 | 259.992
Devonshire Building | 2017-05-14 01:45 | 50228.1542 | 259.992
Devonshire Building | 2017-05-14 02:00 | 50228.2192 | 259.992
Devonshire Building | 2017-05-14 02:15 | 50228.2842 | 259.992
Devonshire Building | 2017-05-14 02:30 | 50228.3492 | 259.992
Devonshire Building | 2017-05-14 02:45 | 50228.4142 | 259.992
Devonshire Building | 2017-05-14 03:00 | 50228.4792 | 259.992
Devonshire Building | 2017-05-14 03:15 | 50228.5442 | 259.992
Devonshire Building | 2017-05-14 03:30 | 50228.6092 | 259.992
Devonshire Building | 2017-05-14 03:45 | 50228.6692 | 240.012
Devonshire Building | 2017-05-14 04:00 | 50228.7342 | 259.992
Devonshire Building | 2017-05-14 04:15 | 50228.7942 | 240.012
Devonshire Building | 2017-05-14 04:30 | 50228.8592 | 259.992
Devonshire Building | 2017-05-14 04:45 | 50228.9192 | 240.012
Devonshire Building | 2017-05-14 05:00 | 50228.9842 | 259.992
Devonshire Building | 2017-05-14 05:15 | 50229.0442 | 240.012
Devonshire Building | 2017-05-14 05:30 | 50229.1092 | 259.992
Devonshire Building | 2017-05-14 05:45 | 50229.1692 | 240.012
Devonshire Building | 2017-05-14 06:00 | 50229.2342 | 259.992
Devonshire Building | 2017-05-14 06:15 | 50229.2942 | 240.012
Devonshire Building | 2017-05-14 06:30 | 50229.3542 | 240.012
Devonshire Building | 2017-05-14 06:45 | 50229.4142 | 240.012
Devonshire Building | 2017-05-14 07:00 | 50229.4742 | 240.012
Devonshire Building | 2017-05-14 07:15 | 50229.5342 | 240.012
Devonshire Building | 2017-05-14 07:30 | 50229.5942 | 240.012
Devonshire Building | 2017-05-14 07:45 | 50229.6592 | 259.992
Devonshire Building | 2017-05-14 08:00 | 50229.7342 | 299.988
Devonshire Building | 2017-05-14 08:15 | 50229.8092 | 299.988
Devonshire Building | 2017-05-14 08:30 | 50229.8842 | 299.988
Devonshire Building | 2017-05-14 08:45 | 50229.9592 | 299.988
Devonshire Building | 2017-05-14 09:00 | 50230.0342 | 299.988
Devonshire Building | 2017-05-14 09:15 | 50230.1092 | 299.988
Devonshire Building | 2017-05-14 09:30 | 50230.2892 | 720
Devonshire Building | 2017-05-14 09:45 | 50230.7592 | 1879.992
Devonshire Building | 2017-05-14 10:00 | 50230.8192 | 240.012
Devonshire Building | 2017-05-14 10:15 | 50230.8842 | 259.992
Devonshire Building | 2017-05-14 10:30 | 50230.9392 | 219.996
Devonshire Building | 2017-05-14 10:45 | 50230.9892 | 200.016
Devonshire Building | 2017-05-14 11:00 | 50231.0342 | 180
Devonshire Building | 2017-05-14 11:15 | 50231.0742 | 159.984
Devonshire Building | 2017-05-14 11:30 | 50231.0842 | 39.996
Devonshire Building | 2017-05-14 11:45 | 50231.0992 | 60.012
Devonshire Building | 2017-05-14 12:00 | 50231.1142 | 60.012
Devonshire Building | 2017-05-14 12:15 | 50231.1342 | 79.992
Devonshire Building | 2017-05-14 12:30 | 50231.1492 | 60.012
Devonshire Building | 2017-05-14 12:45 | 50231.1592 | 39.996
Devonshire Building | 2017-05-14 13:00 | 50231.1742 | 60.012
Devonshire Building | 2017-05-14 13:15 | 50231.1942 | 79.992
Devonshire Building | 2017-05-14 13:30 | 50231.2142 | 79.992
Devonshire Building | 2017-05-14 13:45 | 50231.2392 | 100.008
Devonshire Building | 2017-05-14 14:00 | 50231.2642 | 100.008
Devonshire Building | 2017-05-14 14:15 | 50231.2892 | 100.008
Devonshire Building | 2017-05-14 14:30 | 50231.3142 | 100.008
Devonshire Building | 2017-05-14 14:45 | 50231.3442 | 119.988
Devonshire Building | 2017-05-14 15:00 | 50231.3742 | 119.988
Devonshire Building | 2017-05-14 15:15 | 50231.3992 | 100.008
Devonshire Building | 2017-05-14 15:30 | 50231.4242 | 100.008
Devonshire Building | 2017-05-14 15:45 | 50231.4492 | 100.008
Devonshire Building | 2017-05-14 16:00 | 50231.4742 | 100.008
Devonshire Building | 2017-05-14 16:15 | 50231.4992 | 100.008
Devonshire Building | 2017-05-14 16:30 | 50231.5292 | 119.988
Devonshire Building | 2017-05-14 16:45 | 50231.5542 | 100.008
Devonshire Building | 2017-05-14 17:00 | 50231.5792 | 100.008
Devonshire Building | 2017-05-14 17:15 | 50231.6042 | 100.008
Devonshire Building | 2017-05-14 17:30 | 50231.6292 | 100.008
Devonshire Building | 2017-05-14 17:45 | 50231.6542 | 100.008
Devonshire Building | 2017-05-14 18:00 | 50231.6792 | 100.008
Devonshire Building | 2017-05-14 18:15 | 50231.7042 | 100.008
Devonshire Building | 2017-05-14 18:30 | 50231.7292 | 100.008
Devonshire Building | 2017-05-14 18:45 | 50231.7542 | 100.008
Devonshire Building | 2017-05-14 19:00 | 50231.7792 | 100.008
Devonshire Building | 2017-05-14 19:15 | 50231.8042 | 100.008
Devonshire Building | 2017-05-14 19:30 | 50231.8292 | 100.008
Devonshire Building | 2017-05-14 19:45 | 50231.8492 | 79.992
Devonshire Building | 2017-05-14 20:00 | 50231.8742 | 100.008
Devonshire Building | 2017-05-14 20:15 | 50231.8942 | 79.992
Devonshire Building | 2017-05-14 20:30 | 50231.9192 | 100.008
Devonshire Building | 2017-05-14 20:45 | 50231.9392 | 79.992
Devonshire Building | 2017-05-14 21:00 | 50231.9792 | 159.984
Devonshire Building | 2017-05-14 21:15 | 50231.9992 | 79.992
Devonshire Building | 2017-05-14 21:30 | 50232.0142 | 60.012
Devonshire Building | 2017-05-14 21:45 | 50232.0292 | 60.012
Devonshire Building | 2017-05-14 22:00 | 50232.0492 | 79.992
Devonshire Building | 2017-05-14 22:15 | 50232.0642 | 60.012
Devonshire Building | 2017-05-14 22:30 | 50232.0842 | 79.992
Devonshire Building | 2017-05-14 22:45 | 50232.0992 | 60.012
Devonshire Building | 2017-05-14 23:00 | 50232.1142 | 60.012
Devonshire Building | 2017-05-14 23:15 | 50232.1342 | 79.992
Devonshire Building | 2017-05-14 23:30 | 50232.1492 | 60.012
Devonshire Building | 2017-05-14 23:45 | 50232.1642 | 60.012
Devonshire Building | 2017-05-15 | 50232.1836 | 79.992
Devonshire Building | 2017-05-15 00:15 | 50232.1986 | 60.012
Devonshire Building | 2017-05-15 00:30 | 50232.2136 | 60.012
Devonshire Building | 2017-05-15 00:45 | 50232.2286 | 60.012
Devonshire Building | 2017-05-15 01:00 | 50232.2486 | 79.992
Devonshire Building | 2017-05-15 01:15 | 50232.2636 | 60.012
Devonshire Building | 2017-05-15 01:30 | 50232.2786 | 60.012
Devonshire Building | 2017-05-15 01:45 | 50232.2936 | 60.012
Devonshire Building | 2017-05-15 02:00 | 50232.3136 | 79.992
Devonshire Building | 2017-05-15 02:15 | 50232.3286 | 60.012
Devonshire Building | 2017-05-15 02:30 | 50232.3436 | 60.012
Devonshire Building | 2017-05-15 02:45 | 50232.3586 | 60.012
Devonshire Building | 2017-05-15 03:00 | 50232.3736 | 60.012
Devonshire Building | 2017-05-15 03:15 | 50232.3886 | 60.012
Devonshire Building | 2017-05-15 03:30 | 50232.4086 | 79.992
Devonshire Building | 2017-05-15 03:45 | 50232.4236 | 60.012
Devonshire Building | 2017-05-15 04:00 | 50232.4386 | 60.012
Devonshire Building | 2017-05-15 04:15 | 50232.4536 | 60.012
Devonshire Building | 2017-05-15 04:30 | 50232.4686 | 60.012
Devonshire Building | 2017-05-15 04:45 | 50232.4836 | 60.012
Devonshire Building | 2017-05-15 05:00 | 50232.4986 | 60.012
Devonshire Building | 2017-05-15 05:15 | 50232.5136 | 60.012
Devonshire Building | 2017-05-15 05:30 | 50232.5336 | 79.992
Devonshire Building | 2017-05-15 05:45 | 50232.5536 | 79.992
Devonshire Building | 2017-05-15 06:00 | 50233.0786 | 2099.988
Devonshire Building | 2017-05-15 06:15 | 50233.0986 | 79.992
Devonshire Building | 2017-05-15 06:30 | 50233.1186 | 79.992
Devonshire Building | 2017-05-15 06:45 | 50233.1336 | 60.012
Devonshire Building | 2017-05-15 07:00 | 50233.1586 | 100.008
Devonshire Building | 2017-05-15 07:15 | 50233.1936 | 140.004
Devonshire Building | 2017-05-15 07:30 | 50233.2436 | 200.016
Devonshire Building | 2017-05-15 07:45 | 50233.3086 | 259.992
Devonshire Building | 2017-05-15 08:00 | 50233.3786 | 280.008
Devonshire Building | 2017-05-15 08:15 | 50233.4436 | 259.992
Devonshire Building | 2017-05-15 08:30 | 50233.5086 | 259.992
Devonshire Building | 2017-05-15 08:45 | 50234.1436 | 2540.016
Devonshire Building | 2017-05-15 09:00 | 50234.2036 | 240.012
Devonshire Building | 2017-05-15 09:15 | 50234.2636 | 240.012
Devonshire Building | 2017-05-15 09:30 | 50234.3236 | 240.012
Devonshire Building | 2017-05-15 09:45 | 50234.9186 | 2379.996
Devonshire Building | 2017-05-15 10:00 | 50234.9936 | 299.988
Devonshire Building | 2017-05-15 10:15 | 50235.0936 | 399.996
Devonshire Building | 2017-05-15 10:30 | 50235.2136 | 479.988
Devonshire Building | 2017-05-15 10:45 | 50235.3236 | 439.992
Devonshire Building | 2017-05-15 11:00 | 50235.4136 | 360
Devonshire Building | 2017-05-15 11:15 | 50236.0886 | 2700
Devonshire Building | 2017-05-15 11:30 | 50236.1886 | 399.996
Devonshire Building | 2017-05-15 11:45 | 50236.2836 | 380.016
Devonshire Building | 2017-05-15 12:00 | 50236.3786 | 380.016
Devonshire Building | 2017-05-15 12:15 | 50236.4636 | 339.984
Devonshire Building | 2017-05-15 12:30 | 50236.5386 | 299.988
Devonshire Building | 2017-05-15 12:45 | 50236.8986 | 1440
Devonshire Building | 2017-05-15 13:00 | 50236.9786 | 320.004
Devonshire Building | 2017-05-15 13:15 | 50237.0536 | 299.988
Devonshire Building | 2017-05-15 13:30 | 50237.1186 | 259.992
Devonshire Building | 2017-05-15 13:45 | 50237.1736 | 219.996
Devonshire Building | 2017-05-15 14:00 | 50237.2236 | 200.016
Devonshire Building | 2017-05-15 14:15 | 50237.4236 | 799.992
Devonshire Building | 2017-05-15 14:30 | 50237.5786 | 619.992
Devonshire Building | 2017-05-15 14:45 | 50237.6036 | 100.008
Devonshire Building | 2017-05-15 15:00 | 50237.6236 | 79.992
Devonshire Building | 2017-05-15 15:15 | 50237.6486 | 100.008
Devonshire Building | 2017-05-15 15:30 | 50237.6736 | 100.008
Devonshire Building | 2017-05-15 15:45 | 50237.6986 | 100.008
Devonshire Building | 2017-05-15 16:00 | 50238.0286 | 1320.012
Devonshire Building | 2017-05-15 16:15 | 50238.0486 | 79.992
Devonshire Building | 2017-05-15 16:30 | 50238.0786 | 119.988
Devonshire Building | 2017-05-15 16:45 | 50238.1036 | 100.008
Devonshire Building | 2017-05-15 17:00 | 50238.1236 | 79.992
Devonshire Building | 2017-05-15 17:15 | 50238.1436 | 79.992
Devonshire Building | 2017-05-15 17:30 | 50238.1686 | 100.008
Devonshire Building | 2017-05-15 17:45 | 50238.1886 | 79.992
Devonshire Building | 2017-05-15 18:00 | 50238.2086 | 79.992
Devonshire Building | 2017-05-15 18:15 | 50238.2286 | 79.992
Devonshire Building | 2017-05-15 18:30 | 50238.2436 | 60.012
Devonshire Building | 2017-05-15 18:45 | 50238.2636 | 79.992
Devonshire Building | 2017-05-15 19:00 | 50238.2886 | 100.008
Devonshire Building | 2017-05-15 19:15 | 50238.3086 | 79.992
Devonshire Building | 2017-05-15 19:30 | 50238.3236 | 60.012
Devonshire Building | 2017-05-15 19:45 | 50238.3386 | 60.012
Devonshire Building | 2017-05-15 20:00 | 50238.3586 | 79.992
Devonshire Building | 2017-05-15 20:15 | 50238.3736 | 60.012
Devonshire Building | 2017-05-15 20:30 | 50238.3886 | 60.012
Devonshire Building | 2017-05-15 20:45 | 50238.6686 | 1119.996
Devonshire Building | 2017-05-15 21:00 | 50238.6786 | 39.996
Devonshire Building | 2017-05-15 21:15 | 50238.6886 | 39.996
Devonshire Building | 2017-05-15 21:30 | 50238.6986 | 39.996
Devonshire Building | 2017-05-15 21:45 | 50238.7086 | 39.996
Devonshire Building | 2017-05-15 22:00 | 50238.7186 | 39.996
Devonshire Building | 2017-05-15 22:15 | 50238.7286 | 39.996
Devonshire Building | 2017-05-15 22:30 | 50238.7386 | 39.996
Devonshire Building | 2017-05-15 22:45 | 50238.7486 | 39.996
Devonshire Building | 2017-05-15 23:00 | 50238.7586 | 39.996
Devonshire Building | 2017-05-15 23:15 | 50238.7736 | 60.012
Devonshire Building | 2017-05-15 23:30 | 50238.7836 | 39.996
Devonshire Building | 2017-05-15 23:45 | 50238.7986 | 60.012
Devonshire Building | 2017-05-16 | 50238.8086 | 39.996
Devonshire Building | 2017-05-16 00:15 | 50238.8186 | 39.996
Devonshire Building | 2017-05-16 00:30 | 50238.8286 | 39.996
Devonshire Building | 2017-05-16 00:45 | 50238.8436 | 60.012
Devonshire Building | 2017-05-16 01:00 | 50238.8536 | 39.996
Devonshire Building | 2017-05-16 01:15 | 50238.8636 | 39.996
Devonshire Building | 2017-05-16 01:30 | 50238.8736 | 39.996
Devonshire Building | 2017-05-16 01:45 | 50238.8836 | 39.996
Devonshire Building | 2017-05-16 02:00 | 50238.8936 | 39.996
Devonshire Building | 2017-05-16 02:15 | 50238.9036 | 39.996
Devonshire Building | 2017-05-16 02:30 | 50238.9086 | 20.016
Devonshire Building | 2017-05-16 02:45 | 50238.9186 | 39.996
Devonshire Building | 2017-05-16 03:00 | 50238.9286 | 39.996
Devonshire Building | 2017-05-16 03:15 | 50238.9386 | 39.996
Devonshire Building | 2017-05-16 03:30 | 50238.9436 | 20.016
Devonshire Building | 2017-05-16 03:45 | 50238.9536 | 39.996
Devonshire Building | 2017-05-16 04:00 | 50238.9636 | 39.996
Devonshire Building | 2017-05-16 04:15 | 50238.9686 | 20.016
Devonshire Building | 2017-05-16 04:30 | 50238.9786 | 39.996
Devonshire Building | 2017-05-16 04:45 | 50238.9836 | 20.016
Devonshire Building | 2017-05-16 05:00 | 50238.9886 | 20.016
Devonshire Building | 2017-05-16 05:15 | 50238.9986 | 39.996
Devonshire Building | 2017-05-16 05:30 | 50239.0036 | 20.016
Devonshire Building | 2017-05-16 05:45 | 50239.0136 | 39.996
Devonshire Building | 2017-05-16 06:00 | 50239.0186 | 20.016
Devonshire Building | 2017-05-16 06:15 | 50239.0286 | 39.996
Devonshire Building | 2017-05-16 06:30 | 50239.0336 | 20.016
Devonshire Building | 2017-05-16 06:45 | 50239.0436 | 39.996
Devonshire Building | 2017-05-16 07:00 | 50239.0536 | 39.996
Devonshire Building | 2017-05-16 07:15 | 50239.0636 | 39.996
Devonshire Building | 2017-05-16 07:30 | 50239.0736 | 39.996
Devonshire Building | 2017-05-16 07:45 | 50239.0936 | 79.992
Devonshire Building | 2017-05-16 08:00 | 50239.4236 | 1320.012
Devonshire Building | 2017-05-16 08:15 | 50239.4486 | 100.008
Devonshire Building | 2017-05-16 08:30 | 50239.4736 | 100.008
Devonshire Building | 2017-05-16 08:45 | 50239.5036 | 119.988
Devonshire Building | 2017-05-16 09:00 | 50239.5286 | 100.008
Devonshire Building | 2017-05-16 09:15 | 50239.5636 | 140.004
Devonshire Building | 2017-05-16 09:30 | 50239.8736 | 1239.984
Devonshire Building | 2017-05-16 09:45 | 50239.9586 | 339.984
Devonshire Building | 2017-05-16 10:00 | 50240.0786 | 479.988
Devonshire Building | 2017-05-16 10:15 | 50240.1986 | 479.988
Devonshire Building | 2017-05-16 10:30 | 50240.3836 | 740.016
Devonshire Building | 2017-05-16 10:45 | 50240.5436 | 640.008
Devonshire Building | 2017-05-16 11:00 | 50240.9386 | 1580.004
Devonshire Building | 2017-05-16 11:15 | 50241.0286 | 360
Devonshire Building | 2017-05-16 11:30 | 50241.1036 | 299.988
Devonshire Building | 2017-05-16 11:45 | 50241.1686 | 259.992
Devonshire Building | 2017-05-16 12:00 | 50241.2286 | 240.012
Devonshire Building | 2017-05-16 12:15 | 50241.4886 | 1040.004
Devonshire Building | 2017-05-16 12:30 | 50241.5936 | 420.012
Devonshire Building | 2017-05-16 12:45 | 50241.6236 | 119.988
Devonshire Building | 2017-05-16 13:00 | 50241.6486 | 100.008
Devonshire Building | 2017-05-16 13:15 | 50241.6836 | 140.004
Devonshire Building | 2017-05-16 13:30 | 50241.7136 | 119.988
Devonshire Building | 2017-05-16 13:45 | 50242.0536 | 1360.008
Devonshire Building | 2017-05-16 14:00 | 50242.0986 | 180
Devonshire Building | 2017-05-16 14:15 | 50242.1536 | 219.996
Devonshire Building | 2017-05-16 14:30 | 50242.2136 | 240.012
Devonshire Building | 2017-05-16 14:45 | 50242.2736 | 240.012
Devonshire Building | 2017-05-16 15:00 | 50242.3736 | 399.996
Devonshire Building | 2017-05-16 15:15 | 50242.6686 | 1180.008
Devonshire Building | 2017-05-16 15:30 | 50242.7486 | 320.004
Devonshire Building | 2017-05-16 15:45 | 50242.8536 | 420.012
Devonshire Building | 2017-05-16 16:00 | 50242.9586 | 420.012
Devonshire Building | 2017-05-16 16:15 | 50243.0486 | 360
Devonshire Building | 2017-05-16 16:30 | 50243.1286 | 320.004
Devonshire Building | 2017-05-16 16:45 | 50243.4836 | 1419.984
Devonshire Building | 2017-05-16 17:00 | 50243.5486 | 259.992
Devonshire Building | 2017-05-16 17:15 | 50243.6086 | 240.012
Devonshire Building | 2017-05-16 17:30 | 50243.6636 | 219.996
Devonshire Building | 2017-05-16 17:45 | 50243.7236 | 240.012
Devonshire Building | 2017-05-16 18:00 | 50243.7736 | 200.016
Devonshire Building | 2017-05-16 18:15 | 50243.8136 | 159.984
Devonshire Building | 2017-05-16 18:30 | 50243.8536 | 159.984
Devonshire Building | 2017-05-16 18:45 | 50243.8836 | 119.988
Devonshire Building | 2017-05-16 19:00 | 50243.9136 | 119.988
Devonshire Building | 2017-05-16 19:15 | 50243.9386 | 100.008
Devonshire Building | 2017-05-16 19:30 | 50243.9586 | 79.992
Devonshire Building | 2017-05-16 19:45 | 50243.9836 | 100.008
Devonshire Building | 2017-05-16 20:00 | 50244.0036 | 79.992
Devonshire Building | 2017-05-16 20:15 | 50244.0186 | 60.012
Devonshire Building | 2017-05-16 20:30 | 50244.0386 | 79.992
Devonshire Building | 2017-05-16 20:45 | 50244.0536 | 60.012
Devonshire Building | 2017-05-16 21:00 | 50244.0686 | 60.012
Devonshire Building | 2017-05-16 21:15 | 50244.0786 | 39.996
Devonshire Building | 2017-05-16 21:30 | 50244.0886 | 39.996
Devonshire Building | 2017-05-16 21:45 | 50244.0986 | 39.996
Devonshire Building | 2017-05-16 22:00 | 50244.1136 | 60.012
Devonshire Building | 2017-05-16 22:15 | 50244.1236 | 39.996
Devonshire Building | 2017-05-16 22:30 | 50244.1336 | 39.996
Devonshire Building | 2017-05-16 22:45 | 50244.1436 | 39.996
Devonshire Building | 2017-05-16 23:00 | 50244.1536 | 39.996
Devonshire Building | 2017-05-16 23:15 | 50244.1636 | 39.996
Devonshire Building | 2017-05-16 23:30 | 50244.1736 | 39.996
Devonshire Building | 2017-05-16 23:45 | 50244.1836 | 39.996
Devonshire Building | 2017-05-17 | 50244.1953 | 39.996
Devonshire Building | 2017-05-17 00:15 | 50244.2053 | 39.996
Devonshire Building | 2017-05-17 00:30 | 50244.2153 | 39.996
Devonshire Building | 2017-05-17 00:45 | 50244.2253 | 39.996
Devonshire Building | 2017-05-17 01:00 | 50244.2303 | 20.016
Devonshire Building | 2017-05-17 01:15 | 50244.2403 | 39.996
Devonshire Building | 2017-05-17 01:30 | 50244.2503 | 39.996
Devonshire Building | 2017-05-17 01:45 | 50244.2553 | 20.016
Devonshire Building | 2017-05-17 02:00 | 50244.2653 | 39.996
Devonshire Building | 2017-05-17 02:15 | 50244.2753 | 39.996
Devonshire Building | 2017-05-17 02:30 | 50244.2803 | 20.016
Devonshire Building | 2017-05-17 02:45 | 50244.2853 | 20.016
Devonshire Building | 2017-05-17 03:00 | 50244.2953 | 39.996
Devonshire Building | 2017-05-17 03:15 | 50244.3003 | 20.016
Devonshire Building | 2017-05-17 03:30 | 50244.3053 | 20.016
Devonshire Building | 2017-05-17 03:45 | 50244.3103 | 20.016
Devonshire Building | 2017-05-17 04:00 | 50244.3153 | 20.016
Devonshire Building | 2017-05-17 04:15 | 50244.3203 | 20.016
Devonshire Building | 2017-05-17 04:30 | 50244.3253 | 20.016
Devonshire Building | 2017-05-17 04:45 | 50244.3303 | 20.016
Devonshire Building | 2017-05-17 05:00 | 50244.3354 | 20.016
Devonshire Building | 2017-05-17 05:15 | 50244.3404 | 20.016
Devonshire Building | 2017-05-17 05:30 | 50244.3404 | 0
Devonshire Building | 2017-05-17 05:45 | 50244.3454 | 20.016
Devonshire Building | 2017-05-17 06:00 | 50244.3504 | 20.016
Devonshire Building | 2017-05-17 06:15 | 50244.3554 | 20.016
Devonshire Building | 2017-05-17 06:30 | 50244.3604 | 20.016
Devonshire Building | 2017-05-17 06:45 | 50244.3604 | 0
Devonshire Building | 2017-05-17 07:00 | 50244.3704 | 39.996
Devonshire Building | 2017-05-17 07:15 | 50244.6304 | 1040.004
Devonshire Building | 2017-05-17 07:30 | 50244.6404 | 39.996
Devonshire Building | 2017-05-17 07:45 | 50244.6604 | 79.992
Devonshire Building | 2017-05-17 08:00 | 50244.6904 | 119.988
Devonshire Building | 2017-05-17 08:15 | 50244.7154 | 100.008
Devonshire Building | 2017-05-17 08:30 | 50244.7454 | 119.988
Devonshire Building | 2017-05-17 08:45 | 50244.7704 | 100.008
Devonshire Building | 2017-05-17 09:00 | 50244.7954 | 100.008
Devonshire Building | 2017-05-17 09:15 | 50245.1104 | 1260
Devonshire Building | 2017-05-17 09:30 | 50245.1454 | 140.004
Devonshire Building | 2017-05-17 09:45 | 50245.2104 | 259.992
Devonshire Building | 2017-05-17 10:00 | 50245.3204 | 439.992
Devonshire Building | 2017-05-17 10:15 | 50245.4504 | 519.984
Devonshire Building | 2017-05-17 10:30 | 50245.6654 | 860.004
Devonshire Building | 2017-05-17 10:45 | 50246.1504 | 1940.004
Devonshire Building | 2017-05-17 11:00 | 50246.2704 | 479.988
Devonshire Building | 2017-05-17 11:15 | 50246.3754 | 420.012
Devonshire Building | 2017-05-17 11:30 | 50246.4704 | 380.016
Devonshire Building | 2017-05-17 11:45 | 50246.5454 | 299.988
Devonshire Building | 2017-05-17 12:00 | 50246.9204 | 1500.012
Devonshire Building | 2017-05-17 12:15 | 50247.2654 | 1379.988
Devonshire Building | 2017-05-17 12:30 | 50247.3354 | 280.008
Devonshire Building | 2017-05-17 12:45 | 50247.3904 | 219.996
Devonshire Building | 2017-05-17 13:00 | 50247.4654 | 299.988
Devonshire Building | 2017-05-17 13:15 | 50247.5654 | 399.996
Devonshire Building | 2017-05-17 13:30 | 50248.1804 | 2459.988
Devonshire Building | 2017-05-17 13:45 | 50248.3754 | 780.012
Devonshire Building | 2017-05-17 14:00 | 50248.4654 | 360
Devonshire Building | 2017-05-17 14:15 | 50248.5354 | 280.008
Devonshire Building | 2017-05-17 14:30 | 50248.6004 | 259.992
Devonshire Building | 2017-05-17 14:45 | 50248.6504 | 200.016
Devonshire Building | 2017-05-17 15:00 | 50249.2404 | 2360.016
Devonshire Building | 2017-05-17 15:15 | 50249.3254 | 339.984
Devonshire Building | 2017-05-17 15:30 | 50249.4704 | 579.996
Devonshire Building | 2017-05-17 15:45 | 50249.6704 | 799.992
Devonshire Building | 2017-05-17 16:00 | 50249.8104 | 560.016
Devonshire Building | 2017-05-17 16:15 | 50250.4704 | 2639.988
Devonshire Building | 2017-05-17 16:30 | 50250.5554 | 339.984
Devonshire Building | 2017-05-17 16:45 | 50250.6204 | 259.992
Devonshire Building | 2017-05-17 17:00 | 50250.6754 | 219.996
Devonshire Building | 2017-05-17 17:15 | 50250.7154 | 159.984
Devonshire Building | 2017-05-17 17:30 | 50250.7504 | 140.004
Devonshire Building | 2017-05-17 17:45 | 50250.7754 | 100.008
Devonshire Building | 2017-05-17 18:00 | 50250.8004 | 100.008
Devonshire Building | 2017-05-17 18:15 | 50250.8204 | 79.992
Devonshire Building | 2017-05-17 18:30 | 50250.8404 | 79.992
Devonshire Building | 2017-05-17 18:45 | 50250.8554 | 60.012
Devonshire Building | 2017-05-17 19:00 | 50250.8704 | 60.012
Devonshire Building | 2017-05-17 19:15 | 50250.8854 | 60.012
Devonshire Building | 2017-05-17 19:30 | 50250.9004 | 60.012
Devonshire Building | 2017-05-17 19:45 | 50250.9054 | 20.016
Devonshire Building | 2017-05-17 20:00 | 50250.9154 | 39.996
Devonshire Building | 2017-05-17 20:15 | 50250.9254 | 39.996
Devonshire Building | 2017-05-17 20:30 | 50250.9304 | 20.016
Devonshire Building | 2017-05-17 20:45 | 50250.9554 | 100.008
Devonshire Building | 2017-05-17 21:00 | 50250.9654 | 39.996
Devonshire Building | 2017-05-17 21:15 | 50250.9704 | 20.016
Devonshire Building | 2017-05-17 21:30 | 50250.9704 | 0
Devonshire Building | 2017-05-17 21:45 | 50250.9754 | 20.016
Devonshire Building | 2017-05-17 22:00 | 50250.9804 | 20.016
Devonshire Building | 2017-05-17 22:15 | 50250.9804 | 0
Devonshire Building | 2017-05-17 22:30 | 50250.9854 | 20.016
Devonshire Building | 2017-05-17 22:45 | 50250.9904 | 20.016
Devonshire Building | 2017-05-17 23:00 | 50250.9904 | 0
Devonshire Building | 2017-05-17 23:15 | 50250.9954 | 20.016
Devonshire Building | 2017-05-17 23:30 | 50251.0004 | 20.016
Devonshire Building | 2017-05-17 23:45 | 50251.0004 | 0
Devonshire Building | 2017-05-18 | 50251.0039 | 20.016
Devonshire Building | 2017-05-18 00:15 | 50251.0039 | 0
Devonshire Building | 2017-05-18 00:30 | 50251.0089 | 20.016
Devonshire Building | 2017-05-18 00:45 | 50251.0139 | 20.016
Devonshire Building | 2017-05-18 01:00 | 50251.0139 | 0
Devonshire Building | 2017-05-18 01:15 | 50251.0189 | 20.016
Devonshire Building | 2017-05-18 01:30 | 50251.0189 | 0
Devonshire Building | 2017-05-18 01:45 | 50251.0339 | 60.012
Devonshire Building | 2017-05-18 02:00 | 50251.0539 | 79.992
Devonshire Building | 2017-05-18 02:15 | 50251.0739 | 79.992
Devonshire Building | 2017-05-18 02:30 | 50251.0939 | 79.992
Devonshire Building | 2017-05-18 02:45 | 50251.1139 | 79.992
Devonshire Building | 2017-05-18 03:00 | 50251.1339 | 79.992
Devonshire Building | 2017-05-18 03:15 | 50251.1539 | 79.992
Devonshire Building | 2017-05-18 03:30 | 50251.1689 | 60.012
Devonshire Building | 2017-05-18 03:45 | 50251.1789 | 39.996
Devonshire Building | 2017-05-18 04:00 | 50251.1789 | 0
Devonshire Building | 2017-05-18 04:15 | 50251.1839 | 20.016
Devonshire Building | 2017-05-18 04:30 | 50251.1889 | 20.016
Devonshire Building | 2017-05-18 04:45 | 50251.1889 | 0
Devonshire Building | 2017-05-18 05:00 | 50251.1939 | 20.016
Devonshire Building | 2017-05-18 05:15 | 50251.1989 | 20.016
Devonshire Building | 2017-05-18 05:30 | 50251.1989 | 0
Devonshire Building | 2017-05-18 05:45 | 50251.2039 | 20.016
Devonshire Building | 2017-05-18 06:00 | 50251.2089 | 20.016
Devonshire Building | 2017-05-18 06:15 | 50251.2139 | 20.016
Devonshire Building | 2017-05-18 06:30 | 50251.2239 | 39.996
Devonshire Building | 2017-05-18 06:45 | 50251.6889 | 1860.012
Devonshire Building | 2017-05-18 07:00 | 50251.7639 | 299.988
Devonshire Building | 2017-05-18 07:15 | 50251.7689 | 20.016
Devonshire Building | 2017-05-18 07:30 | 50251.7789 | 39.996
Devonshire Building | 2017-05-18 07:45 | 50251.7839 | 20.016
Devonshire Building | 2017-05-18 08:00 | 50251.809 | 100.008
Devonshire Building | 2017-05-18 08:15 | 50251.819 | 39.996
Devonshire Building | 2017-05-18 08:30 | 50251.8289 | 39.996
Devonshire Building | 2017-05-18 08:45 | 50251.844 | 60.012
Devonshire Building | 2017-05-18 09:00 | 50252.399 | 2220.012
Devonshire Building | 2017-05-18 09:15 | 50252.409 | 39.996
Devonshire Building | 2017-05-18 09:30 | 50252.429 | 79.992
Devonshire Building | 2017-05-18 09:45 | 50252.464 | 140.004
Devonshire Building | 2017-05-18 10:00 | 50252.544 | 320.004
Devonshire Building | 2017-05-18 10:15 | 50253.149 | 2419.992
Devonshire Building | 2017-05-18 10:30 | 50253.219 | 280.008
Devonshire Building | 2017-05-18 10:45 | 50253.319 | 399.996
Devonshire Building | 2017-05-18 11:00 | 50253.399 | 320.004
Devonshire Building | 2017-05-18 11:15 | 50253.479 | 320.004
Devonshire Building | 2017-05-18 11:30 | 50254.084 | 2419.992
Devonshire Building | 2017-05-18 11:45 | 50254.184 | 399.996
Devonshire Building | 2017-05-18 12:00 | 50254.299 | 460.008
Devonshire Building | 2017-05-18 12:15 | 50254.409 | 439.992
Devonshire Building | 2017-05-18 12:30 | 50254.514 | 420.012
Devonshire Building | 2017-05-18 12:45 | 50254.599 | 339.984
Devonshire Building | 2017-05-18 13:00 | 50254.8889 | 1159.992
Devonshire Building | 2017-05-18 13:15 | 50255.2889 | 1599.984
Devonshire Building | 2017-05-18 13:30 | 50255.3389 | 200.016
Devonshire Building | 2017-05-18 13:45 | 50255.3939 | 219.996
Devonshire Building | 2017-05-18 14:00 | 50255.4389 | 180
Devonshire Building | 2017-05-18 14:15 | 50255.4839 | 180
Devonshire Building | 2017-05-18 14:30 | 50255.5239 | 159.984
Devonshire Building | 2017-05-18 14:45 | 50256.1189 | 2379.996
Devonshire Building | 2017-05-18 15:00 | 50256.1739 | 219.996
Devonshire Building | 2017-05-18 15:15 | 50256.2239 | 200.016
Devonshire Building | 2017-05-18 15:30 | 50256.274 | 200.016
Devonshire Building | 2017-05-18 15:45 | 50256.324 | 200.016
Devonshire Building | 2017-05-18 16:00 | 50256.369 | 180
Devonshire Building | 2017-05-18 16:15 | 50256.9489 | 2319.984
Devonshire Building | 2017-05-18 16:30 | 50256.999 | 200.016
Devonshire Building | 2017-05-18 16:45 | 50257.054 | 219.996
Devonshire Building | 2017-05-18 17:00 | 50257.099 | 180
Devonshire Building | 2017-05-18 17:15 | 50257.134 | 140.004
Devonshire Building | 2017-05-18 17:30 | 50257.169 | 140.004
Devonshire Building | 2017-05-18 17:45 | 50257.204 | 140.004
Devonshire Building | 2017-05-18 18:00 | 50257.234 | 119.988
Devonshire Building | 2017-05-18 18:15 | 50257.264 | 119.988
Devonshire Building | 2017-05-18 18:30 | 50257.2939 | 119.988
Devonshire Building | 2017-05-18 18:45 | 50257.3189 | 100.008
Devonshire Building | 2017-05-18 19:00 | 50257.344 | 100.008
Devonshire Building | 2017-05-18 19:15 | 50257.369 | 100.008
Devonshire Building | 2017-05-18 19:30 | 50257.389 | 79.992
Devonshire Building | 2017-05-18 19:45 | 50257.414 | 100.008
Devonshire Building | 2017-05-18 20:00 | 50257.429 | 60.012
Devonshire Building | 2017-05-18 20:15 | 50257.449 | 79.992
Devonshire Building | 2017-05-18 20:30 | 50257.464 | 60.012
Devonshire Building | 2017-05-18 20:45 | 50257.494 | 119.988
Devonshire Building | 2017-05-18 21:00 | 50257.509 | 60.012
Devonshire Building | 2017-05-18 21:15 | 50257.514 | 20.016
Devonshire Building | 2017-05-18 21:30 | 50257.519 | 20.016
Devonshire Building | 2017-05-18 21:45 | 50257.524 | 20.016
Devonshire Building | 2017-05-18 22:00 | 50257.529 | 20.016
Devonshire Building | 2017-05-18 22:15 | 50257.539 | 39.996
Devonshire Building | 2017-05-18 22:30 | 50257.544 | 20.016
Devonshire Building | 2017-05-18 22:45 | 50257.549 | 20.016
Devonshire Building | 2017-05-18 23:00 | 50257.554 | 20.016
Devonshire Building | 2017-05-18 23:15 | 50257.559 | 20.016
Devonshire Building | 2017-05-18 23:30 | 50257.564 | 20.016
Devonshire Building | 2017-05-18 23:45 | 50257.569 | 20.016
Devonshire Building | 2017-05-19 | 50257.5742 | 20.016
Devonshire Building | 2017-05-19 00:15 | 50257.5792 | 20.016
Devonshire Building | 2017-05-19 00:30 | 50257.5842 | 20.016
Devonshire Building | 2017-05-19 00:45 | 50257.5892 | 20.016
Devonshire Building | 2017-05-19 01:00 | 50257.5942 | 20.016
Devonshire Building | 2017-05-19 01:15 | 50257.5992 | 20.016
Devonshire Building | 2017-05-19 01:30 | 50257.6042 | 20.016
Devonshire Building | 2017-05-19 01:45 | 50257.6092 | 20.016
Devonshire Building | 2017-05-19 02:00 | 50257.6143 | 20.016
Devonshire Building | 2017-05-19 02:15 | 50257.6193 | 20.016
Devonshire Building | 2017-05-19 02:30 | 50257.6243 | 20.016
Devonshire Building | 2017-05-19 02:45 | 50257.6243 | 0
Devonshire Building | 2017-05-19 03:00 | 50257.6293 | 20.016
Devonshire Building | 2017-05-19 03:15 | 50257.6343 | 20.016
Devonshire Building | 2017-05-19 03:30 | 50257.6393 | 20.016
Devonshire Building | 2017-05-19 03:45 | 50257.6443 | 20.016
Devonshire Building | 2017-05-19 04:00 | 50257.6493 | 20.016
Devonshire Building | 2017-05-19 04:15 | 50257.6543 | 20.016
Devonshire Building | 2017-05-19 04:30 | 50257.6543 | 0
Devonshire Building | 2017-05-19 04:45 | 50257.6593 | 20.016
Devonshire Building | 2017-05-19 05:00 | 50257.6643 | 20.016
Devonshire Building | 2017-05-19 05:15 | 50257.6693 | 20.016
Devonshire Building | 2017-05-19 05:30 | 50257.6743 | 20.016
Devonshire Building | 2017-05-19 05:45 | 50257.6793 | 20.016
Devonshire Building | 2017-05-19 06:00 | 50258.1893 | 2040.012
Devonshire Building | 2017-05-19 06:15 | 50258.1943 | 20.016
Devonshire Building | 2017-05-19 06:30 | 50258.1993 | 20.016
Devonshire Building | 2017-05-19 06:45 | 50258.2043 | 20.016
Devonshire Building | 2017-05-19 07:00 | 50258.2143 | 39.996
Devonshire Building | 2017-05-19 07:15 | 50258.2193 | 20.016
Devonshire Building | 2017-05-19 07:30 | 50258.2293 | 39.996
Devonshire Building | 2017-05-19 07:45 | 50258.2393 | 39.996
Devonshire Building | 2017-05-19 08:00 | 50258.2643 | 100.008
Devonshire Building | 2017-05-19 08:15 | 50258.2993 | 140.004
Devonshire Building | 2017-05-19 08:30 | 50258.3493 | 200.016
Devonshire Building | 2017-05-19 08:45 | 50258.5793 | 920.016
Devonshire Building | 2017-05-19 09:00 | 50259.0893 | 2040.012
Devonshire Building | 2017-05-19 09:15 | 50259.2093 | 479.988
Devonshire Building | 2017-05-19 09:30 | 50259.4393 | 920.016
Devonshire Building | 2017-05-19 09:45 | 50259.8043 | 1460.016
Devonshire Building | 2017-05-19 10:00 | 50260.1443 | 1360.008
Devonshire Building | 2017-05-19 10:15 | 50260.8993 | 3020.004
Devonshire Building | 2017-05-19 10:30 | 50261.0393 | 560.016
Devonshire Building | 2017-05-19 10:45 | 50261.1293 | 360
Devonshire Building | 2017-05-19 11:00 | 50261.1943 | 259.992
Devonshire Building | 2017-05-19 11:15 | 50261.2543 | 240.012
Devonshire Building | 2017-05-19 11:30 | 50261.5793 | 1299.996
Devonshire Building | 2017-05-19 11:45 | 50261.6143 | 140.004
Devonshire Building | 2017-05-19 12:00 | 50261.6393 | 100.008
Devonshire Building | 2017-05-19 12:15 | 50261.6644 | 100.008
Devonshire Building | 2017-05-19 12:30 | 50261.6794 | 60.012
Devonshire Building | 2017-05-19 12:45 | 50262.0044 | 1299.996
Devonshire Building | 2017-05-19 13:00 | 50262.0344 | 119.988
Devonshire Building | 2017-05-19 13:15 | 50262.0594 | 100.008
Devonshire Building | 2017-05-19 13:30 | 50262.1094 | 200.016
Devonshire Building | 2017-05-19 13:45 | 50262.1644 | 219.996
Devonshire Building | 2017-05-19 14:00 | 50262.2294 | 259.992
Devonshire Building | 2017-05-19 14:15 | 50262.3644 | 540
Devonshire Building | 2017-05-19 14:30 | 50262.6494 | 1140.012
Devonshire Building | 2017-05-19 14:45 | 50262.7094 | 240.012
Devonshire Building | 2017-05-19 15:00 | 50262.7744 | 259.992
Devonshire Building | 2017-05-19 15:15 | 50262.8394 | 259.992
Devonshire Building | 2017-05-19 15:30 | 50262.9144 | 299.988
Devonshire Building | 2017-05-19 15:45 | 50262.9893 | 299.988
Devonshire Building | 2017-05-19 16:00 | 50263.6244 | 2540.016
Devonshire Building | 2017-05-19 16:15 | 50263.6994 | 299.988
Devonshire Building | 2017-05-19 16:30 | 50263.7643 | 259.992
Devonshire Building | 2017-05-19 16:45 | 50263.8293 | 259.992
Devonshire Building | 2017-05-19 17:00 | 50263.8843 | 219.996
Devonshire Building | 2017-05-19 17:15 | 50263.9293 | 180
Devonshire Building | 2017-05-19 17:30 | 50263.9693 | 159.984
Devonshire Building | 2017-05-19 17:45 | 50264.0043 | 140.004
Devonshire Building | 2017-05-19 18:00 | 50264.0343 | 119.988
Devonshire Building | 2017-05-19 18:15 | 50264.0643 | 119.988
Devonshire Building | 2017-05-19 18:30 | 50264.0893 | 100.008
Devonshire Building | 2017-05-19 18:45 | 50264.1093 | 79.992
Devonshire Building | 2017-05-19 19:00 | 50264.1293 | 79.992
Devonshire Building | 2017-05-19 19:15 | 50264.1443 | 60.012
Devonshire Building | 2017-05-19 19:30 | 50264.1643 | 79.992
Devonshire Building | 2017-05-19 19:45 | 50264.1843 | 79.992
Devonshire Building | 2017-05-19 20:00 | 50264.2143 | 119.988
Devonshire Building | 2017-05-19 20:15 | 50264.2443 | 119.988
Devonshire Building | 2017-05-19 20:30 | 50264.2743 | 119.988
Devonshire Building | 2017-05-19 20:45 | 50264.3193 | 180
Devonshire Building | 2017-05-19 21:00 | 50264.3393 | 79.992
Devonshire Building | 2017-05-19 21:15 | 50264.3593 | 79.992
Devonshire Building | 2017-05-19 21:30 | 50264.3793 | 79.992
Devonshire Building | 2017-05-19 21:45 | 50264.3993 | 79.992
Devonshire Building | 2017-05-19 22:00 | 50264.4043 | 20.016
Devonshire Building | 2017-05-19 22:15 | 50264.4093 | 20.016
Devonshire Building | 2017-05-19 22:30 | 50264.4093 | 0
Devonshire Building | 2017-05-19 22:45 | 50264.4143 | 20.016
Devonshire Building | 2017-05-19 23:00 | 50264.4193 | 20.016
Devonshire Building | 2017-05-19 23:15 | 50264.4243 | 20.016
Devonshire Building | 2017-05-19 23:30 | 50264.4243 | 0
Devonshire Building | 2017-05-19 23:45 | 50264.4293 | 20.016
Devonshire Building | 2017-05-20 | 50264.4336 | 20.016
Devonshire Building | 2017-05-20 00:15 | 50264.4336 | 0
Devonshire Building | 2017-05-20 00:30 | 50264.4386 | 20.016
Devonshire Building | 2017-05-20 00:45 | 50264.4436 | 20.016
Devonshire Building | 2017-05-20 01:00 | 50264.4486 | 20.016
Devonshire Building | 2017-05-20 01:15 | 50264.4486 | 0
Devonshire Building | 2017-05-20 01:30 | 50264.4536 | 20.016
Devonshire Building | 2017-05-20 01:45 | 50264.4586 | 20.016
Devonshire Building | 2017-05-20 02:00 | 50264.4586 | 0
Devonshire Building | 2017-05-20 02:15 | 50264.4636 | 20.016
Devonshire Building | 2017-05-20 02:30 | 50264.4686 | 20.016
Devonshire Building | 2017-05-20 02:45 | 50264.4686 | 0
Devonshire Building | 2017-05-20 03:00 | 50264.4736 | 20.016
Devonshire Building | 2017-05-20 03:15 | 50264.4786 | 20.016
Devonshire Building | 2017-05-20 03:30 | 50264.4786 | 0
Devonshire Building | 2017-05-20 03:45 | 50264.4836 | 20.016
Devonshire Building | 2017-05-20 04:00 | 50264.4886 | 20.016
Devonshire Building | 2017-05-20 04:15 | 50265.0086 | 2080.008
Devonshire Building | 2017-05-20 04:30 | 50265.0136 | 20.016
Devonshire Building | 2017-05-20 04:45 | 50265.0136 | 0
Devonshire Building | 2017-05-20 05:00 | 50265.0186 | 20.016
Devonshire Building | 2017-05-20 05:15 | 50265.0236 | 20.016
Devonshire Building | 2017-05-20 05:30 | 50265.0236 | 0
Devonshire Building | 2017-05-20 05:45 | 50265.0287 | 20.016
Devonshire Building | 2017-05-20 06:00 | 50265.0337 | 20.016
Devonshire Building | 2017-05-20 06:15 | 50265.0337 | 0
Devonshire Building | 2017-05-20 06:30 | 50265.0387 | 20.016
Devonshire Building | 2017-05-20 06:45 | 50265.0437 | 20.016
Devonshire Building | 2017-05-20 07:00 | 50265.0437 | 0
Devonshire Building | 2017-05-20 07:15 | 50265.0487 | 20.016
Devonshire Building | 2017-05-20 07:30 | 50265.0487 | 0
Devonshire Building | 2017-05-20 07:45 | 50265.0537 | 20.016
Devonshire Building | 2017-05-20 08:00 | 50265.0587 | 20.016
Devonshire Building | 2017-05-20 08:15 | 50265.0587 | 0
Devonshire Building | 2017-05-20 08:30 | 50265.0637 | 20.016
Devonshire Building | 2017-05-20 08:45 | 50265.0687 | 20.016
Devonshire Building | 2017-05-20 09:00 | 50265.0687 | 0
Devonshire Building | 2017-05-20 09:15 | 50265.0737 | 20.016
Devonshire Building | 2017-05-20 09:30 | 50265.0737 | 0
Devonshire Building | 2017-05-20 09:45 | 50265.0787 | 20.016
Devonshire Building | 2017-05-20 10:00 | 50265.0887 | 39.996
Devonshire Building | 2017-05-20 10:15 | 50265.0887 | 0
Devonshire Building | 2017-05-20 10:30 | 50265.0937 | 20.016
Devonshire Building | 2017-05-20 10:45 | 50265.0987 | 20.016
Devonshire Building | 2017-05-20 11:00 | 50265.1037 | 20.016
Devonshire Building | 2017-05-20 11:15 | 50265.1037 | 0
Devonshire Building | 2017-05-20 11:30 | 50265.1087 | 20.016
Devonshire Building | 2017-05-20 11:45 | 50265.1137 | 20.016
Devonshire Building | 2017-05-20 12:00 | 50265.1187 | 20.016
Devonshire Building | 2017-05-20 12:15 | 50265.1187 | 0
Devonshire Building | 2017-05-20 12:30 | 50265.1237 | 20.016
Devonshire Building | 2017-05-20 12:45 | 50265.1287 | 20.016
Devonshire Building | 2017-05-20 13:00 | 50265.1337 | 20.016
Devonshire Building | 2017-05-20 13:15 | 50265.1387 | 20.016
Devonshire Building | 2017-05-20 13:30 | 50265.1387 | 0
Devonshire Building | 2017-05-20 13:45 | 50265.1587 | 79.992
Devonshire Building | 2017-05-20 14:00 | 50265.1787 | 79.992
Devonshire Building | 2017-05-20 14:15 | 50265.1987 | 79.992
Devonshire Building | 2017-05-20 14:30 | 50265.2187 | 79.992
Devonshire Building | 2017-05-20 14:45 | 50265.2387 | 79.992
Devonshire Building | 2017-05-20 15:00 | 50265.2587 | 79.992
Devonshire Building | 2017-05-20 15:15 | 50265.2787 | 79.992
Devonshire Building | 2017-05-20 15:30 | 50265.3037 | 100.008
Devonshire Building | 2017-05-20 15:45 | 50265.3087 | 20.016
Devonshire Building | 2017-05-20 16:00 | 50265.3137 | 20.016
Devonshire Building | 2017-05-20 16:15 | 50265.3187 | 20.016
Devonshire Building | 2017-05-20 16:30 | 50265.3237 | 20.016
Devonshire Building | 2017-05-20 16:45 | 50265.3237 | 0
Devonshire Building | 2017-05-20 17:00 | 50265.3287 | 20.016
Devonshire Building | 2017-05-20 17:15 | 50265.3337 | 20.016
Devonshire Building | 2017-05-20 17:30 | 50265.3337 | 0
Devonshire Building | 2017-05-20 17:45 | 50265.3387 | 20.016
Devonshire Building | 2017-05-20 18:00 | 50265.3438 | 20.016
Devonshire Building | 2017-05-20 18:15 | 50265.3488 | 20.016
Devonshire Building | 2017-05-20 18:30 | 50265.3488 | 0
Devonshire Building | 2017-05-20 18:45 | 50265.3538 | 20.016
Devonshire Building | 2017-05-20 19:00 | 50265.3588 | 20.016
Devonshire Building | 2017-05-20 19:15 | 50265.3638 | 20.016
Devonshire Building | 2017-05-20 19:30 | 50265.3638 | 0
Devonshire Building | 2017-05-20 19:45 | 50265.3738 | 39.996
Devonshire Building | 2017-05-20 20:00 | 50265.3788 | 20.016
Devonshire Building | 2017-05-20 20:15 | 50265.3838 | 20.016
Devonshire Building | 2017-05-20 20:30 | 50265.3888 | 20.016
Devonshire Building | 2017-05-20 20:45 | 50265.9038 | 2059.992
Devonshire Building | 2017-05-20 21:00 | 50265.9088 | 20.016
Devonshire Building | 2017-05-20 21:15 | 50265.9088 | 0
Devonshire Building | 2017-05-20 21:30 | 50265.9138 | 20.016
Devonshire Building | 2017-05-20 21:45 | 50265.9188 | 20.016
Devonshire Building | 2017-05-20 22:00 | 50265.9238 | 20.016
Devonshire Building | 2017-05-20 22:15 | 50265.9288 | 20.016
Devonshire Building | 2017-05-20 22:30 | 50265.9338 | 20.016
Devonshire Building | 2017-05-20 22:45 | 50265.9388 | 20.016
Devonshire Building | 2017-05-20 23:00 | 50265.9438 | 20.016
Devonshire Building | 2017-05-20 23:15 | 50265.9488 | 20.016
Devonshire Building | 2017-05-20 23:30 | 50265.9538 | 20.016
Devonshire Building | 2017-05-20 23:45 | 50265.9588 | 20.016
Devonshire Building | 2017-05-21 | 50265.9648 | 20.016
Devonshire Building | 2017-05-21 00:15 | 50265.9698 | 20.016
Devonshire Building | 2017-05-21 00:30 | 50265.9748 | 20.016
Devonshire Building | 2017-05-21 00:45 | 50265.9799 | 20.016
Devonshire Building | 2017-05-21 01:00 | 50265.9849 | 20.016
Devonshire Building | 2017-05-21 01:15 | 50265.9899 | 20.016
Devonshire Building | 2017-05-21 01:30 | 50265.9999 | 39.996
Devonshire Building | 2017-05-21 01:45 | 50266.0049 | 20.016
Devonshire Building | 2017-05-21 02:00 | 50266.0099 | 20.016
Devonshire Building | 2017-05-21 02:15 | 50266.0199 | 39.996
Devonshire Building | 2017-05-21 02:30 | 50266.0249 | 20.016
Devonshire Building | 2017-05-21 02:45 | 50266.0299 | 20.016
Devonshire Building | 2017-05-21 03:00 | 50266.0399 | 39.996
Devonshire Building | 2017-05-21 03:15 | 50266.0449 | 20.016
Devonshire Building | 2017-05-21 03:30 | 50266.0499 | 20.016
Devonshire Building | 2017-05-21 03:45 | 50266.0549 | 20.016
Devonshire Building | 2017-05-21 04:00 | 50266.0649 | 39.996
Devonshire Building | 2017-05-21 04:15 | 50266.0699 | 20.016
Devonshire Building | 2017-05-21 04:30 | 50266.0749 | 20.016
Devonshire Building | 2017-05-21 04:45 | 50266.0799 | 20.016
Devonshire Building | 2017-05-21 05:00 | 50266.0849 | 20.016
Devonshire Building | 2017-05-21 05:15 | 50266.0899 | 20.016
Devonshire Building | 2017-05-21 05:30 | 50266.0949 | 20.016
Devonshire Building | 2017-05-21 05:45 | 50266.0999 | 20.016
Devonshire Building | 2017-05-21 06:00 | 50266.1049 | 20.016
Devonshire Building | 2017-05-21 06:15 | 50266.1149 | 39.996
Devonshire Building | 2017-05-21 06:30 | 50266.1199 | 20.016
Devonshire Building | 2017-05-21 06:45 | 50266.1249 | 20.016
Devonshire Building | 2017-05-21 07:00 | 50266.1299 | 20.016
Devonshire Building | 2017-05-21 07:15 | 50266.1349 | 20.016
Devonshire Building | 2017-05-21 07:30 | 50266.1399 | 20.016
Devonshire Building | 2017-05-21 07:45 | 50266.1449 | 20.016
Devonshire Building | 2017-05-21 08:00 | 50266.1499 | 20.016
Devonshire Building | 2017-05-21 08:15 | 50266.1549 | 20.016
Devonshire Building | 2017-05-21 08:30 | 50266.16 | 20.016
Devonshire Building | 2017-05-21 08:45 | 50266.165 | 20.016
Devonshire Building | 2017-05-21 09:00 | 50266.17 | 20.016
Devonshire Building | 2017-05-21 09:15 | 50266.17 | 0
Devonshire Building | 2017-05-21 09:30 | 50266.18 | 39.996
Devonshire Building | 2017-05-21 09:45 | 50266.185 | 20.016
Devonshire Building | 2017-05-21 10:00 | 50266.19 | 20.016
Devonshire Building | 2017-05-21 10:15 | 50266.195 | 20.016
Devonshire Building | 2017-05-21 10:30 | 50266.2 | 20.016
Devonshire Building | 2017-05-21 10:45 | 50266.205 | 20.016
Devonshire Building | 2017-05-21 11:00 | 50266.21 | 20.016
Devonshire Building | 2017-05-21 11:15 | 50266.215 | 20.016
Devonshire Building | 2017-05-21 11:30 | 50266.22 | 20.016
Devonshire Building | 2017-05-21 11:45 | 50266.225 | 20.016
Devonshire Building | 2017-05-21 12:00 | 50266.23 | 20.016
Devonshire Building | 2017-05-21 12:15 | 50266.235 | 20.016
Devonshire Building | 2017-05-21 12:30 | 50266.235 | 0
Devonshire Building | 2017-05-21 12:45 | 50266.24 | 20.016
Devonshire Building | 2017-05-21 13:00 | 50266.245 | 20.016
Devonshire Building | 2017-05-21 13:15 | 50266.25 | 20.016
Devonshire Building | 2017-05-21 13:30 | 50266.26 | 39.996
Devonshire Building | 2017-05-21 13:45 | 50266.28 | 79.992
Devonshire Building | 2017-05-21 14:00 | 50266.305 | 100.008
Devonshire Building | 2017-05-21 14:15 | 50266.325 | 79.992
Devonshire Building | 2017-05-21 14:30 | 50266.35 | 100.008
Devonshire Building | 2017-05-21 14:45 | 50266.37 | 79.992
Devonshire Building | 2017-05-21 15:00 | 50266.39 | 79.992
Devonshire Building | 2017-05-21 15:15 | 50266.41 | 79.992
Devonshire Building | 2017-05-21 15:30 | 50266.43 | 79.992
Devonshire Building | 2017-05-21 15:45 | 50266.46 | 119.988
Devonshire Building | 2017-05-21 16:00 | 50266.465 | 20.016
Devonshire Building | 2017-05-21 16:15 | 50266.47 | 20.016
Devonshire Building | 2017-05-21 16:30 | 50266.475 | 20.016
Devonshire Building | 2017-05-21 16:45 | 50266.475 | 0
Devonshire Building | 2017-05-21 17:00 | 50266.48 | 20.016
Devonshire Building | 2017-05-21 17:15 | 50266.485 | 20.016
Devonshire Building | 2017-05-21 17:30 | 50266.49 | 20.016
Devonshire Building | 2017-05-21 17:45 | 50266.49 | 0
Devonshire Building | 2017-05-21 18:00 | 50266.495 | 20.016
Devonshire Building | 2017-05-21 18:15 | 50266.5 | 20.016
Devonshire Building | 2017-05-21 18:30 | 50267.005 | 2019.996
Devonshire Building | 2017-05-21 18:45 | 50267.01 | 20.016
Devonshire Building | 2017-05-21 19:00 | 50267.015 | 20.016
Devonshire Building | 2017-05-21 19:15 | 50267.02 | 20.016
Devonshire Building | 2017-05-21 19:30 | 50267.02 | 0
Devonshire Building | 2017-05-21 19:45 | 50267.025 | 20.016
Devonshire Building | 2017-05-21 20:00 | 50267.0301 | 20.016
Devonshire Building | 2017-05-21 20:15 | 50267.0301 | 0
Devonshire Building | 2017-05-21 20:30 | 50267.0351 | 20.016
Devonshire Building | 2017-05-21 20:45 | 50267.0451 | 39.996
Devonshire Building | 2017-05-21 21:00 | 50267.0501 | 20.016
Devonshire Building | 2017-05-21 21:15 | 50267.0551 | 20.016
Devonshire Building | 2017-05-21 21:30 | 50267.0551 | 0
Devonshire Building | 2017-05-21 21:45 | 50267.0601 | 20.016
Devonshire Building | 2017-05-21 22:00 | 50267.0651 | 20.016
Devonshire Building | 2017-05-21 22:15 | 50267.0651 | 0
Devonshire Building | 2017-05-21 22:30 | 50267.0701 | 20.016
Devonshire Building | 2017-05-21 22:45 | 50267.0751 | 20.016
Devonshire Building | 2017-05-21 23:00 | 50267.0751 | 0
Devonshire Building | 2017-05-21 23:15 | 50267.0801 | 20.016
Devonshire Building | 2017-05-21 23:30 | 50267.0851 | 20.016
Devonshire Building | 2017-05-21 23:45 | 50267.0901 | 20.016
Devonshire Building | 2017-05-22 | 50267.0898 | 0
Devonshire Building | 2017-05-22 00:15 | 50267.0948 | 20.016
Devonshire Building | 2017-05-22 00:30 | 50267.0998 | 20.016
Devonshire Building | 2017-05-22 00:45 | 50267.1049 | 20.016
Devonshire Building | 2017-05-22 01:00 | 50267.1099 | 20.016
Devonshire Building | 2017-05-22 01:15 | 50267.1149 | 20.016
Devonshire Building | 2017-05-22 01:30 | 50267.1149 | 0
Devonshire Building | 2017-05-22 01:45 | 50267.1199 | 20.016
Devonshire Building | 2017-05-22 02:00 | 50267.1249 | 20.016
Devonshire Building | 2017-05-22 02:15 | 50267.1299 | 20.016
Devonshire Building | 2017-05-22 02:30 | 50267.1349 | 20.016
Devonshire Building | 2017-05-22 02:45 | 50267.1399 | 20.016
Devonshire Building | 2017-05-22 03:00 | 50267.1449 | 20.016
Devonshire Building | 2017-05-22 03:15 | 50267.1449 | 0
Devonshire Building | 2017-05-22 03:30 | 50267.1499 | 20.016
Devonshire Building | 2017-05-22 03:45 | 50267.1549 | 20.016
Devonshire Building | 2017-05-22 04:00 | 50267.1599 | 20.016
Devonshire Building | 2017-05-22 04:15 | 50267.1649 | 20.016
Devonshire Building | 2017-05-22 04:30 | 50267.1649 | 0
Devonshire Building | 2017-05-22 04:45 | 50267.1699 | 20.016
Devonshire Building | 2017-05-22 05:00 | 50267.1749 | 20.016
Devonshire Building | 2017-05-22 05:15 | 50267.1799 | 20.016
Devonshire Building | 2017-05-22 05:30 | 50267.1849 | 20.016
Devonshire Building | 2017-05-22 05:45 | 50267.1899 | 20.016
Devonshire Building | 2017-05-22 06:00 | 50267.1949 | 20.016
Devonshire Building | 2017-05-22 06:15 | 50267.1999 | 20.016
Devonshire Building | 2017-05-22 06:30 | 50267.2049 | 20.016
Devonshire Building | 2017-05-22 06:45 | 50267.2099 | 20.016
Devonshire Building | 2017-05-22 07:00 | 50267.2299 | 79.992
Devonshire Building | 2017-05-22 07:15 | 50267.2399 | 39.996
Devonshire Building | 2017-05-22 07:30 | 50267.2499 | 39.996
Devonshire Building | 2017-05-22 07:45 | 50267.2599 | 39.996
Devonshire Building | 2017-05-22 08:00 | 50267.7949 | 2139.984
Devonshire Building | 2017-05-22 08:15 | 50267.8099 | 60.012
Devonshire Building | 2017-05-22 08:30 | 50267.8299 | 79.992
Devonshire Building | 2017-05-22 08:45 | 50267.8599 | 119.988
Devonshire Building | 2017-05-22 09:00 | 50267.9849 | 500.004
Devonshire Building | 2017-05-22 09:15 | 50268.6749 | 2760.012
Devonshire Building | 2017-05-22 09:30 | 50269.0949 | 1680.012
Devonshire Building | 2017-05-22 09:45 | 50269.3749 | 1119.996
Devonshire Building | 2017-05-22 10:00 | 50269.5049 | 519.984
Devonshire Building | 2017-05-22 10:15 | 50269.5899 | 339.984
Devonshire Building | 2017-05-22 10:30 | 50270.1999 | 2440.008
Devonshire Building | 2017-05-22 10:45 | 50270.2849 | 339.984
Devonshire Building | 2017-05-22 11:00 | 50270.4349 | 600.012
Devonshire Building | 2017-05-22 11:15 | 50270.5949 | 640.008
Devonshire Building | 2017-05-22 11:30 | 50270.7149 | 479.988
Devonshire Building | 2017-05-22 11:45 | 50271.3399 | 2499.984
Devonshire Building | 2017-05-22 12:00 | 50271.3999 | 240.012
Devonshire Building | 2017-05-22 12:15 | 50271.4599 | 240.012
Devonshire Building | 2017-05-22 12:30 | 50271.5149 | 219.996
Devonshire Building | 2017-05-22 12:45 | 50271.5699 | 219.996
Devonshire Building | 2017-05-22 13:00 | 50271.6199 | 200.016
Devonshire Building | 2017-05-22 13:15 | 50272.2299 | 2440.008
Devonshire Building | 2017-05-22 13:30 | 50272.2849 | 219.996
Devonshire Building | 2017-05-22 13:45 | 50272.3599 | 299.988
Devonshire Building | 2017-05-22 14:00 | 50272.4349 | 299.988
Devonshire Building | 2017-05-22 14:15 | 50272.5099 | 299.988
Devonshire Building | 2017-05-22 14:30 | 50272.6149 | 420.012
Devonshire Building | 2017-05-22 14:45 | 50272.7699 | 619.992
Devonshire Building | 2017-05-22 15:00 | 50273.4649 | 2779.992
Devonshire Building | 2017-05-22 15:15 | 50273.6099 | 579.996
Devonshire Building | 2017-05-22 15:30 | 50273.7299 | 479.988
Devonshire Building | 2017-05-22 15:45 | 50273.8249 | 380.016
Devonshire Building | 2017-05-22 16:00 | 50273.9049 | 320.004
Devonshire Building | 2017-05-22 16:15 | 50273.9749 | 280.008
Devonshire Building | 2017-05-22 16:30 | 50274.5949 | 2480.004
Devonshire Building | 2017-05-22 16:45 | 50274.6449 | 200.016
Devonshire Building | 2017-05-22 17:00 | 50274.6749 | 119.988
Devonshire Building | 2017-05-22 17:15 | 50274.6999 | 100.008
Devonshire Building | 2017-05-22 17:30 | 50274.7249 | 100.008
Devonshire Building | 2017-05-22 17:45 | 50274.7499 | 100.008
Devonshire Building | 2017-05-22 18:00 | 50274.7699 | 79.992
Devonshire Building | 2017-05-22 18:15 | 50274.7949 | 100.008
Devonshire Building | 2017-05-22 18:30 | 50274.8199 | 100.008
Devonshire Building | 2017-05-22 18:45 | 50274.8399 | 79.992
Devonshire Building | 2017-05-22 19:00 | 50274.8599 | 79.992
Devonshire Building | 2017-05-22 19:15 | 50274.8799 | 79.992
Devonshire Building | 2017-05-22 19:30 | 50274.8999 | 79.992
Devonshire Building | 2017-05-22 19:45 | 50274.9199 | 79.992
Devonshire Building | 2017-05-22 20:00 | 50274.9399 | 79.992
Devonshire Building | 2017-05-22 20:15 | 50274.9599 | 79.992
Devonshire Building | 2017-05-22 20:30 | 50274.9799 | 79.992
Devonshire Building | 2017-05-22 20:45 | 50275.0099 | 119.988
Devonshire Building | 2017-05-22 21:00 | 50275.0249 | 60.012
Devonshire Building | 2017-05-22 21:15 | 50275.0349 | 39.996
Devonshire Building | 2017-05-22 21:30 | 50275.0499 | 60.012
Devonshire Building | 2017-05-22 21:45 | 50275.0649 | 60.012
Devonshire Building | 2017-05-22 22:00 | 50275.0799 | 60.012
Devonshire Building | 2017-05-22 22:15 | 50275.0899 | 39.996
Devonshire Building | 2017-05-22 22:30 | 50275.1049 | 60.012
Devonshire Building | 2017-05-22 22:45 | 50275.1199 | 60.012
Devonshire Building | 2017-05-22 23:00 | 50275.1299 | 39.996
Devonshire Building | 2017-05-22 23:15 | 50275.1449 | 60.012
Devonshire Building | 2017-05-22 23:30 | 50275.1599 | 60.012
Devonshire Building | 2017-05-22 23:45 | 50275.1699 | 39.996
Devonshire Building | 2017-05-23 | 50275.1836 | 60.012
Devonshire Building | 2017-05-23 00:15 | 50275.1936 | 39.996
Devonshire Building | 2017-05-23 00:30 | 50275.2086 | 60.012
Devonshire Building | 2017-05-23 00:45 | 50275.2186 | 39.996
Devonshire Building | 2017-05-23 01:00 | 50275.2336 | 60.012
Devonshire Building | 2017-05-23 01:15 | 50275.2436 | 39.996
Devonshire Building | 2017-05-23 01:30 | 50275.2586 | 60.012
Devonshire Building | 2017-05-23 01:45 | 50275.2686 | 39.996
Devonshire Building | 2017-05-23 02:00 | 50275.2836 | 60.012
Devonshire Building | 2017-05-23 02:15 | 50275.2936 | 39.996
Devonshire Building | 2017-05-23 02:30 | 50275.3086 | 60.012
Devonshire Building | 2017-05-23 02:45 | 50275.3186 | 39.996
Devonshire Building | 2017-05-23 03:00 | 50275.3336 | 60.012
Devonshire Building | 2017-05-23 03:15 | 50275.3436 | 39.996
Devonshire Building | 2017-05-23 03:30 | 50275.3586 | 60.012
Devonshire Building | 2017-05-23 03:45 | 50275.3686 | 39.996
Devonshire Building | 2017-05-23 04:00 | 50275.3786 | 39.996
Devonshire Building | 2017-05-23 04:15 | 50275.3936 | 60.012
Devonshire Building | 2017-05-23 04:30 | 50275.4036 | 39.996
Devonshire Building | 2017-05-23 04:45 | 50275.4136 | 39.996
Devonshire Building | 2017-05-23 05:00 | 50275.4286 | 60.012
Devonshire Building | 2017-05-23 05:15 | 50275.4386 | 39.996
Devonshire Building | 2017-05-23 05:30 | 50275.4536 | 60.012
Devonshire Building | 2017-05-23 05:45 | 50275.4686 | 60.012
Devonshire Building | 2017-05-23 06:00 | 50275.4786 | 39.996
Devonshire Building | 2017-05-23 06:15 | 50275.4936 | 60.012
Devonshire Building | 2017-05-23 06:30 | 50275.5036 | 39.996
Devonshire Building | 2017-05-23 06:45 | 50276.0136 | 2040.012
Devonshire Building | 2017-05-23 07:00 | 50276.0436 | 119.988
Devonshire Building | 2017-05-23 07:15 | 50276.0686 | 100.008
Devonshire Building | 2017-05-23 07:30 | 50276.1136 | 180
Devonshire Building | 2017-05-23 07:45 | 50276.1836 | 280.008
Devonshire Building | 2017-05-23 08:00 | 50276.2786 | 380.016
Devonshire Building | 2017-05-23 08:15 | 50276.3636 | 339.984
Devonshire Building | 2017-05-23 08:30 | 50276.4436 | 320.004
Devonshire Building | 2017-05-23 08:45 | 50276.5186 | 299.988
Devonshire Building | 2017-05-23 09:00 | 50276.6086 | 360
Devonshire Building | 2017-05-23 09:15 | 50277.2136 | 2419.992
Devonshire Building | 2017-05-23 09:30 | 50277.2836 | 280.008
Devonshire Building | 2017-05-23 09:45 | 50277.3686 | 339.984
Devonshire Building | 2017-05-23 10:00 | 50277.4536 | 339.984
Devonshire Building | 2017-05-23 10:15 | 50278.1086 | 2620.008
Devonshire Building | 2017-05-23 10:30 | 50278.1836 | 299.988
Devonshire Building | 2017-05-23 10:45 | 50278.2636 | 320.004
Devonshire Building | 2017-05-23 11:00 | 50278.3486 | 339.984
Devonshire Building | 2017-05-23 11:15 | 50278.4836 | 540
Devonshire Building | 2017-05-23 11:30 | 50278.8886 | 1620
Devonshire Building | 2017-05-23 11:45 | 50279.3886 | 2000.016
Devonshire Building | 2017-05-23 12:00 | 50279.5586 | 680.004
Devonshire Building | 2017-05-23 12:15 | 50279.7486 | 759.996
Devonshire Building | 2017-05-23 12:30 | 50279.9036 | 619.992
Devonshire Building | 2017-05-23 12:45 | 50280.0336 | 519.984
Devonshire Building | 2017-05-23 13:00 | 50280.6736 | 2559.996
Devonshire Building | 2017-05-23 13:15 | 50280.7636 | 360
Devonshire Building | 2017-05-23 13:30 | 50280.8386 | 299.988
Devonshire Building | 2017-05-23 13:45 | 50280.9036 | 259.992
Devonshire Building | 2017-05-23 14:00 | 50280.9786 | 299.988
Devonshire Building | 2017-05-23 14:15 | 50281.1036 | 500.004
Devonshire Building | 2017-05-23 14:30 | 50281.3386 | 939.996
Devonshire Building | 2017-05-23 14:45 | 50282.1386 | 3200.004
Devonshire Building | 2017-05-23 15:00 | 50282.3136 | 699.984
Devonshire Building | 2017-05-23 15:15 | 50282.4286 | 460.008
Devonshire Building | 2017-05-23 15:30 | 50282.5136 | 339.984
Devonshire Building | 2017-05-23 15:45 | 50282.5886 | 299.988
Devonshire Building | 2017-05-23 16:00 | 50282.6586 | 280.008
Devonshire Building | 2017-05-23 16:15 | 50283.2586 | 2400.012
Devonshire Building | 2017-05-23 16:30 | 50283.3086 | 200.016
Devonshire Building | 2017-05-23 16:45 | 50283.3636 | 219.996
Devonshire Building | 2017-05-23 17:00 | 50283.4136 | 200.016
Devonshire Building | 2017-05-23 17:15 | 50283.4636 | 200.016
Devonshire Building | 2017-05-23 17:30 | 50283.5086 | 180
Devonshire Building | 2017-05-23 17:45 | 50283.5436 | 140.004
Devonshire Building | 2017-05-23 18:00 | 50283.5786 | 140.004
Devonshire Building | 2017-05-23 18:15 | 50283.6036 | 100.008
Devonshire Building | 2017-05-23 18:30 | 50283.6286 | 100.008
Devonshire Building | 2017-05-23 18:45 | 50283.6486 | 79.992
Devonshire Building | 2017-05-23 19:00 | 50283.6686 | 79.992
Devonshire Building | 2017-05-23 19:15 | 50283.6836 | 60.012
Devonshire Building | 2017-05-23 19:30 | 50283.7036 | 79.992
Devonshire Building | 2017-05-23 19:45 | 50283.7186 | 60.012
Devonshire Building | 2017-05-23 20:00 | 50283.7386 | 79.992
Devonshire Building | 2017-05-23 20:15 | 50283.7586 | 79.992
Devonshire Building | 2017-05-23 20:30 | 50283.7736 | 60.012
Devonshire Building | 2017-05-23 20:45 | 50283.8086 | 140.004
Devonshire Building | 2017-05-23 21:00 | 50283.8136 | 20.016
Devonshire Building | 2017-05-23 21:15 | 50283.8186 | 20.016
Devonshire Building | 2017-05-23 21:30 | 50283.8236 | 20.016
Devonshire Building | 2017-05-23 21:45 | 50283.8286 | 20.016
Devonshire Building | 2017-05-23 22:00 | 50283.8286 | 0
Devonshire Building | 2017-05-23 22:15 | 50283.8336 | 20.016
Devonshire Building | 2017-05-23 22:30 | 50283.8386 | 20.016
Devonshire Building | 2017-05-23 22:45 | 50283.8436 | 20.016
Devonshire Building | 2017-05-23 23:00 | 50283.8486 | 20.016
Devonshire Building | 2017-05-23 23:15 | 50283.8536 | 20.016
Devonshire Building | 2017-05-23 23:30 | 50283.8586 | 20.016
Devonshire Building | 2017-05-23 23:45 | 50283.8636 | 20.016
Devonshire Building | 2017-05-24 | 50283.8633 | 0
Devonshire Building | 2017-05-24 00:15 | 50283.8683 | 20.016
Devonshire Building | 2017-05-24 00:30 | 50283.8733 | 20.016
Devonshire Building | 2017-05-24 00:45 | 50283.8783 | 20.016
Devonshire Building | 2017-05-24 01:00 | 50283.8833 | 20.016
Devonshire Building | 2017-05-24 01:15 | 50283.8883 | 20.016
Devonshire Building | 2017-05-24 01:30 | 50283.8883 | 0
Devonshire Building | 2017-05-24 01:45 | 50283.8933 | 20.016
Devonshire Building | 2017-05-24 02:00 | 50283.8983 | 20.016
Devonshire Building | 2017-05-24 02:15 | 50283.9033 | 20.016
Devonshire Building | 2017-05-24 02:30 | 50283.9083 | 20.016
Devonshire Building | 2017-05-24 02:45 | 50283.9133 | 20.016
Devonshire Building | 2017-05-24 03:00 | 50283.9183 | 20.016
Devonshire Building | 2017-05-24 03:15 | 50283.9233 | 20.016
Devonshire Building | 2017-05-24 03:30 | 50283.9233 | 0
Devonshire Building | 2017-05-24 03:45 | 50283.9283 | 20.016
Devonshire Building | 2017-05-24 04:00 | 50283.9333 | 20.016
Devonshire Building | 2017-05-24 04:15 | 50283.9383 | 20.016
Devonshire Building | 2017-05-24 04:30 | 50283.9433 | 20.016
Devonshire Building | 2017-05-24 04:45 | 50283.9483 | 20.016
Devonshire Building | 2017-05-24 05:00 | 50283.9583 | 39.996
Devonshire Building | 2017-05-24 05:15 | 50283.9634 | 20.016
Devonshire Building | 2017-05-24 05:30 | 50284.4883 | 2099.988
Devonshire Building | 2017-05-24 05:45 | 50284.4983 | 39.996
Devonshire Building | 2017-05-24 06:00 | 50284.5083 | 39.996
Devonshire Building | 2017-05-24 06:15 | 50284.5183 | 39.996
Devonshire Building | 2017-05-24 06:30 | 50284.5283 | 39.996
Devonshire Building | 2017-05-24 06:45 | 50284.5383 | 39.996
Devonshire Building | 2017-05-24 07:00 | 50284.5583 | 79.992
Devonshire Building | 2017-05-24 07:15 | 50284.5733 | 60.012
Devonshire Building | 2017-05-24 07:30 | 50284.5933 | 79.992
Devonshire Building | 2017-05-24 07:45 | 50284.6333 | 159.984
Devonshire Building | 2017-05-24 08:00 | 50284.7733 | 560.016
Devonshire Building | 2017-05-24 08:15 | 50285.0533 | 1119.996
Devonshire Building | 2017-05-24 08:30 | 50285.2383 | 740.016
Devonshire Building | 2017-05-24 08:45 | 50285.3633 | 500.004
Devonshire Building | 2017-05-24 09:00 | 50285.9833 | 2480.004
Devonshire Building | 2017-05-24 09:15 | 50286.0383 | 219.996
Devonshire Building | 2017-05-24 09:30 | 50286.0933 | 219.996
Devonshire Building | 2017-05-24 09:45 | 50286.1483 | 219.996
Devonshire Building | 2017-05-24 10:00 | 50286.2033 | 219.996
Devonshire Building | 2017-05-24 10:15 | 50286.2583 | 219.996
Devonshire Building | 2017-05-24 10:30 | 50286.8683 | 2440.008
Devonshire Building | 2017-05-24 10:45 | 50287.0033 | 540
Devonshire Building | 2017-05-24 11:00 | 50287.1783 | 699.984
Devonshire Building | 2017-05-24 11:15 | 50287.3333 | 619.992
Devonshire Building | 2017-05-24 11:30 | 50287.8533 | 2080.008
Devonshire Building | 2017-05-24 11:45 | 50288.1133 | 1040.004
Devonshire Building | 2017-05-24 12:00 | 50288.2233 | 439.992
Devonshire Building | 2017-05-24 12:15 | 50288.3283 | 420.012
Devonshire Building | 2017-05-24 12:30 | 50288.4433 | 460.008
Devonshire Building | 2017-05-24 12:45 | 50288.5483 | 420.012
Devonshire Building | 2017-05-24 13:00 | 50288.6383 | 360
Devonshire Building | 2017-05-24 13:15 | 50289.2734 | 2540.016
Devonshire Building | 2017-05-24 13:30 | 50289.3234 | 200.016
Devonshire Building | 2017-05-24 13:45 | 50289.3834 | 240.012
Devonshire Building | 2017-05-24 14:00 | 50289.4384 | 219.996
Devonshire Building | 2017-05-24 14:15 | 50289.4984 | 240.012
Devonshire Building | 2017-05-24 14:30 | 50289.5584 | 240.012
Devonshire Building | 2017-05-24 14:45 | 50290.1534 | 2379.996
Devonshire Building | 2017-05-24 15:00 | 50290.2184 | 259.992
Devonshire Building | 2017-05-24 15:15 | 50290.2734 | 219.996
Devonshire Building | 2017-05-24 15:30 | 50290.3284 | 219.996
Devonshire Building | 2017-05-24 15:45 | 50290.3784 | 200.016
Devonshire Building | 2017-05-24 16:00 | 50290.4234 | 180
Devonshire Building | 2017-05-24 16:15 | 50290.4634 | 159.984
Devonshire Building | 2017-05-24 16:30 | 50290.4984 | 140.004
Devonshire Building | 2017-05-24 16:45 | 50291.0384 | 2160
Devonshire Building | 2017-05-24 17:00 | 50291.0534 | 60.012
Devonshire Building | 2017-05-24 17:15 | 50291.0634 | 39.996
Devonshire Building | 2017-05-24 17:30 | 50291.0784 | 60.012
Devonshire Building | 2017-05-24 17:45 | 50291.0884 | 39.996
Devonshire Building | 2017-05-24 18:00 | 50291.1034 | 60.012
Devonshire Building | 2017-05-24 18:15 | 50291.1184 | 60.012
Devonshire Building | 2017-05-24 18:30 | 50291.1334 | 60.012
Devonshire Building | 2017-05-24 18:45 | 50291.1434 | 39.996
Devonshire Building | 2017-05-24 19:00 | 50291.1584 | 60.012
Devonshire Building | 2017-05-24 19:15 | 50291.1784 | 79.992
Devonshire Building | 2017-05-24 19:30 | 50291.1884 | 39.996
Devonshire Building | 2017-05-24 19:45 | 50291.1984 | 39.996
Devonshire Building | 2017-05-24 20:00 | 50291.2084 | 39.996
Devonshire Building | 2017-05-24 20:15 | 50291.2184 | 39.996
Devonshire Building | 2017-05-24 20:30 | 50291.2334 | 60.012
Devonshire Building | 2017-05-24 20:45 | 50291.2484 | 60.012
Devonshire Building | 2017-05-24 21:00 | 50291.2584 | 39.996
Devonshire Building | 2017-05-24 21:15 | 50291.2684 | 39.996
Devonshire Building | 2017-05-24 21:30 | 50291.2784 | 39.996
Devonshire Building | 2017-05-24 21:45 | 50291.2884 | 39.996
Devonshire Building | 2017-05-24 22:00 | 50291.2984 | 39.996
Devonshire Building | 2017-05-24 22:15 | 50291.3084 | 39.996
Devonshire Building | 2017-05-24 22:30 | 50291.3184 | 39.996
Devonshire Building | 2017-05-24 22:45 | 50291.3284 | 39.996
Devonshire Building | 2017-05-24 23:00 | 50291.3384 | 39.996
Devonshire Building | 2017-05-24 23:15 | 50291.3484 | 39.996
Devonshire Building | 2017-05-24 23:30 | 50291.3534 | 20.016
Devonshire Building | 2017-05-24 23:45 | 50291.3634 | 39.996
Devonshire Building | 2017-05-25 | 50291.375 | 39.996
Devonshire Building | 2017-05-25 00:15 | 50291.385 | 39.996
Devonshire Building | 2017-05-25 00:30 | 50291.39 | 20.016
Devonshire Building | 2017-05-25 00:45 | 50291.4 | 39.996
Devonshire Building | 2017-05-25 01:00 | 50291.41 | 39.996
Devonshire Building | 2017-05-25 01:15 | 50291.415 | 20.016
Devonshire Building | 2017-05-25 01:30 | 50291.425 | 39.996
Devonshire Building | 2017-05-25 01:45 | 50291.445 | 79.992
Devonshire Building | 2017-05-25 02:00 | 50291.47 | 100.008
Devonshire Building | 2017-05-25 02:15 | 50291.495 | 100.008
Devonshire Building | 2017-05-25 02:30 | 50291.515 | 79.992
Devonshire Building | 2017-05-25 02:45 | 50291.54 | 100.008
Devonshire Building | 2017-05-25 03:00 | 50291.565 | 100.008
Devonshire Building | 2017-05-25 03:15 | 50291.59 | 100.008
Devonshire Building | 2017-05-25 03:30 | 50291.615 | 100.008
Devonshire Building | 2017-05-25 03:45 | 50291.63 | 60.012
Devonshire Building | 2017-05-25 04:00 | 50291.64 | 39.996
Devonshire Building | 2017-05-25 04:15 | 50291.645 | 20.016
Devonshire Building | 2017-05-25 04:30 | 50291.655 | 39.996
Devonshire Building | 2017-05-25 04:45 | 50291.66 | 20.016
Devonshire Building | 2017-05-25 05:00 | 50291.67 | 39.996
Devonshire Building | 2017-05-25 05:15 | 50291.68 | 39.996
Devonshire Building | 2017-05-25 05:30 | 50291.69 | 39.996
Devonshire Building | 2017-05-25 05:45 | 50291.695 | 20.016
Devonshire Building | 2017-05-25 06:00 | 50291.705 | 39.996
Devonshire Building | 2017-05-25 06:15 | 50291.715 | 39.996
Devonshire Building | 2017-05-25 06:30 | 50291.725 | 39.996
Devonshire Building | 2017-05-25 06:45 | 50292.26 | 2139.984
Devonshire Building | 2017-05-25 07:00 | 50292.275 | 60.012
Devonshire Building | 2017-05-25 07:15 | 50292.29 | 60.012
Devonshire Building | 2017-05-25 07:30 | 50292.305 | 60.012
Devonshire Building | 2017-05-25 07:45 | 50292.325 | 79.992
Devonshire Building | 2017-05-25 08:00 | 50292.36 | 140.004
Devonshire Building | 2017-05-25 08:15 | 50292.4 | 159.984
Devonshire Building | 2017-05-25 08:30 | 50292.475 | 299.988
Devonshire Building | 2017-05-25 08:45 | 50292.565 | 360
Devonshire Building | 2017-05-25 09:00 | 50292.65 | 339.984
Devonshire Building | 2017-05-25 09:15 | 50292.91 | 1040.004
Devonshire Building | 2017-05-25 09:30 | 50293.36 | 1800
Devonshire Building | 2017-05-25 09:45 | 50293.435 | 299.988
Devonshire Building | 2017-05-25 10:00 | 50293.5 | 259.992
Devonshire Building | 2017-05-25 10:15 | 50293.57 | 280.008
Devonshire Building | 2017-05-25 10:30 | 50293.715 | 579.996
Devonshire Building | 2017-05-25 10:45 | 50294.275 | 2239.992
Devonshire Building | 2017-05-25 11:00 | 50294.37 | 380.016
Devonshire Building | 2017-05-25 11:15 | 50294.455 | 339.984
Devonshire Building | 2017-05-25 11:30 | 50294.53 | 299.988
Devonshire Building | 2017-05-25 11:45 | 50294.59 | 240.012
Devonshire Building | 2017-05-25 12:00 | 50294.65 | 240.012
Devonshire Building | 2017-05-25 12:15 | 50295.13 | 1919.988
Devonshire Building | 2017-05-25 12:30 | 50295.265 | 540
Devonshire Building | 2017-05-25 12:45 | 50295.3 | 140.004
Devonshire Building | 2017-05-25 13:00 | 50295.345 | 180
Devonshire Building | 2017-05-25 13:15 | 50295.41 | 259.992
Devonshire Building | 2017-05-25 13:30 | 50295.66 | 1000.008
Devonshire Building | 2017-05-25 13:45 | 50296.07 | 1640.016
Devonshire Building | 2017-05-25 14:00 | 50296.16 | 360
Devonshire Building | 2017-05-25 14:15 | 50296.24 | 320.004
Devonshire Building | 2017-05-25 14:30 | 50296.49 | 1000.008
Devonshire Building | 2017-05-25 14:45 | 50296.86 | 1479.996
Devonshire Building | 2017-05-25 15:00 | 50297.13 | 1080
Devonshire Building | 2017-05-25 15:15 | 50297.335 | 820.008
Devonshire Building | 2017-05-25 15:30 | 50297.66 | 1299.996
Devonshire Building | 2017-05-25 15:45 | 50298.145 | 1940.004
Devonshire Building | 2017-05-25 16:00 | 50298.245 | 399.996
Devonshire Building | 2017-05-25 16:15 | 50298.34 | 380.016
Devonshire Building | 2017-05-25 16:30 | 50298.425 | 339.984
Devonshire Building | 2017-05-25 16:45 | 50298.5 | 299.988
Devonshire Building | 2017-05-25 17:00 | 50298.565 | 259.992
Devonshire Building | 2017-05-25 17:15 | 50298.61 | 180
Devonshire Building | 2017-05-25 17:30 | 50298.645 | 140.004
Devonshire Building | 2017-05-25 17:45 | 50298.675 | 119.988
Devonshire Building | 2017-05-25 18:00 | 50298.705 | 119.988
Devonshire Building | 2017-05-25 18:15 | 50298.73 | 100.008
Devonshire Building | 2017-05-25 18:30 | 50298.75 | 79.992
Devonshire Building | 2017-05-25 18:45 | 50299.28 | 2120.004
Devonshire Building | 2017-05-25 19:00 | 50299.29 | 39.996
Devonshire Building | 2017-05-25 19:15 | 50299.295 | 20.016
Devonshire Building | 2017-05-25 19:30 | 50299.3 | 20.016
Devonshire Building | 2017-05-25 19:45 | 50299.31 | 39.996
Devonshire Building | 2017-05-25 20:00 | 50299.315 | 20.016
Devonshire Building | 2017-05-25 20:15 | 50299.325 | 39.996
Devonshire Building | 2017-05-25 20:30 | 50299.33 | 20.016
Devonshire Building | 2017-05-25 20:45 | 50299.34 | 39.996
Devonshire Building | 2017-05-25 21:00 | 50299.345 | 20.016
Devonshire Building | 2017-05-25 21:15 | 50299.35 | 20.016
Devonshire Building | 2017-05-25 21:30 | 50299.36 | 39.996
Devonshire Building | 2017-05-25 21:45 | 50299.365 | 20.016
Devonshire Building | 2017-05-25 22:00 | 50299.37 | 20.016
Devonshire Building | 2017-05-25 22:15 | 50299.375 | 20.016
Devonshire Building | 2017-05-25 22:30 | 50299.385 | 39.996
Devonshire Building | 2017-05-25 22:45 | 50299.39 | 20.016
Devonshire Building | 2017-05-25 23:00 | 50299.395 | 20.016
Devonshire Building | 2017-05-25 23:15 | 50299.405 | 39.996
Devonshire Building | 2017-05-25 23:30 | 50299.41 | 20.016
Devonshire Building | 2017-05-25 23:45 | 50299.4151 | 20.016
Devonshire Building | 2017-05-26 | 50299.4258 | 39.996
Devonshire Building | 2017-05-26 00:15 | 50299.4308 | 20.016
Devonshire Building | 2017-05-26 00:30 | 50299.4358 | 20.016
Devonshire Building | 2017-05-26 00:45 | 50299.4408 | 20.016
Devonshire Building | 2017-05-26 01:00 | 50299.4508 | 39.996
Devonshire Building | 2017-05-26 01:15 | 50299.4558 | 20.016
Devonshire Building | 2017-05-26 01:30 | 50299.4608 | 20.016
Devonshire Building | 2017-05-26 01:45 | 50299.4708 | 39.996
Devonshire Building | 2017-05-26 02:00 | 50299.4758 | 20.016
Devonshire Building | 2017-05-26 02:15 | 50299.4808 | 20.016
Devonshire Building | 2017-05-26 02:30 | 50299.4908 | 39.996
Devonshire Building | 2017-05-26 02:45 | 50299.4958 | 20.016
Devonshire Building | 2017-05-26 03:00 | 50299.5008 | 20.016
Devonshire Building | 2017-05-26 03:15 | 50299.5108 | 39.996
Devonshire Building | 2017-05-26 03:30 | 50299.5158 | 20.016
Devonshire Building | 2017-05-26 03:45 | 50299.5208 | 20.016
Devonshire Building | 2017-05-26 04:00 | 50299.5308 | 39.996
Devonshire Building | 2017-05-26 04:15 | 50299.5358 | 20.016
Devonshire Building | 2017-05-26 04:30 | 50299.5458 | 39.996
Devonshire Building | 2017-05-26 04:45 | 50299.5508 | 20.016
Devonshire Building | 2017-05-26 05:00 | 50299.5608 | 39.996
Devonshire Building | 2017-05-26 05:15 | 50299.5658 | 20.016
Devonshire Building | 2017-05-26 05:30 | 50299.5758 | 39.996
Devonshire Building | 2017-05-26 05:45 | 50299.5808 | 20.016
Devonshire Building | 2017-05-26 06:00 | 50299.5908 | 39.996
Devonshire Building | 2017-05-26 06:15 | 50299.6008 | 39.996
Devonshire Building | 2017-05-26 06:30 | 50299.6058 | 20.016
Devonshire Building | 2017-05-26 06:45 | 50299.6158 | 39.996
Devonshire Building | 2017-05-26 07:00 | 50299.6258 | 39.996
Devonshire Building | 2017-05-26 07:15 | 50299.6358 | 39.996
Devonshire Building | 2017-05-26 07:30 | 50299.8258 | 759.996
Devonshire Building | 2017-05-26 07:45 | 50300.2008 | 1500.012
Devonshire Building | 2017-05-26 08:00 | 50300.2408 | 159.984
Devonshire Building | 2017-05-26 08:15 | 50300.2708 | 119.988
Devonshire Building | 2017-05-26 08:30 | 50300.3158 | 180
Devonshire Building | 2017-05-26 08:45 | 50300.3558 | 159.984
Devonshire Building | 2017-05-26 09:00 | 50300.4058 | 200.016
Devonshire Building | 2017-05-26 09:15 | 50300.4458 | 159.984
Devonshire Building | 2017-05-26 09:30 | 50301.0408 | 2379.996
Devonshire Building | 2017-05-26 09:45 | 50301.1158 | 299.988
Devonshire Building | 2017-05-26 10:00 | 50301.2008 | 339.984
Devonshire Building | 2017-05-26 10:15 | 50301.3158 | 460.008
Devonshire Building | 2017-05-26 10:30 | 50301.4208 | 420.012
Devonshire Building | 2017-05-26 10:45 | 50301.5158 | 380.016
Devonshire Building | 2017-05-26 11:00 | 50301.6058 | 360
Devonshire Building | 2017-05-26 11:15 | 50302.2208 | 2459.988
Devonshire Building | 2017-05-26 11:30 | 50302.3208 | 399.996
Devonshire Building | 2017-05-26 11:45 | 50302.4658 | 579.996
Devonshire Building | 2017-05-26 12:00 | 50302.6358 | 680.004
Devonshire Building | 2017-05-26 12:15 | 50302.8008 | 659.988
Devonshire Building | 2017-05-26 12:30 | 50302.9808 | 720
Devonshire Building | 2017-05-26 12:45 | 50303.7208 | 2959.992
Devonshire Building | 2017-05-26 13:00 | 50303.9058 | 740.016
Devonshire Building | 2017-05-26 13:15 | 50304.0858 | 720
Devonshire Building | 2017-05-26 13:30 | 50304.2408 | 619.992
Devonshire Building | 2017-05-26 13:45 | 50304.3758 | 540
Devonshire Building | 2017-05-26 14:00 | 50304.4958 | 479.988
Devonshire Building | 2017-05-26 14:15 | 50304.6208 | 500.004
Devonshire Building | 2017-05-26 14:30 | 50305.2958 | 2700
Devonshire Building | 2017-05-26 14:45 | 50305.4608 | 659.988
Devonshire Building | 2017-05-26 15:00 | 50305.7008 | 960.012
Devonshire Building | 2017-05-26 15:15 | 50306.0108 | 1239.984
Devonshire Building | 2017-05-26 15:30 | 50306.2208 | 839.988
Devonshire Building | 2017-05-26 15:45 | 50306.3558 | 540
Devonshire Building | 2017-05-26 16:00 | 50306.5708 | 860.004
Devonshire Building | 2017-05-26 16:15 | 50307.0458 | 1900.008
Devonshire Building | 2017-05-26 16:30 | 50307.0908 | 180
Devonshire Building | 2017-05-26 16:45 | 50307.1308 | 159.984
Devonshire Building | 2017-05-26 17:00 | 50307.1758 | 180
Devonshire Building | 2017-05-26 17:15 | 50307.2058 | 119.988
Devonshire Building | 2017-05-26 17:30 | 50307.2408 | 140.004
Devonshire Building | 2017-05-26 17:45 | 50307.2858 | 180
Devonshire Building | 2017-05-26 18:00 | 50307.3408 | 219.996
Devonshire Building | 2017-05-26 18:15 | 50307.3908 | 200.016
Devonshire Building | 2017-05-26 18:30 | 50307.4358 | 180
Devonshire Building | 2017-05-26 18:45 | 50307.4808 | 180
Devonshire Building | 2017-05-26 19:00 | 50307.5258 | 180
Devonshire Building | 2017-05-26 19:15 | 50307.5658 | 159.984
Devonshire Building | 2017-05-26 19:30 | 50307.6008 | 140.004
Devonshire Building | 2017-05-26 19:45 | 50307.6358 | 140.004
Devonshire Building | 2017-05-26 20:00 | 50307.6658 | 119.988
Devonshire Building | 2017-05-26 20:15 | 50307.6958 | 119.988
Devonshire Building | 2017-05-26 20:30 | 50307.7208 | 100.008
Devonshire Building | 2017-05-26 20:45 | 50307.7658 | 180
Devonshire Building | 2017-05-26 21:00 | 50307.7758 | 39.996
Devonshire Building | 2017-05-26 21:15 | 50307.7858 | 39.996
Devonshire Building | 2017-05-26 21:30 | 50307.7908 | 20.016
Devonshire Building | 2017-05-26 21:45 | 50307.8008 | 39.996
Devonshire Building | 2017-05-26 22:00 | 50307.8108 | 39.996
Devonshire Building | 2017-05-26 22:15 | 50307.8208 | 39.996
Devonshire Building | 2017-05-26 22:30 | 50307.8258 | 20.016
Devonshire Building | 2017-05-26 22:45 | 50307.8358 | 39.996
Devonshire Building | 2017-05-26 23:00 | 50307.8458 | 39.996
Devonshire Building | 2017-05-26 23:15 | 50307.8508 | 20.016
Devonshire Building | 2017-05-26 23:30 | 50307.8608 | 39.996
Devonshire Building | 2017-05-26 23:45 | 50307.8708 | 39.996
Devonshire Building | 2017-05-27 | 50307.875 | 20.016
Devonshire Building | 2017-05-27 00:15 | 50307.885 | 39.996
Devonshire Building | 2017-05-27 00:30 | 50307.89 | 20.016
Devonshire Building | 2017-05-27 00:45 | 50307.9 | 39.996
Devonshire Building | 2017-05-27 01:00 | 50307.905 | 20.016
Devonshire Building | 2017-05-27 01:15 | 50307.915 | 39.996
Devonshire Building | 2017-05-27 01:30 | 50307.92 | 20.016
Devonshire Building | 2017-05-27 01:45 | 50307.93 | 39.996
Devonshire Building | 2017-05-27 02:00 | 50307.935 | 20.016
Devonshire Building | 2017-05-27 02:15 | 50307.94 | 20.016
Devonshire Building | 2017-05-27 02:30 | 50307.95 | 39.996
Devonshire Building | 2017-05-27 02:45 | 50307.955 | 20.016
Devonshire Building | 2017-05-27 03:00 | 50307.96 | 20.016
Devonshire Building | 2017-05-27 03:15 | 50307.97 | 39.996
Devonshire Building | 2017-05-27 03:30 | 50307.975 | 20.016
Devonshire Building | 2017-05-27 03:45 | 50307.98 | 20.016
Devonshire Building | 2017-05-27 04:00 | 50307.99 | 39.996
Devonshire Building | 2017-05-27 04:15 | 50307.995 | 20.016
Devonshire Building | 2017-05-27 04:30 | 50308 | 20.016
Devonshire Building | 2017-05-27 04:45 | 50308.01 | 39.996
Devonshire Building | 2017-05-27 05:00 | 50308.015 | 20.016
Devonshire Building | 2017-05-27 05:15 | 50308.02 | 20.016
Devonshire Building | 2017-05-27 05:30 | 50308.025 | 20.016
Devonshire Building | 2017-05-27 05:45 | 50308.035 | 39.996
Devonshire Building | 2017-05-27 06:00 | 50308.0401 | 20.016
Devonshire Building | 2017-05-27 06:15 | 50308.0451 | 20.016
Devonshire Building | 2017-05-27 06:30 | 50308.0501 | 20.016
Devonshire Building | 2017-05-27 06:45 | 50308.0551 | 20.016
Devonshire Building | 2017-05-27 07:00 | 50308.0651 | 39.996
Devonshire Building | 2017-05-27 07:15 | 50308.0701 | 20.016
Devonshire Building | 2017-05-27 07:30 | 50308.0751 | 20.016
Devonshire Building | 2017-05-27 07:45 | 50308.0801 | 20.016
Devonshire Building | 2017-05-27 08:00 | 50308.0851 | 20.016
Devonshire Building | 2017-05-27 08:15 | 50308.0901 | 20.016
Devonshire Building | 2017-05-27 08:30 | 50308.0951 | 20.016
Devonshire Building | 2017-05-27 08:45 | 50308.1001 | 20.016
Devonshire Building | 2017-05-27 09:00 | 50308.1051 | 20.016
Devonshire Building | 2017-05-27 09:15 | 50308.1151 | 39.996
Devonshire Building | 2017-05-27 09:30 | 50308.1201 | 20.016
Devonshire Building | 2017-05-27 09:45 | 50308.1251 | 20.016
Devonshire Building | 2017-05-27 10:00 | 50308.6401 | 2059.992
Devonshire Building | 2017-05-27 10:15 | 50308.6451 | 20.016
Devonshire Building | 2017-05-27 10:30 | 50308.6501 | 20.016
Devonshire Building | 2017-05-27 10:45 | 50308.6601 | 39.996
Devonshire Building | 2017-05-27 11:00 | 50308.6651 | 20.016
Devonshire Building | 2017-05-27 11:15 | 50308.6701 | 20.016
Devonshire Building | 2017-05-27 11:30 | 50308.6751 | 20.016
Devonshire Building | 2017-05-27 11:45 | 50308.6851 | 39.996
Devonshire Building | 2017-05-27 12:00 | 50308.6901 | 20.016
Devonshire Building | 2017-05-27 12:15 | 50308.7001 | 39.996
Devonshire Building | 2017-05-27 12:30 | 50308.7051 | 20.016
Devonshire Building | 2017-05-27 12:45 | 50308.7151 | 39.996
Devonshire Building | 2017-05-27 13:00 | 50308.7201 | 20.016
Devonshire Building | 2017-05-27 13:15 | 50308.7301 | 39.996
Devonshire Building | 2017-05-27 13:30 | 50308.7451 | 60.012
Devonshire Building | 2017-05-27 13:45 | 50308.7751 | 119.988
Devonshire Building | 2017-05-27 14:00 | 50308.8001 | 100.008
Devonshire Building | 2017-05-27 14:15 | 50308.8251 | 100.008
Devonshire Building | 2017-05-27 14:30 | 50308.8501 | 100.008
Devonshire Building | 2017-05-27 14:45 | 50308.8801 | 119.988
Devonshire Building | 2017-05-27 15:00 | 50308.9051 | 100.008
Devonshire Building | 2017-05-27 15:15 | 50308.9301 | 100.008
Devonshire Building | 2017-05-27 15:30 | 50308.9551 | 100.008
Devonshire Building | 2017-05-27 15:45 | 50308.9801 | 100.008
Devonshire Building | 2017-05-27 16:00 | 50308.9901 | 39.996
Devonshire Building | 2017-05-27 16:15 | 50309.0001 | 39.996
Devonshire Building | 2017-05-27 16:30 | 50309.0101 | 39.996
Devonshire Building | 2017-05-27 16:45 | 50309.0201 | 39.996
Devonshire Building | 2017-05-27 17:00 | 50309.0301 | 39.996
Devonshire Building | 2017-05-27 17:15 | 50309.0351 | 20.016
Devonshire Building | 2017-05-27 17:30 | 50309.0451 | 39.996
Devonshire Building | 2017-05-27 17:45 | 50309.0501 | 20.016
Devonshire Building | 2017-05-27 18:00 | 50309.0601 | 39.996
Devonshire Building | 2017-05-27 18:15 | 50309.0701 | 39.996
Devonshire Building | 2017-05-27 18:30 | 50309.0751 | 20.016
Devonshire Building | 2017-05-27 18:45 | 50309.0851 | 39.996
Devonshire Building | 2017-05-27 19:00 | 50309.0901 | 20.016
Devonshire Building | 2017-05-27 19:15 | 50309.1001 | 39.996
Devonshire Building | 2017-05-27 19:30 | 50309.1051 | 20.016
Devonshire Building | 2017-05-27 19:45 | 50309.1102 | 20.016
Devonshire Building | 2017-05-27 20:00 | 50309.1202 | 39.996
Devonshire Building | 2017-05-27 20:15 | 50309.1252 | 20.016
Devonshire Building | 2017-05-27 20:30 | 50309.1352 | 39.996
Devonshire Building | 2017-05-27 20:45 | 50309.1602 | 100.008
Devonshire Building | 2017-05-27 21:00 | 50309.1702 | 39.996
Devonshire Building | 2017-05-27 21:15 | 50309.1752 | 20.016
Devonshire Building | 2017-05-27 21:30 | 50309.1802 | 20.016
Devonshire Building | 2017-05-27 21:45 | 50309.1902 | 39.996
Devonshire Building | 2017-05-27 22:00 | 50309.1952 | 20.016
Devonshire Building | 2017-05-27 22:15 | 50309.2052 | 39.996
Devonshire Building | 2017-05-27 22:30 | 50309.2102 | 20.016
Devonshire Building | 2017-05-27 22:45 | 50309.2202 | 39.996
Devonshire Building | 2017-05-27 23:00 | 50309.2252 | 20.016
Devonshire Building | 2017-05-27 23:15 | 50309.2302 | 20.016
Devonshire Building | 2017-05-27 23:30 | 50309.2402 | 39.996
Devonshire Building | 2017-05-27 23:45 | 50309.2452 | 20.016
Devonshire Building | 2017-05-28 | 50309.2539 | 39.996
Devonshire Building | 2017-05-28 00:15 | 50309.2589 | 20.016
Devonshire Building | 2017-05-28 00:30 | 50309.2689 | 39.996
Devonshire Building | 2017-05-28 00:45 | 50309.2739 | 20.016
Devonshire Building | 2017-05-28 01:00 | 50309.2839 | 39.996
Devonshire Building | 2017-05-28 01:15 | 50309.2889 | 20.016
Devonshire Building | 2017-05-28 01:30 | 50309.2989 | 39.996
Devonshire Building | 2017-05-28 01:45 | 50309.3039 | 20.016
Devonshire Building | 2017-05-28 02:00 | 50309.3089 | 20.016
Devonshire Building | 2017-05-28 02:15 | 50309.3189 | 39.996
Devonshire Building | 2017-05-28 02:30 | 50309.3239 | 20.016
Devonshire Building | 2017-05-28 02:45 | 50309.3289 | 20.016
Devonshire Building | 2017-05-28 03:00 | 50309.3389 | 39.996
Devonshire Building | 2017-05-28 03:15 | 50309.3439 | 20.016
Devonshire Building | 2017-05-28 03:30 | 50309.3489 | 20.016
Devonshire Building | 2017-05-28 03:45 | 50309.3589 | 39.996
Devonshire Building | 2017-05-28 04:00 | 50309.3639 | 20.016
Devonshire Building | 2017-05-28 04:15 | 50309.3689 | 20.016
Devonshire Building | 2017-05-28 04:30 | 50309.3789 | 39.996
Devonshire Building | 2017-05-28 04:45 | 50309.384 | 20.016
Devonshire Building | 2017-05-28 05:00 | 50309.389 | 20.016
Devonshire Building | 2017-05-28 05:15 | 50309.399 | 39.996
Devonshire Building | 2017-05-28 05:30 | 50309.404 | 20.016
Devonshire Building | 2017-05-28 05:45 | 50309.409 | 20.016
Devonshire Building | 2017-05-28 06:00 | 50309.419 | 39.996
Devonshire Building | 2017-05-28 06:15 | 50309.424 | 20.016
Devonshire Building | 2017-05-28 06:30 | 50309.429 | 20.016
Devonshire Building | 2017-05-28 06:45 | 50309.434 | 20.016
Devonshire Building | 2017-05-28 07:00 | 50309.444 | 39.996
Devonshire Building | 2017-05-28 07:15 | 50309.954 | 2040.012
Devonshire Building | 2017-05-28 07:30 | 50309.959 | 20.016
Devonshire Building | 2017-05-28 07:45 | 50309.964 | 20.016
Devonshire Building | 2017-05-28 08:00 | 50309.969 | 20.016
Devonshire Building | 2017-05-28 08:15 | 50309.974 | 20.016
Devonshire Building | 2017-05-28 08:30 | 50309.979 | 20.016
Devonshire Building | 2017-05-28 08:45 | 50309.989 | 39.996
Devonshire Building | 2017-05-28 09:00 | 50309.994 | 20.016
Devonshire Building | 2017-05-28 09:15 | 50309.999 | 20.016
Devonshire Building | 2017-05-28 09:30 | 50310.004 | 20.016
Devonshire Building | 2017-05-28 09:45 | 50310.009 | 20.016
Devonshire Building | 2017-05-28 10:00 | 50310.014 | 20.016
Devonshire Building | 2017-05-28 10:15 | 50310.019 | 20.016
Devonshire Building | 2017-05-28 10:30 | 50310.029 | 39.996
Devonshire Building | 2017-05-28 10:45 | 50310.034 | 20.016
Devonshire Building | 2017-05-28 11:00 | 50310.044 | 39.996
Devonshire Building | 2017-05-28 11:15 | 50310.049 | 20.016
Devonshire Building | 2017-05-28 11:30 | 50310.059 | 39.996
Devonshire Building | 2017-05-28 11:45 | 50310.064 | 20.016
Devonshire Building | 2017-05-28 12:00 | 50310.074 | 39.996
Devonshire Building | 2017-05-28 12:15 | 50310.084 | 39.996
Devonshire Building | 2017-05-28 12:30 | 50310.094 | 39.996
Devonshire Building | 2017-05-28 12:45 | 50310.099 | 20.016
Devonshire Building | 2017-05-28 13:00 | 50310.109 | 39.996
Devonshire Building | 2017-05-28 13:15 | 50310.114 | 20.016
Devonshire Building | 2017-05-28 13:30 | 50310.124 | 39.996
Devonshire Building | 2017-05-28 13:45 | 50310.129 | 20.016
Devonshire Building | 2017-05-28 14:00 | 50310.139 | 39.996
Devonshire Building | 2017-05-28 14:15 | 50310.144 | 20.016
Devonshire Building | 2017-05-28 14:30 | 50310.154 | 39.996
Devonshire Building | 2017-05-28 14:45 | 50310.159 | 20.016
Devonshire Building | 2017-05-28 15:00 | 50310.164 | 20.016
Devonshire Building | 2017-05-28 15:15 | 50310.174 | 39.996
Devonshire Building | 2017-05-28 15:30 | 50310.179 | 20.016
Devonshire Building | 2017-05-28 15:45 | 50310.189 | 39.996
Devonshire Building | 2017-05-28 16:00 | 50310.194 | 20.016
Devonshire Building | 2017-05-28 16:15 | 50310.1991 | 20.016
Devonshire Building | 2017-05-28 16:30 | 50310.2041 | 20.016
Devonshire Building | 2017-05-28 16:45 | 50310.2141 | 39.996
Devonshire Building | 2017-05-28 17:00 | 50310.2191 | 20.016
Devonshire Building | 2017-05-28 17:15 | 50310.2241 | 20.016
Devonshire Building | 2017-05-28 17:30 | 50310.2341 | 39.996
Devonshire Building | 2017-05-28 17:45 | 50310.2391 | 20.016
Devonshire Building | 2017-05-28 18:00 | 50310.2441 | 20.016
Devonshire Building | 2017-05-28 18:15 | 50310.2541 | 39.996
Devonshire Building | 2017-05-28 18:30 | 50310.2591 | 20.016
Devonshire Building | 2017-05-28 18:45 | 50310.2641 | 20.016
Devonshire Building | 2017-05-28 19:00 | 50310.2691 | 20.016
Devonshire Building | 2017-05-28 19:15 | 50310.2791 | 39.996
Devonshire Building | 2017-05-28 19:30 | 50310.2841 | 20.016
Devonshire Building | 2017-05-28 19:45 | 50310.2891 | 20.016
Devonshire Building | 2017-05-28 20:00 | 50310.2941 | 20.016
Devonshire Building | 2017-05-28 20:15 | 50310.3041 | 39.996
Devonshire Building | 2017-05-28 20:30 | 50310.3091 | 20.016
Devonshire Building | 2017-05-28 20:45 | 50310.3341 | 100.008
Devonshire Building | 2017-05-28 21:00 | 50310.3441 | 39.996
Devonshire Building | 2017-05-28 21:15 | 50310.3491 | 20.016
Devonshire Building | 2017-05-28 21:30 | 50310.3541 | 20.016
Devonshire Building | 2017-05-28 21:45 | 50310.3591 | 20.016
Devonshire Building | 2017-05-28 22:00 | 50310.3641 | 20.016
Devonshire Building | 2017-05-28 22:15 | 50310.3691 | 20.016
Devonshire Building | 2017-05-28 22:30 | 50310.3741 | 20.016
Devonshire Building | 2017-05-28 22:45 | 50310.3791 | 20.016
Devonshire Building | 2017-05-28 23:00 | 50310.3841 | 20.016
Devonshire Building | 2017-05-28 23:15 | 50310.3891 | 20.016
Devonshire Building | 2017-05-28 23:30 | 50310.3941 | 20.016
Devonshire Building | 2017-05-28 23:45 | 50310.3991 | 20.016
Devonshire Building | 2017-05-29 | 50310.4062 | 20.016
Devonshire Building | 2017-05-29 00:15 | 50310.4113 | 20.016
Devonshire Building | 2017-05-29 00:30 | 50310.4163 | 20.016
Devonshire Building | 2017-05-29 00:45 | 50310.9263 | 2040.012
Devonshire Building | 2017-05-29 01:00 | 50310.9313 | 20.016
Devonshire Building | 2017-05-29 01:15 | 50310.9363 | 20.016
Devonshire Building | 2017-05-29 01:30 | 50310.9413 | 20.016
Devonshire Building | 2017-05-29 01:45 | 50310.9613 | 79.992
Devonshire Building | 2017-05-29 02:00 | 50310.9813 | 79.992
Devonshire Building | 2017-05-29 02:15 | 50311.0013 | 79.992
Devonshire Building | 2017-05-29 02:30 | 50311.0213 | 79.992
Devonshire Building | 2017-05-29 02:45 | 50311.0413 | 79.992
Devonshire Building | 2017-05-29 03:00 | 50311.0663 | 100.008
Devonshire Building | 2017-05-29 03:15 | 50311.0863 | 79.992
Devonshire Building | 2017-05-29 03:30 | 50311.1063 | 79.992
Devonshire Building | 2017-05-29 03:45 | 50311.1263 | 79.992
Devonshire Building | 2017-05-29 04:00 | 50311.1313 | 20.016
Devonshire Building | 2017-05-29 04:15 | 50311.1363 | 20.016
Devonshire Building | 2017-05-29 04:30 | 50311.1463 | 39.996
Devonshire Building | 2017-05-29 04:45 | 50311.1513 | 20.016
Devonshire Building | 2017-05-29 05:00 | 50311.1563 | 20.016
Devonshire Building | 2017-05-29 05:15 | 50311.1663 | 39.996
Devonshire Building | 2017-05-29 05:30 | 50311.1713 | 20.016
Devonshire Building | 2017-05-29 05:45 | 50311.1813 | 39.996
Devonshire Building | 2017-05-29 06:00 | 50311.1863 | 20.016
Devonshire Building | 2017-05-29 06:15 | 50311.1913 | 20.016
Devonshire Building | 2017-05-29 06:30 | 50311.2013 | 39.996
Devonshire Building | 2017-05-29 06:45 | 50311.2063 | 20.016
Devonshire Building | 2017-05-29 07:00 | 50311.2163 | 39.996
Devonshire Building | 2017-05-29 07:15 | 50311.2213 | 20.016
Devonshire Building | 2017-05-29 07:30 | 50311.2263 | 20.016
Devonshire Building | 2017-05-29 07:45 | 50311.2363 | 39.996
Devonshire Building | 2017-05-29 08:00 | 50311.2413 | 20.016
Devonshire Building | 2017-05-29 08:15 | 50311.2463 | 20.016
Devonshire Building | 2017-05-29 08:30 | 50311.2513 | 20.016
Devonshire Building | 2017-05-29 08:45 | 50311.2563 | 20.016
Devonshire Building | 2017-05-29 09:00 | 50311.2663 | 39.996
Devonshire Building | 2017-05-29 09:15 | 50311.2713 | 20.016
Devonshire Building | 2017-05-29 09:30 | 50311.2763 | 20.016
Devonshire Building | 2017-05-29 09:45 | 50311.2963 | 79.992
Devonshire Building | 2017-05-29 10:00 | 50311.3013 | 20.016
Devonshire Building | 2017-05-29 10:15 | 50311.3063 | 20.016
Devonshire Building | 2017-05-29 10:30 | 50311.3163 | 39.996
Devonshire Building | 2017-05-29 10:45 | 50311.3213 | 20.016
Devonshire Building | 2017-05-29 11:00 | 50311.3263 | 20.016
Devonshire Building | 2017-05-29 11:15 | 50311.3363 | 39.996
Devonshire Building | 2017-05-29 11:30 | 50311.3413 | 20.016
Devonshire Building | 2017-05-29 11:45 | 50311.3463 | 20.016
Devonshire Building | 2017-05-29 12:00 | 50311.3563 | 39.996
Devonshire Building | 2017-05-29 12:15 | 50311.3613 | 20.016
Devonshire Building | 2017-05-29 12:30 | 50311.3663 | 20.016
Devonshire Building | 2017-05-29 12:45 | 50311.3713 | 20.016
Devonshire Building | 2017-05-29 13:00 | 50311.3813 | 39.996
Devonshire Building | 2017-05-29 13:15 | 50311.3864 | 20.016
Devonshire Building | 2017-05-29 13:30 | 50311.3963 | 39.996
Devonshire Building | 2017-05-29 13:45 | 50311.4014 | 20.016
Devonshire Building | 2017-05-29 14:00 | 50311.4114 | 39.996
Devonshire Building | 2017-05-29 14:15 | 50311.4164 | 20.016
Devonshire Building | 2017-05-29 14:30 | 50311.4214 | 20.016
Devonshire Building | 2017-05-29 14:45 | 50311.4314 | 39.996
Devonshire Building | 2017-05-29 15:00 | 50311.4364 | 20.016
Devonshire Building | 2017-05-29 15:15 | 50311.4414 | 20.016
Devonshire Building | 2017-05-29 15:30 | 50311.4514 | 39.996
Devonshire Building | 2017-05-29 15:45 | 50311.9514 | 2000.016
Devonshire Building | 2017-05-29 16:00 | 50311.9564 | 20.016
Devonshire Building | 2017-05-29 16:15 | 50311.9664 | 39.996
Devonshire Building | 2017-05-29 16:30 | 50311.9714 | 20.016
Devonshire Building | 2017-05-29 16:45 | 50311.9764 | 20.016
Devonshire Building | 2017-05-29 17:00 | 50311.9864 | 39.996
Devonshire Building | 2017-05-29 17:15 | 50311.9914 | 20.016
Devonshire Building | 2017-05-29 17:30 | 50311.9964 | 20.016
Devonshire Building | 2017-05-29 17:45 | 50312.0064 | 39.996
Devonshire Building | 2017-05-29 18:00 | 50312.0164 | 39.996
Devonshire Building | 2017-05-29 18:15 | 50312.0214 | 20.016
Devonshire Building | 2017-05-29 18:30 | 50312.0314 | 39.996
Devonshire Building | 2017-05-29 18:45 | 50312.0414 | 39.996
Devonshire Building | 2017-05-29 19:00 | 50312.0514 | 39.996
Devonshire Building | 2017-05-29 19:15 | 50312.0614 | 39.996
Devonshire Building | 2017-05-29 19:30 | 50312.0714 | 39.996
Devonshire Building | 2017-05-29 19:45 | 50312.0914 | 79.992
Devonshire Building | 2017-05-29 20:00 | 50312.1164 | 100.008
Devonshire Building | 2017-05-29 20:15 | 50312.1464 | 119.988
Devonshire Building | 2017-05-29 20:30 | 50312.1714 | 100.008
Devonshire Building | 2017-05-29 20:45 | 50312.2064 | 140.004
Devonshire Building | 2017-05-29 21:00 | 50312.2364 | 119.988
Devonshire Building | 2017-05-29 21:15 | 50312.2614 | 100.008
Devonshire Building | 2017-05-29 21:30 | 50312.2864 | 100.008
Devonshire Building | 2017-05-29 21:45 | 50312.3064 | 79.992
Devonshire Building | 2017-05-29 22:00 | 50312.3164 | 39.996
Devonshire Building | 2017-05-29 22:15 | 50312.3264 | 39.996
Devonshire Building | 2017-05-29 22:30 | 50312.3364 | 39.996
Devonshire Building | 2017-05-29 22:45 | 50312.3464 | 39.996
Devonshire Building | 2017-05-29 23:00 | 50312.3564 | 39.996
Devonshire Building | 2017-05-29 23:15 | 50312.3664 | 39.996
Devonshire Building | 2017-05-29 23:30 | 50312.3764 | 39.996
Devonshire Building | 2017-05-29 23:45 | 50312.3864 | 39.996
Devonshire Building | 2017-05-30 | 50312.3945 | 39.996
Devonshire Building | 2017-05-30 00:15 | 50312.3995 | 20.016
Devonshire Building | 2017-05-30 00:30 | 50312.4095 | 39.996
Devonshire Building | 2017-05-30 00:45 | 50312.4195 | 39.996
Devonshire Building | 2017-05-30 01:00 | 50312.4295 | 39.996
Devonshire Building | 2017-05-30 01:15 | 50312.4345 | 20.016
Devonshire Building | 2017-05-30 01:30 | 50312.4445 | 39.996
Devonshire Building | 2017-05-30 01:45 | 50312.4545 | 39.996
Devonshire Building | 2017-05-30 02:00 | 50312.4595 | 20.016
Devonshire Building | 2017-05-30 02:15 | 50312.4695 | 39.996
Devonshire Building | 2017-05-30 02:30 | 50312.4795 | 39.996
Devonshire Building | 2017-05-30 02:45 | 50312.4895 | 39.996
Devonshire Building | 2017-05-30 03:00 | 50312.4945 | 20.016
Devonshire Building | 2017-05-30 03:15 | 50312.5045 | 39.996
Devonshire Building | 2017-05-30 03:30 | 50312.5145 | 39.996
Devonshire Building | 2017-05-30 03:45 | 50312.5245 | 39.996
Devonshire Building | 2017-05-30 04:00 | 50312.5295 | 20.016
Devonshire Building | 2017-05-30 04:15 | 50312.5395 | 39.996
Devonshire Building | 2017-05-30 04:30 | 50312.5495 | 39.996
Devonshire Building | 2017-05-30 04:45 | 50312.5545 | 20.016
Devonshire Building | 2017-05-30 05:00 | 50312.5645 | 39.996
Devonshire Building | 2017-05-30 05:15 | 50312.5745 | 39.996
Devonshire Building | 2017-05-30 05:30 | 50312.5845 | 39.996
Devonshire Building | 2017-05-30 05:45 | 50312.5945 | 39.996
Devonshire Building | 2017-05-30 06:00 | 50312.6045 | 39.996
Devonshire Building | 2017-05-30 06:15 | 50312.6145 | 39.996
Devonshire Building | 2017-05-30 06:30 | 50312.6195 | 20.016
Devonshire Building | 2017-05-30 06:45 | 50312.6295 | 39.996
Devonshire Building | 2017-05-30 07:00 | 50312.6445 | 60.012
Devonshire Building | 2017-05-30 07:15 | 50313.1845 | 2160
Devonshire Building | 2017-05-30 07:30 | 50313.2045 | 79.992
Devonshire Building | 2017-05-30 07:45 | 50313.2245 | 79.992
Devonshire Building | 2017-05-30 08:00 | 50313.2745 | 200.016
Devonshire Building | 2017-05-30 08:15 | 50313.3245 | 200.016
Devonshire Building | 2017-05-30 08:30 | 50313.3845 | 240.012
Devonshire Building | 2017-05-30 08:45 | 50313.4395 | 219.996
Devonshire Building | 2017-05-30 09:00 | 50313.4845 | 180
Devonshire Building | 2017-05-30 09:15 | 50314.0895 | 2419.992
Devonshire Building | 2017-05-30 09:30 | 50314.1295 | 159.984
Devonshire Building | 2017-05-30 09:45 | 50314.1795 | 200.016
Devonshire Building | 2017-05-30 10:00 | 50314.2495 | 280.008
Devonshire Building | 2017-05-30 10:15 | 50314.3295 | 320.004
Devonshire Building | 2017-05-30 10:30 | 50314.7095 | 1519.992
Devonshire Building | 2017-05-30 10:45 | 50315.0395 | 1320.012
Devonshire Building | 2017-05-30 11:00 | 50315.1295 | 360
Devonshire Building | 2017-05-30 11:15 | 50315.2145 | 339.984
Devonshire Building | 2017-05-30 11:30 | 50315.2995 | 339.984
Devonshire Building | 2017-05-30 11:45 | 50315.3845 | 339.984
Devonshire Building | 2017-05-30 12:00 | 50315.9895 | 2419.992
Devonshire Building | 2017-05-30 12:15 | 50316.0745 | 339.984
Devonshire Building | 2017-05-30 12:30 | 50316.1495 | 299.988
Devonshire Building | 2017-05-30 12:45 | 50316.2195 | 280.008
Devonshire Building | 2017-05-30 13:00 | 50316.2895 | 280.008
Devonshire Building | 2017-05-30 13:15 | 50316.3595 | 280.008
Devonshire Building | 2017-05-30 13:30 | 50316.4295 | 280.008
Devonshire Building | 2017-05-30 13:45 | 50316.4945 | 259.992
Devonshire Building | 2017-05-30 14:00 | 50317.1045 | 2440.008
Devonshire Building | 2017-05-30 14:15 | 50317.1645 | 240.012
Devonshire Building | 2017-05-30 14:30 | 50317.2245 | 240.012
Devonshire Building | 2017-05-30 14:45 | 50317.2745 | 200.016
Devonshire Building | 2017-05-30 15:00 | 50317.3195 | 180
Devonshire Building | 2017-05-30 15:15 | 50317.3696 | 200.016
Devonshire Building | 2017-05-30 15:30 | 50317.4196 | 200.016
Devonshire Building | 2017-05-30 15:45 | 50317.4646 | 180
Devonshire Building | 2017-05-30 16:00 | 50318.0646 | 2400.012
Devonshire Building | 2017-05-30 16:15 | 50318.0996 | 140.004
Devonshire Building | 2017-05-30 16:30 | 50318.1346 | 140.004
Devonshire Building | 2017-05-30 16:45 | 50318.1696 | 140.004
Devonshire Building | 2017-05-30 17:00 | 50318.2096 | 159.984
Devonshire Building | 2017-05-30 17:15 | 50318.2396 | 119.988
Devonshire Building | 2017-05-30 17:30 | 50318.2746 | 140.004
Devonshire Building | 2017-05-30 17:45 | 50318.3046 | 119.988
Devonshire Building | 2017-05-30 18:00 | 50318.3296 | 100.008
Devonshire Building | 2017-05-30 18:15 | 50318.3546 | 100.008
Devonshire Building | 2017-05-30 18:30 | 50318.3746 | 79.992
Devonshire Building | 2017-05-30 18:45 | 50318.3946 | 79.992
Devonshire Building | 2017-05-30 19:00 | 50318.4145 | 79.992
Devonshire Building | 2017-05-30 19:15 | 50318.4296 | 60.012
Devonshire Building | 2017-05-30 19:30 | 50318.4495 | 79.992
Devonshire Building | 2017-05-30 19:45 | 50318.4646 | 60.012
Devonshire Building | 2017-05-30 20:00 | 50318.4846 | 79.992
Devonshire Building | 2017-05-30 20:15 | 50318.4996 | 60.012
Devonshire Building | 2017-05-30 20:30 | 50318.5096 | 39.996
Devonshire Building | 2017-05-30 20:45 | 50318.5446 | 140.004
Devonshire Building | 2017-05-30 21:00 | 50318.5496 | 20.016
Devonshire Building | 2017-05-30 21:15 | 50318.5546 | 20.016
Devonshire Building | 2017-05-30 21:30 | 50318.5596 | 20.016
Devonshire Building | 2017-05-30 21:45 | 50318.5646 | 20.016
Devonshire Building | 2017-05-30 22:00 | 50318.5696 | 20.016
Devonshire Building | 2017-05-30 22:15 | 50318.5746 | 20.016
Devonshire Building | 2017-05-30 22:30 | 50318.5796 | 20.016
Devonshire Building | 2017-05-30 22:45 | 50318.5846 | 20.016
Devonshire Building | 2017-05-30 23:00 | 50318.5896 | 20.016
Devonshire Building | 2017-05-30 23:15 | 50318.5946 | 20.016
Devonshire Building | 2017-05-30 23:30 | 50318.5996 | 20.016
Devonshire Building | 2017-05-30 23:45 | 50318.6046 | 20.016
Devonshire Building | 2017-05-31 | 50318.6094 | 20.016
Devonshire Building | 2017-05-31 00:15 | 50318.6144 | 20.016
Devonshire Building | 2017-05-31 00:30 | 50318.6194 | 20.016
Devonshire Building | 2017-05-31 00:45 | 50318.6244 | 20.016
Devonshire Building | 2017-05-31 01:00 | 50318.6294 | 20.016
Devonshire Building | 2017-05-31 01:15 | 50318.6394 | 39.996
Devonshire Building | 2017-05-31 01:30 | 50318.6444 | 20.016
Devonshire Building | 2017-05-31 01:45 | 50318.6444 | 0
Devonshire Building | 2017-05-31 02:00 | 50318.6494 | 20.016
Devonshire Building | 2017-05-31 02:15 | 50318.6594 | 39.996
Devonshire Building | 2017-05-31 02:30 | 50318.6594 | 0
Devonshire Building | 2017-05-31 02:45 | 50318.6644 | 20.016
Devonshire Building | 2017-05-31 03:00 | 50318.6694 | 20.016
Devonshire Building | 2017-05-31 03:15 | 50318.6744 | 20.016
Devonshire Building | 2017-05-31 03:30 | 50318.6794 | 20.016
Devonshire Building | 2017-05-31 03:45 | 50318.6844 | 20.016
Devonshire Building | 2017-05-31 04:00 | 50318.6894 | 20.016
Devonshire Building | 2017-05-31 04:15 | 50318.6944 | 20.016
Devonshire Building | 2017-05-31 04:30 | 50318.6994 | 20.016
Devonshire Building | 2017-05-31 04:45 | 50318.7044 | 20.016
Devonshire Building | 2017-05-31 05:00 | 50318.7094 | 20.016
Devonshire Building | 2017-05-31 05:15 | 50318.7144 | 20.016
Devonshire Building | 2017-05-31 05:30 | 50319.2294 | 2059.992
Devonshire Building | 2017-05-31 05:45 | 50319.2344 | 20.016
Devonshire Building | 2017-05-31 06:00 | 50319.2395 | 20.016
Devonshire Building | 2017-05-31 06:15 | 50319.2445 | 20.016
Devonshire Building | 2017-05-31 06:30 | 50319.2545 | 39.996
Devonshire Building | 2017-05-31 06:45 | 50319.2595 | 20.016
Devonshire Building | 2017-05-31 07:00 | 50319.2645 | 20.016
Devonshire Building | 2017-05-31 07:15 | 50319.2745 | 39.996
Devonshire Building | 2017-05-31 07:30 | 50319.2845 | 39.996
Devonshire Building | 2017-05-31 07:45 | 50319.2945 | 39.996
Devonshire Building | 2017-05-31 08:00 | 50319.3295 | 140.004
Devonshire Building | 2017-05-31 08:15 | 50319.3645 | 140.004
Devonshire Building | 2017-05-31 08:30 | 50319.4095 | 180
Devonshire Building | 2017-05-31 08:45 | 50319.4645 | 219.996
Devonshire Building | 2017-05-31 09:00 | 50320.0595 | 2379.996
Devonshire Building | 2017-05-31 09:15 | 50320.1345 | 299.988
Devonshire Building | 2017-05-31 09:30 | 50320.2045 | 280.008
Devonshire Building | 2017-05-31 09:45 | 50320.2795 | 299.988
Devonshire Building | 2017-05-31 10:00 | 50320.3595 | 320.004
Devonshire Building | 2017-05-31 10:15 | 50320.9545 | 2379.996
Devonshire Building | 2017-05-31 10:30 | 50321.0095 | 219.996
Devonshire Building | 2017-05-31 10:45 | 50321.0595 | 200.016
Devonshire Building | 2017-05-31 11:00 | 50321.1095 | 200.016
Devonshire Building | 2017-05-31 11:15 | 50321.1645 | 219.996
Devonshire Building | 2017-05-31 11:30 | 50321.2295 | 259.992
Devonshire Building | 2017-05-31 11:45 | 50321.5645 | 1339.992
Devonshire Building | 2017-05-31 12:00 | 50321.9045 | 1360.008
Devonshire Building | 2017-05-31 12:15 | 50321.9845 | 320.004
Devonshire Building | 2017-05-31 12:30 | 50322.0695 | 339.984
Devonshire Building | 2017-05-31 12:45 | 50322.1495 | 320.004
Devonshire Building | 2017-05-31 13:00 | 50322.2195 | 280.008
Devonshire Building | 2017-05-31 13:15 | 50322.2845 | 259.992
Devonshire Building | 2017-05-31 13:30 | 50322.3495 | 259.992
Devonshire Building | 2017-05-31 13:45 | 50322.9445 | 2379.996
Devonshire Building | 2017-05-31 14:00 | 50323.0045 | 240.012
Devonshire Building | 2017-05-31 14:15 | 50323.0595 | 219.996
Devonshire Building | 2017-05-31 14:30 | 50323.1145 | 219.996
Devonshire Building | 2017-05-31 14:45 | 50323.1845 | 280.008
Devonshire Building | 2017-05-31 15:00 | 50323.2595 | 299.988
Devonshire Building | 2017-05-31 15:15 | 50323.3245 | 259.992
Devonshire Building | 2017-05-31 15:30 | 50323.8944 | 2279.988
Devonshire Building | 2017-05-31 15:45 | 50323.9545 | 240.012
Devonshire Building | 2017-05-31 16:00 | 50324.0195 | 259.992
Devonshire Building | 2017-05-31 16:15 | 50324.0795 | 240.012
Devonshire Building | 2017-05-31 16:30 | 50324.1395 | 240.012
Devonshire Building | 2017-05-31 16:45 | 50324.1945 | 219.996
Devonshire Building | 2017-05-31 17:00 | 50324.2495 | 219.996
Devonshire Building | 2017-05-31 17:15 | 50324.2995 | 200.016
Devonshire Building | 2017-05-31 17:30 | 50324.3495 | 200.016
Devonshire Building | 2017-05-31 17:45 | 50324.4045 | 219.996
Devonshire Building | 2017-05-31 18:00 | 50324.4545 | 200.016
Devonshire Building | 2017-05-31 18:15 | 50324.5045 | 200.016
Devonshire Building | 2017-05-31 18:30 | 50324.5495 | 180
Devonshire Building | 2017-05-31 18:45 | 50324.5845 | 140.004
Devonshire Building | 2017-05-31 19:00 | 50325.1245 | 2160
Devonshire Building | 2017-05-31 19:15 | 50325.1395 | 60.012
Devonshire Building | 2017-05-31 19:30 | 50325.1545 | 60.012
Devonshire Building | 2017-05-31 19:45 | 50325.1745 | 79.992
Devonshire Building | 2017-05-31 20:00 | 50325.1895 | 60.012
Devonshire Building | 2017-05-31 20:15 | 50325.2095 | 79.992
Devonshire Building | 2017-05-31 20:30 | 50325.2295 | 79.992
Devonshire Building | 2017-05-31 20:45 | 50325.2545 | 100.008
Devonshire Building | 2017-05-31 21:00 | 50325.2695 | 60.012
Devonshire Building | 2017-05-31 21:15 | 50325.2795 | 39.996
Devonshire Building | 2017-05-31 21:30 | 50325.2945 | 60.012
Devonshire Building | 2017-05-31 21:45 | 50325.3045 | 39.996
Devonshire Building | 2017-05-31 22:00 | 50325.3195 | 60.012
Devonshire Building | 2017-05-31 22:15 | 50325.3295 | 39.996
Devonshire Building | 2017-05-31 22:30 | 50325.3445 | 60.012
Devonshire Building | 2017-05-31 22:45 | 50325.3545 | 39.996
Devonshire Building | 2017-05-31 23:00 | 50325.3645 | 39.996
Devonshire Building | 2017-05-31 23:15 | 50325.3795 | 60.012
Devonshire Building | 2017-05-31 23:30 | 50325.3895 | 39.996
Devonshire Building | 2017-05-31 23:45 | 50325.3995 | 39.996
Devonshire Building | 2017-06-01 | 50325.4102 | 39.996
Devonshire Building | 2017-06-01 00:15 | 50325.4202 | 39.996
Devonshire Building | 2017-06-01 00:30 | 50325.4302 | 39.996
Devonshire Building | 2017-06-01 00:45 | 50325.4402 | 39.996
Devonshire Building | 2017-06-01 01:00 | 50325.4502 | 39.996
Devonshire Building | 2017-06-01 01:15 | 50325.4602 | 39.996
Devonshire Building | 2017-06-01 01:30 | 50325.4702 | 39.996
Devonshire Building | 2017-06-01 01:45 | 50325.4802 | 39.996
Devonshire Building | 2017-06-01 02:00 | 50325.4902 | 39.996
Devonshire Building | 2017-06-01 02:15 | 50325.5002 | 39.996
Devonshire Building | 2017-06-01 02:30 | 50325.5102 | 39.996
Devonshire Building | 2017-06-01 02:45 | 50325.5201 | 39.996
Devonshire Building | 2017-06-01 03:00 | 50325.5252 | 20.016
Devonshire Building | 2017-06-01 03:15 | 50325.5352 | 39.996
Devonshire Building | 2017-06-01 03:30 | 50325.5452 | 39.996
Devonshire Building | 2017-06-01 03:45 | 50325.5552 | 39.996
Devonshire Building | 2017-06-01 04:00 | 50325.5651 | 39.996
Devonshire Building | 2017-06-01 04:15 | 50325.5702 | 20.016
Devonshire Building | 2017-06-01 04:30 | 50325.5802 | 39.996
Devonshire Building | 2017-06-01 04:45 | 50325.5902 | 39.996
Devonshire Building | 2017-06-01 05:00 | 50325.6001 | 39.996
Devonshire Building | 2017-06-01 05:15 | 50325.6101 | 39.996
Devonshire Building | 2017-06-01 05:30 | 50325.6152 | 20.016
Devonshire Building | 2017-06-01 05:45 | 50325.6402 | 100.008
Devonshire Building | 2017-06-01 06:00 | 50325.6502 | 39.996
Devonshire Building | 2017-06-01 06:15 | 50325.6602 | 39.996
Devonshire Building | 2017-06-01 06:30 | 50325.6702 | 39.996
Devonshire Building | 2017-06-01 06:45 | 50325.6752 | 20.016
Devonshire Building | 2017-06-01 07:00 | 50325.6852 | 39.996
Devonshire Building | 2017-06-01 07:15 | 50325.6952 | 39.996
Devonshire Building | 2017-06-01 07:30 | 50325.7052 | 39.996
Devonshire Building | 2017-06-01 07:45 | 50326.2202 | 2059.992
Devonshire Building | 2017-06-01 08:00 | 50326.2501 | 119.988
Devonshire Building | 2017-06-01 08:15 | 50326.2901 | 159.984
Devonshire Building | 2017-06-01 08:30 | 50326.3201 | 119.988
Devonshire Building | 2017-06-01 08:45 | 50326.3501 | 119.988
Devonshire Building | 2017-06-01 09:00 | 50326.3801 | 119.988
Devonshire Building | 2017-06-01 09:15 | 50326.5951 | 860.004
Devonshire Building | 2017-06-01 09:30 | 50326.9651 | 1479.996
Devonshire Building | 2017-06-01 09:45 | 50327.0101 | 180
Devonshire Building | 2017-06-01 10:00 | 50327.0851 | 299.988
Devonshire Building | 2017-06-01 10:15 | 50327.1751 | 360
Devonshire Building | 2017-06-01 10:30 | 50327.2401 | 259.992
Devonshire Building | 2017-06-01 10:45 | 50327.5501 | 1239.984
Devonshire Building | 2017-06-01 11:00 | 50327.8601 | 1239.984
Devonshire Building | 2017-06-01 11:15 | 50327.9151 | 219.996
Devonshire Building | 2017-06-01 11:30 | 50327.9651 | 200.016
Devonshire Building | 2017-06-01 11:45 | 50328.0151 | 200.016
Devonshire Building | 2017-06-01 12:00 | 50328.0601 | 180
Devonshire Building | 2017-06-01 12:15 | 50328.5151 | 1820.016
Devonshire Building | 2017-06-01 12:30 | 50328.6651 | 600.012
Devonshire Building | 2017-06-01 12:45 | 50328.7001 | 140.004
Devonshire Building | 2017-06-01 13:00 | 50328.7301 | 119.988
Devonshire Building | 2017-06-01 13:15 | 50328.7651 | 140.004
Devonshire Building | 2017-06-01 13:30 | 50328.8051 | 159.984
Devonshire Building | 2017-06-01 13:45 | 50328.8451 | 159.984
Devonshire Building | 2017-06-01 14:00 | 50329.4051 | 2239.992
Devonshire Building | 2017-06-01 14:15 | 50329.4351 | 119.988
Devonshire Building | 2017-06-01 14:30 | 50329.4751 | 159.984
Devonshire Building | 2017-06-01 14:45 | 50329.5051 | 119.988
Devonshire Building | 2017-06-01 15:00 | 50329.5401 | 140.004
Devonshire Building | 2017-06-01 15:15 | 50329.5751 | 140.004
Devonshire Building | 2017-06-01 15:30 | 50329.6101 | 140.004
Devonshire Building | 2017-06-01 15:45 | 50329.6401 | 119.988
Devonshire Building | 2017-06-01 16:00 | 50330.2101 | 2279.988
Devonshire Building | 2017-06-01 16:15 | 50330.2501 | 159.984
Devonshire Building | 2017-06-01 16:30 | 50330.2851 | 140.004
Devonshire Building | 2017-06-01 16:45 | 50330.3201 | 140.004
Devonshire Building | 2017-06-01 17:00 | 50330.3551 | 140.004
Devonshire Building | 2017-06-01 17:15 | 50330.3851 | 119.988
Devonshire Building | 2017-06-01 17:30 | 50330.4151 | 119.988
Devonshire Building | 2017-06-01 17:45 | 50330.4451 | 119.988
Devonshire Building | 2017-06-01 18:00 | 50330.4701 | 100.008
Devonshire Building | 2017-06-01 18:15 | 50330.4951 | 100.008
Devonshire Building | 2017-06-01 18:30 | 50330.5201 | 100.008
Devonshire Building | 2017-06-01 18:45 | 50330.5451 | 100.008
Devonshire Building | 2017-06-01 19:00 | 50330.5651 | 79.992
Devonshire Building | 2017-06-01 19:15 | 50330.5851 | 79.992
Devonshire Building | 2017-06-01 19:30 | 50330.6051 | 79.992
Devonshire Building | 2017-06-01 19:45 | 50330.6251 | 79.992
Devonshire Building | 2017-06-01 20:00 | 50330.6451 | 79.992
Devonshire Building | 2017-06-01 20:15 | 50330.6601 | 60.012
Devonshire Building | 2017-06-01 20:30 | 50330.6751 | 60.012
Devonshire Building | 2017-06-01 20:45 | 50330.7101 | 140.004
Devonshire Building | 2017-06-01 21:00 | 50330.7151 | 20.016
Devonshire Building | 2017-06-01 21:15 | 50330.7251 | 39.996
Devonshire Building | 2017-06-01 21:30 | 50330.7301 | 20.016
Devonshire Building | 2017-06-01 21:45 | 50330.9951 | 1059.984
Devonshire Building | 2017-06-01 22:00 | 50331.2401 | 979.992
Devonshire Building | 2017-06-01 22:15 | 50331.2451 | 20.016
Devonshire Building | 2017-06-01 22:30 | 50331.2501 | 20.016
Devonshire Building | 2017-06-01 22:45 | 50331.2551 | 20.016
Devonshire Building | 2017-06-01 23:00 | 50331.2601 | 20.016
Devonshire Building | 2017-06-01 23:15 | 50331.2651 | 20.016
Devonshire Building | 2017-06-01 23:30 | 50331.2751 | 39.996
Devonshire Building | 2017-06-01 23:45 | 50331.2801 | 20.016
Devonshire Building | 2017-06-02 | 50331.2852 | 20.016
Devonshire Building | 2017-06-02 00:15 | 50331.2902 | 20.016
Devonshire Building | 2017-06-02 00:30 | 50331.2952 | 20.016
Devonshire Building | 2017-06-02 00:45 | 50331.3002 | 20.016
Devonshire Building | 2017-06-02 01:00 | 50331.3052 | 20.016
Devonshire Building | 2017-06-02 01:15 | 50331.3152 | 39.996
Devonshire Building | 2017-06-02 01:30 | 50331.3202 | 20.016
Devonshire Building | 2017-06-02 01:45 | 50331.3302 | 39.996
Devonshire Building | 2017-06-02 02:00 | 50331.3552 | 100.008
Devonshire Building | 2017-06-02 02:15 | 50331.3752 | 79.992
Devonshire Building | 2017-06-02 02:30 | 50331.4002 | 100.008
Devonshire Building | 2017-06-02 02:45 | 50331.4202 | 79.992
Devonshire Building | 2017-06-02 03:00 | 50331.4452 | 100.008
Devonshire Building | 2017-06-02 03:15 | 50331.4652 | 79.992
Devonshire Building | 2017-06-02 03:30 | 50331.4902 | 100.008
Devonshire Building | 2017-06-02 03:45 | 50331.5002 | 39.996
Devonshire Building | 2017-06-02 04:00 | 50331.5052 | 20.016
Devonshire Building | 2017-06-02 04:15 | 50331.5102 | 20.016
Devonshire Building | 2017-06-02 04:30 | 50331.5152 | 20.016
Devonshire Building | 2017-06-02 04:45 | 50331.5202 | 20.016
Devonshire Building | 2017-06-02 05:00 | 50331.5302 | 39.996
Devonshire Building | 2017-06-02 05:15 | 50331.5352 | 20.016
Devonshire Building | 2017-06-02 05:30 | 50331.5402 | 20.016
Devonshire Building | 2017-06-02 05:45 | 50331.5502 | 39.996
Devonshire Building | 2017-06-02 06:00 | 50331.5552 | 20.016
Devonshire Building | 2017-06-02 06:15 | 50331.5602 | 20.016
Devonshire Building | 2017-06-02 06:30 | 50331.5702 | 39.996
Devonshire Building | 2017-06-02 06:45 | 50331.5752 | 20.016
Devonshire Building | 2017-06-02 07:00 | 50331.5852 | 39.996
Devonshire Building | 2017-06-02 07:15 | 50331.6002 | 60.012
Devonshire Building | 2017-06-02 07:30 | 50331.6352 | 140.004
Devonshire Building | 2017-06-02 07:45 | 50331.6702 | 140.004
Devonshire Building | 2017-06-02 08:00 | 50332.1002 | 1720.008
Devonshire Building | 2017-06-02 08:15 | 50332.3452 | 979.992
Devonshire Building | 2017-06-02 08:30 | 50332.4152 | 280.008
Devonshire Building | 2017-06-02 08:45 | 50332.4802 | 259.992
Devonshire Building | 2017-06-02 09:00 | 50332.5352 | 219.996
Devonshire Building | 2017-06-02 09:15 | 50332.5902 | 219.996
Devonshire Building | 2017-06-02 09:30 | 50332.6402 | 200.016
Devonshire Building | 2017-06-02 09:45 | 50332.6952 | 219.996
Devonshire Building | 2017-06-02 10:00 | 50332.7452 | 200.016
Devonshire Building | 2017-06-02 10:15 | 50333.3202 | 2300.004
Devonshire Building | 2017-06-02 10:30 | 50333.3602 | 159.984
Devonshire Building | 2017-06-02 10:45 | 50333.4052 | 180
Devonshire Building | 2017-06-02 11:00 | 50333.4552 | 200.016
Devonshire Building | 2017-06-02 11:15 | 50333.5002 | 180
Devonshire Building | 2017-06-02 11:30 | 50333.5502 | 200.016
Devonshire Building | 2017-06-02 11:45 | 50334.0902 | 2160
Devonshire Building | 2017-06-02 12:00 | 50334.1252 | 140.004
Devonshire Building | 2017-06-02 12:15 | 50334.1502 | 100.008
Devonshire Building | 2017-06-02 12:30 | 50334.1802 | 119.988
Devonshire Building | 2017-06-02 12:45 | 50334.2052 | 100.008
Devonshire Building | 2017-06-02 13:00 | 50334.2402 | 140.004
Devonshire Building | 2017-06-02 13:15 | 50334.2802 | 159.984
Devonshire Building | 2017-06-02 13:30 | 50334.3302 | 200.016
Devonshire Building | 2017-06-02 13:45 | 50334.9002 | 2279.988
Devonshire Building | 2017-06-02 14:00 | 50334.9502 | 200.016
Devonshire Building | 2017-06-02 14:15 | 50335.0052 | 219.996
Devonshire Building | 2017-06-02 14:30 | 50335.0602 | 219.996
Devonshire Building | 2017-06-02 14:45 | 50335.1102 | 200.016
Devonshire Building | 2017-06-02 15:00 | 50335.1652 | 219.996
Devonshire Building | 2017-06-02 15:15 | 50335.2102 | 180
Devonshire Building | 2017-06-02 15:30 | 50335.2552 | 180
Devonshire Building | 2017-06-02 15:45 | 50335.8152 | 2239.992
Devonshire Building | 2017-06-02 16:00 | 50335.8552 | 159.984
Devonshire Building | 2017-06-02 16:15 | 50335.8952 | 159.984
Devonshire Building | 2017-06-02 16:30 | 50335.9402 | 180
Devonshire Building | 2017-06-02 16:45 | 50335.9802 | 159.984
Devonshire Building | 2017-06-02 17:00 | 50336.0152 | 140.004
Devonshire Building | 2017-06-02 17:15 | 50336.0552 | 159.984
Devonshire Building | 2017-06-02 17:30 | 50336.0902 | 140.004
Devonshire Building | 2017-06-02 17:45 | 50336.1252 | 140.004
Devonshire Building | 2017-06-02 18:00 | 50336.1602 | 140.004
Devonshire Building | 2017-06-02 18:15 | 50336.1902 | 119.988
Devonshire Building | 2017-06-02 18:30 | 50336.2152 | 100.008
Devonshire Building | 2017-06-02 18:45 | 50336.2452 | 119.988
Devonshire Building | 2017-06-02 19:00 | 50336.2702 | 100.008
Devonshire Building | 2017-06-02 19:15 | 50336.2952 | 100.008
Devonshire Building | 2017-06-02 19:30 | 50336.3152 | 79.992
Devonshire Building | 2017-06-02 19:45 | 50336.3502 | 140.004
Devonshire Building | 2017-06-02 20:00 | 50336.3852 | 140.004
Devonshire Building | 2017-06-02 20:15 | 50336.4152 | 119.988
Devonshire Building | 2017-06-02 20:30 | 50336.4452 | 119.988
Devonshire Building | 2017-06-02 20:45 | 50336.5002 | 219.996
Devonshire Building | 2017-06-02 21:00 | 50336.5202 | 79.992
Devonshire Building | 2017-06-02 21:15 | 50336.5452 | 100.008
Devonshire Building | 2017-06-02 21:30 | 50336.5652 | 79.992
Devonshire Building | 2017-06-02 21:45 | 50336.5902 | 100.008
Devonshire Building | 2017-06-02 22:00 | 50336.5952 | 20.016
Devonshire Building | 2017-06-02 22:15 | 50336.6002 | 20.016
Devonshire Building | 2017-06-02 22:30 | 50336.6102 | 39.996
Devonshire Building | 2017-06-02 22:45 | 50336.6152 | 20.016
Devonshire Building | 2017-06-02 23:00 | 50336.6202 | 20.016
Devonshire Building | 2017-06-02 23:15 | 50336.6302 | 39.996
Devonshire Building | 2017-06-02 23:30 | 50336.6352 | 20.016
Devonshire Building | 2017-06-02 23:45 | 50336.6402 | 20.016
Devonshire Building | 2017-06-03 | 50336.6484 | 39.996
Devonshire Building | 2017-06-03 00:15 | 50336.6534 | 20.016
Devonshire Building | 2017-06-03 00:30 | 50336.6584 | 20.016
Devonshire Building | 2017-06-03 00:45 | 50336.6635 | 20.016
Devonshire Building | 2017-06-03 01:00 | 50336.6735 | 39.996
Devonshire Building | 2017-06-03 01:15 | 50336.6785 | 20.016
Devonshire Building | 2017-06-03 01:30 | 50336.6835 | 20.016
Devonshire Building | 2017-06-03 01:45 | 50336.6885 | 20.016
Devonshire Building | 2017-06-03 02:00 | 50336.6935 | 20.016
Devonshire Building | 2017-06-03 02:15 | 50336.6985 | 20.016
Devonshire Building | 2017-06-03 02:30 | 50336.7085 | 39.996
Devonshire Building | 2017-06-03 02:45 | 50336.7135 | 20.016
Devonshire Building | 2017-06-03 03:00 | 50336.7185 | 20.016
Devonshire Building | 2017-06-03 03:15 | 50336.7235 | 20.016
Devonshire Building | 2017-06-03 03:30 | 50336.7285 | 20.016
Devonshire Building | 2017-06-03 03:45 | 50336.7335 | 20.016
Devonshire Building | 2017-06-03 04:00 | 50337.2435 | 2040.012
Devonshire Building | 2017-06-03 04:15 | 50337.2485 | 20.016
Devonshire Building | 2017-06-03 04:30 | 50337.2535 | 20.016
Devonshire Building | 2017-06-03 04:45 | 50337.2585 | 20.016
Devonshire Building | 2017-06-03 05:00 | 50337.2635 | 20.016
Devonshire Building | 2017-06-03 05:15 | 50337.2685 | 20.016
Devonshire Building | 2017-06-03 05:30 | 50337.2735 | 20.016
Devonshire Building | 2017-06-03 05:45 | 50337.2785 | 20.016
Devonshire Building | 2017-06-03 06:00 | 50337.2835 | 20.016
Devonshire Building | 2017-06-03 06:15 | 50337.2885 | 20.016
Devonshire Building | 2017-06-03 06:30 | 50337.2935 | 20.016
Devonshire Building | 2017-06-03 06:45 | 50337.2985 | 20.016
Devonshire Building | 2017-06-03 07:00 | 50337.3035 | 20.016
Devonshire Building | 2017-06-03 07:15 | 50337.3135 | 39.996
Devonshire Building | 2017-06-03 07:30 | 50337.3185 | 20.016
Devonshire Building | 2017-06-03 07:45 | 50337.3235 | 20.016
Devonshire Building | 2017-06-03 08:00 | 50337.3286 | 20.016
Devonshire Building | 2017-06-03 08:15 | 50337.3386 | 39.996
Devonshire Building | 2017-06-03 08:30 | 50337.3436 | 20.016
Devonshire Building | 2017-06-03 08:45 | 50337.3486 | 20.016
Devonshire Building | 2017-06-03 09:00 | 50337.3586 | 39.996
Devonshire Building | 2017-06-03 09:15 | 50337.3636 | 20.016
Devonshire Building | 2017-06-03 09:30 | 50337.3686 | 20.016
Devonshire Building | 2017-06-03 09:45 | 50337.3786 | 39.996
Devonshire Building | 2017-06-03 10:00 | 50337.3836 | 20.016
Devonshire Building | 2017-06-03 10:15 | 50337.3886 | 20.016
Devonshire Building | 2017-06-03 10:30 | 50337.3986 | 39.996
Devonshire Building | 2017-06-03 10:45 | 50337.4086 | 39.996
Devonshire Building | 2017-06-03 11:00 | 50337.4136 | 20.016
Devonshire Building | 2017-06-03 11:15 | 50337.4236 | 39.996
Devonshire Building | 2017-06-03 11:30 | 50337.4286 | 20.016
Devonshire Building | 2017-06-03 11:45 | 50337.4336 | 20.016
Devonshire Building | 2017-06-03 12:00 | 50337.4386 | 20.016
Devonshire Building | 2017-06-03 12:15 | 50337.4436 | 20.016
Devonshire Building | 2017-06-03 12:30 | 50337.4486 | 20.016
Devonshire Building | 2017-06-03 12:45 | 50337.4586 | 39.996
Devonshire Building | 2017-06-03 13:00 | 50337.4636 | 20.016
Devonshire Building | 2017-06-03 13:15 | 50337.4686 | 20.016
Devonshire Building | 2017-06-03 13:30 | 50337.4736 | 20.016
Devonshire Building | 2017-06-03 13:45 | 50337.4936 | 79.992
Devonshire Building | 2017-06-03 14:00 | 50337.5186 | 100.008
Devonshire Building | 2017-06-03 14:15 | 50337.5386 | 79.992
Devonshire Building | 2017-06-03 14:30 | 50337.5586 | 79.992
Devonshire Building | 2017-06-03 14:45 | 50337.5836 | 100.008
Devonshire Building | 2017-06-03 15:00 | 50337.6036 | 79.992
Devonshire Building | 2017-06-03 15:15 | 50337.6286 | 100.008
Devonshire Building | 2017-06-03 15:30 | 50337.6486 | 79.992
Devonshire Building | 2017-06-03 15:45 | 50337.6586 | 39.996
Devonshire Building | 2017-06-03 16:00 | 50337.6636 | 20.016
Devonshire Building | 2017-06-03 16:15 | 50337.6686 | 20.016
Devonshire Building | 2017-06-03 16:30 | 50337.6736 | 20.016
Devonshire Building | 2017-06-03 16:45 | 50337.6786 | 20.016
Devonshire Building | 2017-06-03 17:00 | 50337.6836 | 20.016
Devonshire Building | 2017-06-03 17:15 | 50337.6936 | 39.996
Devonshire Building | 2017-06-03 17:30 | 50337.6986 | 20.016
Devonshire Building | 2017-06-03 17:45 | 50337.7036 | 20.016
Devonshire Building | 2017-06-03 18:00 | 50337.7086 | 20.016
Devonshire Building | 2017-06-03 18:15 | 50337.7136 | 20.016
Devonshire Building | 2017-06-03 18:30 | 50337.7186 | 20.016
Devonshire Building | 2017-06-03 18:45 | 50337.7236 | 20.016
Devonshire Building | 2017-06-03 19:00 | 50337.7286 | 20.016
Devonshire Building | 2017-06-03 19:15 | 50337.7386 | 39.996
Devonshire Building | 2017-06-03 19:30 | 50337.7436 | 20.016
Devonshire Building | 2017-06-03 19:45 | 50337.7487 | 20.016
Devonshire Building | 2017-06-03 20:00 | 50337.7537 | 20.016
Devonshire Building | 2017-06-03 20:15 | 50337.7587 | 20.016
Devonshire Building | 2017-06-03 20:30 | 50337.7637 | 20.016
Devonshire Building | 2017-06-03 20:45 | 50338.2737 | 2040.012
Devonshire Building | 2017-06-03 21:00 | 50338.2837 | 39.996
Devonshire Building | 2017-06-03 21:15 | 50338.2937 | 39.996
Devonshire Building | 2017-06-03 21:30 | 50338.2987 | 20.016
Devonshire Building | 2017-06-03 21:45 | 50338.3087 | 39.996
Devonshire Building | 2017-06-03 22:00 | 50338.3137 | 20.016
Devonshire Building | 2017-06-03 22:15 | 50338.3237 | 39.996
Devonshire Building | 2017-06-03 22:30 | 50338.3337 | 39.996
Devonshire Building | 2017-06-03 22:45 | 50338.3437 | 39.996
Devonshire Building | 2017-06-03 23:00 | 50338.3537 | 39.996
Devonshire Building | 2017-06-03 23:15 | 50338.3637 | 39.996
Devonshire Building | 2017-06-03 23:30 | 50338.3787 | 60.012
Devonshire Building | 2017-06-03 23:45 | 50338.3937 | 60.012
Devonshire Building | 2017-06-04 | 50338.4062 | 39.996
Devonshire Building | 2017-06-04 00:15 | 50338.4213 | 60.012
Devonshire Building | 2017-06-04 00:30 | 50338.4313 | 39.996
Devonshire Building | 2017-06-04 00:45 | 50338.4463 | 60.012
Devonshire Building | 2017-06-04 01:00 | 50338.4563 | 39.996
Devonshire Building | 2017-06-04 01:15 | 50338.4663 | 39.996
Devonshire Building | 2017-06-04 01:30 | 50338.4813 | 60.012
Devonshire Building | 2017-06-04 01:45 | 50338.4913 | 39.996
Devonshire Building | 2017-06-04 02:00 | 50338.5013 | 39.996
Devonshire Building | 2017-06-04 02:15 | 50338.5113 | 39.996
Devonshire Building | 2017-06-04 02:30 | 50338.5213 | 39.996
Devonshire Building | 2017-06-04 02:45 | 50338.5363 | 60.012
Devonshire Building | 2017-06-04 03:00 | 50338.5463 | 39.996
Devonshire Building | 2017-06-04 03:15 | 50338.5563 | 39.996
Devonshire Building | 2017-06-04 03:30 | 50338.5613 | 20.016
Devonshire Building | 2017-06-04 03:45 | 50338.5713 | 39.996
Devonshire Building | 2017-06-04 04:00 | 50338.5813 | 39.996
Devonshire Building | 2017-06-04 04:15 | 50338.5913 | 39.996
Devonshire Building | 2017-06-04 04:30 | 50338.6013 | 39.996
Devonshire Building | 2017-06-04 04:45 | 50338.6113 | 39.996
Devonshire Building | 2017-06-04 05:00 | 50338.6163 | 20.016
Devonshire Building | 2017-06-04 05:15 | 50338.6263 | 39.996
Devonshire Building | 2017-06-04 05:30 | 50338.6363 | 39.996
Devonshire Building | 2017-06-04 05:45 | 50338.6413 | 20.016
Devonshire Building | 2017-06-04 06:00 | 50338.6513 | 39.996
Devonshire Building | 2017-06-04 06:15 | 50338.6613 | 39.996
Devonshire Building | 2017-06-04 06:30 | 50338.6663 | 20.016
Devonshire Building | 2017-06-04 06:45 | 50338.6763 | 39.996
Devonshire Building | 2017-06-04 07:00 | 50338.6813 | 20.016
Devonshire Building | 2017-06-04 07:15 | 50338.6913 | 39.996
Devonshire Building | 2017-06-04 07:30 | 50338.7013 | 39.996
Devonshire Building | 2017-06-04 07:45 | 50338.7063 | 20.016
Devonshire Building | 2017-06-04 08:00 | 50338.7163 | 39.996
Devonshire Building | 2017-06-04 08:15 | 50338.7213 | 20.016
Devonshire Building | 2017-06-04 08:30 | 50338.7313 | 39.996
Devonshire Building | 2017-06-04 08:45 | 50338.7413 | 39.996
Devonshire Building | 2017-06-04 09:00 | 50338.7463 | 20.016
Devonshire Building | 2017-06-04 09:15 | 50338.7563 | 39.996
Devonshire Building | 2017-06-04 09:30 | 50338.7613 | 20.016
Devonshire Building | 2017-06-04 09:45 | 50338.7713 | 39.996
Devonshire Building | 2017-06-04 10:00 | 50338.7763 | 20.016
Devonshire Building | 2017-06-04 10:15 | 50338.7863 | 39.996
Devonshire Building | 2017-06-04 10:30 | 50338.7913 | 20.016
Devonshire Building | 2017-06-04 10:45 | 50338.7963 | 20.016
Devonshire Building | 2017-06-04 11:00 | 50338.8063 | 39.996
Devonshire Building | 2017-06-04 11:15 | 50338.8113 | 20.016
Devonshire Building | 2017-06-04 11:30 | 50338.8213 | 39.996
Devonshire Building | 2017-06-04 11:45 | 50338.8263 | 20.016
Devonshire Building | 2017-06-04 12:00 | 50338.8363 | 39.996
Devonshire Building | 2017-06-04 12:15 | 50338.8413 | 20.016
Devonshire Building | 2017-06-04 12:30 | 50339.3313 | 1959.984
Devonshire Building | 2017-06-04 12:45 | 50339.3563 | 100.008
Devonshire Building | 2017-06-04 13:00 | 50339.3613 | 20.016
Devonshire Building | 2017-06-04 13:15 | 50339.3713 | 39.996
Devonshire Building | 2017-06-04 13:30 | 50339.3763 | 20.016
Devonshire Building | 2017-06-04 13:45 | 50339.3913 | 60.012
Devonshire Building | 2017-06-04 14:00 | 50339.4113 | 79.992
Devonshire Building | 2017-06-04 14:15 | 50339.4363 | 100.008
Devonshire Building | 2017-06-04 14:30 | 50339.4563 | 79.992
Devonshire Building | 2017-06-04 14:45 | 50339.4813 | 100.008
Devonshire Building | 2017-06-04 15:00 | 50339.5013 | 79.992
Devonshire Building | 2017-06-04 15:15 | 50339.5263 | 100.008
Devonshire Building | 2017-06-04 15:30 | 50339.5463 | 79.992
Devonshire Building | 2017-06-04 15:45 | 50339.5613 | 60.012
Devonshire Building | 2017-06-04 16:00 | 50339.5713 | 39.996
Devonshire Building | 2017-06-04 16:15 | 50339.5763 | 20.016
Devonshire Building | 2017-06-04 16:30 | 50339.5863 | 39.996
Devonshire Building | 2017-06-04 16:45 | 50339.5963 | 39.996
Devonshire Building | 2017-06-04 17:00 | 50339.6013 | 20.016
Devonshire Building | 2017-06-04 17:15 | 50339.6113 | 39.996
Devonshire Building | 2017-06-04 17:30 | 50339.6163 | 20.016
Devonshire Building | 2017-06-04 17:45 | 50339.6263 | 39.996
Devonshire Building | 2017-06-04 18:00 | 50339.6313 | 20.016
Devonshire Building | 2017-06-04 18:15 | 50339.6413 | 39.996
Devonshire Building | 2017-06-04 18:30 | 50339.6463 | 20.016
Devonshire Building | 2017-06-04 18:45 | 50339.6513 | 20.016
Devonshire Building | 2017-06-04 19:00 | 50339.6613 | 39.996
Devonshire Building | 2017-06-04 19:15 | 50339.6663 | 20.016
Devonshire Building | 2017-06-04 19:30 | 50339.6763 | 39.996
Devonshire Building | 2017-06-04 19:45 | 50339.6813 | 20.016
Devonshire Building | 2017-06-04 20:00 | 50339.6863 | 20.016
Devonshire Building | 2017-06-04 20:15 | 50339.6963 | 39.996
Devonshire Building | 2017-06-04 20:30 | 50339.7013 | 20.016
Devonshire Building | 2017-06-04 20:45 | 50339.7263 | 100.008
Devonshire Building | 2017-06-04 21:00 | 50339.7313 | 20.016
Devonshire Building | 2017-06-04 21:15 | 50339.7413 | 39.996
Devonshire Building | 2017-06-04 21:30 | 50339.7463 | 20.016
Devonshire Building | 2017-06-04 21:45 | 50339.7513 | 20.016
Devonshire Building | 2017-06-04 22:00 | 50339.7563 | 20.016
Devonshire Building | 2017-06-04 22:15 | 50339.7663 | 39.996
Devonshire Building | 2017-06-04 22:30 | 50339.7714 | 20.016
Devonshire Building | 2017-06-04 22:45 | 50339.7764 | 20.016
Devonshire Building | 2017-06-04 23:00 | 50339.7814 | 20.016
Devonshire Building | 2017-06-04 23:15 | 50339.7914 | 39.996
Devonshire Building | 2017-06-04 23:30 | 50339.7964 | 20.016
Devonshire Building | 2017-06-04 23:45 | 50339.8014 | 20.016
Devonshire Building | 2017-06-05 | 50339.8047 | 20.016
Devonshire Building | 2017-06-05 00:15 | 50339.8147 | 39.996
Devonshire Building | 2017-06-05 00:30 | 50339.8197 | 20.016
Devonshire Building | 2017-06-05 00:45 | 50339.8247 | 20.016
Devonshire Building | 2017-06-05 01:00 | 50339.8297 | 20.016
Devonshire Building | 2017-06-05 01:15 | 50339.8347 | 20.016
Devonshire Building | 2017-06-05 01:30 | 50339.8397 | 20.016
Devonshire Building | 2017-06-05 01:45 | 50339.8497 | 39.996
Devonshire Building | 2017-06-05 02:00 | 50339.8547 | 20.016
Devonshire Building | 2017-06-05 02:15 | 50339.8597 | 20.016
Devonshire Building | 2017-06-05 02:30 | 50339.8647 | 20.016
Devonshire Building | 2017-06-05 02:45 | 50339.8697 | 20.016
Devonshire Building | 2017-06-05 03:00 | 50339.8797 | 39.996
Devonshire Building | 2017-06-05 03:15 | 50339.8847 | 20.016
Devonshire Building | 2017-06-05 03:30 | 50339.8897 | 20.016
Devonshire Building | 2017-06-05 03:45 | 50339.8947 | 20.016
Devonshire Building | 2017-06-05 04:00 | 50339.8997 | 20.016
Devonshire Building | 2017-06-05 04:15 | 50339.9047 | 20.016
Devonshire Building | 2017-06-05 04:30 | 50339.9097 | 20.016
Devonshire Building | 2017-06-05 04:45 | 50339.9148 | 20.016
Devonshire Building | 2017-06-05 05:00 | 50339.9247 | 39.996
Devonshire Building | 2017-06-05 05:15 | 50339.9298 | 20.016
Devonshire Building | 2017-06-05 05:30 | 50339.9348 | 20.016
Devonshire Building | 2017-06-05 05:45 | 50339.9448 | 39.996
Devonshire Building | 2017-06-05 06:00 | 50339.9498 | 20.016
Devonshire Building | 2017-06-05 06:15 | 50339.9548 | 20.016
Devonshire Building | 2017-06-05 06:30 | 50339.9698 | 60.012
Devonshire Building | 2017-06-05 06:45 | 50340.4998 | 2120.004
Devonshire Building | 2017-06-05 07:00 | 50340.5148 | 60.012
Devonshire Building | 2017-06-05 07:15 | 50340.5498 | 140.004
Devonshire Building | 2017-06-05 07:30 | 50340.5898 | 159.984
Devonshire Building | 2017-06-05 07:45 | 50340.6348 | 180
Devonshire Building | 2017-06-05 08:00 | 50340.6998 | 259.992
Devonshire Building | 2017-06-05 08:15 | 50340.7498 | 200.016
Devonshire Building | 2017-06-05 08:30 | 50340.7898 | 159.984
Devonshire Building | 2017-06-05 08:45 | 50340.8348 | 180
Devonshire Building | 2017-06-05 09:00 | 50340.8748 | 159.984
Devonshire Building | 2017-06-05 09:15 | 50341.4348 | 2239.992
Devonshire Building | 2017-06-05 09:30 | 50341.4748 | 159.984
Devonshire Building | 2017-06-05 09:45 | 50341.5248 | 200.016
Devonshire Building | 2017-06-05 10:00 | 50341.5848 | 240.012
Devonshire Building | 2017-06-05 10:15 | 50342.1998 | 2459.988
Devonshire Building | 2017-06-05 10:30 | 50342.3148 | 460.008
Devonshire Building | 2017-06-05 10:45 | 50342.4098 | 380.016
Devonshire Building | 2017-06-05 11:00 | 50342.4948 | 339.984
Devonshire Building | 2017-06-05 11:15 | 50342.5748 | 320.004
Devonshire Building | 2017-06-05 11:30 | 50343.1648 | 2360.016
Devonshire Building | 2017-06-05 11:45 | 50343.2398 | 299.988
Devonshire Building | 2017-06-05 12:00 | 50343.3148 | 299.988
Devonshire Building | 2017-06-05 12:15 | 50343.3998 | 339.984
Devonshire Building | 2017-06-05 12:30 | 50343.5248 | 500.004
Devonshire Building | 2017-06-05 12:45 | 50343.6548 | 519.984
Devonshire Building | 2017-06-05 13:00 | 50344.0148 | 1440
Devonshire Building | 2017-06-05 13:15 | 50344.4048 | 1559.988
Devonshire Building | 2017-06-05 13:30 | 50344.5247 | 479.988
Devonshire Building | 2017-06-05 13:45 | 50344.6597 | 540
Devonshire Building | 2017-06-05 14:00 | 50344.7998 | 560.016
Devonshire Building | 2017-06-05 14:15 | 50344.9297 | 519.984
Devonshire Building | 2017-06-05 14:30 | 50345.0348 | 420.012
Devonshire Building | 2017-06-05 14:45 | 50345.6497 | 2459.988
Devonshire Building | 2017-06-05 15:00 | 50345.7247 | 299.988
Devonshire Building | 2017-06-05 15:15 | 50345.7947 | 280.008
Devonshire Building | 2017-06-05 15:30 | 50345.8597 | 259.992
Devonshire Building | 2017-06-05 15:45 | 50345.9197 | 240.012
Devonshire Building | 2017-06-05 16:00 | 50345.9647 | 180
Devonshire Building | 2017-06-05 16:15 | 50346.3048 | 1360.008
Devonshire Building | 2017-06-05 16:30 | 50346.5198 | 860.004
Devonshire Building | 2017-06-05 16:45 | 50346.5348 | 60.012
Devonshire Building | 2017-06-05 17:00 | 50346.5548 | 79.992
Devonshire Building | 2017-06-05 17:15 | 50346.5648 | 39.996
Devonshire Building | 2017-06-05 17:30 | 50346.5798 | 60.012
Devonshire Building | 2017-06-05 17:45 | 50346.5898 | 39.996
Devonshire Building | 2017-06-05 18:00 | 50346.6048 | 60.012
Devonshire Building | 2017-06-05 18:15 | 50346.6198 | 60.012
Devonshire Building | 2017-06-05 18:30 | 50346.6348 | 60.012
Devonshire Building | 2017-06-05 18:45 | 50346.6448 | 39.996
Devonshire Building | 2017-06-05 19:00 | 50346.6598 | 60.012
Devonshire Building | 2017-06-05 19:15 | 50346.6698 | 39.996
Devonshire Building | 2017-06-05 19:30 | 50346.6848 | 60.012
Devonshire Building | 2017-06-05 19:45 | 50346.6998 | 60.012
Devonshire Building | 2017-06-05 20:00 | 50346.7098 | 39.996
Devonshire Building | 2017-06-05 20:15 | 50346.7198 | 39.996
Devonshire Building | 2017-06-05 20:30 | 50346.7348 | 60.012
Devonshire Building | 2017-06-05 20:45 | 50346.7698 | 140.004
Devonshire Building | 2017-06-05 21:00 | 50346.7748 | 20.016
Devonshire Building | 2017-06-05 21:15 | 50346.7798 | 20.016
Devonshire Building | 2017-06-05 21:30 | 50346.7898 | 39.996
Devonshire Building | 2017-06-05 21:45 | 50346.7948 | 20.016
Devonshire Building | 2017-06-05 22:00 | 50346.8048 | 39.996
Devonshire Building | 2017-06-05 22:15 | 50346.8098 | 20.016
Devonshire Building | 2017-06-05 22:30 | 50346.8198 | 39.996
Devonshire Building | 2017-06-05 22:45 | 50346.8248 | 20.016
Devonshire Building | 2017-06-05 23:00 | 50346.8348 | 39.996
Devonshire Building | 2017-06-05 23:15 | 50346.8398 | 20.016
Devonshire Building | 2017-06-05 23:30 | 50346.8448 | 20.016
Devonshire Building | 2017-06-05 23:45 | 50346.8548 | 39.996
Devonshire Building | 2017-06-06 | 50346.8594 | 20.016
Devonshire Building | 2017-06-06 00:15 | 50346.8644 | 20.016
Devonshire Building | 2017-06-06 00:30 | 50346.8694 | 20.016
Devonshire Building | 2017-06-06 00:45 | 50346.8794 | 39.996
Devonshire Building | 2017-06-06 01:00 | 50346.8844 | 20.016
Devonshire Building | 2017-06-06 01:15 | 50346.8894 | 20.016
Devonshire Building | 2017-06-06 01:30 | 50346.8944 | 20.016
Devonshire Building | 2017-06-06 01:45 | 50346.9044 | 39.996
Devonshire Building | 2017-06-06 02:00 | 50346.9094 | 20.016
Devonshire Building | 2017-06-06 02:15 | 50346.9144 | 20.016
Devonshire Building | 2017-06-06 02:30 | 50346.9194 | 20.016
Devonshire Building | 2017-06-06 02:45 | 50346.9244 | 20.016
Devonshire Building | 2017-06-06 03:00 | 50346.9344 | 39.996
Devonshire Building | 2017-06-06 03:15 | 50346.9394 | 20.016
Devonshire Building | 2017-06-06 03:30 | 50346.9444 | 20.016
Devonshire Building | 2017-06-06 03:45 | 50346.9494 | 20.016
Devonshire Building | 2017-06-06 04:00 | 50346.9544 | 20.016
Devonshire Building | 2017-06-06 04:15 | 50346.9594 | 20.016
Devonshire Building | 2017-06-06 04:30 | 50346.9694 | 39.996
Devonshire Building | 2017-06-06 04:45 | 50347.4794 | 2040.012
Devonshire Building | 2017-06-06 05:00 | 50347.4844 | 20.016
Devonshire Building | 2017-06-06 05:15 | 50347.4894 | 20.016
Devonshire Building | 2017-06-06 05:30 | 50347.4994 | 39.996
Devonshire Building | 2017-06-06 05:45 | 50347.5044 | 20.016
Devonshire Building | 2017-06-06 06:00 | 50347.5094 | 20.016
Devonshire Building | 2017-06-06 06:15 | 50347.5145 | 20.016
Devonshire Building | 2017-06-06 06:30 | 50347.5245 | 39.996
Devonshire Building | 2017-06-06 06:45 | 50347.5345 | 39.996
Devonshire Building | 2017-06-06 07:00 | 50347.5445 | 39.996
Devonshire Building | 2017-06-06 07:15 | 50347.5595 | 60.012
Devonshire Building | 2017-06-06 07:30 | 50347.5845 | 100.008
Devonshire Building | 2017-06-06 07:45 | 50347.5995 | 60.012
Devonshire Building | 2017-06-06 08:00 | 50347.6245 | 100.008
Devonshire Building | 2017-06-06 08:15 | 50348.1745 | 2199.996
Devonshire Building | 2017-06-06 08:30 | 50348.2045 | 119.988
Devonshire Building | 2017-06-06 08:45 | 50348.2395 | 140.004
Devonshire Building | 2017-06-06 09:00 | 50348.2945 | 219.996
Devonshire Building | 2017-06-06 09:15 | 50348.3645 | 280.008
Devonshire Building | 2017-06-06 09:30 | 50348.9595 | 2379.996
Devonshire Building | 2017-06-06 09:45 | 50349.0395 | 320.004
Devonshire Building | 2017-06-06 10:00 | 50349.1145 | 299.988
Devonshire Building | 2017-06-06 10:15 | 50349.1945 | 320.004
Devonshire Building | 2017-06-06 10:30 | 50349.2795 | 339.984
Devonshire Building | 2017-06-06 10:45 | 50349.3695 | 360
Devonshire Building | 2017-06-06 11:00 | 50349.9995 | 2520
Devonshire Building | 2017-06-06 11:15 | 50350.0795 | 320.004
Devonshire Building | 2017-06-06 11:30 | 50350.1545 | 299.988
Devonshire Building | 2017-06-06 11:45 | 50350.2445 | 360
Devonshire Building | 2017-06-06 12:00 | 50350.3245 | 320.004
Devonshire Building | 2017-06-06 12:15 | 50350.4045 | 320.004
Devonshire Building | 2017-06-06 12:30 | 50351.0294 | 2499.984
Devonshire Building | 2017-06-06 12:45 | 50351.1095 | 320.004
Devonshire Building | 2017-06-06 13:00 | 50351.1844 | 299.988
Devonshire Building | 2017-06-06 13:15 | 50351.2394 | 219.996
Devonshire Building | 2017-06-06 13:30 | 50351.2944 | 219.996
Devonshire Building | 2017-06-06 13:45 | 50351.3444 | 200.016
Devonshire Building | 2017-06-06 14:00 | 50351.9594 | 2459.988
Devonshire Building | 2017-06-06 14:15 | 50351.9994 | 159.984
Devonshire Building | 2017-06-06 14:30 | 50352.0744 | 299.988
Devonshire Building | 2017-06-06 14:45 | 50352.2394 | 659.988
Devonshire Building | 2017-06-06 15:00 | 50352.4094 | 680.004
Devonshire Building | 2017-06-06 15:15 | 50352.5394 | 519.984
Devonshire Building | 2017-06-06 15:30 | 50353.0944 | 2220.012
Devonshire Building | 2017-06-06 15:45 | 50353.2394 | 579.996
Devonshire Building | 2017-06-06 16:00 | 50353.3194 | 320.004
Devonshire Building | 2017-06-06 16:15 | 50353.3944 | 299.988
Devonshire Building | 2017-06-06 16:30 | 50353.4544 | 240.012
Devonshire Building | 2017-06-06 16:45 | 50353.5044 | 200.016
Devonshire Building | 2017-06-06 17:00 | 50353.5444 | 159.984
Devonshire Building | 2017-06-06 17:15 | 50354.0894 | 2180.016
Devonshire Building | 2017-06-06 17:30 | 50354.0994 | 39.996
Devonshire Building | 2017-06-06 17:45 | 50354.1194 | 79.992
Devonshire Building | 2017-06-06 18:00 | 50354.1344 | 60.012
Devonshire Building | 2017-06-06 18:15 | 50354.1444 | 39.996
Devonshire Building | 2017-06-06 18:30 | 50354.1594 | 60.012
Devonshire Building | 2017-06-06 18:45 | 50354.1694 | 39.996
Devonshire Building | 2017-06-06 19:00 | 50354.1844 | 60.012
Devonshire Building | 2017-06-06 19:15 | 50354.1994 | 60.012
Devonshire Building | 2017-06-06 19:30 | 50354.2094 | 39.996
Devonshire Building | 2017-06-06 19:45 | 50354.2244 | 60.012
Devonshire Building | 2017-06-06 20:00 | 50354.2395 | 60.012
Devonshire Building | 2017-06-06 20:15 | 50354.2545 | 60.012
Devonshire Building | 2017-06-06 20:30 | 50354.2645 | 39.996
Devonshire Building | 2017-06-06 20:45 | 50354.2845 | 79.992
Devonshire Building | 2017-06-06 21:00 | 50354.2945 | 39.996
Devonshire Building | 2017-06-06 21:15 | 50354.3095 | 60.012
Devonshire Building | 2017-06-06 21:30 | 50354.3195 | 39.996
Devonshire Building | 2017-06-06 21:45 | 50354.3295 | 39.996
Devonshire Building | 2017-06-06 22:00 | 50354.3395 | 39.996
Devonshire Building | 2017-06-06 22:15 | 50354.3545 | 60.012
Devonshire Building | 2017-06-06 22:30 | 50354.3645 | 39.996
Devonshire Building | 2017-06-06 22:45 | 50354.3745 | 39.996
Devonshire Building | 2017-06-06 23:00 | 50354.3895 | 60.012
Devonshire Building | 2017-06-06 23:15 | 50354.3995 | 39.996
Devonshire Building | 2017-06-06 23:30 | 50354.4095 | 39.996
Devonshire Building | 2017-06-06 23:45 | 50354.4195 | 39.996
Devonshire Building | 2017-06-07 | 50354.4297 | 39.996
Devonshire Building | 2017-06-07 00:15 | 50354.4397 | 39.996
Devonshire Building | 2017-06-07 00:30 | 50354.4497 | 39.996
Devonshire Building | 2017-06-07 00:45 | 50354.4597 | 39.996
Devonshire Building | 2017-06-07 01:00 | 50354.4697 | 39.996
Devonshire Building | 2017-06-07 01:15 | 50354.4797 | 39.996
Devonshire Building | 2017-06-07 01:30 | 50354.4897 | 39.996
Devonshire Building | 2017-06-07 01:45 | 50354.5047 | 60.012
Devonshire Building | 2017-06-07 02:00 | 50354.5297 | 100.008
Devonshire Building | 2017-06-07 02:15 | 50354.5547 | 100.008
Devonshire Building | 2017-06-07 02:30 | 50354.5797 | 100.008
Devonshire Building | 2017-06-07 02:45 | 50354.6047 | 100.008
Devonshire Building | 2017-06-07 03:00 | 50354.6347 | 119.988
Devonshire Building | 2017-06-07 03:15 | 50354.6597 | 100.008
Devonshire Building | 2017-06-07 03:30 | 50354.6847 | 100.008
Devonshire Building | 2017-06-07 03:45 | 50354.6997 | 60.012
Devonshire Building | 2017-06-07 04:00 | 50354.7097 | 39.996
Devonshire Building | 2017-06-07 04:15 | 50354.7197 | 39.996
Devonshire Building | 2017-06-07 04:30 | 50354.7297 | 39.996
Devonshire Building | 2017-06-07 04:45 | 50354.7397 | 39.996
Devonshire Building | 2017-06-07 05:00 | 50354.7497 | 39.996
Devonshire Building | 2017-06-07 05:15 | 50354.7597 | 39.996
Devonshire Building | 2017-06-07 05:30 | 50354.7697 | 39.996
Devonshire Building | 2017-06-07 05:45 | 50354.7797 | 39.996
Devonshire Building | 2017-06-07 06:00 | 50354.7897 | 39.996
Devonshire Building | 2017-06-07 06:15 | 50354.7997 | 39.996
Devonshire Building | 2017-06-07 06:30 | 50354.8097 | 39.996
Devonshire Building | 2017-06-07 06:45 | 50355.2847 | 1900.008
Devonshire Building | 2017-06-07 07:00 | 50355.3497 | 259.992
Devonshire Building | 2017-06-07 07:15 | 50355.3647 | 60.012
Devonshire Building | 2017-06-07 07:30 | 50355.3697 | 20.016
Devonshire Building | 2017-06-07 07:45 | 50355.3847 | 60.012
Devonshire Building | 2017-06-07 08:00 | 50355.4097 | 100.008
Devonshire Building | 2017-06-07 08:15 | 50355.4297 | 79.992
Devonshire Building | 2017-06-07 08:30 | 50355.4497 | 79.992
Devonshire Building | 2017-06-07 08:45 | 50355.4797 | 119.988
Devonshire Building | 2017-06-07 09:00 | 50356.0697 | 2360.016
Devonshire Building | 2017-06-07 09:15 | 50356.1347 | 259.992
Devonshire Building | 2017-06-07 09:30 | 50356.2197 | 339.984
Devonshire Building | 2017-06-07 09:45 | 50356.2997 | 320.004
Devonshire Building | 2017-06-07 10:00 | 50356.3797 | 320.004
Devonshire Building | 2017-06-07 10:15 | 50357.0197 | 2559.996
Devonshire Building | 2017-06-07 10:30 | 50357.0847 | 259.992
Devonshire Building | 2017-06-07 10:45 | 50357.1547 | 280.008
Devonshire Building | 2017-06-07 11:00 | 50357.2197 | 259.992
Devonshire Building | 2017-06-07 11:15 | 50357.2897 | 280.008
Devonshire Building | 2017-06-07 11:30 | 50357.6697 | 1519.992
Devonshire Building | 2017-06-07 11:45 | 50357.9547 | 1140.012
Devonshire Building | 2017-06-07 12:00 | 50358.0247 | 280.008
Devonshire Building | 2017-06-07 12:15 | 50358.0997 | 299.988
Devonshire Building | 2017-06-07 12:30 | 50358.1697 | 280.008
Devonshire Building | 2017-06-07 12:45 | 50358.2347 | 259.992
Devonshire Building | 2017-06-07 13:00 | 50358.2997 | 259.992
Devonshire Building | 2017-06-07 13:15 | 50358.8897 | 2360.016
Devonshire Building | 2017-06-07 13:30 | 50358.9347 | 180
Devonshire Building | 2017-06-07 13:45 | 50358.9847 | 200.016
Devonshire Building | 2017-06-07 14:00 | 50359.0347 | 200.016
Devonshire Building | 2017-06-07 14:15 | 50359.0897 | 219.996
Devonshire Building | 2017-06-07 14:30 | 50359.1547 | 259.992
Devonshire Building | 2017-06-07 14:45 | 50359.2247 | 280.008
Devonshire Building | 2017-06-07 15:00 | 50359.8297 | 2419.992
Devonshire Building | 2017-06-07 15:15 | 50359.8747 | 180
Devonshire Building | 2017-06-07 15:30 | 50359.9147 | 159.984
Devonshire Building | 2017-06-07 15:45 | 50359.9647 | 200.016
Devonshire Building | 2017-06-07 16:00 | 50360.0047 | 159.984
Devonshire Building | 2017-06-07 16:15 | 50360.0447 | 159.984
Devonshire Building | 2017-06-07 16:30 | 50360.0747 | 119.988
Devonshire Building | 2017-06-07 16:45 | 50360.6247 | 2199.996
Devonshire Building | 2017-06-07 17:00 | 50360.6497 | 100.008
Devonshire Building | 2017-06-07 17:15 | 50360.6747 | 100.008
Devonshire Building | 2017-06-07 17:30 | 50360.7047 | 119.988
Devonshire Building | 2017-06-07 17:45 | 50360.7297 | 100.008
Devonshire Building | 2017-06-07 18:00 | 50360.7647 | 140.004
Devonshire Building | 2017-06-07 18:15 | 50360.7897 | 100.008
Devonshire Building | 2017-06-07 18:30 | 50360.8097 | 79.992
Devonshire Building | 2017-06-07 18:45 | 50360.8347 | 100.008
Devonshire Building | 2017-06-07 19:00 | 50360.8547 | 79.992
Devonshire Building | 2017-06-07 19:15 | 50360.8747 | 79.992
Devonshire Building | 2017-06-07 19:30 | 50360.8897 | 60.012
Devonshire Building | 2017-06-07 19:45 | 50360.9097 | 79.992
Devonshire Building | 2017-06-07 20:00 | 50360.9247 | 60.012
Devonshire Building | 2017-06-07 20:15 | 50360.9397 | 60.012
Devonshire Building | 2017-06-07 20:30 | 50360.9547 | 60.012
Devonshire Building | 2017-06-07 20:45 | 50360.9847 | 119.988
Devonshire Building | 2017-06-07 21:00 | 50360.9897 | 20.016
Devonshire Building | 2017-06-07 21:15 | 50360.9997 | 39.996
Devonshire Building | 2017-06-07 21:30 | 50361.0047 | 20.016
Devonshire Building | 2017-06-07 21:45 | 50361.0097 | 20.016
Devonshire Building | 2017-06-07 22:00 | 50361.0197 | 39.996
Devonshire Building | 2017-06-07 22:15 | 50361.0247 | 20.016
Devonshire Building | 2017-06-07 22:30 | 50361.0347 | 39.996
Devonshire Building | 2017-06-07 22:45 | 50361.0397 | 20.016
Devonshire Building | 2017-06-07 23:00 | 50361.0447 | 20.016
Devonshire Building | 2017-06-07 23:15 | 50361.0547 | 39.996
Devonshire Building | 2017-06-07 23:30 | 50361.0597 | 20.016
Devonshire Building | 2017-06-07 23:45 | 50361.0647 | 20.016
Devonshire Building | 2017-06-08 | 50361.0742 | 39.996
Devonshire Building | 2017-06-08 00:15 | 50361.0792 | 20.016
Devonshire Building | 2017-06-08 00:30 | 50361.0842 | 20.016
Devonshire Building | 2017-06-08 00:45 | 50361.0892 | 20.016
Devonshire Building | 2017-06-08 01:00 | 50361.0992 | 39.996
Devonshire Building | 2017-06-08 01:15 | 50361.1042 | 20.016
Devonshire Building | 2017-06-08 01:30 | 50361.1092 | 20.016
Devonshire Building | 2017-06-08 01:45 | 50361.1142 | 20.016
Devonshire Building | 2017-06-08 02:00 | 50361.1242 | 39.996
Devonshire Building | 2017-06-08 02:15 | 50361.1292 | 20.016
Devonshire Building | 2017-06-08 02:30 | 50361.1343 | 20.016
Devonshire Building | 2017-06-08 02:45 | 50361.1393 | 20.016
Devonshire Building | 2017-06-08 03:00 | 50361.1493 | 39.996
Devonshire Building | 2017-06-08 03:15 | 50361.1543 | 20.016
Devonshire Building | 2017-06-08 03:30 | 50361.1593 | 20.016
Devonshire Building | 2017-06-08 03:45 | 50361.1643 | 20.016
Devonshire Building | 2017-06-08 04:00 | 50361.1693 | 20.016
Devonshire Building | 2017-06-08 04:15 | 50361.1743 | 20.016
Devonshire Building | 2017-06-08 04:30 | 50361.1793 | 20.016
Devonshire Building | 2017-06-08 04:45 | 50361.1893 | 39.996
Devonshire Building | 2017-06-08 05:00 | 50361.1943 | 20.016
Devonshire Building | 2017-06-08 05:15 | 50361.1993 | 20.016
Devonshire Building | 2017-06-08 05:30 | 50361.2043 | 20.016
Devonshire Building | 2017-06-08 05:45 | 50361.2143 | 39.996
Devonshire Building | 2017-06-08 06:00 | 50361.2193 | 20.016
Devonshire Building | 2017-06-08 06:15 | 50361.2243 | 20.016
Devonshire Building | 2017-06-08 06:30 | 50361.7743 | 2199.996
Devonshire Building | 2017-06-08 06:45 | 50361.7793 | 20.016
Devonshire Building | 2017-06-08 07:00 | 50361.7893 | 39.996
Devonshire Building | 2017-06-08 07:15 | 50361.7993 | 39.996
Devonshire Building | 2017-06-08 07:30 | 50361.8043 | 20.016
Devonshire Building | 2017-06-08 07:45 | 50361.8193 | 60.012
Devonshire Building | 2017-06-08 08:00 | 50361.8343 | 60.012
Devonshire Building | 2017-06-08 08:15 | 50361.8593 | 100.008
Devonshire Building | 2017-06-08 08:30 | 50361.8743 | 60.012
Devonshire Building | 2017-06-08 08:45 | 50361.9143 | 159.984
Devonshire Building | 2017-06-08 09:00 | 50362.1093 | 780.012
Devonshire Building | 2017-06-08 09:15 | 50362.5743 | 1860.012
Devonshire Building | 2017-06-08 09:30 | 50362.6593 | 339.984
Devonshire Building | 2017-06-08 09:45 | 50362.7493 | 360
Devonshire Building | 2017-06-08 10:00 | 50362.8543 | 420.012
Devonshire Building | 2017-06-08 10:15 | 50363.2343 | 1519.992
Devonshire Building | 2017-06-08 10:30 | 50363.5793 | 1379.988
Devonshire Building | 2017-06-08 10:45 | 50363.6793 | 399.996
Devonshire Building | 2017-06-08 11:00 | 50363.7943 | 460.008
Devonshire Building | 2017-06-08 11:15 | 50363.9093 | 460.008
Devonshire Building | 2017-06-08 11:30 | 50364.5693 | 2639.988
Devonshire Building | 2017-06-08 11:45 | 50364.6993 | 519.984
Devonshire Building | 2017-06-08 12:00 | 50364.8243 | 500.004
Devonshire Building | 2017-06-08 12:15 | 50364.9293 | 420.012
Devonshire Building | 2017-06-08 12:30 | 50365.0243 | 380.016
Devonshire Building | 2017-06-08 12:45 | 50365.1093 | 339.984
Devonshire Building | 2017-06-08 13:00 | 50365.7093 | 2400.012
Devonshire Building | 2017-06-08 13:15 | 50365.7643 | 219.996
Devonshire Building | 2017-06-08 13:30 | 50365.8243 | 240.012
Devonshire Building | 2017-06-08 13:45 | 50365.8793 | 219.996
Devonshire Building | 2017-06-08 14:00 | 50365.9443 | 259.992
Devonshire Building | 2017-06-08 14:15 | 50365.9893 | 180
Devonshire Building | 2017-06-08 14:30 | 50366.5693 | 2319.984
Devonshire Building | 2017-06-08 14:45 | 50366.5943 | 100.008
Devonshire Building | 2017-06-08 15:00 | 50366.6243 | 119.988
Devonshire Building | 2017-06-08 15:15 | 50366.6543 | 119.988
Devonshire Building | 2017-06-08 15:30 | 50366.6893 | 140.004
Devonshire Building | 2017-06-08 15:45 | 50367.2043 | 2059.992
Devonshire Building | 2017-06-08 16:00 | 50367.2993 | 380.016
Devonshire Building | 2017-06-08 16:15 | 50367.3393 | 159.984
Devonshire Building | 2017-06-08 16:30 | 50367.3793 | 159.984
Devonshire Building | 2017-06-08 16:45 | 50367.4193 | 159.984
Devonshire Building | 2017-06-08 17:00 | 50367.4593 | 159.984
Devonshire Building | 2017-06-08 17:15 | 50367.4943 | 140.004
Devonshire Building | 2017-06-08 17:30 | 50367.5293 | 140.004
Devonshire Building | 2017-06-08 17:45 | 50367.5643 | 140.004
Devonshire Building | 2017-06-08 18:00 | 50367.5993 | 140.004
Devonshire Building | 2017-06-08 18:15 | 50367.6293 | 119.988
Devonshire Building | 2017-06-08 18:30 | 50367.6543 | 100.008
Devonshire Building | 2017-06-08 18:45 | 50367.6843 | 119.988
Devonshire Building | 2017-06-08 19:00 | 50367.7093 | 100.008
Devonshire Building | 2017-06-08 19:15 | 50367.7343 | 100.008
Devonshire Building | 2017-06-08 19:30 | 50367.7543 | 79.992
Devonshire Building | 2017-06-08 19:45 | 50368.2693 | 2059.992
Devonshire Building | 2017-06-08 20:00 | 50368.2793 | 39.996
Devonshire Building | 2017-06-08 20:15 | 50368.2943 | 60.012
Devonshire Building | 2017-06-08 20:30 | 50368.3043 | 39.996
Devonshire Building | 2017-06-08 20:45 | 50368.3193 | 60.012
Devonshire Building | 2017-06-08 21:00 | 50368.3293 | 39.996
Devonshire Building | 2017-06-08 21:15 | 50368.3393 | 39.996
Devonshire Building | 2017-06-08 21:30 | 50368.3493 | 39.996
Devonshire Building | 2017-06-08 21:45 | 50368.3593 | 39.996
Devonshire Building | 2017-06-08 22:00 | 50368.3743 | 60.012
Devonshire Building | 2017-06-08 22:15 | 50368.3843 | 39.996
Devonshire Building | 2017-06-08 22:30 | 50368.3943 | 39.996
Devonshire Building | 2017-06-08 22:45 | 50368.4093 | 60.012
Devonshire Building | 2017-06-08 23:00 | 50368.4193 | 39.996
Devonshire Building | 2017-06-08 23:15 | 50368.4293 | 39.996
Devonshire Building | 2017-06-08 23:30 | 50368.4393 | 39.996
Devonshire Building | 2017-06-08 23:45 | 50368.4493 | 39.996
Devonshire Building | 2017-06-09 | 50368.4609 | 39.996
Devonshire Building | 2017-06-09 00:15 | 50368.4709 | 39.996
Devonshire Building | 2017-06-09 00:30 | 50368.4809 | 39.996
Devonshire Building | 2017-06-09 00:45 | 50368.4909 | 39.996
Devonshire Building | 2017-06-09 01:00 | 50368.5009 | 39.996
Devonshire Building | 2017-06-09 01:15 | 50368.5109 | 39.996
Devonshire Building | 2017-06-09 01:30 | 50368.5209 | 39.996
Devonshire Building | 2017-06-09 01:45 | 50368.5309 | 39.996
Devonshire Building | 2017-06-09 02:00 | 50368.5359 | 20.016
Devonshire Building | 2017-06-09 02:15 | 50368.5459 | 39.996
Devonshire Building | 2017-06-09 02:30 | 50368.5559 | 39.996
Devonshire Building | 2017-06-09 02:45 | 50368.5659 | 39.996
Devonshire Building | 2017-06-09 03:00 | 50368.5709 | 20.016
Devonshire Building | 2017-06-09 03:15 | 50368.5809 | 39.996
Devonshire Building | 2017-06-09 03:30 | 50368.5909 | 39.996
Devonshire Building | 2017-06-09 03:45 | 50368.5959 | 20.016
Devonshire Building | 2017-06-09 04:00 | 50368.6059 | 39.996
Devonshire Building | 2017-06-09 04:15 | 50368.6109 | 20.016
Devonshire Building | 2017-06-09 04:30 | 50368.6209 | 39.996
Devonshire Building | 2017-06-09 04:45 | 50368.6309 | 39.996
Devonshire Building | 2017-06-09 05:00 | 50368.6359 | 20.016
Devonshire Building | 2017-06-09 05:15 | 50368.6459 | 39.996
Devonshire Building | 2017-06-09 05:30 | 50368.6559 | 39.996
Devonshire Building | 2017-06-09 05:45 | 50368.6609 | 20.016
Devonshire Building | 2017-06-09 06:00 | 50368.6709 | 39.996
Devonshire Building | 2017-06-09 06:15 | 50368.6809 | 39.996
Devonshire Building | 2017-06-09 06:30 | 50368.6909 | 39.996
Devonshire Building | 2017-06-09 06:45 | 50368.7109 | 79.992
Devonshire Building | 2017-06-09 07:00 | 50368.7209 | 39.996
Devonshire Building | 2017-06-09 07:15 | 50368.7309 | 39.996
Devonshire Building | 2017-06-09 07:30 | 50368.7409 | 39.996
Devonshire Building | 2017-06-09 07:45 | 50368.8159 | 299.988
Devonshire Building | 2017-06-09 08:00 | 50369.3109 | 1980
Devonshire Building | 2017-06-09 08:15 | 50369.3359 | 100.008
Devonshire Building | 2017-06-09 08:30 | 50369.3659 | 119.988
Devonshire Building | 2017-06-09 08:45 | 50369.3909 | 100.008
Devonshire Building | 2017-06-09 09:00 | 50369.4259 | 140.004
Devonshire Building | 2017-06-09 09:15 | 50369.4559 | 119.988
Devonshire Building | 2017-06-09 09:30 | 50369.4959 | 159.984
Devonshire Building | 2017-06-09 09:45 | 50370.0859 | 2360.016
Devonshire Building | 2017-06-09 10:00 | 50370.1859 | 399.996
Devonshire Building | 2017-06-09 10:15 | 50370.2859 | 399.996
Devonshire Building | 2017-06-09 10:30 | 50370.3659 | 320.004
Devonshire Building | 2017-06-09 10:45 | 50370.4409 | 299.988
Devonshire Building | 2017-06-09 11:00 | 50370.5009 | 240.012
Devonshire Building | 2017-06-09 11:15 | 50370.5609 | 240.012
Devonshire Building | 2017-06-09 11:30 | 50370.7759 | 860.004
Devonshire Building | 2017-06-09 11:45 | 50371.1759 | 1599.984
Devonshire Building | 2017-06-09 12:00 | 50371.2259 | 200.016
Devonshire Building | 2017-06-09 12:15 | 50371.2709 | 180
Devonshire Building | 2017-06-09 12:30 | 50371.3109 | 159.984
Devonshire Building | 2017-06-09 12:45 | 50371.3459 | 140.004
Devonshire Building | 2017-06-09 13:00 | 50371.3859 | 159.984
Devonshire Building | 2017-06-09 13:15 | 50371.4259 | 159.984
Devonshire Building | 2017-06-09 13:30 | 50371.4609 | 140.004
Devonshire Building | 2017-06-09 13:45 | 50372.0659 | 2419.992
Devonshire Building | 2017-06-09 14:00 | 50372.1109 | 180
Devonshire Building | 2017-06-09 14:15 | 50372.1509 | 159.984
Devonshire Building | 2017-06-09 14:30 | 50372.2009 | 200.016
Devonshire Building | 2017-06-09 14:45 | 50372.2709 | 280.008
Devonshire Building | 2017-06-09 15:00 | 50372.3509 | 320.004
Devonshire Building | 2017-06-09 15:15 | 50372.4309 | 320.004
Devonshire Building | 2017-06-09 15:30 | 50372.4959 | 259.992
Devonshire Building | 2017-06-09 15:45 | 50373.0759 | 2319.984
Devonshire Building | 2017-06-09 16:00 | 50373.1759 | 399.996
Devonshire Building | 2017-06-09 16:15 | 50373.2359 | 240.012
Devonshire Building | 2017-06-09 16:30 | 50373.2959 | 240.012
Devonshire Building | 2017-06-09 16:45 | 50373.3459 | 200.016
Devonshire Building | 2017-06-09 17:00 | 50373.3909 | 180
Devonshire Building | 2017-06-09 17:15 | 50373.4309 | 159.984
Devonshire Building | 2017-06-09 17:30 | 50373.4659 | 140.004
Devonshire Building | 2017-06-09 17:45 | 50373.4959 | 119.988
Devonshire Building | 2017-06-09 18:00 | 50373.5209 | 100.008
Devonshire Building | 2017-06-09 18:15 | 50373.5459 | 100.008
Devonshire Building | 2017-06-09 18:30 | 50373.5709 | 100.008
Devonshire Building | 2017-06-09 18:45 | 50373.5909 | 79.992
Devonshire Building | 2017-06-09 19:00 | 50373.6109 | 79.992
Devonshire Building | 2017-06-09 19:15 | 50373.6359 | 100.008
Devonshire Building | 2017-06-09 19:30 | 50373.6509 | 60.012
Devonshire Building | 2017-06-09 19:45 | 50373.6709 | 79.992
Devonshire Building | 2017-06-09 20:00 | 50373.6859 | 60.012
Devonshire Building | 2017-06-09 20:15 | 50373.7009 | 60.012
Devonshire Building | 2017-06-09 20:30 | 50373.7159 | 60.012
Devonshire Building | 2017-06-09 20:45 | 50373.7509 | 140.004
Devonshire Building | 2017-06-09 21:00 | 50373.7559 | 20.016
Devonshire Building | 2017-06-09 21:15 | 50373.7659 | 39.996
Devonshire Building | 2017-06-09 21:30 | 50373.7709 | 20.016
Devonshire Building | 2017-06-09 21:45 | 50373.776 | 20.016
Devonshire Building | 2017-06-09 22:00 | 50373.781 | 20.016
Devonshire Building | 2017-06-09 22:15 | 50373.786 | 20.016
Devonshire Building | 2017-06-09 22:30 | 50373.796 | 39.996
Devonshire Building | 2017-06-09 22:45 | 50373.801 | 20.016
Devonshire Building | 2017-06-09 23:00 | 50373.806 | 20.016
Devonshire Building | 2017-06-09 23:15 | 50373.811 | 20.016
Devonshire Building | 2017-06-09 23:30 | 50373.816 | 20.016
Devonshire Building | 2017-06-09 23:45 | 50373.821 | 20.016
Devonshire Building | 2017-06-10 | 50373.8281 | 39.996
Devonshire Building | 2017-06-10 00:15 | 50373.8331 | 20.016
Devonshire Building | 2017-06-10 00:30 | 50373.8381 | 20.016
Devonshire Building | 2017-06-10 00:45 | 50373.8431 | 20.016
Devonshire Building | 2017-06-10 01:00 | 50373.8481 | 20.016
Devonshire Building | 2017-06-10 01:15 | 50373.8532 | 20.016
Devonshire Building | 2017-06-10 01:30 | 50373.8582 | 20.016
Devonshire Building | 2017-06-10 01:45 | 50373.8682 | 39.996
Devonshire Building | 2017-06-10 02:00 | 50373.8732 | 20.016
Devonshire Building | 2017-06-10 02:15 | 50373.8782 | 20.016
Devonshire Building | 2017-06-10 02:30 | 50373.8832 | 20.016
Devonshire Building | 2017-06-10 02:45 | 50373.8882 | 20.016
Devonshire Building | 2017-06-10 03:00 | 50373.8932 | 20.016
Devonshire Building | 2017-06-10 03:15 | 50373.8982 | 20.016
Devonshire Building | 2017-06-10 03:30 | 50373.9032 | 20.016
Devonshire Building | 2017-06-10 03:45 | 50373.9082 | 20.016
Devonshire Building | 2017-06-10 04:00 | 50373.9132 | 20.016
Devonshire Building | 2017-06-10 04:15 | 50373.9182 | 20.016
Devonshire Building | 2017-06-10 04:30 | 50373.9232 | 20.016
Devonshire Building | 2017-06-10 04:45 | 50373.9282 | 20.016
Devonshire Building | 2017-06-10 05:00 | 50373.9332 | 20.016
Devonshire Building | 2017-06-10 05:15 | 50374.4482 | 2059.992
Devonshire Building | 2017-06-10 05:30 | 50374.4532 | 20.016
Devonshire Building | 2017-06-10 05:45 | 50374.4582 | 20.016
Devonshire Building | 2017-06-10 06:00 | 50374.4632 | 20.016
Devonshire Building | 2017-06-10 06:15 | 50374.4682 | 20.016
Devonshire Building | 2017-06-10 06:30 | 50374.4782 | 39.996
Devonshire Building | 2017-06-10 06:45 | 50374.4832 | 20.016
Devonshire Building | 2017-06-10 07:00 | 50374.4882 | 20.016
Devonshire Building | 2017-06-10 07:15 | 50374.4932 | 20.016
Devonshire Building | 2017-06-10 07:30 | 50374.4982 | 20.016
Devonshire Building | 2017-06-10 07:45 | 50374.5132 | 60.012
Devonshire Building | 2017-06-10 08:00 | 50374.5332 | 79.992
Devonshire Building | 2017-06-10 08:15 | 50374.5582 | 100.008
Devonshire Building | 2017-06-10 08:30 | 50374.5782 | 79.992
Devonshire Building | 2017-06-10 08:45 | 50374.5982 | 79.992
Devonshire Building | 2017-06-10 09:00 | 50374.6232 | 100.008
Devonshire Building | 2017-06-10 09:15 | 50374.6432 | 79.992
Devonshire Building | 2017-06-10 09:30 | 50374.6682 | 100.008
Devonshire Building | 2017-06-10 09:45 | 50374.6932 | 100.008
Devonshire Building | 2017-06-10 10:00 | 50374.7132 | 79.992
Devonshire Building | 2017-06-10 10:15 | 50374.7232 | 39.996
Devonshire Building | 2017-06-10 10:30 | 50374.7282 | 20.016
Devonshire Building | 2017-06-10 10:45 | 50374.7332 | 20.016
Devonshire Building | 2017-06-10 11:00 | 50374.7432 | 39.996
Devonshire Building | 2017-06-10 11:15 | 50374.7482 | 20.016
Devonshire Building | 2017-06-10 11:30 | 50374.7582 | 39.996
Devonshire Building | 2017-06-10 11:45 | 50374.7632 | 20.016
Devonshire Building | 2017-06-10 12:00 | 50374.7683 | 20.016
Devonshire Building | 2017-06-10 12:15 | 50374.7733 | 20.016
Devonshire Building | 2017-06-10 12:30 | 50374.7833 | 39.996
Devonshire Building | 2017-06-10 12:45 | 50374.7883 | 20.016
Devonshire Building | 2017-06-10 13:00 | 50374.7933 | 20.016
Devonshire Building | 2017-06-10 13:15 | 50374.7983 | 20.016
Devonshire Building | 2017-06-10 13:30 | 50374.8033 | 20.016
Devonshire Building | 2017-06-10 13:45 | 50374.8133 | 39.996
Devonshire Building | 2017-06-10 14:00 | 50374.8183 | 20.016
Devonshire Building | 2017-06-10 14:15 | 50374.8233 | 20.016
Devonshire Building | 2017-06-10 14:30 | 50374.8333 | 39.996
Devonshire Building | 2017-06-10 14:45 | 50374.8383 | 20.016
Devonshire Building | 2017-06-10 15:00 | 50374.8483 | 39.996
Devonshire Building | 2017-06-10 15:15 | 50374.8533 | 20.016
Devonshire Building | 2017-06-10 15:30 | 50374.8633 | 39.996
Devonshire Building | 2017-06-10 15:45 | 50374.8683 | 20.016
Devonshire Building | 2017-06-10 16:00 | 50374.8733 | 20.016
Devonshire Building | 2017-06-10 16:15 | 50374.8783 | 20.016
Devonshire Building | 2017-06-10 16:30 | 50374.8883 | 39.996
Devonshire Building | 2017-06-10 16:45 | 50374.8933 | 20.016
Devonshire Building | 2017-06-10 17:00 | 50374.8983 | 20.016
Devonshire Building | 2017-06-10 17:15 | 50374.9033 | 20.016
Devonshire Building | 2017-06-10 17:30 | 50374.9083 | 20.016
Devonshire Building | 2017-06-10 17:45 | 50374.9133 | 20.016
Devonshire Building | 2017-06-10 18:00 | 50374.9183 | 20.016
Devonshire Building | 2017-06-10 18:15 | 50374.9283 | 39.996
Devonshire Building | 2017-06-10 18:30 | 50374.9333 | 20.016
Devonshire Building | 2017-06-10 18:45 | 50374.9383 | 20.016
Devonshire Building | 2017-06-10 19:00 | 50374.9433 | 20.016
Devonshire Building | 2017-06-10 19:15 | 50374.9483 | 20.016
Devonshire Building | 2017-06-10 19:30 | 50374.9533 | 20.016
Devonshire Building | 2017-06-10 19:45 | 50374.9583 | 20.016
Devonshire Building | 2017-06-10 20:00 | 50374.9633 | 20.016
Devonshire Building | 2017-06-10 20:15 | 50374.9683 | 20.016
Devonshire Building | 2017-06-10 20:30 | 50374.9783 | 39.996
Devonshire Building | 2017-06-10 20:45 | 50375.0033 | 100.008
Devonshire Building | 2017-06-10 21:00 | 50375.0133 | 39.996
Devonshire Building | 2017-06-10 21:15 | 50375.0233 | 39.996
Devonshire Building | 2017-06-10 21:30 | 50375.0333 | 39.996
Devonshire Building | 2017-06-10 21:45 | 50375.0433 | 39.996
Devonshire Building | 2017-06-10 22:00 | 50375.0483 | 20.016
Devonshire Building | 2017-06-10 22:15 | 50375.0583 | 39.996
Devonshire Building | 2017-06-10 22:30 | 50375.0683 | 39.996
Devonshire Building | 2017-06-10 22:45 | 50375.0783 | 39.996
Devonshire Building | 2017-06-10 23:00 | 50375.3084 | 920.016
Devonshire Building | 2017-06-10 23:15 | 50375.6034 | 1180.008
Devonshire Building | 2017-06-10 23:30 | 50375.6134 | 39.996
Devonshire Building | 2017-06-10 23:45 | 50375.6234 | 39.996
Devonshire Building | 2017-06-11 | 50375.6328 | 39.996
Devonshire Building | 2017-06-11 00:15 | 50375.6378 | 20.016
Devonshire Building | 2017-06-11 00:30 | 50375.6478 | 39.996
Devonshire Building | 2017-06-11 00:45 | 50375.6578 | 39.996
Devonshire Building | 2017-06-11 01:00 | 50375.6678 | 39.996
Devonshire Building | 2017-06-11 01:15 | 50375.6828 | 60.012
Devonshire Building | 2017-06-11 01:30 | 50375.6928 | 39.996
Devonshire Building | 2017-06-11 01:45 | 50375.7078 | 60.012
Devonshire Building | 2017-06-11 02:00 | 50375.7228 | 60.012
Devonshire Building | 2017-06-11 02:15 | 50375.7328 | 39.996
Devonshire Building | 2017-06-11 02:30 | 50375.7478 | 60.012
Devonshire Building | 2017-06-11 02:45 | 50375.7578 | 39.996
Devonshire Building | 2017-06-11 03:00 | 50375.7728 | 60.012
Devonshire Building | 2017-06-11 03:15 | 50375.7828 | 39.996
Devonshire Building | 2017-06-11 03:30 | 50375.7978 | 60.012
Devonshire Building | 2017-06-11 03:45 | 50375.8078 | 39.996
Devonshire Building | 2017-06-11 04:00 | 50375.8178 | 39.996
Devonshire Building | 2017-06-11 04:15 | 50375.8328 | 60.012
Devonshire Building | 2017-06-11 04:30 | 50375.8428 | 39.996
Devonshire Building | 2017-06-11 04:45 | 50375.8528 | 39.996
Devonshire Building | 2017-06-11 05:00 | 50375.8628 | 39.996
Devonshire Building | 2017-06-11 05:15 | 50375.8728 | 39.996
Devonshire Building | 2017-06-11 05:30 | 50375.8828 | 39.996
Devonshire Building | 2017-06-11 05:45 | 50375.8928 | 39.996
Devonshire Building | 2017-06-11 06:00 | 50375.9028 | 39.996
Devonshire Building | 2017-06-11 06:15 | 50375.9078 | 20.016
Devonshire Building | 2017-06-11 06:30 | 50375.9178 | 39.996
Devonshire Building | 2017-06-11 06:45 | 50375.9278 | 39.996
Devonshire Building | 2017-06-11 07:00 | 50375.9328 | 20.016
Devonshire Building | 2017-06-11 07:15 | 50375.9428 | 39.996
Devonshire Building | 2017-06-11 07:30 | 50375.9528 | 39.996
Devonshire Building | 2017-06-11 07:45 | 50375.9678 | 60.012
Devonshire Building | 2017-06-11 08:00 | 50375.9878 | 79.992
Devonshire Building | 2017-06-11 08:15 | 50376.0128 | 100.008
Devonshire Building | 2017-06-11 08:30 | 50376.0378 | 100.008
Devonshire Building | 2017-06-11 08:45 | 50376.0628 | 100.008
Devonshire Building | 2017-06-11 09:00 | 50376.0878 | 100.008
Devonshire Building | 2017-06-11 09:15 | 50376.1078 | 79.992
Devonshire Building | 2017-06-11 09:30 | 50376.1328 | 100.008
Devonshire Building | 2017-06-11 09:45 | 50376.1578 | 100.008
Devonshire Building | 2017-06-11 10:00 | 50376.1778 | 79.992
Devonshire Building | 2017-06-11 10:15 | 50376.1878 | 39.996
Devonshire Building | 2017-06-11 10:30 | 50376.1928 | 20.016
Devonshire Building | 2017-06-11 10:45 | 50376.2028 | 39.996
Devonshire Building | 2017-06-11 11:00 | 50376.2078 | 20.016
Devonshire Building | 2017-06-11 11:15 | 50376.2178 | 39.996
Devonshire Building | 2017-06-11 11:30 | 50376.2228 | 20.016
Devonshire Building | 2017-06-11 11:45 | 50376.2328 | 39.996
Devonshire Building | 2017-06-11 12:00 | 50376.2378 | 20.016
Devonshire Building | 2017-06-11 12:15 | 50376.2478 | 39.996
Devonshire Building | 2017-06-11 12:30 | 50376.2528 | 20.016
Devonshire Building | 2017-06-11 12:45 | 50376.2579 | 20.016
Devonshire Building | 2017-06-11 13:00 | 50376.2678 | 39.996
Devonshire Building | 2017-06-11 13:15 | 50376.2729 | 20.016
Devonshire Building | 2017-06-11 13:30 | 50376.2829 | 39.996
Devonshire Building | 2017-06-11 13:45 | 50376.2929 | 39.996
Devonshire Building | 2017-06-11 14:00 | 50376.2979 | 20.016
Devonshire Building | 2017-06-11 14:15 | 50376.3029 | 20.016
Devonshire Building | 2017-06-11 14:30 | 50376.3129 | 39.996
Devonshire Building | 2017-06-11 14:45 | 50376.3179 | 20.016
Devonshire Building | 2017-06-11 15:00 | 50376.3279 | 39.996
Devonshire Building | 2017-06-11 15:15 | 50376.3329 | 20.016
Devonshire Building | 2017-06-11 15:30 | 50376.3379 | 20.016
Devonshire Building | 2017-06-11 15:45 | 50376.3479 | 39.996
Devonshire Building | 2017-06-11 16:00 | 50376.3629 | 60.012
Devonshire Building | 2017-06-11 16:15 | 50376.3679 | 20.016
Devonshire Building | 2017-06-11 16:30 | 50376.3779 | 39.996
Devonshire Building | 2017-06-11 16:45 | 50376.3829 | 20.016
Devonshire Building | 2017-06-11 17:00 | 50376.3929 | 39.996
Devonshire Building | 2017-06-11 17:15 | 50376.3979 | 20.016
Devonshire Building | 2017-06-11 17:30 | 50376.4029 | 20.016
Devonshire Building | 2017-06-11 17:45 | 50376.4129 | 39.996
Devonshire Building | 2017-06-11 18:00 | 50376.4179 | 20.016
Devonshire Building | 2017-06-11 18:15 | 50376.4279 | 39.996
Devonshire Building | 2017-06-11 18:30 | 50376.4329 | 20.016
Devonshire Building | 2017-06-11 18:45 | 50376.4429 | 39.996
Devonshire Building | 2017-06-11 19:00 | 50376.9279 | 1940.004
Devonshire Building | 2017-06-11 19:15 | 50376.9679 | 159.984
Devonshire Building | 2017-06-11 19:30 | 50376.9729 | 20.016
Devonshire Building | 2017-06-11 19:45 | 50376.9779 | 20.016
Devonshire Building | 2017-06-11 20:00 | 50376.9879 | 39.996
Devonshire Building | 2017-06-11 20:15 | 50376.9929 | 20.016
Devonshire Building | 2017-06-11 20:30 | 50376.9979 | 20.016
Devonshire Building | 2017-06-11 20:45 | 50377.0079 | 39.996
Devonshire Building | 2017-06-11 21:00 | 50377.0129 | 20.016
Devonshire Building | 2017-06-11 21:15 | 50377.0179 | 20.016
Devonshire Building | 2017-06-11 21:30 | 50377.0279 | 39.996
Devonshire Building | 2017-06-11 21:45 | 50377.0329 | 20.016
Devonshire Building | 2017-06-11 22:00 | 50377.0379 | 20.016
Devonshire Building | 2017-06-11 22:15 | 50377.0479 | 39.996
Devonshire Building | 2017-06-11 22:30 | 50377.0529 | 20.016
Devonshire Building | 2017-06-11 22:45 | 50377.0629 | 39.996
Devonshire Building | 2017-06-11 23:00 | 50377.0729 | 39.996
Devonshire Building | 2017-06-11 23:15 | 50377.0779 | 20.016
Devonshire Building | 2017-06-11 23:30 | 50377.0879 | 39.996
Devonshire Building | 2017-06-11 23:45 | 50377.0929 | 20.016
Devonshire Building | 2017-06-12 | 50377.1055 | 39.996
Devonshire Building | 2017-06-12 00:15 | 50377.1155 | 39.996
Devonshire Building | 2017-06-12 00:30 | 50377.1205 | 20.016
Devonshire Building | 2017-06-12 00:45 | 50377.1305 | 39.996
Devonshire Building | 2017-06-12 01:00 | 50377.1355 | 20.016
Devonshire Building | 2017-06-12 01:15 | 50377.1455 | 39.996
Devonshire Building | 2017-06-12 01:30 | 50377.1505 | 20.016
Devonshire Building | 2017-06-12 01:45 | 50377.1605 | 39.996
Devonshire Building | 2017-06-12 02:00 | 50377.1655 | 20.016
Devonshire Building | 2017-06-12 02:15 | 50377.1705 | 20.016
Devonshire Building | 2017-06-12 02:30 | 50377.1805 | 39.996
Devonshire Building | 2017-06-12 02:45 | 50377.1855 | 20.016
Devonshire Building | 2017-06-12 03:00 | 50377.1905 | 20.016
Devonshire Building | 2017-06-12 03:15 | 50377.2005 | 39.996
Devonshire Building | 2017-06-12 03:30 | 50377.2055 | 20.016
Devonshire Building | 2017-06-12 03:45 | 50377.2155 | 39.996
Devonshire Building | 2017-06-12 04:00 | 50377.2205 | 20.016
Devonshire Building | 2017-06-12 04:15 | 50377.2255 | 20.016
Devonshire Building | 2017-06-12 04:30 | 50377.2305 | 20.016
Devonshire Building | 2017-06-12 04:45 | 50377.2405 | 39.996
Devonshire Building | 2017-06-12 05:00 | 50377.2455 | 20.016
Devonshire Building | 2017-06-12 05:15 | 50377.2505 | 20.016
Devonshire Building | 2017-06-12 05:30 | 50377.2605 | 39.996
Devonshire Building | 2017-06-12 05:45 | 50377.2655 | 20.016
Devonshire Building | 2017-06-12 06:00 | 50377.2755 | 39.996
Devonshire Building | 2017-06-12 06:15 | 50377.2805 | 20.016
Devonshire Building | 2017-06-12 06:30 | 50377.2905 | 39.996
Devonshire Building | 2017-06-12 06:45 | 50377.2955 | 20.016
Devonshire Building | 2017-06-12 07:00 | 50377.3105 | 60.012
Devonshire Building | 2017-06-12 07:15 | 50377.3205 | 39.996
Devonshire Building | 2017-06-12 07:30 | 50377.8505 | 2120.004
Devonshire Building | 2017-06-12 07:45 | 50377.8905 | 159.984
Devonshire Building | 2017-06-12 08:00 | 50377.9205 | 119.988
Devonshire Building | 2017-06-12 08:15 | 50377.9605 | 159.984
Devonshire Building | 2017-06-12 08:30 | 50378.0055 | 180
Devonshire Building | 2017-06-12 08:45 | 50378.0755 | 280.008
Devonshire Building | 2017-06-12 09:00 | 50378.6705 | 2379.996
Devonshire Building | 2017-06-12 09:15 | 50378.7555 | 339.984
Devonshire Building | 2017-06-12 09:30 | 50378.8355 | 320.004
Devonshire Building | 2017-06-12 09:45 | 50378.9105 | 299.988
Devonshire Building | 2017-06-12 10:00 | 50378.9705 | 240.012
Devonshire Building | 2017-06-12 10:15 | 50379.5555 | 2340
Devonshire Building | 2017-06-12 10:30 | 50379.5955 | 159.984
Devonshire Building | 2017-06-12 10:45 | 50379.6405 | 180
Devonshire Building | 2017-06-12 11:00 | 50379.6955 | 219.996
Devonshire Building | 2017-06-12 11:15 | 50379.7455 | 200.016
Devonshire Building | 2017-06-12 11:30 | 50380.3005 | 2220.012
Devonshire Building | 2017-06-12 11:45 | 50380.3505 | 200.016
Devonshire Building | 2017-06-12 12:00 | 50380.3955 | 180
Devonshire Building | 2017-06-12 12:15 | 50380.4455 | 200.016
Devonshire Building | 2017-06-12 12:30 | 50380.4955 | 200.016
Devonshire Building | 2017-06-12 12:45 | 50380.5505 | 219.996
Devonshire Building | 2017-06-12 13:00 | 50381.1255 | 2300.004
Devonshire Building | 2017-06-12 13:15 | 50381.1655 | 159.984
Devonshire Building | 2017-06-12 13:30 | 50381.2105 | 180
Devonshire Building | 2017-06-12 13:45 | 50381.2705 | 240.012
Devonshire Building | 2017-06-12 14:00 | 50381.3155 | 180
Devonshire Building | 2017-06-12 14:15 | 50381.3555 | 159.984
Devonshire Building | 2017-06-12 14:30 | 50381.4555 | 399.996
Devonshire Building | 2017-06-12 14:45 | 50381.9755 | 2080.008
Devonshire Building | 2017-06-12 15:00 | 50382.0205 | 180
Devonshire Building | 2017-06-12 15:15 | 50382.0755 | 219.996
Devonshire Building | 2017-06-12 15:30 | 50382.1305 | 219.996
Devonshire Building | 2017-06-12 15:45 | 50382.1955 | 259.992
Devonshire Building | 2017-06-12 16:00 | 50382.5255 | 1320.012
Devonshire Building | 2017-06-12 16:15 | 50382.8655 | 1360.008
Devonshire Building | 2017-06-12 16:30 | 50382.9905 | 500.004
Devonshire Building | 2017-06-12 16:45 | 50383.1055 | 460.008
Devonshire Building | 2017-06-12 17:00 | 50383.1955 | 360
Devonshire Building | 2017-06-12 17:15 | 50383.2605 | 259.992
Devonshire Building | 2017-06-12 17:30 | 50383.3105 | 200.016
Devonshire Building | 2017-06-12 17:45 | 50383.3505 | 159.984
Devonshire Building | 2017-06-12 18:00 | 50383.3855 | 140.004
Devonshire Building | 2017-06-12 18:15 | 50383.4105 | 100.008
Devonshire Building | 2017-06-12 18:30 | 50383.4355 | 100.008
Devonshire Building | 2017-06-12 18:45 | 50383.4655 | 119.988
Devonshire Building | 2017-06-12 19:00 | 50383.4805 | 60.012
Devonshire Building | 2017-06-12 19:15 | 50383.4955 | 60.012
Devonshire Building | 2017-06-12 19:30 | 50383.5155 | 79.992
Devonshire Building | 2017-06-12 19:45 | 50383.5305 | 60.012
Devonshire Building | 2017-06-12 20:00 | 50383.5455 | 60.012
Devonshire Building | 2017-06-12 20:15 | 50383.5555 | 39.996
Devonshire Building | 2017-06-12 20:30 | 50383.5705 | 60.012
Devonshire Building | 2017-06-12 20:45 | 50383.6055 | 140.004
Devonshire Building | 2017-06-12 21:00 | 50383.6055 | 0
Devonshire Building | 2017-06-12 21:15 | 50383.6105 | 20.016
Devonshire Building | 2017-06-12 21:30 | 50383.6155 | 20.016
Devonshire Building | 2017-06-12 21:45 | 50383.6206 | 20.016
Devonshire Building | 2017-06-12 22:00 | 50383.6256 | 20.016
Devonshire Building | 2017-06-12 22:15 | 50383.6306 | 20.016
Devonshire Building | 2017-06-12 22:30 | 50383.6356 | 20.016
Devonshire Building | 2017-06-12 22:45 | 50383.6406 | 20.016
Devonshire Building | 2017-06-12 23:00 | 50383.6456 | 20.016
Devonshire Building | 2017-06-12 23:15 | 50383.6506 | 20.016
Devonshire Building | 2017-06-12 23:30 | 50383.6556 | 20.016
Devonshire Building | 2017-06-12 23:45 | 50383.6606 | 20.016
Devonshire Building | 2017-06-13 | 50383.6602 | 0
Devonshire Building | 2017-06-13 00:15 | 50383.6652 | 20.016
Devonshire Building | 2017-06-13 00:30 | 50383.6702 | 20.016
Devonshire Building | 2017-06-13 00:45 | 50383.6752 | 20.016
Devonshire Building | 2017-06-13 01:00 | 50383.6802 | 20.016
Devonshire Building | 2017-06-13 01:15 | 50383.6852 | 20.016
Devonshire Building | 2017-06-13 01:30 | 50383.6902 | 20.016
Devonshire Building | 2017-06-13 01:45 | 50383.6902 | 0
Devonshire Building | 2017-06-13 02:00 | 50383.6952 | 20.016
Devonshire Building | 2017-06-13 02:15 | 50383.7002 | 20.016
Devonshire Building | 2017-06-13 02:30 | 50383.7052 | 20.016
Devonshire Building | 2017-06-13 02:45 | 50383.7102 | 20.016
Devonshire Building | 2017-06-13 03:00 | 50383.7152 | 20.016
Devonshire Building | 2017-06-13 03:15 | 50383.7152 | 0
Devonshire Building | 2017-06-13 03:30 | 50383.7202 | 20.016
Devonshire Building | 2017-06-13 03:45 | 50384.2352 | 2059.992
Devonshire Building | 2017-06-13 04:00 | 50384.2402 | 20.016
Devonshire Building | 2017-06-13 04:15 | 50384.2452 | 20.016
Devonshire Building | 2017-06-13 04:30 | 50384.2502 | 20.016
Devonshire Building | 2017-06-13 04:45 | 50384.2502 | 0
Devonshire Building | 2017-06-13 05:00 | 50384.2552 | 20.016
Devonshire Building | 2017-06-13 05:15 | 50384.2602 | 20.016
Devonshire Building | 2017-06-13 05:30 | 50384.2652 | 20.016
Devonshire Building | 2017-06-13 05:45 | 50384.2702 | 20.016
Devonshire Building | 2017-06-13 06:00 | 50384.2852 | 60.012
Devonshire Building | 2017-06-13 06:15 | 50384.2902 | 20.016
Devonshire Building | 2017-06-13 06:30 | 50384.2952 | 20.016
Devonshire Building | 2017-06-13 06:45 | 50384.3002 | 20.016
Devonshire Building | 2017-06-13 07:00 | 50384.3053 | 20.016
Devonshire Building | 2017-06-13 07:15 | 50384.3203 | 60.012
Devonshire Building | 2017-06-13 07:30 | 50384.3353 | 60.012
Devonshire Building | 2017-06-13 07:45 | 50384.3653 | 119.988
Devonshire Building | 2017-06-13 08:00 | 50384.9303 | 2260.008
Devonshire Building | 2017-06-13 08:15 | 50384.9853 | 219.996
Devonshire Building | 2017-06-13 08:30 | 50385.0403 | 219.996
Devonshire Building | 2017-06-13 08:45 | 50385.0903 | 200.016
Devonshire Building | 2017-06-13 09:00 | 50385.1453 | 219.996
Devonshire Building | 2017-06-13 09:15 | 50385.2403 | 380.016
Devonshire Building | 2017-06-13 09:30 | 50386.0053 | 3060
Devonshire Building | 2017-06-13 09:45 | 50386.2453 | 960.012
Devonshire Building | 2017-06-13 10:00 | 50386.4453 | 799.992
Devonshire Building | 2017-06-13 10:15 | 50386.6153 | 680.004
Devonshire Building | 2017-06-13 10:30 | 50386.7753 | 640.008
Devonshire Building | 2017-06-13 10:45 | 50387.4753 | 2800.008
Devonshire Building | 2017-06-13 11:00 | 50387.6253 | 600.012
Devonshire Building | 2017-06-13 11:15 | 50387.7453 | 479.988
Devonshire Building | 2017-06-13 11:30 | 50387.8553 | 439.992
Devonshire Building | 2017-06-13 11:45 | 50387.9653 | 439.992
Devonshire Building | 2017-06-13 12:00 | 50388.0703 | 420.012
Devonshire Building | 2017-06-13 12:15 | 50388.7453 | 2700
Devonshire Building | 2017-06-13 12:30 | 50388.8753 | 519.984
Devonshire Building | 2017-06-13 12:45 | 50388.9903 | 460.008
Devonshire Building | 2017-06-13 13:00 | 50389.0803 | 360
Devonshire Building | 2017-06-13 13:15 | 50389.1553 | 299.988
Devonshire Building | 2017-06-13 13:30 | 50389.2253 | 280.008
Devonshire Building | 2017-06-13 13:45 | 50389.2953 | 280.008
Devonshire Building | 2017-06-13 14:00 | 50389.8753 | 2319.984
Devonshire Building | 2017-06-13 14:15 | 50389.9253 | 200.016
Devonshire Building | 2017-06-13 14:30 | 50390.0203 | 380.016
Devonshire Building | 2017-06-13 14:45 | 50390.2603 | 960.012
Devonshire Building | 2017-06-13 15:00 | 50390.4853 | 900
Devonshire Building | 2017-06-13 15:15 | 50391.1903 | 2819.988
Devonshire Building | 2017-06-13 15:30 | 50391.3603 | 680.004
Devonshire Building | 2017-06-13 15:45 | 50391.5603 | 799.992
Devonshire Building | 2017-06-13 16:00 | 50391.7103 | 600.012
Devonshire Building | 2017-06-13 16:15 | 50391.8103 | 399.996
Devonshire Building | 2017-06-13 16:30 | 50391.8753 | 259.992
Devonshire Building | 2017-06-13 16:45 | 50391.9253 | 200.016
Devonshire Building | 2017-06-13 17:00 | 50391.9653 | 159.984
Devonshire Building | 2017-06-13 17:15 | 50392.5053 | 2160
Devonshire Building | 2017-06-13 17:30 | 50392.5153 | 39.996
Devonshire Building | 2017-06-13 17:45 | 50392.5253 | 39.996
Devonshire Building | 2017-06-13 18:00 | 50392.5353 | 39.996
Devonshire Building | 2017-06-13 18:15 | 50392.5453 | 39.996
Devonshire Building | 2017-06-13 18:30 | 50392.5553 | 39.996
Devonshire Building | 2017-06-13 18:45 | 50392.5653 | 39.996
Devonshire Building | 2017-06-13 19:00 | 50392.5803 | 60.012
Devonshire Building | 2017-06-13 19:15 | 50392.5903 | 39.996
Devonshire Building | 2017-06-13 19:30 | 50392.6003 | 39.996
Devonshire Building | 2017-06-13 19:45 | 50392.6103 | 39.996
Devonshire Building | 2017-06-13 20:00 | 50392.6203 | 39.996
Devonshire Building | 2017-06-13 20:15 | 50392.6253 | 20.016
Devonshire Building | 2017-06-13 20:30 | 50392.6353 | 39.996
Devonshire Building | 2017-06-13 20:45 | 50392.6603 | 100.008
Devonshire Building | 2017-06-13 21:00 | 50392.6703 | 39.996
Devonshire Building | 2017-06-13 21:15 | 50392.6753 | 20.016
Devonshire Building | 2017-06-13 21:30 | 50392.6853 | 39.996
Devonshire Building | 2017-06-13 21:45 | 50392.6903 | 20.016
Devonshire Building | 2017-06-13 22:00 | 50392.7003 | 39.996
Devonshire Building | 2017-06-13 22:15 | 50392.7053 | 20.016
Devonshire Building | 2017-06-13 22:30 | 50392.7153 | 39.996
Devonshire Building | 2017-06-13 22:45 | 50392.7203 | 20.016
Devonshire Building | 2017-06-13 23:00 | 50392.7253 | 20.016
Devonshire Building | 2017-06-13 23:15 | 50392.7353 | 39.996
Devonshire Building | 2017-06-13 23:30 | 50392.7403 | 20.016
Devonshire Building | 2017-06-13 23:45 | 50392.7453 | 20.016
Devonshire Building | 2017-06-14 | 50392.7539 | 39.996
Devonshire Building | 2017-06-14 00:15 | 50392.7589 | 20.016
Devonshire Building | 2017-06-14 00:30 | 50392.7639 | 20.016
Devonshire Building | 2017-06-14 00:45 | 50392.7739 | 39.996
Devonshire Building | 2017-06-14 01:00 | 50392.7789 | 20.016
Devonshire Building | 2017-06-14 01:15 | 50392.7839 | 20.016
Devonshire Building | 2017-06-14 01:30 | 50392.7889 | 20.016
Devonshire Building | 2017-06-14 01:45 | 50392.7989 | 39.996
Devonshire Building | 2017-06-14 02:00 | 50392.8039 | 20.016
Devonshire Building | 2017-06-14 02:15 | 50392.8089 | 20.016
Devonshire Building | 2017-06-14 02:30 | 50392.8139 | 20.016
Devonshire Building | 2017-06-14 02:45 | 50392.8189 | 20.016
Devonshire Building | 2017-06-14 03:00 | 50392.8239 | 20.016
Devonshire Building | 2017-06-14 03:15 | 50392.8339 | 39.996
Devonshire Building | 2017-06-14 03:30 | 50392.839 | 20.016
Devonshire Building | 2017-06-14 03:45 | 50392.844 | 20.016
Devonshire Building | 2017-06-14 04:00 | 50392.849 | 20.016
Devonshire Building | 2017-06-14 04:15 | 50392.854 | 20.016
Devonshire Building | 2017-06-14 04:30 | 50392.859 | 20.016
Devonshire Building | 2017-06-14 04:45 | 50392.864 | 20.016
Devonshire Building | 2017-06-14 05:00 | 50392.874 | 39.996
Devonshire Building | 2017-06-14 05:15 | 50392.879 | 20.016
Devonshire Building | 2017-06-14 05:30 | 50392.884 | 20.016
Devonshire Building | 2017-06-14 05:45 | 50392.889 | 20.016
Devonshire Building | 2017-06-14 06:00 | 50392.899 | 39.996
Devonshire Building | 2017-06-14 06:15 | 50392.904 | 20.016
Devonshire Building | 2017-06-14 06:30 | 50392.909 | 20.016
Devonshire Building | 2017-06-14 06:45 | 50393.444 | 2139.984
Devonshire Building | 2017-06-14 07:00 | 50393.454 | 39.996
Devonshire Building | 2017-06-14 07:15 | 50393.464 | 39.996
Devonshire Building | 2017-06-14 07:30 | 50393.479 | 60.012
Devonshire Building | 2017-06-14 07:45 | 50393.499 | 79.992
Devonshire Building | 2017-06-14 08:00 | 50393.544 | 180
Devonshire Building | 2017-06-14 08:15 | 50393.589 | 180
Devonshire Building | 2017-06-14 08:30 | 50393.644 | 219.996
Devonshire Building | 2017-06-14 08:45 | 50393.704 | 240.012
Devonshire Building | 2017-06-14 09:00 | 50394.329 | 2499.984
Devonshire Building | 2017-06-14 09:15 | 50394.489 | 640.008
Devonshire Building | 2017-06-14 09:30 | 50394.609 | 479.988
Devonshire Building | 2017-06-14 09:45 | 50394.719 | 439.992
Devonshire Building | 2017-06-14 10:00 | 50394.814 | 380.016
Devonshire Building | 2017-06-14 10:15 | 50395.284 | 1879.992
Devonshire Building | 2017-06-14 10:30 | 50395.434 | 600.012
Devonshire Building | 2017-06-14 10:45 | 50395.469 | 140.004
Devonshire Building | 2017-06-14 11:00 | 50395.509 | 159.984
Devonshire Building | 2017-06-14 11:15 | 50395.549 | 159.984
Devonshire Building | 2017-06-14 11:30 | 50395.589 | 159.984
Devonshire Building | 2017-06-14 11:45 | 50395.624 | 140.004
Devonshire Building | 2017-06-14 12:00 | 50396.194 | 2279.988
Devonshire Building | 2017-06-14 12:15 | 50396.224 | 119.988
Devonshire Building | 2017-06-14 12:30 | 50396.249 | 100.008
Devonshire Building | 2017-06-14 12:45 | 50396.274 | 100.008
Devonshire Building | 2017-06-14 13:00 | 50396.304 | 119.988
Devonshire Building | 2017-06-14 13:15 | 50396.854 | 2199.996
Devonshire Building | 2017-06-14 13:30 | 50396.889 | 140.004
Devonshire Building | 2017-06-14 13:45 | 50396.949 | 240.012
Devonshire Building | 2017-06-14 14:00 | 50397.014 | 259.992
Devonshire Building | 2017-06-14 14:15 | 50397.074 | 240.012
Devonshire Building | 2017-06-14 14:30 | 50397.129 | 219.996
Devonshire Building | 2017-06-14 14:45 | 50397.179 | 200.016
Devonshire Building | 2017-06-14 15:00 | 50397.764 | 2340
Devonshire Building | 2017-06-14 15:15 | 50397.804 | 159.984
Devonshire Building | 2017-06-14 15:30 | 50397.849 | 180
Devonshire Building | 2017-06-14 15:45 | 50397.894 | 180
Devonshire Building | 2017-06-14 16:00 | 50397.934 | 159.984
Devonshire Building | 2017-06-14 16:15 | 50397.974 | 159.984
Devonshire Building | 2017-06-14 16:30 | 50398.249 | 1100.016
Devonshire Building | 2017-06-14 16:45 | 50398.609 | 1440
Devonshire Building | 2017-06-14 17:00 | 50398.644 | 140.004
Devonshire Building | 2017-06-14 17:15 | 50398.694 | 200.016
Devonshire Building | 2017-06-14 17:30 | 50398.734 | 159.984
Devonshire Building | 2017-06-14 17:45 | 50398.779 | 180
Devonshire Building | 2017-06-14 18:00 | 50398.819 | 159.984
Devonshire Building | 2017-06-14 18:15 | 50398.854 | 140.004
Devonshire Building | 2017-06-14 18:30 | 50398.894 | 159.984
Devonshire Building | 2017-06-14 18:45 | 50398.929 | 140.004
Devonshire Building | 2017-06-14 19:00 | 50398.964 | 140.004
Devonshire Building | 2017-06-14 19:15 | 50398.989 | 100.008
Devonshire Building | 2017-06-14 19:30 | 50399.019 | 119.988
Devonshire Building | 2017-06-14 19:45 | 50399.039 | 79.992
Devonshire Building | 2017-06-14 20:00 | 50399.064 | 100.008
Devonshire Building | 2017-06-14 20:15 | 50399.084 | 79.992
Devonshire Building | 2017-06-14 20:30 | 50399.104 | 79.992
Devonshire Building | 2017-06-14 20:45 | 50399.129 | 100.008
Devonshire Building | 2017-06-14 21:00 | 50399.139 | 39.996
Devonshire Building | 2017-06-14 21:15 | 50399.154 | 60.012
Devonshire Building | 2017-06-14 21:30 | 50399.164 | 39.996
Devonshire Building | 2017-06-14 21:45 | 50399.179 | 60.012
Devonshire Building | 2017-06-14 22:00 | 50399.189 | 39.996
Devonshire Building | 2017-06-14 22:15 | 50399.204 | 60.012
Devonshire Building | 2017-06-14 22:30 | 50399.214 | 39.996
Devonshire Building | 2017-06-14 22:45 | 50399.224 | 39.996
Devonshire Building | 2017-06-14 23:00 | 50399.239 | 60.012
Devonshire Building | 2017-06-14 23:15 | 50399.249 | 39.996
Devonshire Building | 2017-06-14 23:30 | 50399.259 | 39.996
Devonshire Building | 2017-06-14 23:45 | 50399.274 | 60.012
Devonshire Building | 2017-06-15 | 50399.2852 | 39.996
Devonshire Building | 2017-06-15 00:15 | 50399.2952 | 39.996
Devonshire Building | 2017-06-15 00:30 | 50399.3052 | 39.996
Devonshire Building | 2017-06-15 00:45 | 50399.3152 | 39.996
Devonshire Building | 2017-06-15 01:00 | 50399.3302 | 60.012
Devonshire Building | 2017-06-15 01:15 | 50399.3402 | 39.996
Devonshire Building | 2017-06-15 01:30 | 50399.3502 | 39.996
Devonshire Building | 2017-06-15 01:45 | 50399.3702 | 79.992
Devonshire Building | 2017-06-15 02:00 | 50399.3952 | 100.008
Devonshire Building | 2017-06-15 02:15 | 50399.4202 | 100.008
Devonshire Building | 2017-06-15 02:30 | 50399.4452 | 100.008
Devonshire Building | 2017-06-15 02:45 | 50399.4752 | 119.988
Devonshire Building | 2017-06-15 03:00 | 50399.5002 | 100.008
Devonshire Building | 2017-06-15 03:15 | 50399.5252 | 100.008
Devonshire Building | 2017-06-15 03:30 | 50399.5502 | 100.008
Devonshire Building | 2017-06-15 03:45 | 50399.5652 | 60.012
Devonshire Building | 2017-06-15 04:00 | 50399.5752 | 39.996
Devonshire Building | 2017-06-15 04:15 | 50399.5852 | 39.996
Devonshire Building | 2017-06-15 04:30 | 50399.5952 | 39.996
Devonshire Building | 2017-06-15 04:45 | 50399.6052 | 39.996
Devonshire Building | 2017-06-15 05:00 | 50399.6152 | 39.996
Devonshire Building | 2017-06-15 05:15 | 50399.6252 | 39.996
Devonshire Building | 2017-06-15 05:30 | 50399.6352 | 39.996
Devonshire Building | 2017-06-15 05:45 | 50399.6452 | 39.996
Devonshire Building | 2017-06-15 06:00 | 50399.6552 | 39.996
Devonshire Building | 2017-06-15 06:15 | 50399.6602 | 20.016
Devonshire Building | 2017-06-15 06:30 | 50399.6702 | 39.996
Devonshire Building | 2017-06-15 06:45 | 50400.1902 | 2080.008
Devonshire Building | 2017-06-15 07:00 | 50400.1952 | 20.016
Devonshire Building | 2017-06-15 07:15 | 50400.2002 | 20.016
Devonshire Building | 2017-06-15 07:30 | 50400.2052 | 20.016
Devonshire Building | 2017-06-15 07:45 | 50400.2152 | 39.996
Devonshire Building | 2017-06-15 08:00 | 50400.2252 | 39.996
Devonshire Building | 2017-06-15 08:15 | 50400.2402 | 60.012
Devonshire Building | 2017-06-15 08:30 | 50400.2502 | 39.996
Devonshire Building | 2017-06-15 08:45 | 50400.7902 | 2160
Devonshire Building | 2017-06-15 09:00 | 50400.7952 | 20.016
Devonshire Building | 2017-06-15 09:15 | 50400.8102 | 60.012
Devonshire Building | 2017-06-15 09:30 | 50400.8202 | 39.996
Devonshire Building | 2017-06-15 09:45 | 50400.9402 | 479.988
Devonshire Building | 2017-06-15 10:00 | 50401.4052 | 1860.012
Devonshire Building | 2017-06-15 10:15 | 50401.4702 | 259.992
Devonshire Building | 2017-06-15 10:30 | 50401.5402 | 280.008
Devonshire Building | 2017-06-15 10:45 | 50401.6002 | 240.012
Devonshire Building | 2017-06-15 11:00 | 50401.7302 | 519.984
Devonshire Building | 2017-06-15 11:15 | 50401.9452 | 860.004
Devonshire Building | 2017-06-15 11:30 | 50402.6502 | 2819.988
Devonshire Building | 2017-06-15 11:45 | 50402.8202 | 680.004
Devonshire Building | 2017-06-15 12:00 | 50402.9702 | 600.012
Devonshire Building | 2017-06-15 12:15 | 50403.0702 | 399.996
Devonshire Building | 2017-06-15 12:30 | 50403.1752 | 420.012
Devonshire Building | 2017-06-15 12:45 | 50403.2802 | 420.012
Devonshire Building | 2017-06-15 13:00 | 50403.6752 | 1580.004
Devonshire Building | 2017-06-15 13:15 | 50404.0102 | 1339.992
Devonshire Building | 2017-06-15 13:30 | 50404.0852 | 299.988
Devonshire Building | 2017-06-15 13:45 | 50404.1552 | 280.008
Devonshire Building | 2017-06-15 14:00 | 50404.2102 | 219.996
Devonshire Building | 2017-06-15 14:15 | 50404.2702 | 240.012
Devonshire Building | 2017-06-15 14:30 | 50404.3252 | 219.996
Devonshire Building | 2017-06-15 14:45 | 50404.3802 | 219.996
Devonshire Building | 2017-06-15 15:00 | 50404.4302 | 200.016
Devonshire Building | 2017-06-15 15:15 | 50405.0052 | 2300.004
Devonshire Building | 2017-06-15 15:30 | 50405.0352 | 119.988
Devonshire Building | 2017-06-15 15:45 | 50405.0652 | 119.988
Devonshire Building | 2017-06-15 16:00 | 50405.1002 | 140.004
Devonshire Building | 2017-06-15 16:15 | 50405.1302 | 119.988
Devonshire Building | 2017-06-15 16:30 | 50405.1602 | 119.988
Devonshire Building | 2017-06-15 16:45 | 50405.6952 | 2139.984
Devonshire Building | 2017-06-15 17:00 | 50405.7302 | 140.004
Devonshire Building | 2017-06-15 17:15 | 50405.7602 | 119.988
Devonshire Building | 2017-06-15 17:30 | 50405.7902 | 119.988
Devonshire Building | 2017-06-15 17:45 | 50405.8202 | 119.988
Devonshire Building | 2017-06-15 18:00 | 50405.8502 | 119.988
Devonshire Building | 2017-06-15 18:15 | 50405.8752 | 100.008
Devonshire Building | 2017-06-15 18:30 | 50405.9052 | 119.988
Devonshire Building | 2017-06-15 18:45 | 50405.9302 | 100.008
Devonshire Building | 2017-06-15 19:00 | 50405.9552 | 100.008
Devonshire Building | 2017-06-15 19:15 | 50405.9752 | 79.992
Devonshire Building | 2017-06-15 19:30 | 50405.9952 | 79.992
Devonshire Building | 2017-06-15 19:45 | 50406.0302 | 140.004
Devonshire Building | 2017-06-15 20:00 | 50406.0652 | 140.004
Devonshire Building | 2017-06-15 20:15 | 50406.1002 | 140.004
Devonshire Building | 2017-06-15 20:30 | 50406.1302 | 119.988
Devonshire Building | 2017-06-15 20:45 | 50406.1802 | 200.016
Devonshire Building | 2017-06-15 21:00 | 50406.2052 | 100.008
Devonshire Building | 2017-06-15 21:15 | 50406.2252 | 79.992
Devonshire Building | 2017-06-15 21:30 | 50406.2452 | 79.992
Devonshire Building | 2017-06-15 21:45 | 50406.2652 | 79.992
Devonshire Building | 2017-06-15 22:00 | 50406.2702 | 20.016
Devonshire Building | 2017-06-15 22:15 | 50406.2752 | 20.016
Devonshire Building | 2017-06-15 22:30 | 50406.2802 | 20.016
Devonshire Building | 2017-06-15 22:45 | 50406.2852 | 20.016
Devonshire Building | 2017-06-15 23:00 | 50406.2902 | 20.016
Devonshire Building | 2017-06-15 23:15 | 50406.2952 | 20.016
Devonshire Building | 2017-06-15 23:30 | 50406.3002 | 20.016
Devonshire Building | 2017-06-15 23:45 | 50406.3052 | 20.016
Devonshire Building | 2017-06-16 | 50406.3086 | 20.016
Devonshire Building | 2017-06-16 00:15 | 50406.3136 | 20.016
Devonshire Building | 2017-06-16 00:30 | 50406.3136 | 0
Devonshire Building | 2017-06-16 00:45 | 50406.3186 | 20.016
Devonshire Building | 2017-06-16 01:00 | 50406.3236 | 20.016
Devonshire Building | 2017-06-16 01:15 | 50406.3286 | 20.016
Devonshire Building | 2017-06-16 01:30 | 50406.3336 | 20.016
Devonshire Building | 2017-06-16 01:45 | 50406.3386 | 20.016
Devonshire Building | 2017-06-16 02:00 | 50406.3436 | 20.016
Devonshire Building | 2017-06-16 02:15 | 50406.3486 | 20.016
Devonshire Building | 2017-06-16 02:30 | 50406.3536 | 20.016
Devonshire Building | 2017-06-16 02:45 | 50406.3586 | 20.016
Devonshire Building | 2017-06-16 03:00 | 50406.3586 | 0
Devonshire Building | 2017-06-16 03:15 | 50406.3636 | 20.016
Devonshire Building | 2017-06-16 03:30 | 50406.3686 | 20.016
Devonshire Building | 2017-06-16 03:45 | 50406.3736 | 20.016
Devonshire Building | 2017-06-16 04:00 | 50406.3786 | 20.016
Devonshire Building | 2017-06-16 04:15 | 50406.3837 | 20.016
Devonshire Building | 2017-06-16 04:30 | 50406.3887 | 20.016
Devonshire Building | 2017-06-16 04:45 | 50406.3887 | 0
Devonshire Building | 2017-06-16 05:00 | 50406.3937 | 20.016
Devonshire Building | 2017-06-16 05:15 | 50406.3987 | 20.016
Devonshire Building | 2017-06-16 05:30 | 50406.4037 | 20.016
Devonshire Building | 2017-06-16 05:45 | 50406.4087 | 20.016
Devonshire Building | 2017-06-16 06:00 | 50406.4187 | 39.996
Devonshire Building | 2017-06-16 06:15 | 50406.4237 | 20.016
Devonshire Building | 2017-06-16 06:30 | 50406.9287 | 2019.996
Devonshire Building | 2017-06-16 06:45 | 50406.9387 | 39.996
Devonshire Building | 2017-06-16 07:00 | 50406.9487 | 39.996
Devonshire Building | 2017-06-16 07:15 | 50406.9737 | 100.008
Devonshire Building | 2017-06-16 07:30 | 50406.9987 | 100.008
Devonshire Building | 2017-06-16 07:45 | 50407.0437 | 180
Devonshire Building | 2017-06-16 08:00 | 50407.0837 | 159.984
Devonshire Building | 2017-06-16 08:15 | 50407.1287 | 180
Devonshire Building | 2017-06-16 08:30 | 50407.1737 | 180
Devonshire Building | 2017-06-16 08:45 | 50407.5237 | 1400.004
Devonshire Building | 2017-06-16 09:00 | 50407.7837 | 1040.004
Devonshire Building | 2017-06-16 09:15 | 50407.8987 | 460.008
Devonshire Building | 2017-06-16 09:30 | 50408.0137 | 460.008
Devonshire Building | 2017-06-16 09:45 | 50408.1287 | 460.008
Devonshire Building | 2017-06-16 10:00 | 50408.7237 | 2379.996
Devonshire Building | 2017-06-16 10:15 | 50408.8337 | 439.992
Devonshire Building | 2017-06-16 10:30 | 50408.8937 | 240.012
Devonshire Building | 2017-06-16 10:45 | 50408.9487 | 219.996
Devonshire Building | 2017-06-16 11:00 | 50409.0037 | 219.996
Devonshire Building | 2017-06-16 11:15 | 50409.0687 | 259.992
Devonshire Building | 2017-06-16 11:30 | 50409.3987 | 1320.012
Devonshire Building | 2017-06-16 11:45 | 50409.7187 | 1280.016
Devonshire Building | 2017-06-16 12:00 | 50409.7587 | 159.984
Devonshire Building | 2017-06-16 12:15 | 50409.7987 | 159.984
Devonshire Building | 2017-06-16 12:30 | 50409.8437 | 180
Devonshire Building | 2017-06-16 12:45 | 50409.8837 | 159.984
Devonshire Building | 2017-06-16 13:00 | 50409.9187 | 140.004
Devonshire Building | 2017-06-16 13:15 | 50409.9537 | 140.004
Devonshire Building | 2017-06-16 13:30 | 50410.1837 | 920.016
Devonshire Building | 2017-06-16 13:45 | 50410.5687 | 1540.008
Devonshire Building | 2017-06-16 14:00 | 50410.6237 | 219.996
Devonshire Building | 2017-06-16 14:15 | 50410.6837 | 240.012
Devonshire Building | 2017-06-16 14:30 | 50410.7487 | 259.992
Devonshire Building | 2017-06-16 14:45 | 50410.8287 | 320.004
Devonshire Building | 2017-06-16 15:00 | 50410.9187 | 360
Devonshire Building | 2017-06-16 15:15 | 50411.0087 | 360
Devonshire Building | 2017-06-16 15:30 | 50411.0937 | 339.984
Devonshire Building | 2017-06-16 15:45 | 50411.1737 | 320.004
Devonshire Building | 2017-06-16 16:00 | 50411.7537 | 2319.984
Devonshire Building | 2017-06-16 16:15 | 50411.7987 | 180
Devonshire Building | 2017-06-16 16:30 | 50411.8487 | 200.016
Devonshire Building | 2017-06-16 16:45 | 50411.8937 | 180
Devonshire Building | 2017-06-16 17:00 | 50411.9337 | 159.984
Devonshire Building | 2017-06-16 17:15 | 50411.9687 | 140.004
Devonshire Building | 2017-06-16 17:30 | 50412.0037 | 140.004
Devonshire Building | 2017-06-16 17:45 | 50412.0387 | 140.004
Devonshire Building | 2017-06-16 18:00 | 50412.0687 | 119.988
Devonshire Building | 2017-06-16 18:15 | 50412.0987 | 119.988
Devonshire Building | 2017-06-16 18:30 | 50412.1287 | 119.988
Devonshire Building | 2017-06-16 18:45 | 50412.1587 | 119.988
Devonshire Building | 2017-06-16 19:00 | 50412.1837 | 100.008
Devonshire Building | 2017-06-16 19:15 | 50412.2087 | 100.008
Devonshire Building | 2017-06-16 19:30 | 50412.2337 | 100.008
Devonshire Building | 2017-06-16 19:45 | 50412.2587 | 100.008
Devonshire Building | 2017-06-16 20:00 | 50412.2787 | 79.992
Devonshire Building | 2017-06-16 20:15 | 50412.2987 | 79.992
Devonshire Building | 2017-06-16 20:30 | 50412.3187 | 79.992
Devonshire Building | 2017-06-16 20:45 | 50412.3587 | 159.984
Devonshire Building | 2017-06-16 21:00 | 50412.3687 | 39.996
Devonshire Building | 2017-06-16 21:15 | 50412.3737 | 20.016
Devonshire Building | 2017-06-16 21:30 | 50412.3837 | 39.996
Devonshire Building | 2017-06-16 21:45 | 50412.3937 | 39.996
Devonshire Building | 2017-06-16 22:00 | 50412.3987 | 20.016
Devonshire Building | 2017-06-16 22:15 | 50412.4087 | 39.996
Devonshire Building | 2017-06-16 22:30 | 50412.4187 | 39.996
Devonshire Building | 2017-06-16 22:45 | 50412.4237 | 20.016
Devonshire Building | 2017-06-16 23:00 | 50412.4337 | 39.996
Devonshire Building | 2017-06-16 23:15 | 50412.4437 | 39.996
Devonshire Building | 2017-06-16 23:30 | 50412.4487 | 20.016
Devonshire Building | 2017-06-16 23:45 | 50412.4587 | 39.996
Devonshire Building | 2017-06-17 | 50412.4648 | 20.016
Devonshire Building | 2017-06-17 00:15 | 50412.4748 | 39.996
Devonshire Building | 2017-06-17 00:30 | 50412.4798 | 20.016
Devonshire Building | 2017-06-17 00:45 | 50412.4898 | 39.996
Devonshire Building | 2017-06-17 01:00 | 50412.4948 | 20.016
Devonshire Building | 2017-06-17 01:15 | 50412.5048 | 39.996
Devonshire Building | 2017-06-17 01:30 | 50412.5098 | 20.016
Devonshire Building | 2017-06-17 01:45 | 50412.5198 | 39.996
Devonshire Building | 2017-06-17 02:00 | 50412.5249 | 20.016
Devonshire Building | 2017-06-17 02:15 | 50412.5349 | 39.996
Devonshire Building | 2017-06-17 02:30 | 50412.5399 | 20.016
Devonshire Building | 2017-06-17 02:45 | 50412.5449 | 20.016
Devonshire Building | 2017-06-17 03:00 | 50412.5549 | 39.996
Devonshire Building | 2017-06-17 03:15 | 50412.5599 | 20.016
Devonshire Building | 2017-06-17 03:30 | 50412.5699 | 39.996
Devonshire Building | 2017-06-17 03:45 | 50412.5749 | 20.016
Devonshire Building | 2017-06-17 04:00 | 50412.5799 | 20.016
Devonshire Building | 2017-06-17 04:15 | 50412.5899 | 39.996
Devonshire Building | 2017-06-17 04:30 | 50412.5949 | 20.016
Devonshire Building | 2017-06-17 04:45 | 50412.5999 | 20.016
Devonshire Building | 2017-06-17 05:00 | 50412.6099 | 39.996
Devonshire Building | 2017-06-17 05:15 | 50412.6149 | 20.016
Devonshire Building | 2017-06-17 05:30 | 50412.6199 | 20.016
Devonshire Building | 2017-06-17 05:45 | 50412.6249 | 20.016
Devonshire Building | 2017-06-17 06:00 | 50412.6349 | 39.996
Devonshire Building | 2017-06-17 06:15 | 50412.6399 | 20.016
Devonshire Building | 2017-06-17 06:30 | 50412.6449 | 20.016
Devonshire Building | 2017-06-17 06:45 | 50412.6499 | 20.016
Devonshire Building | 2017-06-17 07:00 | 50412.6599 | 39.996
Devonshire Building | 2017-06-17 07:15 | 50412.6649 | 20.016
Devonshire Building | 2017-06-17 07:30 | 50413.1749 | 2040.012
Devonshire Building | 2017-06-17 07:45 | 50413.1849 | 39.996
Devonshire Building | 2017-06-17 08:00 | 50413.1899 | 20.016
Devonshire Building | 2017-06-17 08:15 | 50413.1949 | 20.016
Devonshire Building | 2017-06-17 08:30 | 50413.2049 | 39.996
Devonshire Building | 2017-06-17 08:45 | 50413.2149 | 39.996
Devonshire Building | 2017-06-17 09:00 | 50413.2249 | 39.996
Devonshire Building | 2017-06-17 09:15 | 50413.2299 | 20.016
Devonshire Building | 2017-06-17 09:30 | 50413.2399 | 39.996
Devonshire Building | 2017-06-17 09:45 | 50413.2499 | 39.996
Devonshire Building | 2017-06-17 10:00 | 50413.2599 | 39.996
Devonshire Building | 2017-06-17 10:15 | 50413.2699 | 39.996
Devonshire Building | 2017-06-17 10:30 | 50413.2799 | 39.996
Devonshire Building | 2017-06-17 10:45 | 50413.2899 | 39.996
Devonshire Building | 2017-06-17 11:00 | 50413.2999 | 39.996
Devonshire Building | 2017-06-17 11:15 | 50413.3099 | 39.996
Devonshire Building | 2017-06-17 11:30 | 50413.3199 | 39.996
Devonshire Building | 2017-06-17 11:45 | 50413.3249 | 20.016
Devonshire Building | 2017-06-17 12:00 | 50413.3349 | 39.996
Devonshire Building | 2017-06-17 12:15 | 50413.3449 | 39.996
Devonshire Building | 2017-06-17 12:30 | 50413.3549 | 39.996
Devonshire Building | 2017-06-17 12:45 | 50413.3649 | 39.996
Devonshire Building | 2017-06-17 13:00 | 50413.3699 | 20.016
Devonshire Building | 2017-06-17 13:15 | 50413.3799 | 39.996
Devonshire Building | 2017-06-17 13:30 | 50413.3899 | 39.996
Devonshire Building | 2017-06-17 13:45 | 50413.4149 | 100.008
Devonshire Building | 2017-06-17 14:00 | 50413.4399 | 100.008
Devonshire Building | 2017-06-17 14:15 | 50413.4649 | 100.008
Devonshire Building | 2017-06-17 14:30 | 50413.4899 | 100.008
Devonshire Building | 2017-06-17 14:45 | 50413.5149 | 100.008
Devonshire Building | 2017-06-17 15:00 | 50413.5399 | 100.008
Devonshire Building | 2017-06-17 15:15 | 50413.5599 | 79.992
Devonshire Building | 2017-06-17 15:30 | 50413.5849 | 100.008
Devonshire Building | 2017-06-17 15:45 | 50413.6049 | 79.992
Devonshire Building | 2017-06-17 16:00 | 50413.6099 | 20.016
Devonshire Building | 2017-06-17 16:15 | 50413.6199 | 39.996
Devonshire Building | 2017-06-17 16:30 | 50413.6249 | 20.016
Devonshire Building | 2017-06-17 16:45 | 50413.6299 | 20.016
Devonshire Building | 2017-06-17 17:00 | 50413.6399 | 39.996
Devonshire Building | 2017-06-17 17:15 | 50413.6449 | 20.016
Devonshire Building | 2017-06-17 17:30 | 50413.6499 | 20.016
Devonshire Building | 2017-06-17 17:45 | 50413.6599 | 39.996
Devonshire Building | 2017-06-17 18:00 | 50413.6649 | 20.016
Devonshire Building | 2017-06-17 18:15 | 50413.6749 | 39.996
Devonshire Building | 2017-06-17 18:30 | 50413.6799 | 20.016
Devonshire Building | 2017-06-17 18:45 | 50413.6899 | 39.996
Devonshire Building | 2017-06-17 19:00 | 50413.6949 | 20.016
Devonshire Building | 2017-06-17 19:15 | 50413.6999 | 20.016
Devonshire Building | 2017-06-17 19:30 | 50413.7049 | 20.016
Devonshire Building | 2017-06-17 19:45 | 50413.7149 | 39.996
Devonshire Building | 2017-06-17 20:00 | 50413.72 | 20.016
Devonshire Building | 2017-06-17 20:15 | 50413.725 | 20.016
Devonshire Building | 2017-06-17 20:30 | 50413.735 | 39.996
Devonshire Building | 2017-06-17 20:45 | 50413.765 | 119.988
Devonshire Building | 2017-06-17 21:00 | 50413.775 | 39.996
Devonshire Building | 2017-06-17 21:15 | 50413.78 | 20.016
Devonshire Building | 2017-06-17 21:30 | 50413.79 | 39.996
Devonshire Building | 2017-06-17 21:45 | 50413.795 | 20.016
Devonshire Building | 2017-06-17 22:00 | 50413.805 | 39.996
Devonshire Building | 2017-06-17 22:15 | 50413.81 | 20.016
Devonshire Building | 2017-06-17 22:30 | 50413.82 | 39.996
Devonshire Building | 2017-06-17 22:45 | 50413.825 | 20.016
Devonshire Building | 2017-06-17 23:00 | 50413.835 | 39.996
Devonshire Building | 2017-06-17 23:15 | 50413.845 | 39.996
Devonshire Building | 2017-06-17 23:30 | 50413.85 | 20.016
Devonshire Building | 2017-06-17 23:45 | 50413.86 | 39.996
Devonshire Building | 2017-06-18 | 50413.8711 | 39.996
Devonshire Building | 2017-06-18 00:15 | 50414.1911 | 1280.016
Devonshire Building | 2017-06-18 00:30 | 50414.3811 | 759.996
Devonshire Building | 2017-06-18 00:45 | 50414.3861 | 20.016
Devonshire Building | 2017-06-18 01:00 | 50414.3961 | 39.996
Devonshire Building | 2017-06-18 01:15 | 50414.4011 | 20.016
Devonshire Building | 2017-06-18 01:30 | 50414.4111 | 39.996
Devonshire Building | 2017-06-18 01:45 | 50414.4161 | 20.016
Devonshire Building | 2017-06-18 02:00 | 50414.4261 | 39.996
Devonshire Building | 2017-06-18 02:15 | 50414.4361 | 39.996
Devonshire Building | 2017-06-18 02:30 | 50414.4461 | 39.996
Devonshire Building | 2017-06-18 02:45 | 50414.4511 | 20.016
Devonshire Building | 2017-06-18 03:00 | 50414.4661 | 60.012
Devonshire Building | 2017-06-18 03:15 | 50414.4761 | 39.996
Devonshire Building | 2017-06-18 03:30 | 50414.4861 | 39.996
Devonshire Building | 2017-06-18 03:45 | 50414.4961 | 39.996
Devonshire Building | 2017-06-18 04:00 | 50414.5111 | 60.012
Devonshire Building | 2017-06-18 04:15 | 50414.5211 | 39.996
Devonshire Building | 2017-06-18 04:30 | 50414.5311 | 39.996
Devonshire Building | 2017-06-18 04:45 | 50414.5411 | 39.996
Devonshire Building | 2017-06-18 05:00 | 50414.5511 | 39.996
Devonshire Building | 2017-06-18 05:15 | 50414.5611 | 39.996
Devonshire Building | 2017-06-18 05:30 | 50414.5711 | 39.996
Devonshire Building | 2017-06-18 05:45 | 50414.5811 | 39.996
Devonshire Building | 2017-06-18 06:00 | 50414.5911 | 39.996
Devonshire Building | 2017-06-18 06:15 | 50414.6011 | 39.996
Devonshire Building | 2017-06-18 06:30 | 50414.6111 | 39.996
Devonshire Building | 2017-06-18 06:45 | 50414.6211 | 39.996
Devonshire Building | 2017-06-18 07:00 | 50414.6311 | 39.996
Devonshire Building | 2017-06-18 07:15 | 50414.6411 | 39.996
Devonshire Building | 2017-06-18 07:30 | 50414.6461 | 20.016
Devonshire Building | 2017-06-18 07:45 | 50414.6561 | 39.996
Devonshire Building | 2017-06-18 08:00 | 50414.6661 | 39.996
Devonshire Building | 2017-06-18 08:15 | 50414.6711 | 20.016
Devonshire Building | 2017-06-18 08:30 | 50414.6811 | 39.996
Devonshire Building | 2017-06-18 08:45 | 50414.6861 | 20.016
Devonshire Building | 2017-06-18 09:00 | 50414.7061 | 79.992
Devonshire Building | 2017-06-18 09:15 | 50414.7111 | 20.016
Devonshire Building | 2017-06-18 09:30 | 50414.7161 | 20.016
Devonshire Building | 2017-06-18 09:45 | 50414.7261 | 39.996
Devonshire Building | 2017-06-18 10:00 | 50414.7311 | 20.016
Devonshire Building | 2017-06-18 10:15 | 50414.7411 | 39.996
Devonshire Building | 2017-06-18 10:30 | 50414.7461 | 20.016
Devonshire Building | 2017-06-18 10:45 | 50414.7511 | 20.016
Devonshire Building | 2017-06-18 11:00 | 50414.7611 | 39.996
Devonshire Building | 2017-06-18 11:15 | 50414.7661 | 20.016
Devonshire Building | 2017-06-18 11:30 | 50414.7761 | 39.996
Devonshire Building | 2017-06-18 11:45 | 50414.7811 | 20.016
Devonshire Building | 2017-06-18 12:00 | 50414.7911 | 39.996
Devonshire Building | 2017-06-18 12:15 | 50414.7961 | 20.016
Devonshire Building | 2017-06-18 12:30 | 50414.8061 | 39.996
Devonshire Building | 2017-06-18 12:45 | 50414.8111 | 20.016
Devonshire Building | 2017-06-18 13:00 | 50414.8161 | 20.016
Devonshire Building | 2017-06-18 13:15 | 50414.8261 | 39.996
Devonshire Building | 2017-06-18 13:30 | 50414.8311 | 20.016
Devonshire Building | 2017-06-18 13:45 | 50414.8461 | 60.012
Devonshire Building | 2017-06-18 14:00 | 50414.8661 | 79.992
Devonshire Building | 2017-06-18 14:15 | 50414.8911 | 100.008
Devonshire Building | 2017-06-18 14:30 | 50414.9111 | 79.992
Devonshire Building | 2017-06-18 14:45 | 50414.9361 | 100.008
Devonshire Building | 2017-06-18 15:00 | 50414.9611 | 100.008
Devonshire Building | 2017-06-18 15:15 | 50414.9811 | 79.992
Devonshire Building | 2017-06-18 15:30 | 50415.0011 | 79.992
Devonshire Building | 2017-06-18 15:45 | 50415.0061 | 20.016
Devonshire Building | 2017-06-18 16:00 | 50415.0161 | 39.996
Devonshire Building | 2017-06-18 16:15 | 50415.0211 | 20.016
Devonshire Building | 2017-06-18 16:30 | 50415.0261 | 20.016
Devonshire Building | 2017-06-18 16:45 | 50415.0312 | 20.016
Devonshire Building | 2017-06-18 17:00 | 50415.0412 | 39.996
Devonshire Building | 2017-06-18 17:15 | 50415.0462 | 20.016
Devonshire Building | 2017-06-18 17:30 | 50415.0512 | 20.016
Devonshire Building | 2017-06-18 17:45 | 50415.0562 | 20.016
Devonshire Building | 2017-06-18 18:00 | 50415.0612 | 20.016
Devonshire Building | 2017-06-18 18:15 | 50415.0662 | 20.016
Devonshire Building | 2017-06-18 18:30 | 50415.0762 | 39.996
Devonshire Building | 2017-06-18 18:45 | 50415.0812 | 20.016
Devonshire Building | 2017-06-18 19:00 | 50415.0912 | 39.996
Devonshire Building | 2017-06-18 19:15 | 50415.0962 | 20.016
Devonshire Building | 2017-06-18 19:30 | 50415.1012 | 20.016
Devonshire Building | 2017-06-18 19:45 | 50415.1062 | 20.016
Devonshire Building | 2017-06-18 20:00 | 50415.1112 | 20.016
Devonshire Building | 2017-06-18 20:15 | 50415.1162 | 20.016
Devonshire Building | 2017-06-18 20:30 | 50415.1262 | 39.996
Devonshire Building | 2017-06-18 20:45 | 50415.5712 | 1779.984
Devonshire Building | 2017-06-18 21:00 | 50415.6412 | 280.008
Devonshire Building | 2017-06-18 21:15 | 50415.6462 | 20.016
Devonshire Building | 2017-06-18 21:30 | 50415.6562 | 39.996
Devonshire Building | 2017-06-18 21:45 | 50415.6612 | 20.016
Devonshire Building | 2017-06-18 22:00 | 50415.6662 | 20.016
Devonshire Building | 2017-06-18 22:15 | 50415.6712 | 20.016
Devonshire Building | 2017-06-18 22:30 | 50415.6762 | 20.016
Devonshire Building | 2017-06-18 22:45 | 50415.6812 | 20.016
Devonshire Building | 2017-06-18 23:00 | 50415.6862 | 20.016
Devonshire Building | 2017-06-18 23:15 | 50415.6962 | 39.996
Devonshire Building | 2017-06-18 23:30 | 50415.7012 | 20.016
Devonshire Building | 2017-06-18 23:45 | 50415.7062 | 20.016
Devonshire Building | 2017-06-19 | 50415.7148 | 39.996
Devonshire Building | 2017-06-19 00:15 | 50415.7198 | 20.016
Devonshire Building | 2017-06-19 00:30 | 50415.7298 | 39.996
Devonshire Building | 2017-06-19 00:45 | 50415.7398 | 39.996
Devonshire Building | 2017-06-19 01:00 | 50415.7448 | 20.016
Devonshire Building | 2017-06-19 01:15 | 50415.7548 | 39.996
Devonshire Building | 2017-06-19 01:30 | 50415.7648 | 39.996
Devonshire Building | 2017-06-19 01:45 | 50415.7698 | 20.016
Devonshire Building | 2017-06-19 02:00 | 50415.7798 | 39.996
Devonshire Building | 2017-06-19 02:15 | 50415.7898 | 39.996
Devonshire Building | 2017-06-19 02:30 | 50415.7948 | 20.016
Devonshire Building | 2017-06-19 02:45 | 50415.8048 | 39.996
Devonshire Building | 2017-06-19 03:00 | 50415.8148 | 39.996
Devonshire Building | 2017-06-19 03:15 | 50415.8199 | 20.016
Devonshire Building | 2017-06-19 03:30 | 50415.8299 | 39.996
Devonshire Building | 2017-06-19 03:45 | 50415.8349 | 20.016
Devonshire Building | 2017-06-19 04:00 | 50415.8449 | 39.996
Devonshire Building | 2017-06-19 04:15 | 50415.8499 | 20.016
Devonshire Building | 2017-06-19 04:30 | 50415.8599 | 39.996
Devonshire Building | 2017-06-19 04:45 | 50415.8649 | 20.016
Devonshire Building | 2017-06-19 05:00 | 50415.8749 | 39.996
Devonshire Building | 2017-06-19 05:15 | 50415.8799 | 20.016
Devonshire Building | 2017-06-19 05:30 | 50415.8899 | 39.996
Devonshire Building | 2017-06-19 05:45 | 50415.8949 | 20.016
Devonshire Building | 2017-06-19 06:00 | 50415.9099 | 60.012
Devonshire Building | 2017-06-19 06:15 | 50415.9249 | 60.012
Devonshire Building | 2017-06-19 06:30 | 50415.9349 | 39.996
Devonshire Building | 2017-06-19 06:45 | 50415.9449 | 39.996
Devonshire Building | 2017-06-19 07:00 | 50415.9549 | 39.996
Devonshire Building | 2017-06-19 07:15 | 50415.9699 | 60.012
Devonshire Building | 2017-06-19 07:30 | 50416.4249 | 1820.016
Devonshire Building | 2017-06-19 07:45 | 50416.5349 | 439.992
Devonshire Building | 2017-06-19 08:00 | 50416.5649 | 119.988
Devonshire Building | 2017-06-19 08:15 | 50416.6349 | 280.008
Devonshire Building | 2017-06-19 08:30 | 50416.6849 | 200.016
Devonshire Building | 2017-06-19 08:45 | 50416.7499 | 259.992
Devonshire Building | 2017-06-19 09:00 | 50416.8249 | 299.988
Devonshire Building | 2017-06-19 09:15 | 50417.4499 | 2499.984
Devonshire Building | 2017-06-19 09:30 | 50417.5399 | 360
Devonshire Building | 2017-06-19 09:45 | 50417.6299 | 360
Devonshire Building | 2017-06-19 10:00 | 50417.7149 | 339.984
Devonshire Building | 2017-06-19 10:15 | 50417.8099 | 380.016
Devonshire Building | 2017-06-19 10:30 | 50418.1099 | 1199.988
Devonshire Building | 2017-06-19 10:45 | 50418.6949 | 2340
Devonshire Building | 2017-06-19 11:00 | 50418.8449 | 600.012
Devonshire Building | 2017-06-19 11:15 | 50418.9999 | 619.992
Devonshire Building | 2017-06-19 11:30 | 50419.1499 | 600.012
Devonshire Building | 2017-06-19 11:45 | 50419.2699 | 479.988
Devonshire Building | 2017-06-19 12:00 | 50419.8849 | 2459.988
Devonshire Building | 2017-06-19 12:15 | 50419.9499 | 259.992
Devonshire Building | 2017-06-19 12:30 | 50420.0149 | 259.992
Devonshire Building | 2017-06-19 12:45 | 50420.0799 | 259.992
Devonshire Building | 2017-06-19 13:00 | 50420.1599 | 320.004
Devonshire Building | 2017-06-19 13:15 | 50420.6399 | 1919.988
Devonshire Building | 2017-06-19 13:30 | 50420.8449 | 820.008
Devonshire Building | 2017-06-19 13:45 | 50420.9099 | 259.992
Devonshire Building | 2017-06-19 14:00 | 50420.9849 | 299.988
Devonshire Building | 2017-06-19 14:15 | 50421.0549 | 280.008
Devonshire Building | 2017-06-19 14:30 | 50421.1249 | 280.008
Devonshire Building | 2017-06-19 14:45 | 50421.6949 | 2279.988
Devonshire Building | 2017-06-19 15:00 | 50421.7749 | 320.004
Devonshire Building | 2017-06-19 15:15 | 50421.8449 | 280.008
Devonshire Building | 2017-06-19 15:30 | 50421.9249 | 320.004
Devonshire Building | 2017-06-19 15:45 | 50421.9999 | 299.988
Devonshire Building | 2017-06-19 16:00 | 50422.1949 | 780.012
Devonshire Building | 2017-06-19 16:15 | 50422.7299 | 2139.984
Devonshire Building | 2017-06-19 16:30 | 50422.8449 | 460.008
Devonshire Building | 2017-06-19 16:45 | 50422.9399 | 380.016
Devonshire Building | 2017-06-19 17:00 | 50423.0049 | 259.992
Devonshire Building | 2017-06-19 17:15 | 50423.0599 | 219.996
Devonshire Building | 2017-06-19 17:30 | 50423.1049 | 180
Devonshire Building | 2017-06-19 17:45 | 50423.1349 | 119.988
Devonshire Building | 2017-06-19 18:00 | 50423.1649 | 119.988
Devonshire Building | 2017-06-19 18:15 | 50423.1899 | 100.008
Devonshire Building | 2017-06-19 18:30 | 50423.2099 | 79.992
Devonshire Building | 2017-06-19 18:45 | 50423.2298 | 79.992
Devonshire Building | 2017-06-19 19:00 | 50423.2498 | 79.992
Devonshire Building | 2017-06-19 19:15 | 50423.2648 | 60.012
Devonshire Building | 2017-06-19 19:30 | 50423.2799 | 60.012
Devonshire Building | 2017-06-19 19:45 | 50423.2949 | 60.012
Devonshire Building | 2017-06-19 20:00 | 50423.3049 | 39.996
Devonshire Building | 2017-06-19 20:15 | 50423.3199 | 60.012
Devonshire Building | 2017-06-19 20:30 | 50423.3399 | 79.992
Devonshire Building | 2017-06-19 20:45 | 50423.3699 | 119.988
Devonshire Building | 2017-06-19 21:00 | 50423.3749 | 20.016
Devonshire Building | 2017-06-19 21:15 | 50423.3799 | 20.016
Devonshire Building | 2017-06-19 21:30 | 50423.3849 | 20.016
Devonshire Building | 2017-06-19 21:45 | 50423.3899 | 20.016
Devonshire Building | 2017-06-19 22:00 | 50423.3949 | 20.016
Devonshire Building | 2017-06-19 22:15 | 50423.3999 | 20.016
Devonshire Building | 2017-06-19 22:30 | 50423.4049 | 20.016
Devonshire Building | 2017-06-19 22:45 | 50423.4049 | 0
Devonshire Building | 2017-06-19 23:00 | 50423.4099 | 20.016
Devonshire Building | 2017-06-19 23:15 | 50423.4149 | 20.016
Devonshire Building | 2017-06-19 23:30 | 50423.4199 | 20.016
Devonshire Building | 2017-06-19 23:45 | 50423.4249 | 20.016
Devonshire Building | 2017-06-20 | 50423.4258 | 0
Devonshire Building | 2017-06-20 00:15 | 50423.4308 | 20.016
Devonshire Building | 2017-06-20 00:30 | 50423.4358 | 20.016
Devonshire Building | 2017-06-20 00:45 | 50423.4408 | 20.016
Devonshire Building | 2017-06-20 01:00 | 50423.4408 | 0
Devonshire Building | 2017-06-20 01:15 | 50423.4458 | 20.016
Devonshire Building | 2017-06-20 01:30 | 50423.4508 | 20.016
Devonshire Building | 2017-06-20 01:45 | 50423.4558 | 20.016
Devonshire Building | 2017-06-20 02:00 | 50423.4608 | 20.016
Devonshire Building | 2017-06-20 02:15 | 50423.4608 | 0
Devonshire Building | 2017-06-20 02:30 | 50423.4658 | 20.016
Devonshire Building | 2017-06-20 02:45 | 50423.4708 | 20.016
Devonshire Building | 2017-06-20 03:00 | 50423.4758 | 20.016
Devonshire Building | 2017-06-20 03:15 | 50423.4758 | 0
Devonshire Building | 2017-06-20 03:30 | 50423.4808 | 20.016
Devonshire Building | 2017-06-20 03:45 | 50423.4858 | 20.016
Devonshire Building | 2017-06-20 04:00 | 50423.4908 | 20.016
Devonshire Building | 2017-06-20 04:15 | 50423.4908 | 0
Devonshire Building | 2017-06-20 04:30 | 50423.4958 | 20.016
Devonshire Building | 2017-06-20 04:45 | 50423.5008 | 20.016
Devonshire Building | 2017-06-20 05:00 | 50423.5008 | 0
Devonshire Building | 2017-06-20 05:15 | 50423.5058 | 20.016
Devonshire Building | 2017-06-20 05:30 | 50423.5108 | 20.016
Devonshire Building | 2017-06-20 05:45 | 50424.0109 | 2000.016
Devonshire Building | 2017-06-20 06:00 | 50424.0159 | 20.016
Devonshire Building | 2017-06-20 06:15 | 50424.0209 | 20.016
Devonshire Building | 2017-06-20 06:30 | 50424.0309 | 39.996
Devonshire Building | 2017-06-20 06:45 | 50424.0359 | 20.016
Devonshire Building | 2017-06-20 07:00 | 50424.0459 | 39.996
Devonshire Building | 2017-06-20 07:15 | 50424.0509 | 20.016
Devonshire Building | 2017-06-20 07:30 | 50424.0709 | 79.992
Devonshire Building | 2017-06-20 07:45 | 50424.1009 | 119.988
Devonshire Building | 2017-06-20 08:00 | 50424.1409 | 159.984
Devonshire Building | 2017-06-20 08:15 | 50424.6959 | 2220.012
Devonshire Building | 2017-06-20 08:30 | 50424.7359 | 159.984
Devonshire Building | 2017-06-20 08:45 | 50424.7809 | 180
Devonshire Building | 2017-06-20 09:00 | 50424.8309 | 200.016
Devonshire Building | 2017-06-20 09:15 | 50424.9309 | 399.996
Devonshire Building | 2017-06-20 09:30 | 50425.0659 | 540
Devonshire Building | 2017-06-20 09:45 | 50425.7959 | 2919.996
Devonshire Building | 2017-06-20 10:00 | 50426.0209 | 900
Devonshire Building | 2017-06-20 10:15 | 50426.1459 | 500.004
Devonshire Building | 2017-06-20 10:30 | 50426.2709 | 500.004
Devonshire Building | 2017-06-20 10:45 | 50426.3809 | 439.992
Devonshire Building | 2017-06-20 11:00 | 50426.7009 | 1280.016
Devonshire Building | 2017-06-20 11:15 | 50427.2159 | 2059.992
Devonshire Building | 2017-06-20 11:30 | 50427.3859 | 680.004
Devonshire Building | 2017-06-20 11:45 | 50427.5309 | 579.996
Devonshire Building | 2017-06-20 12:00 | 50427.6559 | 500.004
Devonshire Building | 2017-06-20 12:15 | 50427.7459 | 360
Devonshire Building | 2017-06-20 12:30 | 50428.3759 | 2520
Devonshire Building | 2017-06-20 12:45 | 50428.4959 | 479.988
Devonshire Building | 2017-06-20 13:00 | 50428.6059 | 439.992
Devonshire Building | 2017-06-20 13:15 | 50428.6809 | 299.988
Devonshire Building | 2017-06-20 13:30 | 50428.7509 | 280.008
Devonshire Building | 2017-06-20 13:45 | 50428.8009 | 200.016
Devonshire Building | 2017-06-20 14:00 | 50428.8559 | 219.996
Devonshire Building | 2017-06-20 14:15 | 50429.4609 | 2419.992
Devonshire Building | 2017-06-20 14:30 | 50429.5159 | 219.996
Devonshire Building | 2017-06-20 14:45 | 50429.5759 | 240.012
Devonshire Building | 2017-06-20 15:00 | 50429.7159 | 560.016
Devonshire Building | 2017-06-20 15:15 | 50430.0359 | 1280.016
Devonshire Building | 2017-06-20 15:30 | 50430.2459 | 839.988
Devonshire Building | 2017-06-20 15:45 | 50430.8909 | 2580.012
Devonshire Building | 2017-06-20 16:00 | 50430.9759 | 339.984
Devonshire Building | 2017-06-20 16:15 | 50431.0409 | 259.992
Devonshire Building | 2017-06-20 16:30 | 50431.0959 | 219.996
Devonshire Building | 2017-06-20 16:45 | 50431.1359 | 159.984
Devonshire Building | 2017-06-20 17:00 | 50431.1759 | 159.984
Devonshire Building | 2017-06-20 17:15 | 50431.2058 | 119.988
Devonshire Building | 2017-06-20 17:30 | 50431.2358 | 119.988
Devonshire Building | 2017-06-20 17:45 | 50431.7758 | 2160
Devonshire Building | 2017-06-20 18:00 | 50431.7908 | 60.012
Devonshire Building | 2017-06-20 18:15 | 50431.8059 | 60.012
Devonshire Building | 2017-06-20 18:30 | 50431.8109 | 20.016
Devonshire Building | 2017-06-20 18:45 | 50431.8209 | 39.996
Devonshire Building | 2017-06-20 19:00 | 50431.8309 | 39.996
Devonshire Building | 2017-06-20 19:15 | 50431.8359 | 20.016
Devonshire Building | 2017-06-20 19:30 | 50431.8509 | 60.012
Devonshire Building | 2017-06-20 19:45 | 50431.8759 | 100.008
Devonshire Building | 2017-06-20 20:00 | 50431.9009 | 100.008
Devonshire Building | 2017-06-20 20:15 | 50431.9259 | 100.008
Devonshire Building | 2017-06-20 20:30 | 50431.9559 | 119.988
Devonshire Building | 2017-06-20 20:45 | 50431.9959 | 159.984
Devonshire Building | 2017-06-20 21:00 | 50432.0309 | 140.004
Devonshire Building | 2017-06-20 21:15 | 50432.0709 | 159.984
Devonshire Building | 2017-06-20 21:30 | 50432.1059 | 140.004
Devonshire Building | 2017-06-20 21:45 | 50432.1359 | 119.988
Devonshire Building | 2017-06-20 22:00 | 50432.1609 | 100.008
Devonshire Building | 2017-06-20 22:15 | 50432.1859 | 100.008
Devonshire Building | 2017-06-20 22:30 | 50432.2109 | 100.008
Devonshire Building | 2017-06-20 22:45 | 50432.2359 | 100.008
Devonshire Building | 2017-06-20 23:00 | 50432.2659 | 119.988
Devonshire Building | 2017-06-20 23:15 | 50432.2909 | 100.008
Devonshire Building | 2017-06-20 23:30 | 50432.3209 | 119.988
Devonshire Building | 2017-06-20 23:45 | 50432.3509 | 119.988
Devonshire Building | 2017-06-21 | 50432.3789 | 119.988
Devonshire Building | 2017-06-21 00:15 | 50432.4089 | 119.988
Devonshire Building | 2017-06-21 00:30 | 50432.4339 | 100.008
Devonshire Building | 2017-06-21 00:45 | 50432.4639 | 119.988
Devonshire Building | 2017-06-21 01:00 | 50432.4939 | 119.988
Devonshire Building | 2017-06-21 01:15 | 50432.5239 | 119.988
Devonshire Building | 2017-06-21 01:30 | 50432.5539 | 119.988
Devonshire Building | 2017-06-21 01:45 | 50432.5839 | 119.988
Devonshire Building | 2017-06-21 02:00 | 50432.6139 | 119.988
Devonshire Building | 2017-06-21 02:15 | 50432.6439 | 119.988
Devonshire Building | 2017-06-21 02:30 | 50432.6689 | 100.008
Devonshire Building | 2017-06-21 02:45 | 50432.6989 | 119.988
Devonshire Building | 2017-06-21 03:00 | 50432.7289 | 119.988
Devonshire Building | 2017-06-21 03:15 | 50432.7589 | 119.988
Devonshire Building | 2017-06-21 03:30 | 50432.7889 | 119.988
Devonshire Building | 2017-06-21 03:45 | 50432.8189 | 119.988
Devonshire Building | 2017-06-21 04:00 | 50432.8489 | 119.988
Devonshire Building | 2017-06-21 04:15 | 50432.8789 | 119.988
Devonshire Building | 2017-06-21 04:30 | 50432.9039 | 100.008
Devonshire Building | 2017-06-21 04:45 | 50432.9339 | 119.988
Devonshire Building | 2017-06-21 05:00 | 50432.9639 | 119.988
Devonshire Building | 2017-06-21 05:15 | 50432.9939 | 119.988
Devonshire Building | 2017-06-21 05:30 | 50433.0239 | 119.988
Devonshire Building | 2017-06-21 05:45 | 50433.0539 | 119.988
Devonshire Building | 2017-06-21 06:00 | 50433.0839 | 119.988
Devonshire Building | 2017-06-21 06:15 | 50433.1139 | 119.988
Devonshire Building | 2017-06-21 06:30 | 50433.1389 | 100.008
Devonshire Building | 2017-06-21 06:45 | 50433.6939 | 2220.012
Devonshire Building | 2017-06-21 07:00 | 50433.7439 | 200.016
Devonshire Building | 2017-06-21 07:15 | 50433.8239 | 320.004
Devonshire Building | 2017-06-21 07:30 | 50433.9089 | 339.984
Devonshire Building | 2017-06-21 07:45 | 50433.9839 | 299.988
Devonshire Building | 2017-06-21 08:00 | 50434.0539 | 280.008
Devonshire Building | 2017-06-21 08:15 | 50434.1239 | 280.008
Devonshire Building | 2017-06-21 08:30 | 50434.1889 | 259.992
Devonshire Building | 2017-06-21 08:45 | 50434.2439 | 219.996
Devonshire Building | 2017-06-21 09:00 | 50434.8289 | 2340
Devonshire Building | 2017-06-21 09:15 | 50434.8688 | 159.984
Devonshire Building | 2017-06-21 09:30 | 50434.9088 | 159.984
Devonshire Building | 2017-06-21 09:45 | 50434.9638 | 219.996
Devonshire Building | 2017-06-21 10:00 | 50435.0038 | 159.984
Devonshire Building | 2017-06-21 10:15 | 50435.5938 | 2360.016
Devonshire Building | 2017-06-21 10:30 | 50435.6588 | 259.992
Devonshire Building | 2017-06-21 10:45 | 50435.7388 | 320.004
Devonshire Building | 2017-06-21 11:00 | 50435.8238 | 339.984
Devonshire Building | 2017-06-21 11:15 | 50435.9088 | 339.984
Devonshire Building | 2017-06-21 11:30 | 50435.9888 | 320.004
Devonshire Building | 2017-06-21 11:45 | 50436.5688 | 2319.984
Devonshire Building | 2017-06-21 12:00 | 50436.6438 | 299.988
Devonshire Building | 2017-06-21 12:15 | 50436.7288 | 339.984
Devonshire Building | 2017-06-21 12:30 | 50436.8188 | 360
Devonshire Building | 2017-06-21 12:45 | 50436.9038 | 339.984
Devonshire Building | 2017-06-21 13:00 | 50436.9888 | 339.984
Devonshire Building | 2017-06-21 13:15 | 50437.6038 | 2459.988
Devonshire Building | 2017-06-21 13:30 | 50437.6738 | 280.008
Devonshire Building | 2017-06-21 13:45 | 50437.7588 | 339.984
Devonshire Building | 2017-06-21 14:00 | 50437.8438 | 339.984
Devonshire Building | 2017-06-21 14:15 | 50437.9138 | 280.008
Devonshire Building | 2017-06-21 14:30 | 50437.9838 | 280.008
Devonshire Building | 2017-06-21 14:45 | 50438.2688 | 1140.012
Devonshire Building | 2017-06-21 15:00 | 50438.6388 | 1479.996
Devonshire Building | 2017-06-21 15:15 | 50438.6988 | 240.012
Devonshire Building | 2017-06-21 15:30 | 50438.7538 | 219.996
Devonshire Building | 2017-06-21 15:45 | 50438.7988 | 180
Devonshire Building | 2017-06-21 16:00 | 50439.2688 | 1879.992
Devonshire Building | 2017-06-21 16:15 | 50439.4138 | 579.996
Devonshire Building | 2017-06-21 16:30 | 50439.4538 | 159.984
Devonshire Building | 2017-06-21 16:45 | 50439.5038 | 200.016
Devonshire Building | 2017-06-21 17:00 | 50439.5538 | 200.016
Devonshire Building | 2017-06-21 17:15 | 50439.7188 | 659.988
Devonshire Building | 2017-06-21 17:30 | 50439.8588 | 560.016
Devonshire Building | 2017-06-21 17:45 | 50439.9538 | 380.016
Devonshire Building | 2017-06-21 18:00 | 50440.0188 | 259.992
Devonshire Building | 2017-06-21 18:15 | 50440.0688 | 200.016
Devonshire Building | 2017-06-21 18:30 | 50440.1088 | 159.984
Devonshire Building | 2017-06-21 18:45 | 50440.1438 | 140.004
Devonshire Building | 2017-06-21 19:00 | 50440.1688 | 100.008
Devonshire Building | 2017-06-21 19:15 | 50440.1938 | 100.008
Devonshire Building | 2017-06-21 19:30 | 50440.2238 | 119.988
Devonshire Building | 2017-06-21 19:45 | 50440.2438 | 79.992
Devonshire Building | 2017-06-21 20:00 | 50440.2638 | 79.992
Devonshire Building | 2017-06-21 20:15 | 50440.2788 | 60.012
Devonshire Building | 2017-06-21 20:30 | 50440.7938 | 2059.992
Devonshire Building | 2017-06-21 20:45 | 50440.8038 | 39.996
Devonshire Building | 2017-06-21 21:00 | 50440.8088 | 20.016
Devonshire Building | 2017-06-21 21:15 | 50440.8188 | 39.996
Devonshire Building | 2017-06-21 21:30 | 50440.8238 | 20.016
Devonshire Building | 2017-06-21 21:45 | 50440.8288 | 20.016
Devonshire Building | 2017-06-21 22:00 | 50440.8338 | 20.016
Devonshire Building | 2017-06-21 22:15 | 50440.8388 | 20.016
Devonshire Building | 2017-06-21 22:30 | 50440.8488 | 39.996
Devonshire Building | 2017-06-21 22:45 | 50440.8538 | 20.016
Devonshire Building | 2017-06-21 23:00 | 50440.8588 | 20.016
Devonshire Building | 2017-06-21 23:15 | 50440.8638 | 20.016
Devonshire Building | 2017-06-21 23:30 | 50440.8689 | 20.016
Devonshire Building | 2017-06-21 23:45 | 50440.8789 | 39.996
Devonshire Building | 2017-06-22 | 50440.8828 | 20.016
Devonshire Building | 2017-06-22 00:15 | 50440.8878 | 20.016
Devonshire Building | 2017-06-22 00:30 | 50440.8978 | 39.996
Devonshire Building | 2017-06-22 00:45 | 50440.9028 | 20.016
Devonshire Building | 2017-06-22 01:00 | 50440.9078 | 20.016
Devonshire Building | 2017-06-22 01:15 | 50440.9128 | 20.016
Devonshire Building | 2017-06-22 01:30 | 50440.9228 | 39.996
Devonshire Building | 2017-06-22 01:45 | 50440.9278 | 20.016
Devonshire Building | 2017-06-22 02:00 | 50440.9328 | 20.016
Devonshire Building | 2017-06-22 02:15 | 50440.9378 | 20.016
Devonshire Building | 2017-06-22 02:30 | 50440.9428 | 20.016
Devonshire Building | 2017-06-22 02:45 | 50440.9528 | 39.996
Devonshire Building | 2017-06-22 03:00 | 50440.9578 | 20.016
Devonshire Building | 2017-06-22 03:15 | 50440.9628 | 20.016
Devonshire Building | 2017-06-22 03:30 | 50440.9679 | 20.016
Devonshire Building | 2017-06-22 03:45 | 50440.9729 | 20.016
Devonshire Building | 2017-06-22 04:00 | 50440.9779 | 20.016
Devonshire Building | 2017-06-22 04:15 | 50440.9829 | 20.016
Devonshire Building | 2017-06-22 04:30 | 50440.9929 | 39.996
Devonshire Building | 2017-06-22 04:45 | 50440.9979 | 20.016
Devonshire Building | 2017-06-22 05:00 | 50441.0029 | 20.016
Devonshire Building | 2017-06-22 05:15 | 50441.0079 | 20.016
Devonshire Building | 2017-06-22 05:30 | 50441.0129 | 20.016
Devonshire Building | 2017-06-22 05:45 | 50441.0179 | 20.016
Devonshire Building | 2017-06-22 06:00 | 50441.0279 | 39.996
Devonshire Building | 2017-06-22 06:15 | 50441.0329 | 20.016
Devonshire Building | 2017-06-22 06:30 | 50441.0429 | 39.996
Devonshire Building | 2017-06-22 06:45 | 50441.0479 | 20.016
Devonshire Building | 2017-06-22 07:00 | 50441.5679 | 2080.008
Devonshire Building | 2017-06-22 07:15 | 50441.5779 | 39.996
Devonshire Building | 2017-06-22 07:30 | 50441.5929 | 60.012
Devonshire Building | 2017-06-22 07:45 | 50441.6079 | 60.012
Devonshire Building | 2017-06-22 08:00 | 50441.6229 | 60.012
Devonshire Building | 2017-06-22 08:15 | 50441.6679 | 180
Devonshire Building | 2017-06-22 08:30 | 50441.7529 | 339.984
Devonshire Building | 2017-06-22 08:45 | 50441.8679 | 460.008
Devonshire Building | 2017-06-22 09:00 | 50442.1129 | 979.992
Devonshire Building | 2017-06-22 09:15 | 50442.7029 | 2360.016
Devonshire Building | 2017-06-22 09:30 | 50442.8679 | 659.988
Devonshire Building | 2017-06-22 09:45 | 50443.0079 | 560.016
Devonshire Building | 2017-06-22 10:00 | 50443.1279 | 479.988
Devonshire Building | 2017-06-22 10:15 | 50443.2279 | 399.996
Devonshire Building | 2017-06-22 10:30 | 50443.8379 | 2440.008
Devonshire Building | 2017-06-22 10:45 | 50443.8979 | 240.012
Devonshire Building | 2017-06-22 11:00 | 50443.9629 | 259.992
Devonshire Building | 2017-06-22 11:15 | 50444.0229 | 240.012
Devonshire Building | 2017-06-22 11:30 | 50444.0729 | 200.016
Devonshire Building | 2017-06-22 11:45 | 50444.6529 | 2319.984
Devonshire Building | 2017-06-22 12:00 | 50444.6879 | 140.004
Devonshire Building | 2017-06-22 12:15 | 50444.7279 | 159.984
Devonshire Building | 2017-06-22 12:30 | 50444.7779 | 200.016
Devonshire Building | 2017-06-22 12:45 | 50444.8229 | 180
Devonshire Building | 2017-06-22 13:00 | 50444.8679 | 180
Devonshire Building | 2017-06-22 13:15 | 50445.3429 | 1900.008
Devonshire Building | 2017-06-22 13:30 | 50445.4679 | 500.004
Devonshire Building | 2017-06-22 13:45 | 50445.5129 | 180
Devonshire Building | 2017-06-22 14:00 | 50445.5579 | 180
Devonshire Building | 2017-06-22 14:15 | 50445.6079 | 200.016
Devonshire Building | 2017-06-22 14:30 | 50445.6529 | 180
Devonshire Building | 2017-06-22 14:45 | 50446.0929 | 1760.004
Devonshire Building | 2017-06-22 15:00 | 50446.2729 | 720
Devonshire Building | 2017-06-22 15:15 | 50446.3129 | 159.984
Devonshire Building | 2017-06-22 15:30 | 50446.3429 | 119.988
Devonshire Building | 2017-06-22 15:45 | 50446.3779 | 140.004
Devonshire Building | 2017-06-22 16:00 | 50446.4129 | 140.004
Devonshire Building | 2017-06-22 16:15 | 50446.5979 | 740.016
Devonshire Building | 2017-06-22 16:30 | 50446.9979 | 1599.984
Devonshire Building | 2017-06-22 16:45 | 50447.0279 | 119.988
Devonshire Building | 2017-06-22 17:00 | 50447.0579 | 119.988
Devonshire Building | 2017-06-22 17:15 | 50447.0879 | 119.988
Devonshire Building | 2017-06-22 17:30 | 50447.1129 | 100.008
Devonshire Building | 2017-06-22 17:45 | 50447.1429 | 119.988
Devonshire Building | 2017-06-22 18:00 | 50447.1729 | 119.988
Devonshire Building | 2017-06-22 18:15 | 50447.1979 | 100.008
Devonshire Building | 2017-06-22 18:30 | 50447.2229 | 100.008
Devonshire Building | 2017-06-22 18:45 | 50447.2479 | 100.008
Devonshire Building | 2017-06-22 19:00 | 50447.2729 | 100.008
Devonshire Building | 2017-06-22 19:15 | 50447.2929 | 79.992
Devonshire Building | 2017-06-22 19:30 | 50447.3179 | 100.008
Devonshire Building | 2017-06-22 19:45 | 50447.3379 | 79.992
Devonshire Building | 2017-06-22 20:00 | 50447.3629 | 100.008
Devonshire Building | 2017-06-22 20:15 | 50447.3829 | 79.992
Devonshire Building | 2017-06-22 20:30 | 50447.4029 | 79.992
Devonshire Building | 2017-06-22 20:45 | 50447.4429 | 159.984
Devonshire Building | 2017-06-22 21:00 | 50447.4579 | 60.012
Devonshire Building | 2017-06-22 21:15 | 50447.4729 | 60.012
Devonshire Building | 2017-06-22 21:30 | 50447.4879 | 60.012
Devonshire Building | 2017-06-22 21:45 | 50447.4979 | 39.996
Devonshire Building | 2017-06-22 22:00 | 50447.5129 | 60.012
Devonshire Building | 2017-06-22 22:15 | 50447.5279 | 60.012
Devonshire Building | 2017-06-22 22:30 | 50447.5379 | 39.996
Devonshire Building | 2017-06-22 22:45 | 50447.5529 | 60.012
Devonshire Building | 2017-06-22 23:00 | 50447.5679 | 60.012
Devonshire Building | 2017-06-22 23:15 | 50447.5779 | 39.996
Devonshire Building | 2017-06-22 23:30 | 50447.5929 | 60.012
Devonshire Building | 2017-06-22 23:45 | 50447.6079 | 60.012
Devonshire Building | 2017-06-23 | 50447.6211 | 39.996
Devonshire Building | 2017-06-23 00:15 | 50447.6361 | 60.012
Devonshire Building | 2017-06-23 00:30 | 50447.6461 | 39.996
Devonshire Building | 2017-06-23 00:45 | 50447.6611 | 60.012
Devonshire Building | 2017-06-23 01:00 | 50447.6711 | 39.996
Devonshire Building | 2017-06-23 01:15 | 50447.6861 | 60.012
Devonshire Building | 2017-06-23 01:30 | 50447.6961 | 39.996
Devonshire Building | 2017-06-23 01:45 | 50447.7111 | 60.012
Devonshire Building | 2017-06-23 02:00 | 50447.7211 | 39.996
Devonshire Building | 2017-06-23 02:15 | 50447.7311 | 39.996
Devonshire Building | 2017-06-23 02:30 | 50447.7461 | 60.012
Devonshire Building | 2017-06-23 02:45 | 50447.7561 | 39.996
Devonshire Building | 2017-06-23 03:00 | 50447.7661 | 39.996
Devonshire Building | 2017-06-23 03:15 | 50447.7811 | 60.012
Devonshire Building | 2017-06-23 03:30 | 50447.7911 | 39.996
Devonshire Building | 2017-06-23 03:45 | 50447.8011 | 39.996
Devonshire Building | 2017-06-23 04:00 | 50448.3211 | 2080.008
Devonshire Building | 2017-06-23 04:15 | 50448.3311 | 39.996
Devonshire Building | 2017-06-23 04:30 | 50448.3361 | 20.016
Devonshire Building | 2017-06-23 04:45 | 50448.3411 | 20.016
Devonshire Building | 2017-06-23 05:00 | 50448.3461 | 20.016
Devonshire Building | 2017-06-23 05:15 | 50448.3511 | 20.016
Devonshire Building | 2017-06-23 05:30 | 50448.3611 | 39.996
Devonshire Building | 2017-06-23 05:45 | 50448.3661 | 20.016
Devonshire Building | 2017-06-23 06:00 | 50448.3711 | 20.016
Devonshire Building | 2017-06-23 06:15 | 50448.3811 | 39.996
Devonshire Building | 2017-06-23 06:30 | 50448.3911 | 39.996
Devonshire Building | 2017-06-23 06:45 | 50448.4111 | 79.992
Devonshire Building | 2017-06-23 07:00 | 50448.4161 | 20.016
Devonshire Building | 2017-06-23 07:15 | 50448.4261 | 39.996
Devonshire Building | 2017-06-23 07:30 | 50448.4361 | 39.996
Devonshire Building | 2017-06-23 07:45 | 50448.4511 | 60.012
Devonshire Building | 2017-06-23 08:00 | 50448.4661 | 60.012
Devonshire Building | 2017-06-23 08:15 | 50448.7561 | 1159.992
Devonshire Building | 2017-06-23 08:30 | 50449.0361 | 1119.996
Devonshire Building | 2017-06-23 08:45 | 50449.0511 | 60.012
Devonshire Building | 2017-06-23 09:00 | 50449.0661 | 60.012
Devonshire Building | 2017-06-23 09:15 | 50449.0911 | 100.008
Devonshire Building | 2017-06-23 09:30 | 50449.1311 | 159.984
Devonshire Building | 2017-06-23 09:45 | 50449.1911 | 240.012
Devonshire Building | 2017-06-23 10:00 | 50449.6311 | 1760.004
Devonshire Building | 2017-06-23 10:15 | 50449.8511 | 879.984
Devonshire Building | 2017-06-23 10:30 | 50449.9161 | 259.992
Devonshire Building | 2017-06-23 10:45 | 50449.9811 | 259.992
Devonshire Building | 2017-06-23 11:00 | 50450.0461 | 259.992
Devonshire Building | 2017-06-23 11:15 | 50450.1061 | 240.012
Devonshire Building | 2017-06-23 11:30 | 50450.4811 | 1500.012
Devonshire Building | 2017-06-23 11:45 | 50450.7761 | 1180.008
Devonshire Building | 2017-06-23 12:00 | 50450.8561 | 320.004
Devonshire Building | 2017-06-23 12:15 | 50450.9561 | 399.996
Devonshire Building | 2017-06-23 12:30 | 50451.0661 | 439.992
Devonshire Building | 2017-06-23 12:45 | 50451.1861 | 479.988
Devonshire Building | 2017-06-23 13:00 | 50451.3011 | 460.008
Devonshire Building | 2017-06-23 13:15 | 50451.8961 | 2379.996
Devonshire Building | 2017-06-23 13:30 | 50451.9861 | 360
Devonshire Building | 2017-06-23 13:45 | 50452.0661 | 320.004
Devonshire Building | 2017-06-23 14:00 | 50452.1361 | 280.008
Devonshire Building | 2017-06-23 14:15 | 50452.1961 | 240.012
Devonshire Building | 2017-06-23 14:30 | 50452.2511 | 219.996
Devonshire Building | 2017-06-23 14:45 | 50452.3111 | 240.012
Devonshire Building | 2017-06-23 15:00 | 50452.3761 | 259.992
Devonshire Building | 2017-06-23 15:15 | 50452.4511 | 299.988
Devonshire Building | 2017-06-23 15:30 | 50453.1061 | 2620.008
Devonshire Building | 2017-06-23 15:45 | 50453.2361 | 519.984
Devonshire Building | 2017-06-23 16:00 | 50453.4711 | 939.996
Devonshire Building | 2017-06-23 16:15 | 50453.7461 | 1100.016
Devonshire Building | 2017-06-23 16:30 | 50453.8811 | 540
Devonshire Building | 2017-06-23 16:45 | 50453.9661 | 339.984
Devonshire Building | 2017-06-23 17:00 | 50454.0311 | 259.992
Devonshire Building | 2017-06-23 17:15 | 50454.0761 | 180
Devonshire Building | 2017-06-23 17:30 | 50454.1211 | 180
Devonshire Building | 2017-06-23 17:45 | 50454.1511 | 119.988
Devonshire Building | 2017-06-23 18:00 | 50454.1811 | 119.988
Devonshire Building | 2017-06-23 18:15 | 50454.2111 | 119.988
Devonshire Building | 2017-06-23 18:30 | 50454.2361 | 100.008
Devonshire Building | 2017-06-23 18:45 | 50454.2561 | 79.992
Devonshire Building | 2017-06-23 19:00 | 50454.2761 | 79.992
Devonshire Building | 2017-06-23 19:15 | 50454.3061 | 119.988
Devonshire Building | 2017-06-23 19:30 | 50454.3211 | 60.012
Devonshire Building | 2017-06-23 19:45 | 50454.3911 | 280.008
Devonshire Building | 2017-06-23 20:00 | 50454.8661 | 1900.008
Devonshire Building | 2017-06-23 20:15 | 50454.8711 | 20.016
Devonshire Building | 2017-06-23 20:30 | 50454.8761 | 20.016
Devonshire Building | 2017-06-23 20:45 | 50454.8961 | 79.992
Devonshire Building | 2017-06-23 21:00 | 50454.9011 | 20.016
Devonshire Building | 2017-06-23 21:15 | 50454.9061 | 20.016
Devonshire Building | 2017-06-23 21:30 | 50454.9111 | 20.016
Devonshire Building | 2017-06-23 21:45 | 50454.9161 | 20.016
Devonshire Building | 2017-06-23 22:00 | 50454.9211 | 20.016
Devonshire Building | 2017-06-23 22:15 | 50454.9311 | 39.996
Devonshire Building | 2017-06-23 22:30 | 50454.9361 | 20.016
Devonshire Building | 2017-06-23 22:45 | 50454.9411 | 20.016
Devonshire Building | 2017-06-23 23:00 | 50454.9462 | 20.016
Devonshire Building | 2017-06-23 23:15 | 50454.9512 | 20.016
Devonshire Building | 2017-06-23 23:30 | 50454.9562 | 20.016
Devonshire Building | 2017-06-23 23:45 | 50454.9662 | 39.996
Devonshire Building | 2017-06-24 | 50454.9688 | 20.016
Devonshire Building | 2017-06-24 00:15 | 50454.9738 | 20.016
Devonshire Building | 2017-06-24 00:30 | 50454.9788 | 20.016
Devonshire Building | 2017-06-24 00:45 | 50454.9838 | 20.016
Devonshire Building | 2017-06-24 01:00 | 50454.9938 | 39.996
Devonshire Building | 2017-06-24 01:15 | 50454.9988 | 20.016
Devonshire Building | 2017-06-24 01:30 | 50455.0038 | 20.016
Devonshire Building | 2017-06-24 01:45 | 50455.0088 | 20.016
Devonshire Building | 2017-06-24 02:00 | 50455.0138 | 20.016
Devonshire Building | 2017-06-24 02:15 | 50455.0188 | 20.016
Devonshire Building | 2017-06-24 02:30 | 50455.0288 | 39.996
Devonshire Building | 2017-06-24 02:45 | 50455.0338 | 20.016
Devonshire Building | 2017-06-24 03:00 | 50455.0388 | 20.016
Devonshire Building | 2017-06-24 03:15 | 50455.0438 | 20.016
Devonshire Building | 2017-06-24 03:30 | 50455.0488 | 20.016
Devonshire Building | 2017-06-24 03:45 | 50455.0538 | 20.016
Devonshire Building | 2017-06-24 04:00 | 50455.0588 | 20.016
Devonshire Building | 2017-06-24 04:15 | 50455.0638 | 20.016
Devonshire Building | 2017-06-24 04:30 | 50455.0688 | 20.016
Devonshire Building | 2017-06-24 04:45 | 50455.0738 | 20.016
Devonshire Building | 2017-06-24 05:00 | 50455.0788 | 20.016
Devonshire Building | 2017-06-24 05:15 | 50455.0838 | 20.016
Devonshire Building | 2017-06-24 05:30 | 50455.0888 | 20.016
Devonshire Building | 2017-06-24 05:45 | 50455.0938 | 20.016
Devonshire Building | 2017-06-24 06:00 | 50455.1038 | 39.996
Devonshire Building | 2017-06-24 06:15 | 50455.1088 | 20.016
Devonshire Building | 2017-06-24 06:30 | 50455.1138 | 20.016
Devonshire Building | 2017-06-24 06:45 | 50455.1188 | 20.016
Devonshire Building | 2017-06-24 07:00 | 50455.1238 | 20.016
Devonshire Building | 2017-06-24 07:15 | 50455.1289 | 20.016
Devonshire Building | 2017-06-24 07:30 | 50455.1339 | 20.016
Devonshire Building | 2017-06-24 07:45 | 50455.1389 | 20.016
Devonshire Building | 2017-06-24 08:00 | 50455.1639 | 100.008
Devonshire Building | 2017-06-24 08:15 | 50455.1839 | 79.992
Devonshire Building | 2017-06-24 08:30 | 50455.2089 | 100.008
Devonshire Building | 2017-06-24 08:45 | 50455.2289 | 79.992
Devonshire Building | 2017-06-24 09:00 | 50455.2539 | 100.008
Devonshire Building | 2017-06-24 09:15 | 50455.2739 | 79.992
Devonshire Building | 2017-06-24 09:30 | 50455.2989 | 100.008
Devonshire Building | 2017-06-24 09:45 | 50455.3189 | 79.992
Devonshire Building | 2017-06-24 10:00 | 50455.3289 | 39.996
Devonshire Building | 2017-06-24 10:15 | 50455.3339 | 20.016
Devonshire Building | 2017-06-24 10:30 | 50455.3389 | 20.016
Devonshire Building | 2017-06-24 10:45 | 50455.3439 | 20.016
Devonshire Building | 2017-06-24 11:00 | 50455.3539 | 39.996
Devonshire Building | 2017-06-24 11:15 | 50455.3589 | 20.016
Devonshire Building | 2017-06-24 11:30 | 50455.3639 | 20.016
Devonshire Building | 2017-06-24 11:45 | 50455.3689 | 20.016
Devonshire Building | 2017-06-24 12:00 | 50455.3789 | 39.996
Devonshire Building | 2017-06-24 12:15 | 50455.3839 | 20.016
Devonshire Building | 2017-06-24 12:30 | 50455.3889 | 20.016
Devonshire Building | 2017-06-24 12:45 | 50455.4789 | 360
Devonshire Building | 2017-06-24 13:00 | 50455.9089 | 1720.008
Devonshire Building | 2017-06-24 13:15 | 50455.9189 | 39.996
Devonshire Building | 2017-06-24 13:30 | 50455.9289 | 39.996
Devonshire Building | 2017-06-24 13:45 | 50455.9439 | 60.012
Devonshire Building | 2017-06-24 14:00 | 50455.9539 | 39.996
Devonshire Building | 2017-06-24 14:15 | 50455.9639 | 39.996
Devonshire Building | 2017-06-24 14:30 | 50455.9739 | 39.996
Devonshire Building | 2017-06-24 14:45 | 50455.9889 | 60.012
Devonshire Building | 2017-06-24 15:00 | 50456.0089 | 79.992
Devonshire Building | 2017-06-24 15:15 | 50456.0239 | 60.012
Devonshire Building | 2017-06-24 15:30 | 50456.0389 | 60.012
Devonshire Building | 2017-06-24 15:45 | 50456.0539 | 60.012
Devonshire Building | 2017-06-24 16:00 | 50456.0689 | 60.012
Devonshire Building | 2017-06-24 16:15 | 50456.0839 | 60.012
Devonshire Building | 2017-06-24 16:30 | 50456.1039 | 79.992
Devonshire Building | 2017-06-24 16:45 | 50456.1189 | 60.012
Devonshire Building | 2017-06-24 17:00 | 50456.1289 | 39.996
Devonshire Building | 2017-06-24 17:15 | 50456.1439 | 60.012
Devonshire Building | 2017-06-24 17:30 | 50456.1589 | 60.012
Devonshire Building | 2017-06-24 17:45 | 50456.1689 | 39.996
Devonshire Building | 2017-06-24 18:00 | 50456.1839 | 60.012
Devonshire Building | 2017-06-24 18:15 | 50456.1989 | 60.012
Devonshire Building | 2017-06-24 18:30 | 50456.2089 | 39.996
Devonshire Building | 2017-06-24 18:45 | 50456.2239 | 60.012
Devonshire Building | 2017-06-24 19:00 | 50456.2339 | 39.996
Devonshire Building | 2017-06-24 19:15 | 50456.2439 | 39.996
Devonshire Building | 2017-06-24 19:30 | 50456.2539 | 39.996
Devonshire Building | 2017-06-24 19:45 | 50456.2689 | 60.012
Devonshire Building | 2017-06-24 20:00 | 50456.2789 | 39.996
Devonshire Building | 2017-06-24 20:15 | 50456.2889 | 39.996
Devonshire Building | 2017-06-24 20:30 | 50456.2989 | 39.996
Devonshire Building | 2017-06-24 20:45 | 50456.3289 | 119.988
Devonshire Building | 2017-06-24 21:00 | 50456.3439 | 60.012
Devonshire Building | 2017-06-24 21:15 | 50456.3489 | 20.016
Devonshire Building | 2017-06-24 21:30 | 50456.3589 | 39.996
Devonshire Building | 2017-06-24 21:45 | 50456.3689 | 39.996
Devonshire Building | 2017-06-24 22:00 | 50456.3739 | 20.016
Devonshire Building | 2017-06-24 22:15 | 50456.3839 | 39.996
Devonshire Building | 2017-06-24 22:30 | 50456.3939 | 39.996
Devonshire Building | 2017-06-24 22:45 | 50456.3989 | 20.016
Devonshire Building | 2017-06-24 23:00 | 50456.4089 | 39.996
Devonshire Building | 2017-06-24 23:15 | 50456.4189 | 39.996
Devonshire Building | 2017-06-24 23:30 | 50456.4239 | 20.016
Devonshire Building | 2017-06-24 23:45 | 50456.4339 | 39.996
Devonshire Building | 2017-06-25 | 50456.4453 | 39.996
Devonshire Building | 2017-06-25 00:15 | 50456.4503 | 20.016
Devonshire Building | 2017-06-25 00:30 | 50456.4603 | 39.996
Devonshire Building | 2017-06-25 00:45 | 50456.4703 | 39.996
Devonshire Building | 2017-06-25 01:00 | 50456.4753 | 20.016
Devonshire Building | 2017-06-25 01:15 | 50456.4853 | 39.996
Devonshire Building | 2017-06-25 01:30 | 50456.4903 | 20.016
Devonshire Building | 2017-06-25 01:45 | 50456.5003 | 39.996
Devonshire Building | 2017-06-25 02:00 | 50456.5053 | 20.016
Devonshire Building | 2017-06-25 02:15 | 50456.5153 | 39.996
Devonshire Building | 2017-06-25 02:30 | 50456.5253 | 39.996
Devonshire Building | 2017-06-25 02:45 | 50456.5303 | 20.016
Devonshire Building | 2017-06-25 03:00 | 50456.5403 | 39.996
Devonshire Building | 2017-06-25 03:15 | 50456.5453 | 20.016
Devonshire Building | 2017-06-25 03:30 | 50456.5553 | 39.996
Devonshire Building | 2017-06-25 03:45 | 50456.5603 | 20.016
Devonshire Building | 2017-06-25 04:00 | 50456.5703 | 39.996
Devonshire Building | 2017-06-25 04:15 | 50456.5753 | 20.016
Devonshire Building | 2017-06-25 04:30 | 50456.5853 | 39.996
Devonshire Building | 2017-06-25 04:45 | 50456.5903 | 20.016
Devonshire Building | 2017-06-25 05:00 | 50456.6003 | 39.996
Devonshire Building | 2017-06-25 05:15 | 50456.6103 | 39.996
Devonshire Building | 2017-06-25 05:30 | 50456.6153 | 20.016
Devonshire Building | 2017-06-25 05:45 | 50456.6253 | 39.996
Devonshire Building | 2017-06-25 06:00 | 50456.6303 | 20.016
Devonshire Building | 2017-06-25 06:15 | 50456.6403 | 39.996
Devonshire Building | 2017-06-25 06:30 | 50456.6453 | 20.016
Devonshire Building | 2017-06-25 06:45 | 50457.0953 | 1800
Devonshire Building | 2017-06-25 07:00 | 50457.1553 | 240.012
Devonshire Building | 2017-06-25 07:15 | 50457.1604 | 20.016
Devonshire Building | 2017-06-25 07:30 | 50457.1704 | 39.996
Devonshire Building | 2017-06-25 07:45 | 50457.1903 | 79.992
Devonshire Building | 2017-06-25 08:00 | 50457.2153 | 100.008
Devonshire Building | 2017-06-25 08:15 | 50457.2353 | 79.992
Devonshire Building | 2017-06-25 08:30 | 50457.2603 | 100.008
Devonshire Building | 2017-06-25 08:45 | 50457.2803 | 79.992
Devonshire Building | 2017-06-25 09:00 | 50457.3054 | 100.008
Devonshire Building | 2017-06-25 09:15 | 50457.3304 | 100.008
Devonshire Building | 2017-06-25 09:30 | 50457.3504 | 79.992
Devonshire Building | 2017-06-25 09:45 | 50457.3754 | 100.008
Devonshire Building | 2017-06-25 10:00 | 50457.3854 | 39.996
Devonshire Building | 2017-06-25 10:15 | 50457.3953 | 39.996
Devonshire Building | 2017-06-25 10:30 | 50457.4053 | 39.996
Devonshire Building | 2017-06-25 10:45 | 50457.4104 | 20.016
Devonshire Building | 2017-06-25 11:00 | 50457.4204 | 39.996
Devonshire Building | 2017-06-25 11:15 | 50457.4254 | 20.016
Devonshire Building | 2017-06-25 11:30 | 50457.4404 | 60.012
Devonshire Building | 2017-06-25 11:45 | 50457.4504 | 39.996
Devonshire Building | 2017-06-25 12:00 | 50457.4604 | 39.996
Devonshire Building | 2017-06-25 12:15 | 50457.4654 | 20.016
Devonshire Building | 2017-06-25 12:30 | 50457.4754 | 39.996
Devonshire Building | 2017-06-25 12:45 | 50457.4854 | 39.996
Devonshire Building | 2017-06-25 13:00 | 50457.4904 | 20.016
Devonshire Building | 2017-06-25 13:15 | 50457.5004 | 39.996
Devonshire Building | 2017-06-25 13:30 | 50457.5104 | 39.996
Devonshire Building | 2017-06-25 13:45 | 50457.5154 | 20.016
Devonshire Building | 2017-06-25 14:00 | 50457.5254 | 39.996
Devonshire Building | 2017-06-25 14:15 | 50457.5354 | 39.996
Devonshire Building | 2017-06-25 14:30 | 50457.5404 | 20.016
Devonshire Building | 2017-06-25 14:45 | 50457.5504 | 39.996
Devonshire Building | 2017-06-25 15:00 | 50457.5604 | 39.996
Devonshire Building | 2017-06-25 15:15 | 50457.5654 | 20.016
Devonshire Building | 2017-06-25 15:30 | 50457.5754 | 39.996
Devonshire Building | 2017-06-25 15:45 | 50457.5804 | 20.016
Devonshire Building | 2017-06-25 16:00 | 50457.5904 | 39.996
Devonshire Building | 2017-06-25 16:15 | 50457.5954 | 20.016
Devonshire Building | 2017-06-25 16:30 | 50457.6054 | 39.996
Devonshire Building | 2017-06-25 16:45 | 50457.6104 | 20.016
Devonshire Building | 2017-06-25 17:00 | 50457.6154 | 20.016
Devonshire Building | 2017-06-25 17:15 | 50457.6254 | 39.996
Devonshire Building | 2017-06-25 17:30 | 50457.6304 | 20.016
Devonshire Building | 2017-06-25 17:45 | 50457.6404 | 39.996
Devonshire Building | 2017-06-25 18:00 | 50457.6454 | 20.016
Devonshire Building | 2017-06-25 18:15 | 50457.6504 | 20.016
Devonshire Building | 2017-06-25 18:30 | 50457.6604 | 39.996
Devonshire Building | 2017-06-25 18:45 | 50457.6654 | 20.016
Devonshire Building | 2017-06-25 19:00 | 50457.6704 | 20.016
Devonshire Building | 2017-06-25 19:15 | 50457.6804 | 39.996
Devonshire Building | 2017-06-25 19:30 | 50457.6854 | 20.016
Devonshire Building | 2017-06-25 19:45 | 50457.6904 | 20.016
Devonshire Building | 2017-06-25 20:00 | 50457.7004 | 39.996
Devonshire Building | 2017-06-25 20:15 | 50458.1954 | 1980
Devonshire Building | 2017-06-25 20:30 | 50458.2004 | 20.016
Devonshire Building | 2017-06-25 20:45 | 50458.2154 | 60.012
Devonshire Building | 2017-06-25 21:00 | 50458.2204 | 20.016
Devonshire Building | 2017-06-25 21:15 | 50458.2304 | 39.996
Devonshire Building | 2017-06-25 21:30 | 50458.2354 | 20.016
Devonshire Building | 2017-06-25 21:45 | 50458.2454 | 39.996
Devonshire Building | 2017-06-25 22:00 | 50458.2504 | 20.016
Devonshire Building | 2017-06-25 22:15 | 50458.2604 | 39.996
Devonshire Building | 2017-06-25 22:30 | 50458.2654 | 20.016
Devonshire Building | 2017-06-25 22:45 | 50458.2754 | 39.996
Devonshire Building | 2017-06-25 23:00 | 50458.2854 | 39.996
Devonshire Building | 2017-06-25 23:15 | 50458.2904 | 20.016
Devonshire Building | 2017-06-25 23:30 | 50458.3004 | 39.996
Devonshire Building | 2017-06-25 23:45 | 50458.3104 | 39.996
Devonshire Building | 2017-06-26 | 50458.3203 | 39.996
Devonshire Building | 2017-06-26 00:15 | 50458.3303 | 39.996
Devonshire Building | 2017-06-26 00:30 | 50458.3403 | 39.996
Devonshire Building | 2017-06-26 00:45 | 50458.3503 | 39.996
Devonshire Building | 2017-06-26 01:00 | 50458.3603 | 39.996
Devonshire Building | 2017-06-26 01:15 | 50458.3703 | 39.996
Devonshire Building | 2017-06-26 01:30 | 50458.3803 | 39.996
Devonshire Building | 2017-06-26 01:45 | 50458.3903 | 39.996
Devonshire Building | 2017-06-26 02:00 | 50458.3953 | 20.016
Devonshire Building | 2017-06-26 02:15 | 50458.4053 | 39.996
Devonshire Building | 2017-06-26 02:30 | 50458.4153 | 39.996
Devonshire Building | 2017-06-26 02:45 | 50458.4253 | 39.996
Devonshire Building | 2017-06-26 03:00 | 50458.4303 | 20.016
Devonshire Building | 2017-06-26 03:15 | 50458.4403 | 39.996
Devonshire Building | 2017-06-26 03:30 | 50458.4503 | 39.996
Devonshire Building | 2017-06-26 03:45 | 50458.4603 | 39.996
Devonshire Building | 2017-06-26 04:00 | 50458.4653 | 20.016
Devonshire Building | 2017-06-26 04:15 | 50458.4753 | 39.996
Devonshire Building | 2017-06-26 04:30 | 50458.4803 | 20.016
Devonshire Building | 2017-06-26 04:45 | 50458.4903 | 39.996
Devonshire Building | 2017-06-26 05:00 | 50458.5003 | 39.996
Devonshire Building | 2017-06-26 05:15 | 50458.5103 | 39.996
Devonshire Building | 2017-06-26 05:30 | 50458.5153 | 20.016
Devonshire Building | 2017-06-26 05:45 | 50458.5253 | 39.996
Devonshire Building | 2017-06-26 06:00 | 50458.5353 | 39.996
Devonshire Building | 2017-06-26 06:15 | 50458.5403 | 20.016
Devonshire Building | 2017-06-26 06:30 | 50458.5503 | 39.996
Devonshire Building | 2017-06-26 06:45 | 50458.5653 | 60.012
Devonshire Building | 2017-06-26 07:00 | 50458.5753 | 39.996
Devonshire Building | 2017-06-26 07:15 | 50458.5853 | 39.996
Devonshire Building | 2017-06-26 07:30 | 50458.6103 | 100.008
Devonshire Building | 2017-06-26 07:45 | 50458.6203 | 39.996
Devonshire Building | 2017-06-26 08:00 | 50459.2003 | 2319.984
Devonshire Building | 2017-06-26 08:15 | 50459.2303 | 119.988
Devonshire Building | 2017-06-26 08:30 | 50459.2853 | 219.996
Devonshire Building | 2017-06-26 08:45 | 50459.3553 | 280.008
Devonshire Building | 2017-06-26 09:00 | 50459.4303 | 299.988
Devonshire Building | 2017-06-26 09:15 | 50459.5103 | 320.004
Devonshire Building | 2017-06-26 09:30 | 50459.9853 | 1900.008
Devonshire Building | 2017-06-26 09:45 | 50460.1953 | 839.988
Devonshire Building | 2017-06-26 10:00 | 50460.2653 | 280.008
Devonshire Building | 2017-06-26 10:15 | 50460.3453 | 320.004
Devonshire Building | 2017-06-26 10:30 | 50460.5053 | 640.008
Devonshire Building | 2017-06-26 10:45 | 50460.7853 | 1119.996
Devonshire Building | 2017-06-26 11:00 | 50461.2953 | 2040.012
Devonshire Building | 2017-06-26 11:15 | 50461.4003 | 420.012
Devonshire Building | 2017-06-26 11:30 | 50461.5053 | 420.012
Devonshire Building | 2017-06-26 11:45 | 50461.6053 | 399.996
Devonshire Building | 2017-06-26 12:00 | 50461.7103 | 420.012
Devonshire Building | 2017-06-26 12:15 | 50462.3303 | 2480.004
Devonshire Building | 2017-06-26 12:30 | 50462.4053 | 299.988
Devonshire Building | 2017-06-26 12:45 | 50462.4753 | 280.008
Devonshire Building | 2017-06-26 13:00 | 50462.5453 | 280.008
Devonshire Building | 2017-06-26 13:15 | 50462.6253 | 320.004
Devonshire Building | 2017-06-26 13:30 | 50462.7003 | 299.988
Devonshire Building | 2017-06-26 13:45 | 50463.3103 | 2440.008
Devonshire Building | 2017-06-26 14:00 | 50463.4203 | 439.992
Devonshire Building | 2017-06-26 14:15 | 50463.5253 | 420.012
Devonshire Building | 2017-06-26 14:30 | 50463.6203 | 380.016
Devonshire Building | 2017-06-26 14:45 | 50463.7153 | 380.016
Devonshire Building | 2017-06-26 15:00 | 50463.8103 | 380.016
Devonshire Building | 2017-06-26 15:15 | 50463.9103 | 399.996
Devonshire Building | 2017-06-26 15:30 | 50464.5303 | 2480.004
Devonshire Building | 2017-06-26 15:45 | 50464.6153 | 339.984
Devonshire Building | 2017-06-26 16:00 | 50464.6803 | 259.992
Devonshire Building | 2017-06-26 16:15 | 50464.7503 | 280.008
Devonshire Building | 2017-06-26 16:30 | 50464.8203 | 280.008
Devonshire Building | 2017-06-26 16:45 | 50464.8803 | 240.012
Devonshire Building | 2017-06-26 17:00 | 50464.9403 | 240.012
Devonshire Building | 2017-06-26 17:15 | 50465.3453 | 1620
Devonshire Building | 2017-06-26 17:30 | 50465.5203 | 699.984
Devonshire Building | 2017-06-26 17:45 | 50465.5453 | 100.008
Devonshire Building | 2017-06-26 18:00 | 50465.5703 | 100.008
Devonshire Building | 2017-06-26 18:15 | 50465.5953 | 100.008
Devonshire Building | 2017-06-26 18:30 | 50465.6203 | 100.008
Devonshire Building | 2017-06-26 18:45 | 50465.6453 | 100.008
Devonshire Building | 2017-06-26 19:00 | 50465.6653 | 79.992
Devonshire Building | 2017-06-26 19:15 | 50465.6853 | 79.992
Devonshire Building | 2017-06-26 19:30 | 50465.7053 | 79.992
Devonshire Building | 2017-06-26 19:45 | 50465.7253 | 79.992
Devonshire Building | 2017-06-26 20:00 | 50465.7453 | 79.992
Devonshire Building | 2017-06-26 20:15 | 50465.7603 | 60.012
Devonshire Building | 2017-06-26 20:30 | 50465.7753 | 60.012
Devonshire Building | 2017-06-26 20:45 | 50465.8053 | 119.988
Devonshire Building | 2017-06-26 21:00 | 50465.8103 | 20.016
Devonshire Building | 2017-06-26 21:15 | 50465.8153 | 20.016
Devonshire Building | 2017-06-26 21:30 | 50465.8204 | 20.016
Devonshire Building | 2017-06-26 21:45 | 50465.8304 | 39.996
Devonshire Building | 2017-06-26 22:00 | 50465.8354 | 20.016
Devonshire Building | 2017-06-26 22:15 | 50465.8404 | 20.016
Devonshire Building | 2017-06-26 22:30 | 50465.8454 | 20.016
Devonshire Building | 2017-06-26 22:45 | 50465.8504 | 20.016
Devonshire Building | 2017-06-26 23:00 | 50465.8604 | 39.996
Devonshire Building | 2017-06-26 23:15 | 50465.8654 | 20.016
Devonshire Building | 2017-06-26 23:30 | 50465.8704 | 20.016
Devonshire Building | 2017-06-26 23:45 | 50465.8754 | 20.016
Devonshire Building | 2017-06-27 | 50465.8789 | 20.016
Devonshire Building | 2017-06-27 00:15 | 50465.8839 | 20.016
Devonshire Building | 2017-06-27 00:30 | 50465.8889 | 20.016
Devonshire Building | 2017-06-27 00:45 | 50465.8989 | 39.996
Devonshire Building | 2017-06-27 01:00 | 50465.9039 | 20.016
Devonshire Building | 2017-06-27 01:15 | 50465.9089 | 20.016
Devonshire Building | 2017-06-27 01:30 | 50465.9139 | 20.016
Devonshire Building | 2017-06-27 01:45 | 50465.9189 | 20.016
Devonshire Building | 2017-06-27 02:00 | 50465.9239 | 20.016
Devonshire Building | 2017-06-27 02:15 | 50465.9289 | 20.016
Devonshire Building | 2017-06-27 02:30 | 50465.9339 | 20.016
Devonshire Building | 2017-06-27 02:45 | 50465.9389 | 20.016
Devonshire Building | 2017-06-27 03:00 | 50465.944 | 20.016
Devonshire Building | 2017-06-27 03:15 | 50465.949 | 20.016
Devonshire Building | 2017-06-27 03:30 | 50465.954 | 20.016
Devonshire Building | 2017-06-27 03:45 | 50465.959 | 20.016
Devonshire Building | 2017-06-27 04:00 | 50465.964 | 20.016
Devonshire Building | 2017-06-27 04:15 | 50465.969 | 20.016
Devonshire Building | 2017-06-27 04:30 | 50465.979 | 39.996
Devonshire Building | 2017-06-27 04:45 | 50465.984 | 20.016
Devonshire Building | 2017-06-27 05:00 | 50465.989 | 20.016
Devonshire Building | 2017-06-27 05:15 | 50465.994 | 20.016
Devonshire Building | 2017-06-27 05:30 | 50465.999 | 20.016
Devonshire Building | 2017-06-27 05:45 | 50466.004 | 20.016
Devonshire Building | 2017-06-27 06:00 | 50466.009 | 20.016
Devonshire Building | 2017-06-27 06:15 | 50466.024 | 60.012
Devonshire Building | 2017-06-27 06:30 | 50466.029 | 20.016
Devonshire Building | 2017-06-27 06:45 | 50466.034 | 20.016
Devonshire Building | 2017-06-27 07:00 | 50466.539 | 2019.996
Devonshire Building | 2017-06-27 07:15 | 50466.554 | 60.012
Devonshire Building | 2017-06-27 07:30 | 50466.564 | 39.996
Devonshire Building | 2017-06-27 07:45 | 50466.574 | 39.996
Devonshire Building | 2017-06-27 08:00 | 50466.604 | 119.988
Devonshire Building | 2017-06-27 08:15 | 50466.624 | 79.992
Devonshire Building | 2017-06-27 08:30 | 50466.669 | 180
Devonshire Building | 2017-06-27 08:45 | 50466.729 | 240.012
Devonshire Building | 2017-06-27 09:00 | 50467.314 | 2340
Devonshire Building | 2017-06-27 09:15 | 50467.444 | 519.984
Devonshire Building | 2017-06-27 09:30 | 50467.544 | 399.996
Devonshire Building | 2017-06-27 09:45 | 50467.639 | 380.016
Devonshire Building | 2017-06-27 10:00 | 50467.724 | 339.984
Devonshire Building | 2017-06-27 10:15 | 50468.319 | 2379.996
Devonshire Building | 2017-06-27 10:30 | 50468.384 | 259.992
Devonshire Building | 2017-06-27 10:45 | 50468.449 | 259.992
Devonshire Building | 2017-06-27 11:00 | 50468.509 | 240.012
Devonshire Building | 2017-06-27 11:15 | 50468.564 | 219.996
Devonshire Building | 2017-06-27 11:30 | 50469.134 | 2279.988
Devonshire Building | 2017-06-27 11:45 | 50469.174 | 159.984
Devonshire Building | 2017-06-27 12:00 | 50469.224 | 200.016
Devonshire Building | 2017-06-27 12:15 | 50469.269 | 180
Devonshire Building | 2017-06-27 12:30 | 50469.304 | 140.004
Devonshire Building | 2017-06-27 12:45 | 50469.369 | 259.992
Devonshire Building | 2017-06-27 13:00 | 50469.984 | 2459.988
Devonshire Building | 2017-06-27 13:15 | 50470.079 | 380.016
Devonshire Building | 2017-06-27 13:30 | 50470.164 | 339.984
Devonshire Building | 2017-06-27 13:45 | 50470.244 | 320.004
Devonshire Building | 2017-06-27 14:00 | 50470.324 | 320.004
Devonshire Building | 2017-06-27 14:15 | 50470.389 | 259.992
Devonshire Building | 2017-06-27 14:30 | 50470.989 | 2400.012
Devonshire Building | 2017-06-27 14:45 | 50471.069 | 320.004
Devonshire Building | 2017-06-27 15:00 | 50471.169 | 399.996
Devonshire Building | 2017-06-27 15:15 | 50471.269 | 399.996
Devonshire Building | 2017-06-27 15:30 | 50471.369 | 399.996
Devonshire Building | 2017-06-27 15:45 | 50471.474 | 420.012
Devonshire Building | 2017-06-27 16:00 | 50471.579 | 420.012
Devonshire Building | 2017-06-27 16:15 | 50472.199 | 2480.004
Devonshire Building | 2017-06-27 16:30 | 50472.304 | 420.012
Devonshire Building | 2017-06-27 16:45 | 50472.389 | 339.984
Devonshire Building | 2017-06-27 17:00 | 50472.454 | 259.992
Devonshire Building | 2017-06-27 17:15 | 50472.509 | 219.996
Devonshire Building | 2017-06-27 17:30 | 50472.554 | 180
Devonshire Building | 2017-06-27 17:45 | 50472.594 | 159.984
Devonshire Building | 2017-06-27 18:00 | 50472.629 | 140.004
Devonshire Building | 2017-06-27 18:15 | 50472.659 | 119.988
Devonshire Building | 2017-06-27 18:30 | 50472.684 | 100.008
Devonshire Building | 2017-06-27 18:45 | 50472.709 | 100.008
Devonshire Building | 2017-06-27 19:00 | 50472.729 | 79.992
Devonshire Building | 2017-06-27 19:15 | 50472.754 | 100.008
Devonshire Building | 2017-06-27 19:30 | 50472.769 | 60.012
Devonshire Building | 2017-06-27 19:45 | 50472.789 | 79.992
Devonshire Building | 2017-06-27 20:00 | 50472.809 | 79.992
Devonshire Building | 2017-06-27 20:15 | 50472.824 | 60.012
Devonshire Building | 2017-06-27 20:30 | 50472.839 | 60.012
Devonshire Building | 2017-06-27 20:45 | 50472.879 | 159.984
Devonshire Building | 2017-06-27 21:00 | 50472.884 | 20.016
Devonshire Building | 2017-06-27 21:15 | 50472.889 | 20.016
Devonshire Building | 2017-06-27 21:30 | 50472.894 | 20.016
Devonshire Building | 2017-06-27 21:45 | 50472.904 | 39.996
Devonshire Building | 2017-06-27 22:00 | 50472.909 | 20.016
Devonshire Building | 2017-06-27 22:15 | 50472.914 | 20.016
Devonshire Building | 2017-06-27 22:30 | 50472.924 | 39.996
Devonshire Building | 2017-06-27 22:45 | 50472.929 | 20.016
Devonshire Building | 2017-06-27 23:00 | 50472.934 | 20.016
Devonshire Building | 2017-06-27 23:15 | 50472.944 | 39.996
Devonshire Building | 2017-06-27 23:30 | 50473.464 | 2080.008
Devonshire Building | 2017-06-27 23:45 | 50473.469 | 20.016
Devonshire Building | 2017-06-28 | 50473.4766 | 20.016
Devonshire Building | 2017-06-28 00:15 | 50473.4816 | 20.016
Devonshire Building | 2017-06-28 00:30 | 50473.4916 | 39.996
Devonshire Building | 2017-06-28 00:45 | 50473.4966 | 20.016
Devonshire Building | 2017-06-28 01:00 | 50473.5016 | 20.016
Devonshire Building | 2017-06-28 01:15 | 50473.5066 | 20.016
Devonshire Building | 2017-06-28 01:30 | 50473.5116 | 20.016
Devonshire Building | 2017-06-28 01:45 | 50473.5166 | 20.016
Devonshire Building | 2017-06-28 02:00 | 50473.5266 | 39.996
Devonshire Building | 2017-06-28 02:15 | 50473.5316 | 20.016
Devonshire Building | 2017-06-28 02:30 | 50473.5366 | 20.016
Devonshire Building | 2017-06-28 02:45 | 50473.5416 | 20.016
Devonshire Building | 2017-06-28 03:00 | 50473.5516 | 39.996
Devonshire Building | 2017-06-28 03:15 | 50473.5566 | 20.016
Devonshire Building | 2017-06-28 03:30 | 50473.5616 | 20.016
Devonshire Building | 2017-06-28 03:45 | 50473.5666 | 20.016
Devonshire Building | 2017-06-28 04:00 | 50473.5766 | 39.996
Devonshire Building | 2017-06-28 04:15 | 50473.5816 | 20.016
Devonshire Building | 2017-06-28 04:30 | 50473.5866 | 20.016
Devonshire Building | 2017-06-28 04:45 | 50473.5916 | 20.016
Devonshire Building | 2017-06-28 05:00 | 50473.6016 | 39.996
Devonshire Building | 2017-06-28 05:15 | 50473.6066 | 20.016
Devonshire Building | 2017-06-28 05:30 | 50473.6116 | 20.016
Devonshire Building | 2017-06-28 05:45 | 50473.6216 | 39.996
Devonshire Building | 2017-06-28 06:00 | 50473.6266 | 20.016
Devonshire Building | 2017-06-28 06:15 | 50473.6366 | 39.996
Devonshire Building | 2017-06-28 06:30 | 50473.6516 | 60.012
Devonshire Building | 2017-06-28 06:45 | 50473.6616 | 39.996
Devonshire Building | 2017-06-28 07:00 | 50473.6666 | 20.016
Devonshire Building | 2017-06-28 07:15 | 50473.6816 | 60.012
Devonshire Building | 2017-06-28 07:30 | 50473.7416 | 240.012
Devonshire Building | 2017-06-28 07:45 | 50473.7866 | 180
Devonshire Building | 2017-06-28 08:00 | 50473.8916 | 420.012
Devonshire Building | 2017-06-28 08:15 | 50474.2366 | 1379.988
Devonshire Building | 2017-06-28 08:30 | 50474.2866 | 200.016
Devonshire Building | 2017-06-28 08:45 | 50474.3416 | 219.996
Devonshire Building | 2017-06-28 09:00 | 50474.4066 | 259.992
Devonshire Building | 2017-06-28 09:15 | 50474.4716 | 259.992
Devonshire Building | 2017-06-28 09:30 | 50474.5416 | 280.008
Devonshire Building | 2017-06-28 09:45 | 50474.9066 | 1460.016
Devonshire Building | 2017-06-28 10:00 | 50475.0016 | 380.016
Devonshire Building | 2017-06-28 10:15 | 50475.0866 | 339.984
Devonshire Building | 2017-06-28 10:30 | 50475.1666 | 320.004
Devonshire Building | 2017-06-28 10:45 | 50475.2416 | 299.988
Devonshire Building | 2017-06-28 11:00 | 50475.4566 | 860.004
Devonshire Building | 2017-06-28 11:15 | 50475.8766 | 1680.012
Devonshire Building | 2017-06-28 11:30 | 50476.1816 | 1220.004
Devonshire Building | 2017-06-28 11:45 | 50476.3816 | 799.992
Devonshire Building | 2017-06-28 12:00 | 50476.5666 | 740.016
Devonshire Building | 2017-06-28 12:15 | 50476.7716 | 820.008
Devonshire Building | 2017-06-28 12:30 | 50476.9866 | 860.004
Devonshire Building | 2017-06-28 12:45 | 50477.5317 | 2180.016
Devonshire Building | 2017-06-28 13:00 | 50477.6717 | 560.016
Devonshire Building | 2017-06-28 13:15 | 50477.7717 | 399.996
Devonshire Building | 2017-06-28 13:30 | 50477.8517 | 320.004
Devonshire Building | 2017-06-28 13:45 | 50477.9317 | 320.004
Devonshire Building | 2017-06-28 14:00 | 50478.0167 | 339.984
Devonshire Building | 2017-06-28 14:15 | 50478.0917 | 299.988
Devonshire Building | 2017-06-28 14:30 | 50478.7117 | 2480.004
Devonshire Building | 2017-06-28 14:45 | 50478.7667 | 219.996
Devonshire Building | 2017-06-28 15:00 | 50478.8267 | 240.012
Devonshire Building | 2017-06-28 15:15 | 50478.8817 | 219.996
Devonshire Building | 2017-06-28 15:30 | 50478.9367 | 219.996
Devonshire Building | 2017-06-28 15:45 | 50479.1116 | 699.984
Devonshire Building | 2017-06-28 16:00 | 50479.5716 | 1839.996
Devonshire Building | 2017-06-28 16:15 | 50479.5966 | 100.008
Devonshire Building | 2017-06-28 16:30 | 50479.6166 | 79.992
Devonshire Building | 2017-06-28 16:45 | 50479.6366 | 79.992
Devonshire Building | 2017-06-28 17:00 | 50479.6616 | 100.008
Devonshire Building | 2017-06-28 17:15 | 50479.6867 | 100.008
Devonshire Building | 2017-06-28 17:30 | 50479.7066 | 79.992
Devonshire Building | 2017-06-28 17:45 | 50479.7266 | 79.992
Devonshire Building | 2017-06-28 18:00 | 50479.7466 | 79.992
Devonshire Building | 2017-06-28 18:15 | 50479.7666 | 79.992
Devonshire Building | 2017-06-28 18:30 | 50479.7866 | 79.992
Devonshire Building | 2017-06-28 18:45 | 50479.8066 | 79.992
Devonshire Building | 2017-06-28 19:00 | 50479.8266 | 79.992
Devonshire Building | 2017-06-28 19:15 | 50479.8466 | 79.992
Devonshire Building | 2017-06-28 19:30 | 50479.8666 | 79.992
Devonshire Building | 2017-06-28 19:45 | 50479.8866 | 79.992
Devonshire Building | 2017-06-28 20:00 | 50479.9066 | 79.992
Devonshire Building | 2017-06-28 20:15 | 50479.9266 | 79.992
Devonshire Building | 2017-06-28 20:30 | 50479.9416 | 60.012
Devonshire Building | 2017-06-28 20:45 | 50479.9816 | 159.984
Devonshire Building | 2017-06-28 21:00 | 50479.9966 | 60.012
Devonshire Building | 2017-06-28 21:15 | 50480.0116 | 60.012
Devonshire Building | 2017-06-28 21:30 | 50480.0266 | 60.012
Devonshire Building | 2017-06-28 21:45 | 50480.0416 | 60.012
Devonshire Building | 2017-06-28 22:00 | 50480.0566 | 60.012
Devonshire Building | 2017-06-28 22:15 | 50480.0716 | 60.012
Devonshire Building | 2017-06-28 22:30 | 50480.5816 | 2040.012
Devonshire Building | 2017-06-28 22:45 | 50480.5916 | 39.996
Devonshire Building | 2017-06-28 23:00 | 50480.6016 | 39.996
Devonshire Building | 2017-06-28 23:15 | 50480.6166 | 60.012
Devonshire Building | 2017-06-28 23:30 | 50480.6266 | 39.996
Devonshire Building | 2017-06-28 23:45 | 50480.6366 | 39.996
Devonshire Building | 2017-06-29 | 50480.6445 | 39.996
Devonshire Building | 2017-06-29 00:15 | 50480.6545 | 39.996
Devonshire Building | 2017-06-29 00:30 | 50480.6695 | 60.012
Devonshire Building | 2017-06-29 00:45 | 50480.6795 | 39.996
Devonshire Building | 2017-06-29 01:00 | 50480.6945 | 60.012
Devonshire Building | 2017-06-29 01:15 | 50480.7045 | 39.996
Devonshire Building | 2017-06-29 01:30 | 50480.7145 | 39.996
Devonshire Building | 2017-06-29 01:45 | 50480.7295 | 60.012
Devonshire Building | 2017-06-29 02:00 | 50480.7395 | 39.996
Devonshire Building | 2017-06-29 02:15 | 50480.7495 | 39.996
Devonshire Building | 2017-06-29 02:30 | 50480.7645 | 60.012
Devonshire Building | 2017-06-29 02:45 | 50480.7745 | 39.996
Devonshire Building | 2017-06-29 03:00 | 50480.7845 | 39.996
Devonshire Building | 2017-06-29 03:15 | 50480.7945 | 39.996
Devonshire Building | 2017-06-29 03:30 | 50480.8045 | 39.996
Devonshire Building | 2017-06-29 03:45 | 50480.8195 | 60.012
Devonshire Building | 2017-06-29 04:00 | 50480.8295 | 39.996
Devonshire Building | 2017-06-29 04:15 | 50480.8395 | 39.996
Devonshire Building | 2017-06-29 04:30 | 50480.8495 | 39.996
Devonshire Building | 2017-06-29 04:45 | 50480.8595 | 39.996
Devonshire Building | 2017-06-29 05:00 | 50480.8695 | 39.996
Devonshire Building | 2017-06-29 05:15 | 50480.8795 | 39.996
Devonshire Building | 2017-06-29 05:30 | 50480.8895 | 39.996
Devonshire Building | 2017-06-29 05:45 | 50480.8995 | 39.996
Devonshire Building | 2017-06-29 06:00 | 50480.9095 | 39.996
Devonshire Building | 2017-06-29 06:15 | 50480.9245 | 60.012
Devonshire Building | 2017-06-29 06:30 | 50480.9345 | 39.996
Devonshire Building | 2017-06-29 06:45 | 50480.9445 | 39.996
Devonshire Building | 2017-06-29 07:00 | 50480.9545 | 39.996
Devonshire Building | 2017-06-29 07:15 | 50480.9645 | 39.996
Devonshire Building | 2017-06-29 07:30 | 50481.4895 | 2099.988
Devonshire Building | 2017-06-29 07:45 | 50481.5045 | 60.012
Devonshire Building | 2017-06-29 08:00 | 50481.5295 | 100.008
Devonshire Building | 2017-06-29 08:15 | 50481.5445 | 60.012
Devonshire Building | 2017-06-29 08:30 | 50481.5695 | 100.008
Devonshire Building | 2017-06-29 08:45 | 50481.5895 | 79.992
Devonshire Building | 2017-06-29 09:00 | 50481.6045 | 60.012
Devonshire Building | 2017-06-29 09:15 | 50482.0445 | 1760.004
Devonshire Building | 2017-06-29 09:30 | 50482.2445 | 799.992
Devonshire Building | 2017-06-29 09:45 | 50482.3045 | 240.012
Devonshire Building | 2017-06-29 10:00 | 50482.3645 | 240.012
Devonshire Building | 2017-06-29 10:15 | 50482.4395 | 299.988
Devonshire Building | 2017-06-29 10:30 | 50482.5145 | 299.988
Devonshire Building | 2017-06-29 10:45 | 50483.1095 | 2379.996
Devonshire Building | 2017-06-29 11:00 | 50483.1845 | 299.988
Devonshire Building | 2017-06-29 11:15 | 50483.2545 | 280.008
Devonshire Building | 2017-06-29 11:30 | 50483.3245 | 280.008
Devonshire Building | 2017-06-29 11:45 | 50483.3895 | 259.992
Devonshire Building | 2017-06-29 12:00 | 50483.4445 | 219.996
Devonshire Building | 2017-06-29 12:15 | 50483.4895 | 180
Devonshire Building | 2017-06-29 12:30 | 50484.0395 | 2199.996
Devonshire Building | 2017-06-29 12:45 | 50484.0695 | 119.988
Devonshire Building | 2017-06-29 13:00 | 50484.0995 | 119.988
Devonshire Building | 2017-06-29 13:15 | 50484.1295 | 119.988
Devonshire Building | 2017-06-29 13:30 | 50484.1645 | 140.004
Devonshire Building | 2017-06-29 13:45 | 50484.2145 | 200.016
Devonshire Building | 2017-06-29 14:00 | 50484.2595 | 180
Devonshire Building | 2017-06-29 14:15 | 50484.8295 | 2279.988
Devonshire Building | 2017-06-29 14:30 | 50484.8895 | 240.012
Devonshire Building | 2017-06-29 14:45 | 50484.9545 | 259.992
Devonshire Building | 2017-06-29 15:00 | 50485.0195 | 259.992
Devonshire Building | 2017-06-29 15:15 | 50485.0845 | 259.992
Devonshire Building | 2017-06-29 15:30 | 50485.1645 | 320.004
Devonshire Building | 2017-06-29 15:45 | 50485.5395 | 1500.012
Devonshire Building | 2017-06-29 16:00 | 50485.8445 | 1220.004
Devonshire Building | 2017-06-29 16:15 | 50485.9195 | 299.988
Devonshire Building | 2017-06-29 16:30 | 50485.9845 | 259.992
Devonshire Building | 2017-06-29 16:45 | 50486.0395 | 219.996
Devonshire Building | 2017-06-29 17:00 | 50486.0945 | 219.996
Devonshire Building | 2017-06-29 17:15 | 50486.1345 | 159.984
Devonshire Building | 2017-06-29 17:30 | 50486.1695 | 140.004
Devonshire Building | 2017-06-29 17:45 | 50486.2045 | 140.004
Devonshire Building | 2017-06-29 18:00 | 50486.2345 | 119.988
Devonshire Building | 2017-06-29 18:15 | 50486.2595 | 100.008
Devonshire Building | 2017-06-29 18:30 | 50486.2845 | 100.008
Devonshire Building | 2017-06-29 18:45 | 50486.3045 | 79.992
Devonshire Building | 2017-06-29 19:00 | 50486.3245 | 79.992
Devonshire Building | 2017-06-29 19:15 | 50486.3445 | 79.992
Devonshire Building | 2017-06-29 19:30 | 50486.3645 | 79.992
Devonshire Building | 2017-06-29 19:45 | 50486.3795 | 60.012
Devonshire Building | 2017-06-29 20:00 | 50486.3945 | 60.012
Devonshire Building | 2017-06-29 20:15 | 50486.4095 | 60.012
Devonshire Building | 2017-06-29 20:30 | 50486.4245 | 60.012
Devonshire Building | 2017-06-29 20:45 | 50486.4645 | 159.984
Devonshire Building | 2017-06-29 21:00 | 50486.4695 | 20.016
Devonshire Building | 2017-06-29 21:15 | 50486.4745 | 20.016
Devonshire Building | 2017-06-29 21:30 | 50486.4795 | 20.016
Devonshire Building | 2017-06-29 21:45 | 50486.4895 | 39.996
Devonshire Building | 2017-06-29 22:00 | 50486.4945 | 20.016
Devonshire Building | 2017-06-29 22:15 | 50486.4995 | 20.016
Devonshire Building | 2017-06-29 22:30 | 50486.5045 | 20.016
Devonshire Building | 2017-06-29 22:45 | 50486.5145 | 39.996
Devonshire Building | 2017-06-29 23:00 | 50486.5195 | 20.016
Devonshire Building | 2017-06-29 23:15 | 50486.5245 | 20.016
Devonshire Building | 2017-06-29 23:30 | 50486.5295 | 20.016
Devonshire Building | 2017-06-29 23:45 | 50486.5395 | 39.996
Devonshire Building | 2017-06-30 | 50486.543 | 20.016
Devonshire Building | 2017-06-30 00:15 | 50486.548 | 20.016
Devonshire Building | 2017-06-30 00:30 | 50486.553 | 20.016
Devonshire Building | 2017-06-30 00:45 | 50486.558 | 20.016
Devonshire Building | 2017-06-30 01:00 | 50486.568 | 39.996
Devonshire Building | 2017-06-30 01:15 | 50486.573 | 20.016
Devonshire Building | 2017-06-30 01:30 | 50486.578 | 20.016
Devonshire Building | 2017-06-30 01:45 | 50486.858 | 1119.996
Devonshire Building | 2017-06-30 02:00 | 50487.098 | 960.012
Devonshire Building | 2017-06-30 02:15 | 50487.103 | 20.016
Devonshire Building | 2017-06-30 02:30 | 50487.108 | 20.016
Devonshire Building | 2017-06-30 02:45 | 50487.118 | 39.996
Devonshire Building | 2017-06-30 03:00 | 50487.123 | 20.016
Devonshire Building | 2017-06-30 03:15 | 50487.128 | 20.016
Devonshire Building | 2017-06-30 03:30 | 50487.133 | 20.016
Devonshire Building | 2017-06-30 03:45 | 50487.138 | 20.016
Devonshire Building | 2017-06-30 04:00 | 50487.148 | 39.996
Devonshire Building | 2017-06-30 04:15 | 50487.153 | 20.016
Devonshire Building | 2017-06-30 04:30 | 50487.158 | 20.016
Devonshire Building | 2017-06-30 04:45 | 50487.163 | 20.016
Devonshire Building | 2017-06-30 05:00 | 50487.173 | 39.996
Devonshire Building | 2017-06-30 05:15 | 50487.178 | 20.016
Devonshire Building | 2017-06-30 05:30 | 50487.188 | 39.996
Devonshire Building | 2017-06-30 05:45 | 50487.193 | 20.016
Devonshire Building | 2017-06-30 06:00 | 50487.203 | 39.996
Devonshire Building | 2017-06-30 06:15 | 50487.218 | 60.012
Devonshire Building | 2017-06-30 06:30 | 50487.223 | 20.016
Devonshire Building | 2017-06-30 06:45 | 50487.228 | 20.016
Devonshire Building | 2017-06-30 07:00 | 50487.238 | 39.996
Devonshire Building | 2017-06-30 07:15 | 50487.253 | 60.012
Devonshire Building | 2017-06-30 07:30 | 50487.263 | 39.996
Devonshire Building | 2017-06-30 07:45 | 50487.293 | 119.988
Devonshire Building | 2017-06-30 08:00 | 50487.318 | 100.008
Devonshire Building | 2017-06-30 08:15 | 50487.338 | 79.992
Devonshire Building | 2017-06-30 08:30 | 50487.733 | 1580.004
Devonshire Building | 2017-06-30 08:45 | 50487.908 | 699.984
Devonshire Building | 2017-06-30 09:00 | 50487.943 | 140.004
Devonshire Building | 2017-06-30 09:15 | 50487.983 | 159.984
Devonshire Building | 2017-06-30 09:30 | 50488.063 | 320.004
Devonshire Building | 2017-06-30 09:45 | 50488.148 | 339.984
Devonshire Building | 2017-06-30 10:00 | 50488.763 | 2459.988
Devonshire Building | 2017-06-30 10:15 | 50488.873 | 439.992
Devonshire Building | 2017-06-30 10:30 | 50488.978 | 420.012
Devonshire Building | 2017-06-30 10:45 | 50489.063 | 339.984
Devonshire Building | 2017-06-30 11:00 | 50489.143 | 320.004
Devonshire Building | 2017-06-30 11:15 | 50489.753 | 2440.008
Devonshire Building | 2017-06-30 11:30 | 50489.818 | 259.992
Devonshire Building | 2017-06-30 11:45 | 50489.883 | 259.992
Devonshire Building | 2017-06-30 12:00 | 50489.953 | 280.008
Devonshire Building | 2017-06-30 12:15 | 50490.018 | 259.992
Devonshire Building | 2017-06-30 12:30 | 50490.078 | 240.012
Devonshire Building | 2017-06-30 12:45 | 50490.558 | 1919.988
Devonshire Building | 2017-06-30 13:00 | 50490.723 | 659.988
Devonshire Building | 2017-06-30 13:15 | 50490.768 | 180
Devonshire Building | 2017-06-30 13:30 | 50490.803 | 140.004
Devonshire Building | 2017-06-30 13:45 | 50490.833 | 119.988
Devonshire Building | 2017-06-30 14:00 | 50490.858 | 100.008
Devonshire Building | 2017-06-30 14:15 | 50491.388 | 2120.004
Devonshire Building | 2017-06-30 14:30 | 50491.468 | 320.004
Devonshire Building | 2017-06-30 14:45 | 50491.488 | 79.992
Devonshire Building | 2017-06-30 15:00 | 50491.513 | 100.008
Devonshire Building | 2017-06-30 15:15 | 50491.538 | 100.008
Devonshire Building | 2017-06-30 15:30 | 50491.568 | 119.988
Devonshire Building | 2017-06-30 15:45 | 50491.588 | 79.992
Devonshire Building | 2017-06-30 16:00 | 50491.613 | 100.008
Devonshire Building | 2017-06-30 16:15 | 50492.163 | 2199.996
Devonshire Building | 2017-06-30 16:30 | 50492.198 | 140.004
Devonshire Building | 2017-06-30 16:45 | 50492.233 | 140.004
Devonshire Building | 2017-06-30 17:00 | 50492.268 | 140.004
Devonshire Building | 2017-06-30 17:15 | 50492.298 | 119.988
Devonshire Building | 2017-06-30 17:30 | 50492.333 | 140.004
Devonshire Building | 2017-06-30 17:45 | 50492.363 | 119.988
Devonshire Building | 2017-06-30 18:00 | 50492.393 | 119.988
Devonshire Building | 2017-06-30 18:15 | 50492.423 | 119.988
Devonshire Building | 2017-06-30 18:30 | 50492.453 | 119.988
Devonshire Building | 2017-06-30 18:45 | 50492.478 | 100.008
Devonshire Building | 2017-06-30 19:00 | 50492.508 | 119.988
Devonshire Building | 2017-06-30 19:15 | 50492.533 | 100.008
Devonshire Building | 2017-06-30 19:30 | 50492.558 | 100.008
Devonshire Building | 2017-06-30 19:45 | 50492.583 | 100.008
Devonshire Building | 2017-06-30 20:00 | 50492.603 | 79.992
Devonshire Building | 2017-06-30 20:15 | 50492.628 | 100.008
Devonshire Building | 2017-06-30 20:30 | 50492.648 | 79.992
Devonshire Building | 2017-06-30 20:45 | 50492.693 | 180
Devonshire Building | 2017-06-30 21:00 | 50492.713 | 79.992
Devonshire Building | 2017-06-30 21:15 | 50492.728 | 60.012
Devonshire Building | 2017-06-30 21:30 | 50492.748 | 79.992
Devonshire Building | 2017-06-30 21:45 | 50492.763 | 60.012
Devonshire Building | 2017-06-30 22:00 | 50492.778 | 60.012
Devonshire Building | 2017-06-30 22:15 | 50492.798 | 79.992
Devonshire Building | 2017-06-30 22:30 | 50492.813 | 60.012
Devonshire Building | 2017-06-30 22:45 | 50492.833 | 79.992
Devonshire Building | 2017-06-30 23:00 | 50492.848 | 60.012
Devonshire Building | 2017-06-30 23:15 | 50492.863 | 60.012
Devonshire Building | 2017-06-30 23:30 | 50492.883 | 79.992
Devonshire Building | 2017-06-30 23:45 | 50492.898 | 60.012
Devonshire Building | 2017-07-01 | 50492.9141 | 60.012
Devonshire Building | 2017-07-01 00:15 | 50492.9291 | 60.012
Devonshire Building | 2017-07-01 00:30 | 50492.9491 | 79.992
Devonshire Building | 2017-07-01 00:45 | 50492.9641 | 60.012
Devonshire Building | 2017-07-01 01:00 | 50492.9791 | 60.012
Devonshire Building | 2017-07-01 01:15 | 50492.9991 | 79.992
Devonshire Building | 2017-07-01 01:30 | 50493.0141 | 60.012
Devonshire Building | 2017-07-01 01:45 | 50493.0291 | 60.012
Devonshire Building | 2017-07-01 02:00 | 50493.0441 | 60.012
Devonshire Building | 2017-07-01 02:15 | 50493.0591 | 60.012
Devonshire Building | 2017-07-01 02:30 | 50493.5791 | 2080.008
Devonshire Building | 2017-07-01 02:45 | 50493.5891 | 39.996
Devonshire Building | 2017-07-01 03:00 | 50493.6041 | 60.012
Devonshire Building | 2017-07-01 03:15 | 50493.6141 | 39.996
Devonshire Building | 2017-07-01 03:30 | 50493.6291 | 60.012
Devonshire Building | 2017-07-01 03:45 | 50493.6391 | 39.996
Devonshire Building | 2017-07-01 04:00 | 50493.6541 | 60.012
Devonshire Building | 2017-07-01 04:15 | 50493.6691 | 60.012
Devonshire Building | 2017-07-01 04:30 | 50493.6841 | 60.012
Devonshire Building | 2017-07-01 04:45 | 50493.6991 | 60.012
Devonshire Building | 2017-07-01 05:00 | 50493.7141 | 60.012
Devonshire Building | 2017-07-01 05:15 | 50493.7291 | 60.012
Devonshire Building | 2017-07-01 05:30 | 50493.7441 | 60.012
Devonshire Building | 2017-07-01 05:45 | 50493.7591 | 60.012
Devonshire Building | 2017-07-01 06:00 | 50493.7741 | 60.012
Devonshire Building | 2017-07-01 06:15 | 50493.7891 | 60.012
Devonshire Building | 2017-07-01 06:30 | 50493.8041 | 60.012
Devonshire Building | 2017-07-01 06:45 | 50493.8141 | 39.996
Devonshire Building | 2017-07-01 07:00 | 50493.8291 | 60.012
Devonshire Building | 2017-07-01 07:15 | 50493.8391 | 39.996
Devonshire Building | 2017-07-01 07:30 | 50493.8541 | 60.012
Devonshire Building | 2017-07-01 07:45 | 50493.8741 | 79.992
Devonshire Building | 2017-07-01 08:00 | 50493.9041 | 119.988
Devonshire Building | 2017-07-01 08:15 | 50493.9341 | 119.988
Devonshire Building | 2017-07-01 08:30 | 50493.9641 | 119.988
Devonshire Building | 2017-07-01 08:45 | 50493.9891 | 100.008
Devonshire Building | 2017-07-01 09:00 | 50494.0191 | 119.988
Devonshire Building | 2017-07-01 09:15 | 50494.0441 | 100.008
Devonshire Building | 2017-07-01 09:30 | 50494.0741 | 119.988
Devonshire Building | 2017-07-01 09:45 | 50494.1041 | 119.988
Devonshire Building | 2017-07-01 10:00 | 50494.1291 | 100.008
Devonshire Building | 2017-07-01 10:15 | 50494.1541 | 100.008
Devonshire Building | 2017-07-01 10:30 | 50494.1691 | 60.012
Devonshire Building | 2017-07-01 10:45 | 50494.1841 | 60.012
Devonshire Building | 2017-07-01 11:00 | 50494.1991 | 60.012
Devonshire Building | 2017-07-01 11:15 | 50494.2141 | 60.012
Devonshire Building | 2017-07-01 11:30 | 50494.5391 | 1299.996
Devonshire Building | 2017-07-01 11:45 | 50494.7841 | 979.992
Devonshire Building | 2017-07-01 12:00 | 50494.8091 | 100.008
Devonshire Building | 2017-07-01 12:15 | 50494.8391 | 119.988
Devonshire Building | 2017-07-01 12:30 | 50494.8741 | 140.004
Devonshire Building | 2017-07-01 12:45 | 50494.9091 | 140.004
Devonshire Building | 2017-07-01 13:00 | 50494.9441 | 140.004
Devonshire Building | 2017-07-01 13:15 | 50494.9791 | 140.004
Devonshire Building | 2017-07-01 13:30 | 50495.0091 | 119.988
Devonshire Building | 2017-07-01 13:45 | 50495.0391 | 119.988
Devonshire Building | 2017-07-01 14:00 | 50495.0691 | 119.988
Devonshire Building | 2017-07-01 14:15 | 50495.0991 | 119.988
Devonshire Building | 2017-07-01 14:30 | 50495.1341 | 140.004
Devonshire Building | 2017-07-01 14:45 | 50495.1591 | 100.008
Devonshire Building | 2017-07-01 15:00 | 50495.1841 | 100.008
Devonshire Building | 2017-07-01 15:15 | 50495.2091 | 100.008
Devonshire Building | 2017-07-01 15:30 | 50495.2391 | 119.988
Devonshire Building | 2017-07-01 15:45 | 50495.2641 | 100.008
Devonshire Building | 2017-07-01 16:00 | 50495.2891 | 100.008
Devonshire Building | 2017-07-01 16:15 | 50495.3141 | 100.008
Devonshire Building | 2017-07-01 16:30 | 50495.3341 | 79.992
Devonshire Building | 2017-07-01 16:45 | 50495.3591 | 100.008
Devonshire Building | 2017-07-01 17:00 | 50495.3791 | 79.992
Devonshire Building | 2017-07-01 17:15 | 50495.4041 | 100.008
Devonshire Building | 2017-07-01 17:30 | 50495.4241 | 79.992
Devonshire Building | 2017-07-01 17:45 | 50495.4441 | 79.992
Devonshire Building | 2017-07-01 18:00 | 50495.4641 | 79.992
Devonshire Building | 2017-07-01 18:15 | 50495.4891 | 100.008
Devonshire Building | 2017-07-01 18:30 | 50495.5091 | 79.992
Devonshire Building | 2017-07-01 18:45 | 50495.5291 | 79.992
Devonshire Building | 2017-07-01 19:00 | 50495.5441 | 60.012
Devonshire Building | 2017-07-01 19:15 | 50495.5641 | 79.992
Devonshire Building | 2017-07-01 19:30 | 50495.5841 | 79.992
Devonshire Building | 2017-07-01 19:45 | 50495.6041 | 79.992
Devonshire Building | 2017-07-01 20:00 | 50495.6191 | 60.012
Devonshire Building | 2017-07-01 20:15 | 50496.1341 | 2059.992
Devonshire Building | 2017-07-01 20:30 | 50496.1441 | 39.996
Devonshire Building | 2017-07-01 20:45 | 50496.1591 | 60.012
Devonshire Building | 2017-07-01 21:00 | 50496.1691 | 39.996
Devonshire Building | 2017-07-01 21:15 | 50496.1791 | 39.996
Devonshire Building | 2017-07-01 21:30 | 50496.1891 | 39.996
Devonshire Building | 2017-07-01 21:45 | 50496.1991 | 39.996
Devonshire Building | 2017-07-01 22:00 | 50496.2091 | 39.996
Devonshire Building | 2017-07-01 22:15 | 50496.2241 | 60.012
Devonshire Building | 2017-07-01 22:30 | 50496.2341 | 39.996
Devonshire Building | 2017-07-01 22:45 | 50496.2491 | 60.012
Devonshire Building | 2017-07-01 23:00 | 50496.2591 | 39.996
Devonshire Building | 2017-07-01 23:15 | 50496.2691 | 39.996
Devonshire Building | 2017-07-01 23:30 | 50496.2841 | 60.012
Devonshire Building | 2017-07-01 23:45 | 50496.2941 | 39.996
Devonshire Building | 2017-07-02 | 50496.3047 | 39.996
Devonshire Building | 2017-07-02 00:15 | 50496.3147 | 39.996
Devonshire Building | 2017-07-02 00:30 | 50496.3297 | 60.012
Devonshire Building | 2017-07-02 00:45 | 50496.3397 | 39.996
Devonshire Building | 2017-07-02 01:00 | 50496.3497 | 39.996
Devonshire Building | 2017-07-02 01:15 | 50496.3597 | 39.996
Devonshire Building | 2017-07-02 01:30 | 50496.3697 | 39.996
Devonshire Building | 2017-07-02 01:45 | 50496.3847 | 60.012
Devonshire Building | 2017-07-02 02:00 | 50496.3947 | 39.996
Devonshire Building | 2017-07-02 02:15 | 50496.4047 | 39.996
Devonshire Building | 2017-07-02 02:30 | 50496.4197 | 60.012
Devonshire Building | 2017-07-02 02:45 | 50496.4347 | 60.012
Devonshire Building | 2017-07-02 03:00 | 50496.4497 | 60.012
Devonshire Building | 2017-07-02 03:15 | 50496.4647 | 60.012
Devonshire Building | 2017-07-02 03:30 | 50496.4847 | 79.992
Devonshire Building | 2017-07-02 03:45 | 50496.5097 | 100.008
Devonshire Building | 2017-07-02 04:00 | 50496.5297 | 79.992
Devonshire Building | 2017-07-02 04:15 | 50496.5497 | 79.992
Devonshire Building | 2017-07-02 04:30 | 50496.5697 | 79.992
Devonshire Building | 2017-07-02 04:45 | 50496.5947 | 100.008
Devonshire Building | 2017-07-02 05:00 | 50496.6147 | 79.992
Devonshire Building | 2017-07-02 05:15 | 50496.6347 | 79.992
Devonshire Building | 2017-07-02 05:30 | 50496.6547 | 79.992
Devonshire Building | 2017-07-02 05:45 | 50496.6797 | 100.008
Devonshire Building | 2017-07-02 06:00 | 50496.6997 | 79.992
Devonshire Building | 2017-07-02 06:15 | 50496.7197 | 79.992
Devonshire Building | 2017-07-02 06:30 | 50496.7397 | 79.992
Devonshire Building | 2017-07-02 06:45 | 50496.7647 | 100.008
Devonshire Building | 2017-07-02 07:00 | 50496.7847 | 79.992
Devonshire Building | 2017-07-02 07:15 | 50496.8097 | 100.008
Devonshire Building | 2017-07-02 07:30 | 50496.8297 | 79.992
Devonshire Building | 2017-07-02 07:45 | 50496.8597 | 119.988
Devonshire Building | 2017-07-02 08:00 | 50496.8997 | 159.984
Devonshire Building | 2017-07-02 08:15 | 50496.9347 | 140.004
Devonshire Building | 2017-07-02 08:30 | 50496.9747 | 159.984
Devonshire Building | 2017-07-02 08:45 | 50497.0097 | 140.004
Devonshire Building | 2017-07-02 09:00 | 50497.0497 | 159.984
Devonshire Building | 2017-07-02 09:15 | 50497.0847 | 140.004
Devonshire Building | 2017-07-02 09:30 | 50497.1197 | 140.004
Devonshire Building | 2017-07-02 09:45 | 50497.1547 | 140.004
Devonshire Building | 2017-07-02 10:00 | 50497.1947 | 159.984
Devonshire Building | 2017-07-02 10:15 | 50497.2197 | 100.008
Devonshire Building | 2017-07-02 10:30 | 50497.2397 | 79.992
Devonshire Building | 2017-07-02 10:45 | 50497.2597 | 79.992
Devonshire Building | 2017-07-02 11:00 | 50497.2797 | 79.992
Devonshire Building | 2017-07-02 11:15 | 50497.2997 | 79.992
Devonshire Building | 2017-07-02 11:30 | 50497.3197 | 79.992
Devonshire Building | 2017-07-02 11:45 | 50497.3397 | 79.992
Devonshire Building | 2017-07-02 12:00 | 50497.3597 | 79.992
Devonshire Building | 2017-07-02 12:15 | 50497.3797 | 79.992
Devonshire Building | 2017-07-02 12:30 | 50497.3997 | 79.992
Devonshire Building | 2017-07-02 12:45 | 50497.4197 | 79.992
Devonshire Building | 2017-07-02 13:00 | 50497.4397 | 79.992
Devonshire Building | 2017-07-02 13:15 | 50497.4597 | 79.992
Devonshire Building | 2017-07-02 13:30 | 50497.4796 | 79.992
Devonshire Building | 2017-07-02 13:45 | 50497.4996 | 79.992
Devonshire Building | 2017-07-02 14:00 | 50498.0196 | 2080.008
Devonshire Building | 2017-07-02 14:15 | 50498.0347 | 60.012
Devonshire Building | 2017-07-02 14:30 | 50498.0497 | 60.012
Devonshire Building | 2017-07-02 14:45 | 50498.0647 | 60.012
Devonshire Building | 2017-07-02 15:00 | 50498.0847 | 79.992
Devonshire Building | 2017-07-02 15:15 | 50498.1047 | 79.992
Devonshire Building | 2017-07-02 15:30 | 50498.1247 | 79.992
Devonshire Building | 2017-07-02 15:45 | 50498.1447 | 79.992
Devonshire Building | 2017-07-02 16:00 | 50498.1646 | 79.992
Devonshire Building | 2017-07-02 16:15 | 50498.1846 | 79.992
Devonshire Building | 2017-07-02 16:30 | 50498.2046 | 79.992
Devonshire Building | 2017-07-02 16:45 | 50498.2196 | 60.012
Devonshire Building | 2017-07-02 17:00 | 50498.2396 | 79.992
Devonshire Building | 2017-07-02 17:15 | 50498.2596 | 79.992
Devonshire Building | 2017-07-02 17:30 | 50498.2746 | 60.012
Devonshire Building | 2017-07-02 17:45 | 50498.2946 | 79.992
Devonshire Building | 2017-07-02 18:00 | 50498.3096 | 60.012
Devonshire Building | 2017-07-02 18:15 | 50498.3296 | 79.992
Devonshire Building | 2017-07-02 18:30 | 50498.3446 | 60.012
Devonshire Building | 2017-07-02 18:45 | 50498.3597 | 60.012
Devonshire Building | 2017-07-02 19:00 | 50498.3747 | 60.012
Devonshire Building | 2017-07-02 19:15 | 50498.3947 | 79.992
Devonshire Building | 2017-07-02 19:30 | 50498.4097 | 60.012
Devonshire Building | 2017-07-02 19:45 | 50498.4247 | 60.012
Devonshire Building | 2017-07-02 20:00 | 50498.4397 | 60.012
Devonshire Building | 2017-07-02 20:15 | 50498.4547 | 60.012
Devonshire Building | 2017-07-02 20:30 | 50498.4697 | 60.012
Devonshire Building | 2017-07-02 20:45 | 50498.4997 | 119.988
Devonshire Building | 2017-07-02 21:00 | 50498.5147 | 60.012
Devonshire Building | 2017-07-02 21:15 | 50498.5297 | 60.012
Devonshire Building | 2017-07-02 21:30 | 50498.5447 | 60.012
Devonshire Building | 2017-07-02 21:45 | 50498.5647 | 79.992
Devonshire Building | 2017-07-02 22:00 | 50498.5797 | 60.012
Devonshire Building | 2017-07-02 22:15 | 50498.5947 | 60.012
Devonshire Building | 2017-07-02 22:30 | 50498.6097 | 60.012
Devonshire Building | 2017-07-02 22:45 | 50498.6247 | 60.012
Devonshire Building | 2017-07-02 23:00 | 50498.6397 | 60.012
Devonshire Building | 2017-07-02 23:15 | 50498.6597 | 79.992
Devonshire Building | 2017-07-02 23:30 | 50498.6747 | 60.012
Devonshire Building | 2017-07-02 23:45 | 50498.6897 | 60.012
Devonshire Building | 2017-07-03 | 50498.7031 | 60.012
Devonshire Building | 2017-07-03 00:15 | 50498.7181 | 60.012
Devonshire Building | 2017-07-03 00:30 | 50498.7331 | 60.012
Devonshire Building | 2017-07-03 00:45 | 50498.7481 | 60.012
Devonshire Building | 2017-07-03 01:00 | 50498.7631 | 60.012
Devonshire Building | 2017-07-03 01:15 | 50498.7831 | 79.992
Devonshire Building | 2017-07-03 01:30 | 50498.7981 | 60.012
Devonshire Building | 2017-07-03 01:45 | 50498.8131 | 60.012
Devonshire Building | 2017-07-03 02:00 | 50498.8281 | 60.012
Devonshire Building | 2017-07-03 02:15 | 50498.8432 | 60.012
Devonshire Building | 2017-07-03 02:30 | 50498.8582 | 60.012
Devonshire Building | 2017-07-03 02:45 | 50498.8732 | 60.012
Devonshire Building | 2017-07-03 03:00 | 50498.8882 | 60.012
Devonshire Building | 2017-07-03 03:15 | 50498.9032 | 60.012
Devonshire Building | 2017-07-03 03:30 | 50498.9182 | 60.012
Devonshire Building | 2017-07-03 03:45 | 50498.9332 | 60.012
Devonshire Building | 2017-07-03 04:00 | 50498.9482 | 60.012
Devonshire Building | 2017-07-03 04:15 | 50498.9682 | 79.992
Devonshire Building | 2017-07-03 04:30 | 50498.9832 | 60.012
Devonshire Building | 2017-07-03 04:45 | 50498.9982 | 60.012
Devonshire Building | 2017-07-03 05:00 | 50499.0132 | 60.012
Devonshire Building | 2017-07-03 05:15 | 50499.0282 | 60.012
Devonshire Building | 2017-07-03 05:30 | 50499.0482 | 79.992
Devonshire Building | 2017-07-03 05:45 | 50499.0632 | 60.012
Devonshire Building | 2017-07-03 06:00 | 50499.0782 | 60.012
Devonshire Building | 2017-07-03 06:15 | 50499.0932 | 60.012
Devonshire Building | 2017-07-03 06:30 | 50499.6432 | 2199.996
Devonshire Building | 2017-07-03 06:45 | 50499.6682 | 100.008
Devonshire Building | 2017-07-03 07:00 | 50499.7132 | 180
Devonshire Building | 2017-07-03 07:15 | 50499.7532 | 159.984
Devonshire Building | 2017-07-03 07:30 | 50499.7982 | 180
Devonshire Building | 2017-07-03 07:45 | 50499.8532 | 219.996
Devonshire Building | 2017-07-03 08:00 | 50499.9182 | 259.992
Devonshire Building | 2017-07-03 08:15 | 50499.9832 | 259.992
Devonshire Building | 2017-07-03 08:30 | 50500.0432 | 240.012
Devonshire Building | 2017-07-03 08:45 | 50500.6432 | 2400.012
Devonshire Building | 2017-07-03 09:00 | 50500.7082 | 259.992
Devonshire Building | 2017-07-03 09:15 | 50500.8232 | 460.008
Devonshire Building | 2017-07-03 09:30 | 50500.9582 | 540
Devonshire Building | 2017-07-03 09:45 | 50501.7032 | 2980.008
Devonshire Building | 2017-07-03 10:00 | 50501.9132 | 839.988
Devonshire Building | 2017-07-03 10:15 | 50502.0782 | 659.988
Devonshire Building | 2017-07-03 10:30 | 50502.1982 | 479.988
Devonshire Building | 2017-07-03 10:45 | 50502.2882 | 360
Devonshire Building | 2017-07-03 11:00 | 50502.3682 | 320.004
Devonshire Building | 2017-07-03 11:15 | 50502.9782 | 2440.008
Devonshire Building | 2017-07-03 11:30 | 50503.0682 | 360
Devonshire Building | 2017-07-03 11:45 | 50503.1532 | 339.984
Devonshire Building | 2017-07-03 12:00 | 50503.2282 | 299.988
Devonshire Building | 2017-07-03 12:15 | 50503.2982 | 280.008
Devonshire Building | 2017-07-03 12:30 | 50503.8732 | 2300.004
Devonshire Building | 2017-07-03 12:45 | 50503.9082 | 140.004
Devonshire Building | 2017-07-03 13:00 | 50503.9482 | 159.984
Devonshire Building | 2017-07-03 13:15 | 50503.9932 | 180
Devonshire Building | 2017-07-03 13:30 | 50504.0382 | 180
Devonshire Building | 2017-07-03 13:45 | 50504.0832 | 180
Devonshire Building | 2017-07-03 14:00 | 50504.6682 | 2340
Devonshire Building | 2017-07-03 14:15 | 50504.7282 | 240.012
Devonshire Building | 2017-07-03 14:30 | 50504.7982 | 280.008
Devonshire Building | 2017-07-03 14:45 | 50504.8882 | 360
Devonshire Building | 2017-07-03 15:00 | 50504.9932 | 420.012
Devonshire Building | 2017-07-03 15:15 | 50505.0982 | 420.012
Devonshire Building | 2017-07-03 15:30 | 50505.2782 | 720
Devonshire Building | 2017-07-03 15:45 | 50505.8432 | 2260.008
Devonshire Building | 2017-07-03 16:00 | 50505.9282 | 339.984
Devonshire Building | 2017-07-03 16:15 | 50506.0032 | 299.988
Devonshire Building | 2017-07-03 16:30 | 50506.0782 | 299.988
Devonshire Building | 2017-07-03 16:45 | 50506.1582 | 320.004
Devonshire Building | 2017-07-03 17:00 | 50506.2282 | 280.008
Devonshire Building | 2017-07-03 17:15 | 50506.2732 | 180
Devonshire Building | 2017-07-03 17:30 | 50506.3132 | 159.984
Devonshire Building | 2017-07-03 17:45 | 50506.3482 | 140.004
Devonshire Building | 2017-07-03 18:00 | 50506.3782 | 119.988
Devonshire Building | 2017-07-03 18:15 | 50506.4032 | 100.008
Devonshire Building | 2017-07-03 18:30 | 50506.4282 | 100.008
Devonshire Building | 2017-07-03 18:45 | 50506.4482 | 79.992
Devonshire Building | 2017-07-03 19:00 | 50506.5682 | 479.988
Devonshire Building | 2017-07-03 19:15 | 50506.9782 | 1640.016
Devonshire Building | 2017-07-03 19:30 | 50506.9882 | 39.996
Devonshire Building | 2017-07-03 19:45 | 50506.9932 | 20.016
Devonshire Building | 2017-07-03 20:00 | 50507.0032 | 39.996
Devonshire Building | 2017-07-03 20:15 | 50507.0132 | 39.996
Devonshire Building | 2017-07-03 20:30 | 50507.0182 | 20.016
Devonshire Building | 2017-07-03 20:45 | 50507.0332 | 60.012
Devonshire Building | 2017-07-03 21:00 | 50507.0382 | 20.016
Devonshire Building | 2017-07-03 21:15 | 50507.0482 | 39.996
Devonshire Building | 2017-07-03 21:30 | 50507.0532 | 20.016
Devonshire Building | 2017-07-03 21:45 | 50507.0632 | 39.996
Devonshire Building | 2017-07-03 22:00 | 50507.0682 | 20.016
Devonshire Building | 2017-07-03 22:15 | 50507.0782 | 39.996
Devonshire Building | 2017-07-03 22:30 | 50507.0882 | 39.996
Devonshire Building | 2017-07-03 22:45 | 50507.0932 | 20.016
Devonshire Building | 2017-07-03 23:00 | 50507.1032 | 39.996
Devonshire Building | 2017-07-03 23:15 | 50507.1082 | 20.016
Devonshire Building | 2017-07-03 23:30 | 50507.1182 | 39.996
Devonshire Building | 2017-07-03 23:45 | 50507.1232 | 20.016
Devonshire Building | 2017-07-04 | 50507.1328 | 39.996
Devonshire Building | 2017-07-04 00:15 | 50507.1378 | 20.016
Devonshire Building | 2017-07-04 00:30 | 50507.1478 | 39.996
Devonshire Building | 2017-07-04 00:45 | 50507.1528 | 20.016
Devonshire Building | 2017-07-04 01:00 | 50507.1578 | 20.016
Devonshire Building | 2017-07-04 01:15 | 50507.1678 | 39.996
Devonshire Building | 2017-07-04 01:30 | 50507.1728 | 20.016
Devonshire Building | 2017-07-04 01:45 | 50507.1778 | 20.016
Devonshire Building | 2017-07-04 02:00 | 50507.1878 | 39.996
Devonshire Building | 2017-07-04 02:15 | 50507.1928 | 20.016
Devonshire Building | 2017-07-04 02:30 | 50507.1978 | 20.016
Devonshire Building | 2017-07-04 02:45 | 50507.2078 | 39.996
Devonshire Building | 2017-07-04 03:00 | 50507.2128 | 20.016
Devonshire Building | 2017-07-04 03:15 | 50507.2178 | 20.016
Devonshire Building | 2017-07-04 03:30 | 50507.2278 | 39.996
Devonshire Building | 2017-07-04 03:45 | 50507.2328 | 20.016
Devonshire Building | 2017-07-04 04:00 | 50507.2378 | 20.016
Devonshire Building | 2017-07-04 04:15 | 50507.2429 | 20.016
Devonshire Building | 2017-07-04 04:30 | 50507.2529 | 39.996
Devonshire Building | 2017-07-04 04:45 | 50507.2579 | 20.016
Devonshire Building | 2017-07-04 05:00 | 50507.2629 | 20.016
Devonshire Building | 2017-07-04 05:15 | 50507.2729 | 39.996
Devonshire Building | 2017-07-04 05:30 | 50507.2779 | 20.016
Devonshire Building | 2017-07-04 05:45 | 50507.2879 | 39.996
Devonshire Building | 2017-07-04 06:00 | 50507.2929 | 20.016
Devonshire Building | 2017-07-04 06:15 | 50507.3079 | 60.012
Devonshire Building | 2017-07-04 06:30 | 50507.3179 | 39.996
Devonshire Building | 2017-07-04 06:45 | 50507.3279 | 39.996
Devonshire Building | 2017-07-04 07:00 | 50507.3579 | 119.988
Devonshire Building | 2017-07-04 07:15 | 50507.8729 | 2059.992
Devonshire Building | 2017-07-04 07:30 | 50507.9029 | 119.988
Devonshire Building | 2017-07-04 07:45 | 50507.9529 | 200.016
Devonshire Building | 2017-07-04 08:00 | 50508.0329 | 320.004
Devonshire Building | 2017-07-04 08:15 | 50508.1029 | 280.008
Devonshire Building | 2017-07-04 08:30 | 50508.2429 | 560.016
Devonshire Building | 2017-07-04 08:45 | 50508.6379 | 1580.004
Devonshire Building | 2017-07-04 09:00 | 50509.1429 | 2019.996
Devonshire Building | 2017-07-04 09:15 | 50509.3479 | 820.008
Devonshire Building | 2017-07-04 09:30 | 50509.5329 | 740.016
Devonshire Building | 2017-07-04 09:45 | 50509.7079 | 699.984
Devonshire Building | 2017-07-04 10:00 | 50509.8529 | 579.996
Devonshire Building | 2017-07-04 10:15 | 50510.5229 | 2679.984
Devonshire Building | 2017-07-04 10:30 | 50510.6729 | 600.012
Devonshire Building | 2017-07-04 10:45 | 50510.8029 | 519.984
Devonshire Building | 2017-07-04 11:00 | 50510.9129 | 439.992
Devonshire Building | 2017-07-04 11:15 | 50511.0129 | 399.996
Devonshire Building | 2017-07-04 11:30 | 50511.6479 | 2540.016
Devonshire Building | 2017-07-04 11:45 | 50511.7579 | 439.992
Devonshire Building | 2017-07-04 12:00 | 50511.8729 | 460.008
Devonshire Building | 2017-07-04 12:15 | 50511.9929 | 479.988
Devonshire Building | 2017-07-04 12:30 | 50512.1079 | 460.008
Devonshire Building | 2017-07-04 12:45 | 50512.7629 | 2620.008
Devonshire Building | 2017-07-04 13:00 | 50512.8979 | 540
Devonshire Building | 2017-07-04 13:15 | 50513.0329 | 540
Devonshire Building | 2017-07-04 13:30 | 50513.1979 | 659.988
Devonshire Building | 2017-07-04 13:45 | 50513.3629 | 659.988
Devonshire Building | 2017-07-04 14:00 | 50513.5129 | 600.012
Devonshire Building | 2017-07-04 14:15 | 50514.2279 | 2859.984
Devonshire Building | 2017-07-04 14:30 | 50514.4129 | 740.016
Devonshire Building | 2017-07-04 14:45 | 50514.6679 | 1019.988
Devonshire Building | 2017-07-04 15:00 | 50514.8429 | 699.984
Devonshire Building | 2017-07-04 15:15 | 50514.9729 | 519.984
Devonshire Building | 2017-07-04 15:30 | 50515.3079 | 1339.992
Devonshire Building | 2017-07-04 15:45 | 50515.6628 | 1419.984
Devonshire Building | 2017-07-04 16:00 | 50515.7078 | 180
Devonshire Building | 2017-07-04 16:15 | 50515.7528 | 180
Devonshire Building | 2017-07-04 16:30 | 50515.7928 | 159.984
Devonshire Building | 2017-07-04 16:45 | 50515.8328 | 159.984
Devonshire Building | 2017-07-04 17:00 | 50515.8728 | 159.984
Devonshire Building | 2017-07-04 17:15 | 50515.9128 | 159.984
Devonshire Building | 2017-07-04 17:30 | 50516.2078 | 1180.008
Devonshire Building | 2017-07-04 17:45 | 50516.4928 | 1140.012
Devonshire Building | 2017-07-04 18:00 | 50516.5278 | 140.004
Devonshire Building | 2017-07-04 18:15 | 50516.5628 | 140.004
Devonshire Building | 2017-07-04 18:30 | 50516.6028 | 159.984
Devonshire Building | 2017-07-04 18:45 | 50516.6328 | 119.988
Devonshire Building | 2017-07-04 19:00 | 50516.6678 | 140.004
Devonshire Building | 2017-07-04 19:15 | 50516.6928 | 100.008
Devonshire Building | 2017-07-04 19:30 | 50516.7178 | 100.008
Devonshire Building | 2017-07-04 19:45 | 50516.7428 | 100.008
Devonshire Building | 2017-07-04 20:00 | 50516.7628 | 79.992
Devonshire Building | 2017-07-04 20:15 | 50516.7828 | 79.992
Devonshire Building | 2017-07-04 20:30 | 50516.7978 | 60.012
Devonshire Building | 2017-07-04 20:45 | 50516.8328 | 140.004
Devonshire Building | 2017-07-04 21:00 | 50516.8378 | 20.016
Devonshire Building | 2017-07-04 21:15 | 50516.8428 | 20.016
Devonshire Building | 2017-07-04 21:30 | 50516.8528 | 39.996
Devonshire Building | 2017-07-04 21:45 | 50516.8579 | 20.016
Devonshire Building | 2017-07-04 22:00 | 50516.8629 | 20.016
Devonshire Building | 2017-07-04 22:15 | 50516.8679 | 20.016
Devonshire Building | 2017-07-04 22:30 | 50516.8779 | 39.996
Devonshire Building | 2017-07-04 22:45 | 50516.8829 | 20.016
Devonshire Building | 2017-07-04 23:00 | 50516.8879 | 20.016
Devonshire Building | 2017-07-04 23:15 | 50516.8929 | 20.016
Devonshire Building | 2017-07-04 23:30 | 50516.9029 | 39.996
Devonshire Building | 2017-07-04 23:45 | 50516.9079 | 20.016
Devonshire Building | 2017-07-05 | 50516.9141 | 20.016
Devonshire Building | 2017-07-05 00:15 | 50516.9191 | 20.016
Devonshire Building | 2017-07-05 00:30 | 50516.9241 | 20.016
Devonshire Building | 2017-07-05 00:45 | 50516.9341 | 39.996
Devonshire Building | 2017-07-05 01:00 | 50516.9391 | 20.016
Devonshire Building | 2017-07-05 01:15 | 50516.9441 | 20.016
Devonshire Building | 2017-07-05 01:30 | 50516.9491 | 20.016
Devonshire Building | 2017-07-05 01:45 | 50516.9541 | 20.016
Devonshire Building | 2017-07-05 02:00 | 50516.9641 | 39.996
Devonshire Building | 2017-07-05 02:15 | 50516.9691 | 20.016
Devonshire Building | 2017-07-05 02:30 | 50516.9741 | 20.016
Devonshire Building | 2017-07-05 02:45 | 50516.9791 | 20.016
Devonshire Building | 2017-07-05 03:00 | 50516.9841 | 20.016
Devonshire Building | 2017-07-05 03:15 | 50516.9891 | 20.016
Devonshire Building | 2017-07-05 03:30 | 50516.9941 | 20.016
Devonshire Building | 2017-07-05 03:45 | 50517.0041 | 39.996
Devonshire Building | 2017-07-05 04:00 | 50517.0091 | 20.016
Devonshire Building | 2017-07-05 04:15 | 50517.0141 | 20.016
Devonshire Building | 2017-07-05 04:30 | 50517.0191 | 20.016
Devonshire Building | 2017-07-05 04:45 | 50517.0241 | 20.016
Devonshire Building | 2017-07-05 05:00 | 50517.0291 | 20.016
Devonshire Building | 2017-07-05 05:15 | 50517.1291 | 399.996
Devonshire Building | 2017-07-05 05:30 | 50517.5541 | 1699.992
Devonshire Building | 2017-07-05 05:45 | 50517.5591 | 20.016
Devonshire Building | 2017-07-05 06:00 | 50517.5691 | 39.996
Devonshire Building | 2017-07-05 06:15 | 50517.5741 | 20.016
Devonshire Building | 2017-07-05 06:30 | 50517.5891 | 60.012
Devonshire Building | 2017-07-05 06:45 | 50517.5991 | 39.996
Devonshire Building | 2017-07-05 07:00 | 50517.6241 | 100.008
Devonshire Building | 2017-07-05 07:15 | 50517.6391 | 60.012
Devonshire Building | 2017-07-05 07:30 | 50517.6591 | 79.992
Devonshire Building | 2017-07-05 07:45 | 50517.6791 | 79.992
Devonshire Building | 2017-07-05 08:00 | 50517.7091 | 119.988
Devonshire Building | 2017-07-05 08:15 | 50517.7641 | 219.996
Devonshire Building | 2017-07-05 08:30 | 50518.2541 | 1959.984
Devonshire Building | 2017-07-05 08:45 | 50518.4091 | 619.992
Devonshire Building | 2017-07-05 09:00 | 50518.4691 | 240.012
Devonshire Building | 2017-07-05 09:15 | 50518.5491 | 320.004
Devonshire Building | 2017-07-05 09:30 | 50518.6541 | 420.012
Devonshire Building | 2017-07-05 09:45 | 50518.7291 | 299.988
Devonshire Building | 2017-07-05 10:00 | 50519.3641 | 2540.016
Devonshire Building | 2017-07-05 10:15 | 50519.4891 | 500.004
Devonshire Building | 2017-07-05 10:30 | 50519.6141 | 500.004
Devonshire Building | 2017-07-05 10:45 | 50519.7141 | 399.996
Devonshire Building | 2017-07-05 11:00 | 50519.9191 | 820.008
Devonshire Building | 2017-07-05 11:15 | 50520.4341 | 2059.992
Devonshire Building | 2017-07-05 11:30 | 50520.5241 | 360
Devonshire Building | 2017-07-05 11:45 | 50520.6141 | 360
Devonshire Building | 2017-07-05 12:00 | 50520.7091 | 380.016
Devonshire Building | 2017-07-05 12:15 | 50520.8941 | 740.016
Devonshire Building | 2017-07-05 12:30 | 50521.1791 | 1140.012
Devonshire Building | 2017-07-05 12:45 | 50521.8841 | 2819.988
Devonshire Building | 2017-07-05 13:00 | 50522.0191 | 540
Devonshire Building | 2017-07-05 13:15 | 50522.1091 | 360
Devonshire Building | 2017-07-05 13:30 | 50522.1941 | 339.984
Devonshire Building | 2017-07-05 13:45 | 50522.2791 | 339.984
Devonshire Building | 2017-07-05 14:00 | 50522.5691 | 1159.992
Devonshire Building | 2017-07-05 14:15 | 50522.9191 | 1400.004
Devonshire Building | 2017-07-05 14:30 | 50522.9791 | 240.012
Devonshire Building | 2017-07-05 14:45 | 50523.0441 | 259.992
Devonshire Building | 2017-07-05 15:00 | 50523.0991 | 219.996
Devonshire Building | 2017-07-05 15:15 | 50523.1541 | 219.996
Devonshire Building | 2017-07-05 15:30 | 50523.2091 | 219.996
Devonshire Building | 2017-07-05 15:45 | 50523.7991 | 2360.016
Devonshire Building | 2017-07-05 16:00 | 50523.8541 | 219.996
Devonshire Building | 2017-07-05 16:15 | 50523.9191 | 259.992
Devonshire Building | 2017-07-05 16:30 | 50523.9941 | 299.988
Devonshire Building | 2017-07-05 16:45 | 50524.0641 | 280.008
Devonshire Building | 2017-07-05 17:00 | 50524.1391 | 299.988
Devonshire Building | 2017-07-05 17:15 | 50524.2091 | 280.008
Devonshire Building | 2017-07-05 17:30 | 50524.2741 | 259.992
Devonshire Building | 2017-07-05 17:45 | 50524.3391 | 259.992
Devonshire Building | 2017-07-05 18:00 | 50524.4041 | 259.992
Devonshire Building | 2017-07-05 18:15 | 50524.4641 | 240.012
Devonshire Building | 2017-07-05 18:30 | 50524.5191 | 219.996
Devonshire Building | 2017-07-05 18:45 | 50524.5591 | 159.984
Devonshire Building | 2017-07-05 19:00 | 50524.5991 | 159.984
Devonshire Building | 2017-07-05 19:15 | 50524.6341 | 140.004
Devonshire Building | 2017-07-05 19:30 | 50524.6641 | 119.988
Devonshire Building | 2017-07-05 19:45 | 50524.6891 | 100.008
Devonshire Building | 2017-07-05 20:00 | 50524.7091 | 79.992
Devonshire Building | 2017-07-05 20:15 | 50524.7341 | 100.008
Devonshire Building | 2017-07-05 20:30 | 50525.2441 | 2040.012
Devonshire Building | 2017-07-05 20:45 | 50525.2541 | 39.996
Devonshire Building | 2017-07-05 21:00 | 50525.2641 | 39.996
Devonshire Building | 2017-07-05 21:15 | 50525.2691 | 20.016
Devonshire Building | 2017-07-05 21:30 | 50525.2741 | 20.016
Devonshire Building | 2017-07-05 21:45 | 50525.2841 | 39.996
Devonshire Building | 2017-07-05 22:00 | 50525.2891 | 20.016
Devonshire Building | 2017-07-05 22:15 | 50525.2941 | 20.016
Devonshire Building | 2017-07-05 22:30 | 50525.3041 | 39.996
Devonshire Building | 2017-07-05 22:45 | 50525.3091 | 20.016
Devonshire Building | 2017-07-05 23:00 | 50525.3141 | 20.016
Devonshire Building | 2017-07-05 23:15 | 50525.3241 | 39.996
Devonshire Building | 2017-07-05 23:30 | 50525.3291 | 20.016
Devonshire Building | 2017-07-05 23:45 | 50525.3391 | 39.996
Devonshire Building | 2017-07-06 | 50525.3438 | 20.016
Devonshire Building | 2017-07-06 00:15 | 50525.3488 | 20.016
Devonshire Building | 2017-07-06 00:30 | 50525.3588 | 39.996
Devonshire Building | 2017-07-06 00:45 | 50525.3638 | 20.016
Devonshire Building | 2017-07-06 01:00 | 50525.3738 | 39.996
Devonshire Building | 2017-07-06 01:15 | 50525.3788 | 20.016
Devonshire Building | 2017-07-06 01:30 | 50525.3838 | 20.016
Devonshire Building | 2017-07-06 01:45 | 50525.3988 | 60.012
Devonshire Building | 2017-07-06 02:00 | 50525.4238 | 100.008
Devonshire Building | 2017-07-06 02:15 | 50525.4438 | 79.992
Devonshire Building | 2017-07-06 02:30 | 50525.4688 | 100.008
Devonshire Building | 2017-07-06 02:45 | 50525.4888 | 79.992
Devonshire Building | 2017-07-06 03:00 | 50525.5138 | 100.008
Devonshire Building | 2017-07-06 03:15 | 50525.5338 | 79.992
Devonshire Building | 2017-07-06 03:30 | 50525.5588 | 100.008
Devonshire Building | 2017-07-06 03:45 | 50525.5688 | 39.996
Devonshire Building | 2017-07-06 04:00 | 50525.5738 | 20.016
Devonshire Building | 2017-07-06 04:15 | 50525.5788 | 20.016
Devonshire Building | 2017-07-06 04:30 | 50525.5888 | 39.996
Devonshire Building | 2017-07-06 04:45 | 50525.5938 | 20.016
Devonshire Building | 2017-07-06 05:00 | 50525.6038 | 39.996
Devonshire Building | 2017-07-06 05:15 | 50525.6088 | 20.016
Devonshire Building | 2017-07-06 05:30 | 50525.6188 | 39.996
Devonshire Building | 2017-07-06 05:45 | 50525.6238 | 20.016
Devonshire Building | 2017-07-06 06:00 | 50525.6338 | 39.996
Devonshire Building | 2017-07-06 06:15 | 50525.6438 | 39.996
Devonshire Building | 2017-07-06 06:30 | 50525.6538 | 39.996
Devonshire Building | 2017-07-06 06:45 | 50525.6638 | 39.996
Devonshire Building | 2017-07-06 07:00 | 50525.6738 | 39.996
Devonshire Building | 2017-07-06 07:15 | 50526.0488 | 1500.012
Devonshire Building | 2017-07-06 07:30 | 50526.2338 | 740.016
Devonshire Building | 2017-07-06 07:45 | 50526.2488 | 60.012
Devonshire Building | 2017-07-06 08:00 | 50526.2788 | 119.988
Devonshire Building | 2017-07-06 08:15 | 50526.2988 | 79.992
Devonshire Building | 2017-07-06 08:30 | 50526.3188 | 79.992
Devonshire Building | 2017-07-06 08:45 | 50526.3538 | 140.004
Devonshire Building | 2017-07-06 09:00 | 50526.4138 | 240.012
Devonshire Building | 2017-07-06 09:15 | 50527.1138 | 2800.008
Devonshire Building | 2017-07-06 09:30 | 50527.2538 | 560.016
Devonshire Building | 2017-07-06 09:45 | 50527.3888 | 540
Devonshire Building | 2017-07-06 10:00 | 50527.5138 | 500.004
Devonshire Building | 2017-07-06 10:15 | 50527.6138 | 399.996
Devonshire Building | 2017-07-06 10:30 | 50527.6988 | 339.984
Devonshire Building | 2017-07-06 10:45 | 50528.2988 | 2400.012
Devonshire Building | 2017-07-06 11:00 | 50528.3438 | 180
Devonshire Building | 2017-07-06 11:15 | 50528.3988 | 219.996
Devonshire Building | 2017-07-06 11:30 | 50528.4538 | 219.996
Devonshire Building | 2017-07-06 11:45 | 50528.5088 | 219.996
Devonshire Building | 2017-07-06 12:00 | 50528.5838 | 299.988
Devonshire Building | 2017-07-06 12:15 | 50529.2438 | 2639.988
Devonshire Building | 2017-07-06 12:30 | 50529.3788 | 540
Devonshire Building | 2017-07-06 12:45 | 50529.5088 | 519.984
Devonshire Building | 2017-07-06 13:00 | 50529.6388 | 519.984
Devonshire Building | 2017-07-06 13:15 | 50529.7588 | 479.988
Devonshire Building | 2017-07-06 13:30 | 50529.8738 | 460.008
Devonshire Building | 2017-07-06 13:45 | 50530.5088 | 2540.016
Devonshire Building | 2017-07-06 14:00 | 50530.5988 | 360
Devonshire Building | 2017-07-06 14:15 | 50530.6838 | 339.984
Devonshire Building | 2017-07-06 14:30 | 50530.7838 | 399.996
Devonshire Building | 2017-07-06 14:45 | 50530.8888 | 420.012
Devonshire Building | 2017-07-06 15:00 | 50531.0188 | 519.984
Devonshire Building | 2017-07-06 15:15 | 50531.6488 | 2520
Devonshire Building | 2017-07-06 15:30 | 50531.8038 | 619.992
Devonshire Building | 2017-07-06 15:45 | 50531.9288 | 500.004
Devonshire Building | 2017-07-06 16:00 | 50532.0438 | 460.008
Devonshire Building | 2017-07-06 16:15 | 50532.1538 | 439.992
Devonshire Building | 2017-07-06 16:30 | 50532.2388 | 339.984
Devonshire Building | 2017-07-06 16:45 | 50532.3138 | 299.988
Devonshire Building | 2017-07-06 17:00 | 50532.3738 | 240.012
Devonshire Building | 2017-07-06 17:15 | 50532.4138 | 159.984
Devonshire Building | 2017-07-06 17:30 | 50532.4538 | 159.984
Devonshire Building | 2017-07-06 17:45 | 50532.4838 | 119.988
Devonshire Building | 2017-07-06 18:00 | 50533.0138 | 2120.004
Devonshire Building | 2017-07-06 18:15 | 50533.0288 | 60.012
Devonshire Building | 2017-07-06 18:30 | 50533.0388 | 39.996
Devonshire Building | 2017-07-06 18:45 | 50533.0488 | 39.996
Devonshire Building | 2017-07-06 19:00 | 50533.0588 | 39.996
Devonshire Building | 2017-07-06 19:15 | 50533.0738 | 60.012
Devonshire Building | 2017-07-06 19:30 | 50533.0838 | 39.996
Devonshire Building | 2017-07-06 19:45 | 50533.0938 | 39.996
Devonshire Building | 2017-07-06 20:00 | 50533.1088 | 60.012
Devonshire Building | 2017-07-06 20:15 | 50533.1188 | 39.996
Devonshire Building | 2017-07-06 20:30 | 50533.1288 | 39.996
Devonshire Building | 2017-07-06 20:45 | 50533.1488 | 79.992
Devonshire Building | 2017-07-06 21:00 | 50533.1588 | 39.996
Devonshire Building | 2017-07-06 21:15 | 50533.1738 | 60.012
Devonshire Building | 2017-07-06 21:30 | 50533.1838 | 39.996
Devonshire Building | 2017-07-06 21:45 | 50533.1938 | 39.996
Devonshire Building | 2017-07-06 22:00 | 50533.2038 | 39.996
Devonshire Building | 2017-07-06 22:15 | 50533.2138 | 39.996
Devonshire Building | 2017-07-06 22:30 | 50533.2238 | 39.996
Devonshire Building | 2017-07-06 22:45 | 50533.2338 | 39.996
Devonshire Building | 2017-07-06 23:00 | 50533.2438 | 39.996
Devonshire Building | 2017-07-06 23:15 | 50533.2538 | 39.996
Devonshire Building | 2017-07-06 23:30 | 50533.2637 | 39.996
Devonshire Building | 2017-07-06 23:45 | 50533.2737 | 39.996
Devonshire Building | 2017-07-07 | 50533.2812 | 20.016
Devonshire Building | 2017-07-07 00:15 | 50533.2912 | 39.996
Devonshire Building | 2017-07-07 00:30 | 50533.3012 | 39.996
Devonshire Building | 2017-07-07 00:45 | 50533.3112 | 39.996
Devonshire Building | 2017-07-07 01:00 | 50533.3212 | 39.996
Devonshire Building | 2017-07-07 01:15 | 50533.3262 | 20.016
Devonshire Building | 2017-07-07 01:30 | 50533.3362 | 39.996
Devonshire Building | 2017-07-07 01:45 | 50533.3462 | 39.996
Devonshire Building | 2017-07-07 02:00 | 50533.3562 | 39.996
Devonshire Building | 2017-07-07 02:15 | 50533.3613 | 20.016
Devonshire Building | 2017-07-07 02:30 | 50533.3712 | 39.996
Devonshire Building | 2017-07-07 02:45 | 50533.3812 | 39.996
Devonshire Building | 2017-07-07 03:00 | 50533.3863 | 20.016
Devonshire Building | 2017-07-07 03:15 | 50533.3963 | 39.996
Devonshire Building | 2017-07-07 03:30 | 50533.4013 | 20.016
Devonshire Building | 2017-07-07 03:45 | 50533.4113 | 39.996
Devonshire Building | 2017-07-07 04:00 | 50533.4163 | 20.016
Devonshire Building | 2017-07-07 04:15 | 50533.4263 | 39.996
Devonshire Building | 2017-07-07 04:30 | 50533.4313 | 20.016
Devonshire Building | 2017-07-07 04:45 | 50533.4413 | 39.996
Devonshire Building | 2017-07-07 05:00 | 50533.4513 | 39.996
Devonshire Building | 2017-07-07 05:15 | 50533.4563 | 20.016
Devonshire Building | 2017-07-07 05:30 | 50533.4663 | 39.996
Devonshire Building | 2017-07-07 05:45 | 50533.4713 | 20.016
Devonshire Building | 2017-07-07 06:00 | 50533.4813 | 39.996
Devonshire Building | 2017-07-07 06:15 | 50533.4863 | 20.016
Devonshire Building | 2017-07-07 06:30 | 50533.8963 | 1640.016
Devonshire Building | 2017-07-07 06:45 | 50534.0213 | 500.004
Devonshire Building | 2017-07-07 07:00 | 50534.0313 | 39.996
Devonshire Building | 2017-07-07 07:15 | 50534.0463 | 60.012
Devonshire Building | 2017-07-07 07:30 | 50534.0563 | 39.996
Devonshire Building | 2017-07-07 07:45 | 50534.0713 | 60.012
Devonshire Building | 2017-07-07 08:00 | 50534.1013 | 119.988
Devonshire Building | 2017-07-07 08:15 | 50534.1313 | 119.988
Devonshire Building | 2017-07-07 08:30 | 50534.1813 | 200.016
Devonshire Building | 2017-07-07 08:45 | 50534.2363 | 219.996
Devonshire Building | 2017-07-07 09:00 | 50534.6763 | 1760.004
Devonshire Building | 2017-07-07 09:15 | 50534.8913 | 860.004
Devonshire Building | 2017-07-07 09:30 | 50534.9513 | 240.012
Devonshire Building | 2017-07-07 09:45 | 50535.0163 | 259.992
Devonshire Building | 2017-07-07 10:00 | 50535.0863 | 280.008
Devonshire Building | 2017-07-07 10:15 | 50535.1513 | 259.992
Devonshire Building | 2017-07-07 10:30 | 50535.2213 | 280.008
Devonshire Building | 2017-07-07 10:45 | 50536.0163 | 3179.988
Devonshire Building | 2017-07-07 11:00 | 50536.1863 | 680.004
Devonshire Building | 2017-07-07 11:15 | 50536.3013 | 460.008
Devonshire Building | 2017-07-07 11:30 | 50536.4013 | 399.996
Devonshire Building | 2017-07-07 11:45 | 50536.4913 | 360
Devonshire Building | 2017-07-07 12:00 | 50536.5713 | 320.004
Devonshire Building | 2017-07-07 12:15 | 50537.1463 | 2300.004
Devonshire Building | 2017-07-07 12:30 | 50537.1763 | 119.988
Devonshire Building | 2017-07-07 12:45 | 50537.2063 | 119.988
Devonshire Building | 2017-07-07 13:00 | 50537.2413 | 140.004
Devonshire Building | 2017-07-07 13:15 | 50537.2713 | 119.988
Devonshire Building | 2017-07-07 13:30 | 50537.3013 | 119.988
Devonshire Building | 2017-07-07 13:45 | 50537.3463 | 180
Devonshire Building | 2017-07-07 14:00 | 50537.9413 | 2379.996
Devonshire Building | 2017-07-07 14:15 | 50537.9863 | 180
Devonshire Building | 2017-07-07 14:30 | 50538.0313 | 180
Devonshire Building | 2017-07-07 14:45 | 50538.0813 | 200.016
Devonshire Building | 2017-07-07 15:00 | 50538.1313 | 200.016
Devonshire Building | 2017-07-07 15:15 | 50538.1763 | 180
Devonshire Building | 2017-07-07 15:30 | 50538.2163 | 159.984
Devonshire Building | 2017-07-07 15:45 | 50538.2613 | 180
Devonshire Building | 2017-07-07 16:00 | 50538.8663 | 2419.992
Devonshire Building | 2017-07-07 16:15 | 50538.9263 | 240.012
Devonshire Building | 2017-07-07 16:30 | 50538.9963 | 280.008
Devonshire Building | 2017-07-07 16:45 | 50539.0713 | 299.988
Devonshire Building | 2017-07-07 17:00 | 50539.1413 | 280.008
Devonshire Building | 2017-07-07 17:15 | 50539.1963 | 219.996
Devonshire Building | 2017-07-07 17:30 | 50539.2663 | 280.008
Devonshire Building | 2017-07-07 17:45 | 50539.3463 | 320.004
Devonshire Building | 2017-07-07 18:00 | 50539.4213 | 299.988
Devonshire Building | 2017-07-07 18:15 | 50539.4863 | 259.992
Devonshire Building | 2017-07-07 18:30 | 50539.5413 | 219.996
Devonshire Building | 2017-07-07 18:45 | 50539.5913 | 200.016
Devonshire Building | 2017-07-07 19:00 | 50539.6363 | 180
Devonshire Building | 2017-07-07 19:15 | 50539.6713 | 140.004
Devonshire Building | 2017-07-07 19:30 | 50539.7063 | 140.004
Devonshire Building | 2017-07-07 19:45 | 50539.7363 | 119.988
Devonshire Building | 2017-07-07 20:00 | 50539.7613 | 100.008
Devonshire Building | 2017-07-07 20:15 | 50539.7863 | 100.008
Devonshire Building | 2017-07-07 20:30 | 50539.8063 | 79.992
Devonshire Building | 2017-07-07 20:45 | 50539.8463 | 159.984
Devonshire Building | 2017-07-07 21:00 | 50539.8563 | 39.996
Devonshire Building | 2017-07-07 21:15 | 50539.8613 | 20.016
Devonshire Building | 2017-07-07 21:30 | 50539.8713 | 39.996
Devonshire Building | 2017-07-07 21:45 | 50539.8763 | 20.016
Devonshire Building | 2017-07-07 22:00 | 50539.8863 | 39.996
Devonshire Building | 2017-07-07 22:15 | 50539.8913 | 20.016
Devonshire Building | 2017-07-07 22:30 | 50539.9013 | 39.996
Devonshire Building | 2017-07-07 22:45 | 50539.9063 | 20.016
Devonshire Building | 2017-07-07 23:00 | 50539.9163 | 39.996
Devonshire Building | 2017-07-07 23:15 | 50539.9213 | 20.016
Devonshire Building | 2017-07-07 23:30 | 50539.9313 | 39.996
Devonshire Building | 2017-07-07 23:45 | 50539.9363 | 20.016
Devonshire Building | 2017-07-08 | 50539.9453 | 39.996
Devonshire Building | 2017-07-08 00:15 | 50539.9503 | 20.016
Devonshire Building | 2017-07-08 00:30 | 50539.9553 | 20.016
Devonshire Building | 2017-07-08 00:45 | 50539.9653 | 39.996
Devonshire Building | 2017-07-08 01:00 | 50539.9703 | 20.016
Devonshire Building | 2017-07-08 01:15 | 50539.9803 | 39.996
Devonshire Building | 2017-07-08 01:30 | 50539.9853 | 20.016
Devonshire Building | 2017-07-08 01:45 | 50539.9903 | 20.016
Devonshire Building | 2017-07-08 02:00 | 50540.0003 | 39.996
Devonshire Building | 2017-07-08 02:15 | 50540.0053 | 20.016
Devonshire Building | 2017-07-08 02:30 | 50540.0103 | 20.016
Devonshire Building | 2017-07-08 02:45 | 50540.0153 | 20.016
Devonshire Building | 2017-07-08 03:00 | 50540.0253 | 39.996
Devonshire Building | 2017-07-08 03:15 | 50540.0553 | 119.988
Devonshire Building | 2017-07-08 03:30 | 50540.5503 | 1980
Devonshire Building | 2017-07-08 03:45 | 50540.5553 | 20.016
Devonshire Building | 2017-07-08 04:00 | 50540.5653 | 39.996
Devonshire Building | 2017-07-08 04:15 | 50540.5703 | 20.016
Devonshire Building | 2017-07-08 04:30 | 50540.5803 | 39.996
Devonshire Building | 2017-07-08 04:45 | 50540.5853 | 20.016
Devonshire Building | 2017-07-08 05:00 | 50540.5953 | 39.996
Devonshire Building | 2017-07-08 05:15 | 50540.6053 | 39.996
Devonshire Building | 2017-07-08 05:30 | 50540.6103 | 20.016
Devonshire Building | 2017-07-08 05:45 | 50540.6203 | 39.996
Devonshire Building | 2017-07-08 06:00 | 50540.6303 | 39.996
Devonshire Building | 2017-07-08 06:15 | 50540.6403 | 39.996
Devonshire Building | 2017-07-08 06:30 | 50540.6503 | 39.996
Devonshire Building | 2017-07-08 06:45 | 50540.6603 | 39.996
Devonshire Building | 2017-07-08 07:00 | 50540.6703 | 39.996
Devonshire Building | 2017-07-08 07:15 | 50540.6753 | 20.016
Devonshire Building | 2017-07-08 07:30 | 50540.6853 | 39.996
Devonshire Building | 2017-07-08 07:45 | 50540.6953 | 39.996
Devonshire Building | 2017-07-08 08:00 | 50540.7053 | 39.996
Devonshire Building | 2017-07-08 08:15 | 50540.7153 | 39.996
Devonshire Building | 2017-07-08 08:30 | 50540.7253 | 39.996
Devonshire Building | 2017-07-08 08:45 | 50540.7303 | 20.016
Devonshire Building | 2017-07-08 09:00 | 50540.7403 | 39.996
Devonshire Building | 2017-07-08 09:15 | 50540.7503 | 39.996
Devonshire Building | 2017-07-08 09:30 | 50540.7603 | 39.996
Devonshire Building | 2017-07-08 09:45 | 50540.7703 | 39.996
Devonshire Building | 2017-07-08 10:00 | 50540.7803 | 39.996
Devonshire Building | 2017-07-08 10:15 | 50540.7903 | 39.996
Devonshire Building | 2017-07-08 10:30 | 50540.8053 | 60.012
Devonshire Building | 2017-07-08 10:45 | 50540.8303 | 100.008
Devonshire Building | 2017-07-08 11:00 | 50540.8553 | 100.008
Devonshire Building | 2017-07-08 11:15 | 50540.8803 | 100.008
Devonshire Building | 2017-07-08 11:30 | 50540.9053 | 100.008
Devonshire Building | 2017-07-08 11:45 | 50540.9304 | 100.008
Devonshire Building | 2017-07-08 12:00 | 50540.9554 | 100.008
Devonshire Building | 2017-07-08 12:15 | 50540.9854 | 119.988
Devonshire Building | 2017-07-08 12:30 | 50541.0153 | 119.988
Devonshire Building | 2017-07-08 12:45 | 50541.0253 | 39.996
Devonshire Building | 2017-07-08 13:00 | 50541.0403 | 60.012
Devonshire Building | 2017-07-08 13:15 | 50541.0503 | 39.996
Devonshire Building | 2017-07-08 13:30 | 50541.0603 | 39.996
Devonshire Building | 2017-07-08 13:45 | 50541.0703 | 39.996
Devonshire Building | 2017-07-08 14:00 | 50541.0803 | 39.996
Devonshire Building | 2017-07-08 14:15 | 50541.0903 | 39.996
Devonshire Building | 2017-07-08 14:30 | 50541.1053 | 60.012
Devonshire Building | 2017-07-08 14:45 | 50541.1153 | 39.996
Devonshire Building | 2017-07-08 15:00 | 50541.1303 | 60.012
Devonshire Building | 2017-07-08 15:15 | 50541.1403 | 39.996
Devonshire Building | 2017-07-08 15:30 | 50541.1503 | 39.996
Devonshire Building | 2017-07-08 15:45 | 50541.1603 | 39.996
Devonshire Building | 2017-07-08 16:00 | 50541.5153 | 1419.984
Devonshire Building | 2017-07-08 16:15 | 50541.6953 | 720
Devonshire Building | 2017-07-08 16:30 | 50541.7153 | 79.992
Devonshire Building | 2017-07-08 16:45 | 50541.7303 | 60.012
Devonshire Building | 2017-07-08 17:00 | 50541.7503 | 79.992
Devonshire Building | 2017-07-08 17:15 | 50541.7703 | 79.992
Devonshire Building | 2017-07-08 17:30 | 50541.7953 | 100.008
Devonshire Building | 2017-07-08 17:45 | 50541.8153 | 79.992
Devonshire Building | 2017-07-08 18:00 | 50541.8353 | 79.992
Devonshire Building | 2017-07-08 18:15 | 50541.8603 | 100.008
Devonshire Building | 2017-07-08 18:30 | 50541.8803 | 79.992
Devonshire Building | 2017-07-08 18:45 | 50541.9003 | 79.992
Devonshire Building | 2017-07-08 19:00 | 50541.9153 | 60.012
Devonshire Building | 2017-07-08 19:15 | 50541.9403 | 100.008
Devonshire Building | 2017-07-08 19:30 | 50541.9553 | 60.012
Devonshire Building | 2017-07-08 19:45 | 50541.9703 | 60.012
Devonshire Building | 2017-07-08 20:00 | 50541.9903 | 79.992
Devonshire Building | 2017-07-08 20:15 | 50542.0053 | 60.012
Devonshire Building | 2017-07-08 20:30 | 50542.0203 | 60.012
Devonshire Building | 2017-07-08 20:45 | 50542.0403 | 79.992
Devonshire Building | 2017-07-08 21:00 | 50542.0554 | 60.012
Devonshire Building | 2017-07-08 21:15 | 50542.0653 | 39.996
Devonshire Building | 2017-07-08 21:30 | 50542.0804 | 60.012
Devonshire Building | 2017-07-08 21:45 | 50542.0904 | 39.996
Devonshire Building | 2017-07-08 22:00 | 50542.1054 | 60.012
Devonshire Building | 2017-07-08 22:15 | 50542.1154 | 39.996
Devonshire Building | 2017-07-08 22:30 | 50542.1254 | 39.996
Devonshire Building | 2017-07-08 22:45 | 50542.1404 | 60.012
Devonshire Building | 2017-07-08 23:00 | 50542.1504 | 39.996
Devonshire Building | 2017-07-08 23:15 | 50542.1654 | 60.012
Devonshire Building | 2017-07-08 23:30 | 50542.1754 | 39.996
Devonshire Building | 2017-07-08 23:45 | 50542.1854 | 39.996
Devonshire Building | 2017-07-09 | 50542.1992 | 60.012
Devonshire Building | 2017-07-09 00:15 | 50542.2092 | 39.996
Devonshire Building | 2017-07-09 00:30 | 50542.2242 | 60.012
Devonshire Building | 2017-07-09 00:45 | 50542.2342 | 39.996
Devonshire Building | 2017-07-09 01:00 | 50542.2442 | 39.996
Devonshire Building | 2017-07-09 01:15 | 50542.2542 | 39.996
Devonshire Building | 2017-07-09 01:30 | 50542.2692 | 60.012
Devonshire Building | 2017-07-09 01:45 | 50542.2792 | 39.996
Devonshire Building | 2017-07-09 02:00 | 50542.2892 | 39.996
Devonshire Building | 2017-07-09 02:15 | 50542.3042 | 60.012
Devonshire Building | 2017-07-09 02:30 | 50542.3142 | 39.996
Devonshire Building | 2017-07-09 02:45 | 50542.3242 | 39.996
Devonshire Building | 2017-07-09 03:00 | 50542.3342 | 39.996
Devonshire Building | 2017-07-09 03:15 | 50542.3492 | 60.012
Devonshire Building | 2017-07-09 03:30 | 50542.3592 | 39.996
Devonshire Building | 2017-07-09 03:45 | 50542.3692 | 39.996
Devonshire Building | 2017-07-09 04:00 | 50542.3792 | 39.996
Devonshire Building | 2017-07-09 04:15 | 50542.3942 | 60.012
Devonshire Building | 2017-07-09 04:30 | 50542.4042 | 39.996
Devonshire Building | 2017-07-09 04:45 | 50542.4142 | 39.996
Devonshire Building | 2017-07-09 05:00 | 50542.4242 | 39.996
Devonshire Building | 2017-07-09 05:15 | 50542.4342 | 39.996
Devonshire Building | 2017-07-09 05:30 | 50542.4442 | 39.996
Devonshire Building | 2017-07-09 05:45 | 50542.4592 | 60.012
Devonshire Building | 2017-07-09 06:00 | 50542.4692 | 39.996
Devonshire Building | 2017-07-09 06:15 | 50542.4792 | 39.996
Devonshire Building | 2017-07-09 06:30 | 50542.4892 | 39.996
Devonshire Building | 2017-07-09 06:45 | 50542.4992 | 39.996
Devonshire Building | 2017-07-09 07:00 | 50542.5092 | 39.996
Devonshire Building | 2017-07-09 07:15 | 50542.5192 | 39.996
Devonshire Building | 2017-07-09 07:30 | 50542.5292 | 39.996
Devonshire Building | 2017-07-09 07:45 | 50542.5492 | 79.992
Devonshire Building | 2017-07-09 08:00 | 50542.5742 | 100.008
Devonshire Building | 2017-07-09 08:15 | 50542.5992 | 100.008
Devonshire Building | 2017-07-09 08:30 | 50543.1242 | 2099.988
Devonshire Building | 2017-07-09 08:45 | 50543.1442 | 79.992
Devonshire Building | 2017-07-09 09:00 | 50543.1692 | 100.008
Devonshire Building | 2017-07-09 09:15 | 50543.1892 | 79.992
Devonshire Building | 2017-07-09 09:30 | 50543.2142 | 100.008
Devonshire Building | 2017-07-09 09:45 | 50543.2342 | 79.992
Devonshire Building | 2017-07-09 10:00 | 50543.2542 | 79.992
Devonshire Building | 2017-07-09 10:15 | 50543.2742 | 79.992
Devonshire Building | 2017-07-09 10:30 | 50543.2842 | 39.996
Devonshire Building | 2017-07-09 10:45 | 50543.2892 | 20.016
Devonshire Building | 2017-07-09 11:00 | 50543.2992 | 39.996
Devonshire Building | 2017-07-09 11:15 | 50543.3042 | 20.016
Devonshire Building | 2017-07-09 11:30 | 50543.3142 | 39.996
Devonshire Building | 2017-07-09 11:45 | 50543.3192 | 20.016
Devonshire Building | 2017-07-09 12:00 | 50543.3292 | 39.996
Devonshire Building | 2017-07-09 12:15 | 50543.3392 | 39.996
Devonshire Building | 2017-07-09 12:30 | 50543.3442 | 20.016
Devonshire Building | 2017-07-09 12:45 | 50543.3542 | 39.996
Devonshire Building | 2017-07-09 13:00 | 50543.3592 | 20.016
Devonshire Building | 2017-07-09 13:15 | 50543.3692 | 39.996
Devonshire Building | 2017-07-09 13:30 | 50543.3792 | 39.996
Devonshire Building | 2017-07-09 13:45 | 50543.3892 | 39.996
Devonshire Building | 2017-07-09 14:00 | 50543.3992 | 39.996
Devonshire Building | 2017-07-09 14:15 | 50543.4042 | 20.016
Devonshire Building | 2017-07-09 14:30 | 50543.4142 | 39.996
Devonshire Building | 2017-07-09 14:45 | 50543.4192 | 20.016
Devonshire Building | 2017-07-09 15:00 | 50543.4292 | 39.996
Devonshire Building | 2017-07-09 15:15 | 50543.4392 | 39.996
Devonshire Building | 2017-07-09 15:30 | 50543.4442 | 20.016
Devonshire Building | 2017-07-09 15:45 | 50543.4492 | 20.016
Devonshire Building | 2017-07-09 16:00 | 50543.4592 | 39.996
Devonshire Building | 2017-07-09 16:15 | 50543.4642 | 20.016
Devonshire Building | 2017-07-09 16:30 | 50543.4742 | 39.996
Devonshire Building | 2017-07-09 16:45 | 50543.4792 | 20.016
Devonshire Building | 2017-07-09 17:00 | 50543.4842 | 20.016
Devonshire Building | 2017-07-09 17:15 | 50543.4942 | 39.996
Devonshire Building | 2017-07-09 17:30 | 50543.4992 | 20.016
Devonshire Building | 2017-07-09 17:45 | 50543.5042 | 20.016
Devonshire Building | 2017-07-09 18:00 | 50543.5142 | 39.996
Devonshire Building | 2017-07-09 18:15 | 50543.5192 | 20.016
Devonshire Building | 2017-07-09 18:30 | 50543.5243 | 20.016
Devonshire Building | 2017-07-09 18:45 | 50543.5293 | 20.016
Devonshire Building | 2017-07-09 19:00 | 50543.5393 | 39.996
Devonshire Building | 2017-07-09 19:15 | 50543.5443 | 20.016
Devonshire Building | 2017-07-09 19:30 | 50543.5493 | 20.016
Devonshire Building | 2017-07-09 19:45 | 50543.5593 | 39.996
Devonshire Building | 2017-07-09 20:00 | 50543.5643 | 20.016
Devonshire Building | 2017-07-09 20:15 | 50543.5693 | 20.016
Devonshire Building | 2017-07-09 20:30 | 50543.5743 | 20.016
Devonshire Building | 2017-07-09 20:45 | 50543.6043 | 119.988
Devonshire Building | 2017-07-09 21:00 | 50543.6143 | 39.996
Devonshire Building | 2017-07-09 21:15 | 50543.6243 | 39.996
Devonshire Building | 2017-07-09 21:30 | 50543.6293 | 20.016
Devonshire Building | 2017-07-09 21:45 | 50543.6393 | 39.996
Devonshire Building | 2017-07-09 22:00 | 50543.6493 | 39.996
Devonshire Building | 2017-07-09 22:15 | 50543.6593 | 39.996
Devonshire Building | 2017-07-09 22:30 | 50543.6643 | 20.016
Devonshire Building | 2017-07-09 22:45 | 50543.6743 | 39.996
Devonshire Building | 2017-07-09 23:00 | 50543.6843 | 39.996
Devonshire Building | 2017-07-09 23:15 | 50543.6893 | 20.016
Devonshire Building | 2017-07-09 23:30 | 50543.6993 | 39.996
Devonshire Building | 2017-07-09 23:45 | 50543.7243 | 100.008
Devonshire Building | 2017-07-10 | 50544.2148 | 1959.984
Devonshire Building | 2017-07-10 00:15 | 50544.2248 | 39.996
Devonshire Building | 2017-07-10 00:30 | 50544.2348 | 39.996
Devonshire Building | 2017-07-10 00:45 | 50544.2398 | 20.016
Devonshire Building | 2017-07-10 01:00 | 50544.2498 | 39.996
Devonshire Building | 2017-07-10 01:15 | 50544.2598 | 39.996
Devonshire Building | 2017-07-10 01:30 | 50544.2698 | 39.996
Devonshire Building | 2017-07-10 01:45 | 50544.2798 | 39.996
Devonshire Building | 2017-07-10 02:00 | 50544.2898 | 39.996
Devonshire Building | 2017-07-10 02:15 | 50544.2998 | 39.996
Devonshire Building | 2017-07-10 02:30 | 50544.3098 | 39.996
Devonshire Building | 2017-07-10 02:45 | 50544.3248 | 60.012
Devonshire Building | 2017-07-10 03:00 | 50544.3348 | 39.996
Devonshire Building | 2017-07-10 03:15 | 50544.3498 | 60.012
Devonshire Building | 2017-07-10 03:30 | 50544.3598 | 39.996
Devonshire Building | 2017-07-10 03:45 | 50544.3748 | 60.012
Devonshire Building | 2017-07-10 04:00 | 50544.3848 | 39.996
Devonshire Building | 2017-07-10 04:15 | 50544.3948 | 39.996
Devonshire Building | 2017-07-10 04:30 | 50544.4098 | 60.012
Devonshire Building | 2017-07-10 04:45 | 50544.4198 | 39.996
Devonshire Building | 2017-07-10 05:00 | 50544.4348 | 60.012
Devonshire Building | 2017-07-10 05:15 | 50544.4498 | 60.012
Devonshire Building | 2017-07-10 05:30 | 50544.4598 | 39.996
Devonshire Building | 2017-07-10 05:45 | 50544.4748 | 60.012
Devonshire Building | 2017-07-10 06:00 | 50544.4848 | 39.996
Devonshire Building | 2017-07-10 06:15 | 50544.4948 | 39.996
Devonshire Building | 2017-07-10 06:30 | 50544.5048 | 39.996
Devonshire Building | 2017-07-10 06:45 | 50544.5148 | 39.996
Devonshire Building | 2017-07-10 07:00 | 50544.5298 | 60.012
Devonshire Building | 2017-07-10 07:15 | 50544.5498 | 79.992
Devonshire Building | 2017-07-10 07:30 | 50544.5698 | 79.992
Devonshire Building | 2017-07-10 07:45 | 50544.5948 | 100.008
Devonshire Building | 2017-07-10 08:00 | 50544.6498 | 219.996
Devonshire Building | 2017-07-10 08:15 | 50544.8148 | 659.988
Devonshire Building | 2017-07-10 08:30 | 50545.3448 | 2120.004
Devonshire Building | 2017-07-10 08:45 | 50545.4498 | 420.012
Devonshire Building | 2017-07-10 09:00 | 50545.5498 | 399.996
Devonshire Building | 2017-07-10 09:15 | 50545.6498 | 399.996
Devonshire Building | 2017-07-10 09:30 | 50545.7898 | 560.016
Devonshire Building | 2017-07-10 09:45 | 50546.6499 | 3440.016
Devonshire Building | 2017-07-10 10:00 | 50546.9349 | 1140.012
Devonshire Building | 2017-07-10 10:15 | 50547.1799 | 979.992
Devonshire Building | 2017-07-10 10:30 | 50547.3549 | 699.984
Devonshire Building | 2017-07-10 10:45 | 50547.4998 | 579.996
Devonshire Building | 2017-07-10 11:00 | 50547.5998 | 399.996
Devonshire Building | 2017-07-10 11:15 | 50548.0448 | 1779.984
Devonshire Building | 2017-07-10 11:30 | 50548.2498 | 820.008
Devonshire Building | 2017-07-10 11:45 | 50548.2898 | 159.984
Devonshire Building | 2017-07-10 12:00 | 50548.3398 | 200.016
Devonshire Building | 2017-07-10 12:15 | 50548.3848 | 180
Devonshire Building | 2017-07-10 12:30 | 50548.4398 | 219.996
Devonshire Building | 2017-07-10 12:45 | 50548.4998 | 240.012
Devonshire Building | 2017-07-10 13:00 | 50549.1198 | 2480.004
Devonshire Building | 2017-07-10 13:15 | 50549.2699 | 600.012
Devonshire Building | 2017-07-10 13:30 | 50549.3998 | 519.984
Devonshire Building | 2017-07-10 13:45 | 50549.5148 | 460.008
Devonshire Building | 2017-07-10 14:00 | 50549.6248 | 439.992
Devonshire Building | 2017-07-10 14:15 | 50549.7148 | 360
Devonshire Building | 2017-07-10 14:30 | 50549.8048 | 360
Devonshire Building | 2017-07-10 14:45 | 50550.1198 | 1260
Devonshire Building | 2017-07-10 15:00 | 50550.5148 | 1580.004
Devonshire Building | 2017-07-10 15:15 | 50550.6148 | 399.996
Devonshire Building | 2017-07-10 15:30 | 50550.7099 | 380.016
Devonshire Building | 2017-07-10 15:45 | 50550.7999 | 360
Devonshire Building | 2017-07-10 16:00 | 50550.8999 | 399.996
Devonshire Building | 2017-07-10 16:15 | 50550.9999 | 399.996
Devonshire Building | 2017-07-10 16:30 | 50551.5248 | 2099.988
Devonshire Building | 2017-07-10 16:45 | 50551.6649 | 560.016
Devonshire Building | 2017-07-10 17:00 | 50551.7298 | 259.992
Devonshire Building | 2017-07-10 17:15 | 50551.7848 | 219.996
Devonshire Building | 2017-07-10 17:30 | 50551.8298 | 180
Devonshire Building | 2017-07-10 17:45 | 50551.8698 | 159.984
Devonshire Building | 2017-07-10 18:00 | 50551.8998 | 119.988
Devonshire Building | 2017-07-10 18:15 | 50551.9298 | 119.988
Devonshire Building | 2017-07-10 18:30 | 50551.9548 | 100.008
Devonshire Building | 2017-07-10 18:45 | 50551.9748 | 79.992
Devonshire Building | 2017-07-10 19:00 | 50551.9948 | 79.992
Devonshire Building | 2017-07-10 19:15 | 50552.0148 | 79.992
Devonshire Building | 2017-07-10 19:30 | 50552.0348 | 79.992
Devonshire Building | 2017-07-10 19:45 | 50552.0498 | 60.012
Devonshire Building | 2017-07-10 20:00 | 50552.0698 | 79.992
Devonshire Building | 2017-07-10 20:15 | 50552.0848 | 60.012
Devonshire Building | 2017-07-10 20:30 | 50552.0998 | 60.012
Devonshire Building | 2017-07-10 20:45 | 50552.1348 | 140.004
Devonshire Building | 2017-07-10 21:00 | 50552.1398 | 20.016
Devonshire Building | 2017-07-10 21:15 | 50552.1448 | 20.016
Devonshire Building | 2017-07-10 21:30 | 50552.1499 | 20.016
Devonshire Building | 2017-07-10 21:45 | 50552.1549 | 20.016
Devonshire Building | 2017-07-10 22:00 | 50552.1649 | 39.996
Devonshire Building | 2017-07-10 22:15 | 50552.1699 | 20.016
Devonshire Building | 2017-07-10 22:30 | 50552.1749 | 20.016
Devonshire Building | 2017-07-10 22:45 | 50552.1799 | 20.016
Devonshire Building | 2017-07-10 23:00 | 50552.1849 | 20.016
Devonshire Building | 2017-07-10 23:15 | 50552.1899 | 20.016
Devonshire Building | 2017-07-10 23:30 | 50552.1949 | 20.016
Devonshire Building | 2017-07-10 23:45 | 50552.1999 | 20.016
Devonshire Building | 2017-07-11 | 50552.2031 | 20.016
Devonshire Building | 2017-07-11 00:15 | 50552.2081 | 20.016
Devonshire Building | 2017-07-11 00:30 | 50552.2131 | 20.016
Devonshire Building | 2017-07-11 00:45 | 50552.2181 | 20.016
Devonshire Building | 2017-07-11 01:00 | 50552.2231 | 20.016
Devonshire Building | 2017-07-11 01:15 | 50552.2282 | 20.016
Devonshire Building | 2017-07-11 01:30 | 50552.2332 | 20.016
Devonshire Building | 2017-07-11 01:45 | 50552.2382 | 20.016
Devonshire Building | 2017-07-11 02:00 | 50552.2432 | 20.016
Devonshire Building | 2017-07-11 02:15 | 50552.2482 | 20.016
Devonshire Building | 2017-07-11 02:30 | 50552.2532 | 20.016
Devonshire Building | 2017-07-11 02:45 | 50552.2582 | 20.016
Devonshire Building | 2017-07-11 03:00 | 50552.2632 | 20.016
Devonshire Building | 2017-07-11 03:15 | 50552.2682 | 20.016
Devonshire Building | 2017-07-11 03:30 | 50552.2732 | 20.016
Devonshire Building | 2017-07-11 03:45 | 50552.2782 | 20.016
Devonshire Building | 2017-07-11 04:00 | 50552.2832 | 20.016
Devonshire Building | 2017-07-11 04:15 | 50552.2882 | 20.016
Devonshire Building | 2017-07-11 04:30 | 50552.2932 | 20.016
Devonshire Building | 2017-07-11 04:45 | 50552.7932 | 2000.016
Devonshire Building | 2017-07-11 05:00 | 50552.8032 | 39.996
Devonshire Building | 2017-07-11 05:15 | 50552.8132 | 39.996
Devonshire Building | 2017-07-11 05:30 | 50552.8182 | 20.016
Devonshire Building | 2017-07-11 05:45 | 50552.8282 | 39.996
Devonshire Building | 2017-07-11 06:00 | 50552.8332 | 20.016
Devonshire Building | 2017-07-11 06:15 | 50552.8382 | 20.016
Devonshire Building | 2017-07-11 06:30 | 50552.8482 | 39.996
Devonshire Building | 2017-07-11 06:45 | 50552.8582 | 39.996
Devonshire Building | 2017-07-11 07:00 | 50552.8732 | 60.012
Devonshire Building | 2017-07-11 07:15 | 50552.9182 | 180
Devonshire Building | 2017-07-11 07:30 | 50552.9582 | 159.984
Devonshire Building | 2017-07-11 07:45 | 50553.0182 | 240.012
Devonshire Building | 2017-07-11 08:00 | 50553.1082 | 360
Devonshire Building | 2017-07-11 08:15 | 50553.7682 | 2639.988
Devonshire Building | 2017-07-11 08:30 | 50553.9382 | 680.004
Devonshire Building | 2017-07-11 08:45 | 50554.1032 | 659.988
Devonshire Building | 2017-07-11 09:00 | 50554.2582 | 619.992
Devonshire Building | 2017-07-11 09:15 | 50554.4032 | 579.996
Devonshire Building | 2017-07-11 09:30 | 50554.6432 | 960.012
Devonshire Building | 2017-07-11 09:45 | 50555.4632 | 3279.996
Devonshire Building | 2017-07-11 10:00 | 50555.7932 | 1320.012
Devonshire Building | 2017-07-11 10:15 | 50556.0382 | 979.992
Devonshire Building | 2017-07-11 10:30 | 50556.2182 | 720
Devonshire Building | 2017-07-11 10:45 | 50556.6482 | 1720.008
Devonshire Building | 2017-07-11 11:00 | 50556.9282 | 1119.996
Devonshire Building | 2017-07-11 11:15 | 50557.0082 | 320.004
Devonshire Building | 2017-07-11 11:30 | 50557.0932 | 339.984
Devonshire Building | 2017-07-11 11:45 | 50557.2032 | 439.992
Devonshire Building | 2017-07-11 12:00 | 50557.3182 | 460.008
Devonshire Building | 2017-07-11 12:15 | 50557.7632 | 1779.984
Devonshire Building | 2017-07-11 12:30 | 50558.0982 | 1339.992
Devonshire Building | 2017-07-11 12:45 | 50558.2332 | 540
Devonshire Building | 2017-07-11 13:00 | 50558.3732 | 560.016
Devonshire Building | 2017-07-11 13:15 | 50558.5182 | 579.996
Devonshire Building | 2017-07-11 13:30 | 50558.6482 | 519.984
Devonshire Building | 2017-07-11 13:45 | 50558.7732 | 500.004
Devonshire Building | 2017-07-11 14:00 | 50558.9032 | 519.984
Devonshire Building | 2017-07-11 14:15 | 50559.6532 | 2999.988
Devonshire Building | 2017-07-11 14:30 | 50559.9332 | 1119.996
Devonshire Building | 2017-07-11 14:45 | 50560.1082 | 699.984
Devonshire Building | 2017-07-11 15:00 | 50560.2132 | 420.012
Devonshire Building | 2017-07-11 15:15 | 50560.2882 | 299.988
Devonshire Building | 2017-07-11 15:30 | 50560.3432 | 219.996
Devonshire Building | 2017-07-11 15:45 | 50560.9182 | 2300.004
Devonshire Building | 2017-07-11 16:00 | 50560.9332 | 60.012
Devonshire Building | 2017-07-11 16:15 | 50560.9532 | 79.992
Devonshire Building | 2017-07-11 16:30 | 50560.9732 | 79.992
Devonshire Building | 2017-07-11 16:45 | 50560.9932 | 79.992
Devonshire Building | 2017-07-11 17:00 | 50561.0082 | 60.012
Devonshire Building | 2017-07-11 17:15 | 50561.0232 | 60.012
Devonshire Building | 2017-07-11 17:30 | 50561.0432 | 79.992
Devonshire Building | 2017-07-11 17:45 | 50561.5382 | 1980
Devonshire Building | 2017-07-11 18:00 | 50561.6132 | 299.988
Devonshire Building | 2017-07-11 18:15 | 50561.6332 | 79.992
Devonshire Building | 2017-07-11 18:30 | 50561.6532 | 79.992
Devonshire Building | 2017-07-11 18:45 | 50561.6682 | 60.012
Devonshire Building | 2017-07-11 19:00 | 50561.6882 | 79.992
Devonshire Building | 2017-07-11 19:15 | 50561.7182 | 119.988
Devonshire Building | 2017-07-11 19:30 | 50561.7382 | 79.992
Devonshire Building | 2017-07-11 19:45 | 50561.7582 | 79.992
Devonshire Building | 2017-07-11 20:00 | 50561.7782 | 79.992
Devonshire Building | 2017-07-11 20:15 | 50561.7982 | 79.992
Devonshire Building | 2017-07-11 20:30 | 50561.8132 | 60.012
Devonshire Building | 2017-07-11 20:45 | 50561.8432 | 119.988
Devonshire Building | 2017-07-11 21:00 | 50561.8582 | 60.012
Devonshire Building | 2017-07-11 21:15 | 50561.8732 | 60.012
Devonshire Building | 2017-07-11 21:30 | 50561.8882 | 60.012
Devonshire Building | 2017-07-11 21:45 | 50561.9032 | 60.012
Devonshire Building | 2017-07-11 22:00 | 50561.9182 | 60.012
Devonshire Building | 2017-07-11 22:15 | 50561.9332 | 60.012
Devonshire Building | 2017-07-11 22:30 | 50561.9482 | 60.012
Devonshire Building | 2017-07-11 22:45 | 50561.9632 | 60.012
Devonshire Building | 2017-07-11 23:00 | 50561.9732 | 39.996
Devonshire Building | 2017-07-11 23:15 | 50561.9882 | 60.012
Devonshire Building | 2017-07-11 23:30 | 50562.0032 | 60.012
Devonshire Building | 2017-07-11 23:45 | 50562.0182 | 60.012
Devonshire Building | 2017-07-12 | 50562.0352 | 60.012
Devonshire Building | 2017-07-12 00:15 | 50562.0452 | 39.996
Devonshire Building | 2017-07-12 00:30 | 50562.0602 | 60.012
Devonshire Building | 2017-07-12 00:45 | 50562.0752 | 60.012
Devonshire Building | 2017-07-12 01:00 | 50562.0902 | 60.012
Devonshire Building | 2017-07-12 01:15 | 50562.1052 | 60.012
Devonshire Building | 2017-07-12 01:30 | 50562.1152 | 39.996
Devonshire Building | 2017-07-12 01:45 | 50562.1302 | 60.012
Devonshire Building | 2017-07-12 02:00 | 50562.1452 | 60.012
Devonshire Building | 2017-07-12 02:15 | 50562.1552 | 39.996
Devonshire Building | 2017-07-12 02:30 | 50562.1702 | 60.012
Devonshire Building | 2017-07-12 02:45 | 50562.1852 | 60.012
Devonshire Building | 2017-07-12 03:00 | 50562.1952 | 39.996
Devonshire Building | 2017-07-12 03:15 | 50562.2102 | 60.012
Devonshire Building | 2017-07-12 03:30 | 50562.2252 | 60.012
Devonshire Building | 2017-07-12 03:45 | 50562.2352 | 39.996
Devonshire Building | 2017-07-12 04:00 | 50562.2502 | 60.012
Devonshire Building | 2017-07-12 04:15 | 50562.2602 | 39.996
Devonshire Building | 2017-07-12 04:30 | 50562.2752 | 60.012
Devonshire Building | 2017-07-12 04:45 | 50562.2852 | 39.996
Devonshire Building | 2017-07-12 05:00 | 50562.3002 | 60.012
Devonshire Building | 2017-07-12 05:15 | 50562.3102 | 39.996
Devonshire Building | 2017-07-12 05:30 | 50562.3202 | 39.996
Devonshire Building | 2017-07-12 05:45 | 50562.3302 | 39.996
Devonshire Building | 2017-07-12 06:00 | 50562.3452 | 60.012
Devonshire Building | 2017-07-12 06:15 | 50562.3552 | 39.996
Devonshire Building | 2017-07-12 06:30 | 50562.3702 | 60.012
Devonshire Building | 2017-07-12 06:45 | 50562.3802 | 39.996
Devonshire Building | 2017-07-12 07:00 | 50562.9402 | 2239.992
Devonshire Building | 2017-07-12 07:15 | 50562.9552 | 60.012
Devonshire Building | 2017-07-12 07:30 | 50562.9702 | 60.012
Devonshire Building | 2017-07-12 07:45 | 50562.9752 | 20.016
Devonshire Building | 2017-07-12 08:00 | 50562.9902 | 60.012
Devonshire Building | 2017-07-12 08:15 | 50563.0002 | 39.996
Devonshire Building | 2017-07-12 08:30 | 50563.0102 | 39.996
Devonshire Building | 2017-07-12 08:45 | 50563.0552 | 180
Devonshire Building | 2017-07-12 09:00 | 50563.5752 | 2080.008
Devonshire Building | 2017-07-12 09:15 | 50563.6002 | 100.008
Devonshire Building | 2017-07-12 09:30 | 50563.7002 | 399.996
Devonshire Building | 2017-07-12 09:45 | 50563.8552 | 619.992
Devonshire Building | 2017-07-12 10:00 | 50564.0202 | 659.988
Devonshire Building | 2017-07-12 10:15 | 50564.7052 | 2739.996
Devonshire Building | 2017-07-12 10:30 | 50564.8202 | 460.008
Devonshire Building | 2017-07-12 10:45 | 50564.9152 | 380.016
Devonshire Building | 2017-07-12 11:00 | 50565.0002 | 339.984
Devonshire Building | 2017-07-12 11:15 | 50565.0902 | 360
Devonshire Building | 2017-07-12 11:30 | 50565.1752 | 339.984
Devonshire Building | 2017-07-12 11:45 | 50565.7552 | 2319.984
Devonshire Building | 2017-07-12 12:00 | 50565.8302 | 299.988
Devonshire Building | 2017-07-12 12:15 | 50565.9152 | 339.984
Devonshire Building | 2017-07-12 12:30 | 50566.0452 | 519.984
Devonshire Building | 2017-07-12 12:45 | 50566.1752 | 519.984
Devonshire Building | 2017-07-12 13:00 | 50566.3102 | 540
Devonshire Building | 2017-07-12 13:15 | 50566.4302 | 479.988
Devonshire Building | 2017-07-12 13:30 | 50567.0402 | 2440.008
Devonshire Building | 2017-07-12 13:45 | 50567.1402 | 399.996
Devonshire Building | 2017-07-12 14:00 | 50567.2402 | 399.996
Devonshire Building | 2017-07-12 14:15 | 50567.3352 | 380.016
Devonshire Building | 2017-07-12 14:30 | 50567.4502 | 460.008
Devonshire Building | 2017-07-12 14:45 | 50567.5602 | 439.992
Devonshire Building | 2017-07-12 15:00 | 50567.6552 | 380.016
Devonshire Building | 2017-07-12 15:15 | 50568.2402 | 2340
Devonshire Building | 2017-07-12 15:30 | 50568.3152 | 299.988
Devonshire Building | 2017-07-12 15:45 | 50568.3702 | 219.996
Devonshire Building | 2017-07-12 16:00 | 50568.4202 | 200.016
Devonshire Building | 2017-07-12 16:15 | 50568.4752 | 219.996
Devonshire Building | 2017-07-12 16:30 | 50568.5252 | 200.016
Devonshire Building | 2017-07-12 16:45 | 50568.5752 | 200.016
Devonshire Building | 2017-07-12 17:00 | 50568.6202 | 180
Devonshire Building | 2017-07-12 17:15 | 50568.6652 | 180
Devonshire Building | 2017-07-12 17:30 | 50568.7852 | 479.988
Devonshire Building | 2017-07-12 17:45 | 50569.2552 | 1879.992
Devonshire Building | 2017-07-12 18:00 | 50569.3002 | 180
Devonshire Building | 2017-07-12 18:15 | 50569.3452 | 180
Devonshire Building | 2017-07-12 18:30 | 50569.3902 | 180
Devonshire Building | 2017-07-12 18:45 | 50569.4302 | 159.984
Devonshire Building | 2017-07-12 19:00 | 50569.4702 | 159.984
Devonshire Building | 2017-07-12 19:15 | 50569.5102 | 159.984
Devonshire Building | 2017-07-12 19:30 | 50569.5552 | 180
Devonshire Building | 2017-07-12 19:45 | 50569.5902 | 140.004
Devonshire Building | 2017-07-12 20:00 | 50569.6252 | 140.004
Devonshire Building | 2017-07-12 20:15 | 50569.6552 | 119.988
Devonshire Building | 2017-07-12 20:30 | 50569.6852 | 119.988
Devonshire Building | 2017-07-12 20:45 | 50569.7202 | 140.004
Devonshire Building | 2017-07-12 21:00 | 50569.7352 | 60.012
Devonshire Building | 2017-07-12 21:15 | 50569.7452 | 39.996
Devonshire Building | 2017-07-12 21:30 | 50569.7602 | 60.012
Devonshire Building | 2017-07-12 21:45 | 50569.7702 | 39.996
Devonshire Building | 2017-07-12 22:00 | 50569.7852 | 60.012
Devonshire Building | 2017-07-12 22:15 | 50569.7952 | 39.996
Devonshire Building | 2017-07-12 22:30 | 50569.8102 | 60.012
Devonshire Building | 2017-07-12 22:45 | 50569.8252 | 60.012
Devonshire Building | 2017-07-12 23:00 | 50569.8352 | 39.996
Devonshire Building | 2017-07-12 23:15 | 50569.8502 | 60.012
Devonshire Building | 2017-07-12 23:30 | 50569.8602 | 39.996
Devonshire Building | 2017-07-12 23:45 | 50569.8702 | 39.996
Devonshire Building | 2017-07-13 | 50569.8828 | 60.012
Devonshire Building | 2017-07-13 00:15 | 50569.8928 | 39.996
Devonshire Building | 2017-07-13 00:30 | 50569.9078 | 60.012
Devonshire Building | 2017-07-13 00:45 | 50569.9178 | 39.996
Devonshire Building | 2017-07-13 01:00 | 50569.9278 | 39.996
Devonshire Building | 2017-07-13 01:15 | 50569.9428 | 60.012
Devonshire Building | 2017-07-13 01:30 | 50569.9528 | 39.996
Devonshire Building | 2017-07-13 01:45 | 50569.9628 | 39.996
Devonshire Building | 2017-07-13 02:00 | 50569.9728 | 39.996
Devonshire Building | 2017-07-13 02:15 | 50569.9878 | 60.012
Devonshire Building | 2017-07-13 02:30 | 50569.9978 | 39.996
Devonshire Building | 2017-07-13 02:45 | 50570.0128 | 60.012
Devonshire Building | 2017-07-13 03:00 | 50570.0228 | 39.996
Devonshire Building | 2017-07-13 03:15 | 50570.0328 | 39.996
Devonshire Building | 2017-07-13 03:30 | 50570.0428 | 39.996
Devonshire Building | 2017-07-13 03:45 | 50570.0528 | 39.996
Devonshire Building | 2017-07-13 04:00 | 50570.0628 | 39.996
Devonshire Building | 2017-07-13 04:15 | 50570.0728 | 39.996
Devonshire Building | 2017-07-13 04:30 | 50570.0828 | 39.996
Devonshire Building | 2017-07-13 04:45 | 50570.0928 | 39.996
Devonshire Building | 2017-07-13 05:00 | 50570.1078 | 60.012
Devonshire Building | 2017-07-13 05:15 | 50570.1178 | 39.996
Devonshire Building | 2017-07-13 05:30 | 50570.1278 | 39.996
Devonshire Building | 2017-07-13 05:45 | 50570.1378 | 39.996
Devonshire Building | 2017-07-13 06:00 | 50570.1528 | 60.012
Devonshire Building | 2017-07-13 06:15 | 50570.1728 | 79.992
Devonshire Building | 2017-07-13 06:30 | 50570.1978 | 100.008
Devonshire Building | 2017-07-13 06:45 | 50570.7278 | 2120.004
Devonshire Building | 2017-07-13 07:00 | 50570.7378 | 39.996
Devonshire Building | 2017-07-13 07:15 | 50570.7578 | 79.992
Devonshire Building | 2017-07-13 07:30 | 50570.7628 | 20.016
Devonshire Building | 2017-07-13 07:45 | 50570.7778 | 60.012
Devonshire Building | 2017-07-13 08:00 | 50570.7878 | 39.996
Devonshire Building | 2017-07-13 08:15 | 50570.8028 | 60.012
Devonshire Building | 2017-07-13 08:30 | 50570.8378 | 140.004
Devonshire Building | 2017-07-13 08:45 | 50570.9028 | 259.992
Devonshire Building | 2017-07-13 09:00 | 50571.6178 | 2859.984
Devonshire Building | 2017-07-13 09:15 | 50571.8578 | 960.012
Devonshire Building | 2017-07-13 09:30 | 50572.1028 | 979.992
Devonshire Building | 2017-07-13 09:45 | 50572.3178 | 860.004
Devonshire Building | 2017-07-13 10:00 | 50572.4678 | 600.012
Devonshire Building | 2017-07-13 10:15 | 50572.8428 | 1500.012
Devonshire Building | 2017-07-13 10:30 | 50573.2578 | 1659.996
Devonshire Building | 2017-07-13 10:45 | 50573.3928 | 540
Devonshire Building | 2017-07-13 11:00 | 50573.5228 | 519.984
Devonshire Building | 2017-07-13 11:15 | 50573.6478 | 500.004
Devonshire Building | 2017-07-13 11:30 | 50573.7728 | 500.004
Devonshire Building | 2017-07-13 11:45 | 50573.8978 | 500.004
Devonshire Building | 2017-07-13 12:00 | 50574.5578 | 2639.988
Devonshire Building | 2017-07-13 12:15 | 50574.6928 | 540
Devonshire Building | 2017-07-13 12:30 | 50574.8378 | 579.996
Devonshire Building | 2017-07-13 12:45 | 50575.0028 | 659.988
Devonshire Building | 2017-07-13 13:00 | 50575.1578 | 619.992
Devonshire Building | 2017-07-13 13:15 | 50575.2928 | 540
Devonshire Building | 2017-07-13 13:30 | 50575.6978 | 1620
Devonshire Building | 2017-07-13 13:45 | 50575.9878 | 1159.992
Devonshire Building | 2017-07-13 14:00 | 50576.0728 | 339.984
Devonshire Building | 2017-07-13 14:15 | 50576.1628 | 360
Devonshire Building | 2017-07-13 14:30 | 50576.2678 | 420.012
Devonshire Building | 2017-07-13 14:45 | 50576.3728 | 420.012
Devonshire Building | 2017-07-13 15:00 | 50576.8178 | 1779.984
Devonshire Building | 2017-07-13 15:15 | 50577.2928 | 1900.008
Devonshire Building | 2017-07-13 15:30 | 50577.4728 | 720
Devonshire Building | 2017-07-13 15:45 | 50577.5928 | 479.988
Devonshire Building | 2017-07-13 16:00 | 50577.6778 | 339.984
Devonshire Building | 2017-07-13 16:15 | 50578.2478 | 2279.988
Devonshire Building | 2017-07-13 16:30 | 50578.2778 | 119.988
Devonshire Building | 2017-07-13 16:45 | 50578.3078 | 119.988
Devonshire Building | 2017-07-13 17:00 | 50578.3378 | 119.988
Devonshire Building | 2017-07-13 17:15 | 50578.3678 | 119.988
Devonshire Building | 2017-07-13 17:30 | 50578.3978 | 119.988
Devonshire Building | 2017-07-13 17:45 | 50578.4278 | 119.988
Devonshire Building | 2017-07-13 18:00 | 50578.4578 | 119.988
Devonshire Building | 2017-07-13 18:15 | 50578.4828 | 100.008
Devonshire Building | 2017-07-13 18:30 | 50578.5078 | 100.008
Devonshire Building | 2017-07-13 18:45 | 50578.5528 | 180
Devonshire Building | 2017-07-13 19:00 | 50578.5728 | 79.992
Devonshire Building | 2017-07-13 19:15 | 50578.5928 | 79.992
Devonshire Building | 2017-07-13 19:30 | 50578.6128 | 79.992
Devonshire Building | 2017-07-13 19:45 | 50578.6328 | 79.992
Devonshire Building | 2017-07-13 20:00 | 50578.6478 | 60.012
Devonshire Building | 2017-07-13 20:15 | 50578.6678 | 79.992
Devonshire Building | 2017-07-13 20:30 | 50578.6828 | 60.012
Devonshire Building | 2017-07-13 20:45 | 50578.7128 | 119.988
Devonshire Building | 2017-07-13 21:00 | 50578.7178 | 20.016
Devonshire Building | 2017-07-13 21:15 | 50578.7228 | 20.016
Devonshire Building | 2017-07-13 21:30 | 50578.7328 | 39.996
Devonshire Building | 2017-07-13 21:45 | 50578.7378 | 20.016
Devonshire Building | 2017-07-13 22:00 | 50578.7428 | 20.016
Devonshire Building | 2017-07-13 22:15 | 50578.7478 | 20.016
Devonshire Building | 2017-07-13 22:30 | 50578.7528 | 20.016
Devonshire Building | 2017-07-13 22:45 | 50578.7578 | 20.016
Devonshire Building | 2017-07-13 23:00 | 50578.7678 | 39.996
Devonshire Building | 2017-07-13 23:15 | 50578.7728 | 20.016
Devonshire Building | 2017-07-13 23:30 | 50578.7778 | 20.016
Devonshire Building | 2017-07-13 23:45 | 50578.7828 | 20.016
Devonshire Building | 2017-07-14 | 50578.7891 | 20.016
Devonshire Building | 2017-07-14 00:15 | 50578.7941 | 20.016
Devonshire Building | 2017-07-14 00:30 | 50578.7991 | 20.016
Devonshire Building | 2017-07-14 00:45 | 50578.8041 | 20.016
Devonshire Building | 2017-07-14 01:00 | 50578.8141 | 39.996
Devonshire Building | 2017-07-14 01:15 | 50578.8191 | 20.016
Devonshire Building | 2017-07-14 01:30 | 50578.8241 | 20.016
Devonshire Building | 2017-07-14 01:45 | 50578.8291 | 20.016
Devonshire Building | 2017-07-14 02:00 | 50578.8341 | 20.016
Devonshire Building | 2017-07-14 02:15 | 50578.8391 | 20.016
Devonshire Building | 2017-07-14 02:30 | 50578.8441 | 20.016
Devonshire Building | 2017-07-14 02:45 | 50578.8491 | 20.016
Devonshire Building | 2017-07-14 03:00 | 50578.8541 | 20.016
Devonshire Building | 2017-07-14 03:15 | 50578.8591 | 20.016
Devonshire Building | 2017-07-14 03:30 | 50578.8641 | 20.016
Devonshire Building | 2017-07-14 03:45 | 50578.8691 | 20.016
Devonshire Building | 2017-07-14 04:00 | 50578.8791 | 39.996
Devonshire Building | 2017-07-14 04:15 | 50578.8841 | 20.016
Devonshire Building | 2017-07-14 04:30 | 50578.8891 | 20.016
Devonshire Building | 2017-07-14 04:45 | 50578.8941 | 20.016
Devonshire Building | 2017-07-14 05:00 | 50578.8991 | 20.016
Devonshire Building | 2017-07-14 05:15 | 50578.9241 | 100.008
Devonshire Building | 2017-07-14 05:30 | 50578.9441 | 79.992
Devonshire Building | 2017-07-14 05:45 | 50578.9691 | 100.008
Devonshire Building | 2017-07-14 06:00 | 50578.9941 | 100.008
Devonshire Building | 2017-07-14 06:15 | 50579.0241 | 119.988
Devonshire Building | 2017-07-14 06:30 | 50579.0491 | 100.008
Devonshire Building | 2017-07-14 06:45 | 50579.5941 | 2180.016
Devonshire Building | 2017-07-14 07:00 | 50579.6291 | 140.004
Devonshire Building | 2017-07-14 07:15 | 50579.6541 | 100.008
Devonshire Building | 2017-07-14 07:30 | 50579.6741 | 79.992
Devonshire Building | 2017-07-14 07:45 | 50579.7091 | 140.004
Devonshire Building | 2017-07-14 08:00 | 50579.7391 | 119.988
Devonshire Building | 2017-07-14 08:15 | 50579.7791 | 159.984
Devonshire Building | 2017-07-14 08:30 | 50579.8141 | 140.004
Devonshire Building | 2017-07-14 08:45 | 50579.8591 | 180
Devonshire Building | 2017-07-14 09:00 | 50580.4291 | 2279.988
Devonshire Building | 2017-07-14 09:15 | 50580.4691 | 159.984
Devonshire Building | 2017-07-14 09:30 | 50580.5141 | 180
Devonshire Building | 2017-07-14 09:45 | 50580.5691 | 219.996
Devonshire Building | 2017-07-14 10:00 | 50580.6891 | 479.988
Devonshire Building | 2017-07-14 10:15 | 50581.2041 | 2059.992
Devonshire Building | 2017-07-14 10:30 | 50581.2741 | 280.008
Devonshire Building | 2017-07-14 10:45 | 50581.3441 | 280.008
Devonshire Building | 2017-07-14 11:00 | 50581.3991 | 219.996
Devonshire Building | 2017-07-14 11:15 | 50581.4591 | 240.012
Devonshire Building | 2017-07-14 11:30 | 50581.5091 | 200.016
Devonshire Building | 2017-07-14 11:45 | 50581.5641 | 219.996
Devonshire Building | 2017-07-14 12:00 | 50581.6091 | 180
Devonshire Building | 2017-07-14 12:15 | 50582.1541 | 2180.016
Devonshire Building | 2017-07-14 12:30 | 50582.1841 | 119.988
Devonshire Building | 2017-07-14 12:45 | 50582.2191 | 140.004
Devonshire Building | 2017-07-14 13:00 | 50582.2541 | 140.004
Devonshire Building | 2017-07-14 13:15 | 50582.2841 | 119.988
Devonshire Building | 2017-07-14 13:30 | 50582.3191 | 140.004
Devonshire Building | 2017-07-14 13:45 | 50582.3591 | 159.984
Devonshire Building | 2017-07-14 14:00 | 50582.3941 | 140.004
Devonshire Building | 2017-07-14 14:15 | 50582.9291 | 2139.984
Devonshire Building | 2017-07-14 14:30 | 50582.9591 | 119.988
Devonshire Building | 2017-07-14 14:45 | 50582.9941 | 140.004
Devonshire Building | 2017-07-14 15:00 | 50583.0291 | 140.004
Devonshire Building | 2017-07-14 15:15 | 50583.0691 | 159.984
Devonshire Building | 2017-07-14 15:30 | 50583.1041 | 140.004
Devonshire Building | 2017-07-14 15:45 | 50583.1391 | 140.004
Devonshire Building | 2017-07-14 16:00 | 50583.1741 | 140.004
Devonshire Building | 2017-07-14 16:15 | 50583.2091 | 140.004
Devonshire Building | 2017-07-14 16:30 | 50583.2391 | 119.988
Devonshire Building | 2017-07-14 16:45 | 50583.2691 | 119.988
Devonshire Building | 2017-07-14 17:00 | 50583.5291 | 1040.004
Devonshire Building | 2017-07-14 17:15 | 50583.9041 | 1500.012
Devonshire Building | 2017-07-14 17:30 | 50583.9941 | 360
Devonshire Building | 2017-07-14 17:45 | 50584.0791 | 339.984
Devonshire Building | 2017-07-14 18:00 | 50584.1591 | 320.004
Devonshire Building | 2017-07-14 18:15 | 50584.2391 | 320.004
Devonshire Building | 2017-07-14 18:30 | 50584.3191 | 320.004
Devonshire Building | 2017-07-14 18:45 | 50584.3841 | 259.992
Devonshire Building | 2017-07-14 19:00 | 50584.4391 | 219.996
Devonshire Building | 2017-07-14 19:15 | 50584.4841 | 180
Devonshire Building | 2017-07-14 19:30 | 50584.5191 | 140.004
Devonshire Building | 2017-07-14 19:45 | 50584.5541 | 140.004
Devonshire Building | 2017-07-14 20:00 | 50584.5841 | 119.988
Devonshire Building | 2017-07-14 20:15 | 50584.6091 | 100.008
Devonshire Building | 2017-07-14 20:30 | 50584.6291 | 79.992
Devonshire Building | 2017-07-14 20:45 | 50584.6591 | 119.988
Devonshire Building | 2017-07-14 21:00 | 50584.6741 | 60.012
Devonshire Building | 2017-07-14 21:15 | 50584.6841 | 39.996
Devonshire Building | 2017-07-14 21:30 | 50584.6991 | 60.012
Devonshire Building | 2017-07-14 21:45 | 50584.7141 | 60.012
Devonshire Building | 2017-07-14 22:00 | 50584.7291 | 60.012
Devonshire Building | 2017-07-14 22:15 | 50584.7391 | 39.996
Devonshire Building | 2017-07-14 22:30 | 50584.7541 | 60.012
Devonshire Building | 2017-07-14 22:45 | 50584.7641 | 39.996
Devonshire Building | 2017-07-14 23:00 | 50584.7791 | 60.012
Devonshire Building | 2017-07-14 23:15 | 50584.8091 | 119.988
Devonshire Building | 2017-07-14 23:30 | 50584.8341 | 100.008
Devonshire Building | 2017-07-14 23:45 | 50584.8641 | 119.988
Devonshire Building | 2017-07-15 | 50584.8945 | 119.988
Devonshire Building | 2017-07-15 00:15 | 50584.9195 | 100.008
Devonshire Building | 2017-07-15 00:30 | 50584.9495 | 119.988
Devonshire Building | 2017-07-15 00:45 | 50584.9795 | 119.988
Devonshire Building | 2017-07-15 01:00 | 50585.0045 | 100.008
Devonshire Building | 2017-07-15 01:15 | 50585.0295 | 100.008
Devonshire Building | 2017-07-15 01:30 | 50585.0445 | 60.012
Devonshire Building | 2017-07-15 01:45 | 50585.0545 | 39.996
Devonshire Building | 2017-07-15 02:00 | 50585.0645 | 39.996
Devonshire Building | 2017-07-15 02:15 | 50585.0795 | 60.012
Devonshire Building | 2017-07-15 02:30 | 50585.0895 | 39.996
Devonshire Building | 2017-07-15 02:45 | 50585.0995 | 39.996
Devonshire Building | 2017-07-15 03:00 | 50585.1095 | 39.996
Devonshire Building | 2017-07-15 03:15 | 50585.1195 | 39.996
Devonshire Building | 2017-07-15 03:30 | 50585.1345 | 60.012
Devonshire Building | 2017-07-15 03:45 | 50585.1445 | 39.996
Devonshire Building | 2017-07-15 04:00 | 50585.1545 | 39.996
Devonshire Building | 2017-07-15 04:15 | 50585.1645 | 39.996
Devonshire Building | 2017-07-15 04:30 | 50585.1745 | 39.996
Devonshire Building | 2017-07-15 04:45 | 50585.1845 | 39.996
Devonshire Building | 2017-07-15 05:00 | 50585.1995 | 60.012
Devonshire Building | 2017-07-15 05:15 | 50585.2095 | 39.996
Devonshire Building | 2017-07-15 05:30 | 50585.2195 | 39.996
Devonshire Building | 2017-07-15 05:45 | 50585.2295 | 39.996
Devonshire Building | 2017-07-15 06:00 | 50585.2395 | 39.996
Devonshire Building | 2017-07-15 06:15 | 50585.2545 | 60.012
Devonshire Building | 2017-07-15 06:30 | 50585.2645 | 39.996
Devonshire Building | 2017-07-15 06:45 | 50585.2745 | 39.996
Devonshire Building | 2017-07-15 07:00 | 50585.2845 | 39.996
Devonshire Building | 2017-07-15 07:15 | 50585.2945 | 39.996
Devonshire Building | 2017-07-15 07:30 | 50585.3045 | 39.996
Devonshire Building | 2017-07-15 07:45 | 50585.3245 | 79.992
Devonshire Building | 2017-07-15 08:00 | 50585.3345 | 39.996
Devonshire Building | 2017-07-15 08:15 | 50585.3445 | 39.996
Devonshire Building | 2017-07-15 08:30 | 50585.3545 | 39.996
Devonshire Building | 2017-07-15 08:45 | 50585.3645 | 39.996
Devonshire Building | 2017-07-15 09:00 | 50585.3795 | 60.012
Devonshire Building | 2017-07-15 09:15 | 50585.3895 | 39.996
Devonshire Building | 2017-07-15 09:30 | 50585.3995 | 39.996
Devonshire Building | 2017-07-15 09:45 | 50585.4095 | 39.996
Devonshire Building | 2017-07-15 10:00 | 50585.4195 | 39.996
Devonshire Building | 2017-07-15 10:15 | 50585.4295 | 39.996
Devonshire Building | 2017-07-15 10:30 | 50585.4395 | 39.996
Devonshire Building | 2017-07-15 10:45 | 50585.4495 | 39.996
Devonshire Building | 2017-07-15 11:00 | 50585.4595 | 39.996
Devonshire Building | 2017-07-15 11:15 | 50585.4695 | 39.996
Devonshire Building | 2017-07-15 11:30 | 50585.4795 | 39.996
Devonshire Building | 2017-07-15 11:45 | 50585.4895 | 39.996
Devonshire Building | 2017-07-15 12:00 | 50585.4995 | 39.996
Devonshire Building | 2017-07-15 12:15 | 50585.5395 | 159.984
Devonshire Building | 2017-07-15 12:30 | 50586.0045 | 1860.012
Devonshire Building | 2017-07-15 12:45 | 50586.0145 | 39.996
Devonshire Building | 2017-07-15 13:00 | 50586.0195 | 20.016
Devonshire Building | 2017-07-15 13:15 | 50586.0245 | 20.016
Devonshire Building | 2017-07-15 13:30 | 50586.0295 | 20.016
Devonshire Building | 2017-07-15 13:45 | 50586.0395 | 39.996
Devonshire Building | 2017-07-15 14:00 | 50586.0445 | 20.016
Devonshire Building | 2017-07-15 14:15 | 50586.0545 | 39.996
Devonshire Building | 2017-07-15 14:30 | 50586.0595 | 20.016
Devonshire Building | 2017-07-15 14:45 | 50586.0645 | 20.016
Devonshire Building | 2017-07-15 15:00 | 50586.0745 | 39.996
Devonshire Building | 2017-07-15 15:15 | 50586.0795 | 20.016
Devonshire Building | 2017-07-15 15:30 | 50586.0895 | 39.996
Devonshire Building | 2017-07-15 15:45 | 50586.0995 | 39.996
Devonshire Building | 2017-07-15 16:00 | 50586.1095 | 39.996
Devonshire Building | 2017-07-15 16:15 | 50586.1145 | 20.016
Devonshire Building | 2017-07-15 16:30 | 50586.1245 | 39.996
Devonshire Building | 2017-07-15 16:45 | 50586.1345 | 39.996
Devonshire Building | 2017-07-15 17:00 | 50586.1395 | 20.016
Devonshire Building | 2017-07-15 17:15 | 50586.1495 | 39.996
Devonshire Building | 2017-07-15 17:30 | 50586.1545 | 20.016
Devonshire Building | 2017-07-15 17:45 | 50586.1645 | 39.996
Devonshire Building | 2017-07-15 18:00 | 50586.1695 | 20.016
Devonshire Building | 2017-07-15 18:15 | 50586.1795 | 39.996
Devonshire Building | 2017-07-15 18:30 | 50586.1845 | 20.016
Devonshire Building | 2017-07-15 18:45 | 50586.1945 | 39.996
Devonshire Building | 2017-07-15 19:00 | 50586.1995 | 20.016
Devonshire Building | 2017-07-15 19:15 | 50586.2095 | 39.996
Devonshire Building | 2017-07-15 19:30 | 50586.2195 | 39.996
Devonshire Building | 2017-07-15 19:45 | 50586.2245 | 20.016
Devonshire Building | 2017-07-15 20:00 | 50586.2345 | 39.996
Devonshire Building | 2017-07-15 20:15 | 50586.2396 | 20.016
Devonshire Building | 2017-07-15 20:30 | 50586.2496 | 39.996
Devonshire Building | 2017-07-15 20:45 | 50586.2746 | 100.008
Devonshire Building | 2017-07-15 21:00 | 50586.2846 | 39.996
Devonshire Building | 2017-07-15 21:15 | 50586.2946 | 39.996
Devonshire Building | 2017-07-15 21:30 | 50586.2996 | 20.016
Devonshire Building | 2017-07-15 21:45 | 50586.3096 | 39.996
Devonshire Building | 2017-07-15 22:00 | 50586.3196 | 39.996
Devonshire Building | 2017-07-15 22:15 | 50586.3246 | 20.016
Devonshire Building | 2017-07-15 22:30 | 50586.3346 | 39.996
Devonshire Building | 2017-07-15 22:45 | 50586.3396 | 20.016
Devonshire Building | 2017-07-15 23:00 | 50586.3496 | 39.996
Devonshire Building | 2017-07-15 23:15 | 50586.3596 | 39.996
Devonshire Building | 2017-07-15 23:30 | 50586.3646 | 20.016
Devonshire Building | 2017-07-15 23:45 | 50586.3746 | 39.996
Devonshire Building | 2017-07-16 | 50586.3789 | 20.016
Devonshire Building | 2017-07-16 00:15 | 50586.3889 | 39.996
Devonshire Building | 2017-07-16 00:30 | 50586.3939 | 20.016
Devonshire Building | 2017-07-16 00:45 | 50586.4039 | 39.996
Devonshire Building | 2017-07-16 01:00 | 50586.4089 | 20.016
Devonshire Building | 2017-07-16 01:15 | 50586.4189 | 39.996
Devonshire Building | 2017-07-16 01:30 | 50586.4239 | 20.016
Devonshire Building | 2017-07-16 01:45 | 50586.4339 | 39.996
Devonshire Building | 2017-07-16 02:00 | 50586.4389 | 20.016
Devonshire Building | 2017-07-16 02:15 | 50586.4489 | 39.996
Devonshire Building | 2017-07-16 02:30 | 50586.4539 | 20.016
Devonshire Building | 2017-07-16 02:45 | 50586.4639 | 39.996
Devonshire Building | 2017-07-16 03:00 | 50586.4689 | 20.016
Devonshire Building | 2017-07-16 03:15 | 50586.4789 | 39.996
Devonshire Building | 2017-07-16 03:30 | 50586.4839 | 20.016
Devonshire Building | 2017-07-16 03:45 | 50586.4939 | 39.996
Devonshire Building | 2017-07-16 04:00 | 50586.4989 | 20.016
Devonshire Building | 2017-07-16 04:15 | 50586.5089 | 39.996
Devonshire Building | 2017-07-16 04:30 | 50586.5139 | 20.016
Devonshire Building | 2017-07-16 04:45 | 50586.5239 | 39.996
Devonshire Building | 2017-07-16 05:00 | 50586.5339 | 39.996
Devonshire Building | 2017-07-16 05:15 | 50587.0189 | 1940.004
Devonshire Building | 2017-07-16 05:30 | 50587.0539 | 140.004
Devonshire Building | 2017-07-16 05:45 | 50587.0639 | 39.996
Devonshire Building | 2017-07-16 06:00 | 50587.0739 | 39.996
Devonshire Building | 2017-07-16 06:15 | 50587.0889 | 60.012
Devonshire Building | 2017-07-16 06:30 | 50587.0989 | 39.996
Devonshire Building | 2017-07-16 06:45 | 50587.1139 | 60.012
Devonshire Building | 2017-07-16 07:00 | 50587.1339 | 79.992
Devonshire Building | 2017-07-16 07:15 | 50587.1489 | 60.012
Devonshire Building | 2017-07-16 07:30 | 50587.1639 | 60.012
Devonshire Building | 2017-07-16 07:45 | 50587.1839 | 79.992
Devonshire Building | 2017-07-16 08:00 | 50587.1989 | 60.012
Devonshire Building | 2017-07-16 08:15 | 50587.2139 | 60.012
Devonshire Building | 2017-07-16 08:30 | 50587.2339 | 79.992
Devonshire Building | 2017-07-16 08:45 | 50587.2489 | 60.012
Devonshire Building | 2017-07-16 09:00 | 50587.264 | 60.012
Devonshire Building | 2017-07-16 09:15 | 50587.279 | 60.012
Devonshire Building | 2017-07-16 09:30 | 50587.294 | 60.012
Devonshire Building | 2017-07-16 09:45 | 50587.309 | 60.012
Devonshire Building | 2017-07-16 10:00 | 50587.324 | 60.012
Devonshire Building | 2017-07-16 10:15 | 50587.334 | 39.996
Devonshire Building | 2017-07-16 10:30 | 50587.349 | 60.012
Devonshire Building | 2017-07-16 10:45 | 50587.359 | 39.996
Devonshire Building | 2017-07-16 11:00 | 50587.374 | 60.012
Devonshire Building | 2017-07-16 11:15 | 50587.399 | 100.008
Devonshire Building | 2017-07-16 11:30 | 50587.429 | 119.988
Devonshire Building | 2017-07-16 11:45 | 50587.454 | 100.008
Devonshire Building | 2017-07-16 12:00 | 50587.484 | 119.988
Devonshire Building | 2017-07-16 12:15 | 50587.509 | 100.008
Devonshire Building | 2017-07-16 12:30 | 50587.539 | 119.988
Devonshire Building | 2017-07-16 12:45 | 50587.564 | 100.008
Devonshire Building | 2017-07-16 13:00 | 50587.594 | 119.988
Devonshire Building | 2017-07-16 13:15 | 50587.614 | 79.992
Devonshire Building | 2017-07-16 13:30 | 50587.629 | 60.012
Devonshire Building | 2017-07-16 13:45 | 50587.639 | 39.996
Devonshire Building | 2017-07-16 14:00 | 50587.649 | 39.996
Devonshire Building | 2017-07-16 14:15 | 50587.659 | 39.996
Devonshire Building | 2017-07-16 14:30 | 50587.669 | 39.996
Devonshire Building | 2017-07-16 14:45 | 50587.684 | 60.012
Devonshire Building | 2017-07-16 15:00 | 50587.694 | 39.996
Devonshire Building | 2017-07-16 15:15 | 50587.704 | 39.996
Devonshire Building | 2017-07-16 15:30 | 50587.714 | 39.996
Devonshire Building | 2017-07-16 15:45 | 50587.724 | 39.996
Devonshire Building | 2017-07-16 16:00 | 50587.734 | 39.996
Devonshire Building | 2017-07-16 16:15 | 50587.744 | 39.996
Devonshire Building | 2017-07-16 16:30 | 50587.759 | 60.012
Devonshire Building | 2017-07-16 16:45 | 50587.769 | 39.996
Devonshire Building | 2017-07-16 17:00 | 50587.779 | 39.996
Devonshire Building | 2017-07-16 17:15 | 50587.789 | 39.996
Devonshire Building | 2017-07-16 17:30 | 50587.799 | 39.996
Devonshire Building | 2017-07-16 17:45 | 50587.809 | 39.996
Devonshire Building | 2017-07-16 18:00 | 50587.824 | 60.012
Devonshire Building | 2017-07-16 18:15 | 50587.834 | 39.996
Devonshire Building | 2017-07-16 18:30 | 50587.844 | 39.996
Devonshire Building | 2017-07-16 18:45 | 50587.854 | 39.996
Devonshire Building | 2017-07-16 19:00 | 50587.864 | 39.996
Devonshire Building | 2017-07-16 19:15 | 50587.874 | 39.996
Devonshire Building | 2017-07-16 19:30 | 50587.884 | 39.996
Devonshire Building | 2017-07-16 19:45 | 50587.894 | 39.996
Devonshire Building | 2017-07-16 20:00 | 50587.904 | 39.996
Devonshire Building | 2017-07-16 20:15 | 50587.914 | 39.996
Devonshire Building | 2017-07-16 20:30 | 50587.9239 | 39.996
Devonshire Building | 2017-07-16 20:45 | 50587.959 | 140.004
Devonshire Building | 2017-07-16 21:00 | 50587.964 | 20.016
Devonshire Building | 2017-07-16 21:15 | 50587.969 | 20.016
Devonshire Building | 2017-07-16 21:30 | 50587.979 | 39.996
Devonshire Building | 2017-07-16 21:45 | 50587.984 | 20.016
Devonshire Building | 2017-07-16 22:00 | 50587.994 | 39.996
Devonshire Building | 2017-07-16 22:15 | 50587.999 | 20.016
Devonshire Building | 2017-07-16 22:30 | 50588.009 | 39.996
Devonshire Building | 2017-07-16 22:45 | 50588.014 | 20.016
Devonshire Building | 2017-07-16 23:00 | 50588.024 | 39.996
Devonshire Building | 2017-07-16 23:15 | 50588.029 | 20.016
Devonshire Building | 2017-07-16 23:30 | 50588.034 | 20.016
Devonshire Building | 2017-07-16 23:45 | 50588.534 | 2000.016
Devonshire Building | 2017-07-17 | 50588.5391 | 20.016
Devonshire Building | 2017-07-17 00:15 | 50588.5441 | 20.016
Devonshire Building | 2017-07-17 00:30 | 50588.5541 | 39.996
Devonshire Building | 2017-07-17 00:45 | 50588.5591 | 20.016
Devonshire Building | 2017-07-17 01:00 | 50588.5641 | 20.016
Devonshire Building | 2017-07-17 01:15 | 50588.5741 | 39.996
Devonshire Building | 2017-07-17 01:30 | 50588.5791 | 20.016
Devonshire Building | 2017-07-17 01:45 | 50588.5891 | 39.996
Devonshire Building | 2017-07-17 02:00 | 50588.5941 | 20.016
Devonshire Building | 2017-07-17 02:15 | 50588.5991 | 20.016
Devonshire Building | 2017-07-17 02:30 | 50588.6091 | 39.996
Devonshire Building | 2017-07-17 02:45 | 50588.6191 | 39.996
Devonshire Building | 2017-07-17 03:00 | 50588.6291 | 39.996
Devonshire Building | 2017-07-17 03:15 | 50588.6391 | 39.996
Devonshire Building | 2017-07-17 03:30 | 50588.6441 | 20.016
Devonshire Building | 2017-07-17 03:45 | 50588.6541 | 39.996
Devonshire Building | 2017-07-17 04:00 | 50588.6641 | 39.996
Devonshire Building | 2017-07-17 04:15 | 50588.6691 | 20.016
Devonshire Building | 2017-07-17 04:30 | 50588.6791 | 39.996
Devonshire Building | 2017-07-17 04:45 | 50588.6891 | 39.996
Devonshire Building | 2017-07-17 05:00 | 50588.6991 | 39.996
Devonshire Building | 2017-07-17 05:15 | 50588.7041 | 20.016
Devonshire Building | 2017-07-17 05:30 | 50588.7141 | 39.996
Devonshire Building | 2017-07-17 05:45 | 50588.7191 | 20.016
Devonshire Building | 2017-07-17 06:00 | 50588.7341 | 60.012
Devonshire Building | 2017-07-17 06:15 | 50588.7441 | 39.996
Devonshire Building | 2017-07-17 06:30 | 50588.7641 | 79.992
Devonshire Building | 2017-07-17 06:45 | 50588.7741 | 39.996
Devonshire Building | 2017-07-17 07:00 | 50588.7841 | 39.996
Devonshire Building | 2017-07-17 07:15 | 50588.7941 | 39.996
Devonshire Building | 2017-07-17 07:30 | 50588.8041 | 39.996
Devonshire Building | 2017-07-17 07:45 | 50588.8191 | 60.012
Devonshire Building | 2017-07-17 08:00 | 50588.8491 | 119.988
Devonshire Building | 2017-07-17 08:15 | 50589.3991 | 2199.996
Devonshire Building | 2017-07-17 08:30 | 50589.4141 | 60.012
Devonshire Building | 2017-07-17 08:45 | 50589.4291 | 60.012
Devonshire Building | 2017-07-17 09:00 | 50589.4391 | 39.996
Devonshire Building | 2017-07-17 09:15 | 50589.4541 | 60.012
Devonshire Building | 2017-07-17 09:30 | 50589.8291 | 1500.012
Devonshire Building | 2017-07-17 09:45 | 50590.0691 | 960.012
Devonshire Building | 2017-07-17 10:00 | 50590.1441 | 299.988
Devonshire Building | 2017-07-17 10:15 | 50590.2191 | 299.988
Devonshire Building | 2017-07-17 10:30 | 50590.3341 | 460.008
Devonshire Building | 2017-07-17 10:45 | 50590.4491 | 460.008
Devonshire Building | 2017-07-17 11:00 | 50590.9591 | 2040.012
Devonshire Building | 2017-07-17 11:15 | 50591.1791 | 879.984
Devonshire Building | 2017-07-17 11:30 | 50591.2691 | 360
Devonshire Building | 2017-07-17 11:45 | 50591.3541 | 339.984
Devonshire Building | 2017-07-17 12:00 | 50591.4391 | 339.984
Devonshire Building | 2017-07-17 12:15 | 50591.5191 | 320.004
Devonshire Building | 2017-07-17 12:30 | 50592.1241 | 2419.992
Devonshire Building | 2017-07-17 12:45 | 50592.1991 | 299.988
Devonshire Building | 2017-07-17 13:00 | 50592.2791 | 320.004
Devonshire Building | 2017-07-17 13:15 | 50592.3541 | 299.988
Devonshire Building | 2017-07-17 13:30 | 50592.4141 | 240.012
Devonshire Building | 2017-07-17 13:45 | 50592.4791 | 259.992
Devonshire Building | 2017-07-17 14:00 | 50593.0941 | 2459.988
Devonshire Building | 2017-07-17 14:15 | 50593.1391 | 180
Devonshire Building | 2017-07-17 14:30 | 50593.1841 | 180
Devonshire Building | 2017-07-17 14:45 | 50593.2241 | 159.984
Devonshire Building | 2017-07-17 15:00 | 50593.2691 | 180
Devonshire Building | 2017-07-17 15:15 | 50593.3191 | 200.016
Devonshire Building | 2017-07-17 15:30 | 50593.3591 | 159.984
Devonshire Building | 2017-07-17 15:45 | 50593.9191 | 2239.992
Devonshire Building | 2017-07-17 16:00 | 50593.9591 | 159.984
Devonshire Building | 2017-07-17 16:15 | 50593.9991 | 159.984
Devonshire Building | 2017-07-17 16:30 | 50594.0391 | 159.984
Devonshire Building | 2017-07-17 16:45 | 50594.0741 | 140.004
Devonshire Building | 2017-07-17 17:00 | 50594.1091 | 140.004
Devonshire Building | 2017-07-17 17:15 | 50594.1441 | 140.004
Devonshire Building | 2017-07-17 17:30 | 50594.1741 | 119.988
Devonshire Building | 2017-07-17 17:45 | 50594.1991 | 100.008
Devonshire Building | 2017-07-17 18:00 | 50594.2291 | 119.988
Devonshire Building | 2017-07-17 18:15 | 50594.2491 | 79.992
Devonshire Building | 2017-07-17 18:30 | 50594.2691 | 79.992
Devonshire Building | 2017-07-17 18:45 | 50594.2891 | 79.992
Devonshire Building | 2017-07-17 19:00 | 50594.3091 | 79.992
Devonshire Building | 2017-07-17 19:15 | 50594.329 | 79.992
Devonshire Building | 2017-07-17 19:30 | 50594.3441 | 60.012
Devonshire Building | 2017-07-17 19:45 | 50594.3591 | 60.012
Devonshire Building | 2017-07-17 20:00 | 50594.3791 | 79.992
Devonshire Building | 2017-07-17 20:15 | 50594.3941 | 60.012
Devonshire Building | 2017-07-17 20:30 | 50594.4041 | 39.996
Devonshire Building | 2017-07-17 20:45 | 50594.9291 | 2099.988
Devonshire Building | 2017-07-17 21:00 | 50594.9341 | 20.016
Devonshire Building | 2017-07-17 21:15 | 50594.9391 | 20.016
Devonshire Building | 2017-07-17 21:30 | 50594.9441 | 20.016
Devonshire Building | 2017-07-17 21:45 | 50594.9541 | 39.996
Devonshire Building | 2017-07-17 22:00 | 50594.9591 | 20.016
Devonshire Building | 2017-07-17 22:15 | 50594.9641 | 20.016
Devonshire Building | 2017-07-17 22:30 | 50594.9691 | 20.016
Devonshire Building | 2017-07-17 22:45 | 50594.9791 | 39.996
Devonshire Building | 2017-07-17 23:00 | 50594.9841 | 20.016
Devonshire Building | 2017-07-17 23:15 | 50594.9891 | 20.016
Devonshire Building | 2017-07-17 23:30 | 50594.9941 | 20.016
Devonshire Building | 2017-07-17 23:45 | 50595.0041 | 39.996
Devonshire Building | 2017-07-18 | 50595.0078 | 20.016
Devonshire Building | 2017-07-18 00:15 | 50595.0178 | 39.996
Devonshire Building | 2017-07-18 00:30 | 50595.0228 | 20.016
Devonshire Building | 2017-07-18 00:45 | 50595.0278 | 20.016
Devonshire Building | 2017-07-18 01:00 | 50595.0378 | 39.996
Devonshire Building | 2017-07-18 01:15 | 50595.0428 | 20.016
Devonshire Building | 2017-07-18 01:30 | 50595.0528 | 39.996
Devonshire Building | 2017-07-18 01:45 | 50595.0578 | 20.016
Devonshire Building | 2017-07-18 02:00 | 50595.0678 | 39.996
Devonshire Building | 2017-07-18 02:15 | 50595.0728 | 20.016
Devonshire Building | 2017-07-18 02:30 | 50595.0778 | 20.016
Devonshire Building | 2017-07-18 02:45 | 50595.0878 | 39.996
Devonshire Building | 2017-07-18 03:00 | 50595.0928 | 20.016
Devonshire Building | 2017-07-18 03:15 | 50595.0978 | 20.016
Devonshire Building | 2017-07-18 03:30 | 50595.1028 | 20.016
Devonshire Building | 2017-07-18 03:45 | 50595.1128 | 39.996
Devonshire Building | 2017-07-18 04:00 | 50595.1178 | 20.016
Devonshire Building | 2017-07-18 04:15 | 50595.1228 | 20.016
Devonshire Building | 2017-07-18 04:30 | 50595.1279 | 20.016
Devonshire Building | 2017-07-18 04:45 | 50595.1329 | 20.016
Devonshire Building | 2017-07-18 05:00 | 50595.1379 | 20.016
Devonshire Building | 2017-07-18 05:15 | 50595.1479 | 39.996
Devonshire Building | 2017-07-18 05:30 | 50595.1529 | 20.016
Devonshire Building | 2017-07-18 05:45 | 50595.1579 | 20.016
Devonshire Building | 2017-07-18 06:00 | 50595.1629 | 20.016
Devonshire Building | 2017-07-18 06:15 | 50595.1679 | 20.016
Devonshire Building | 2017-07-18 06:30 | 50595.1779 | 39.996
Devonshire Building | 2017-07-18 06:45 | 50595.1879 | 39.996
Devonshire Building | 2017-07-18 07:00 | 50595.1929 | 20.016
Devonshire Building | 2017-07-18 07:15 | 50595.2029 | 39.996
Devonshire Building | 2017-07-18 07:30 | 50595.2279 | 100.008
Devonshire Building | 2017-07-18 07:45 | 50595.7579 | 2120.004
Devonshire Building | 2017-07-18 08:00 | 50595.8029 | 180
Devonshire Building | 2017-07-18 08:15 | 50595.8329 | 119.988
Devonshire Building | 2017-07-18 08:30 | 50595.8679 | 140.004
Devonshire Building | 2017-07-18 08:45 | 50595.9079 | 159.984
Devonshire Building | 2017-07-18 09:00 | 50595.9629 | 219.996
Devonshire Building | 2017-07-18 09:15 | 50596.2879 | 1299.996
Devonshire Building | 2017-07-18 09:30 | 50596.6279 | 1360.008
Devonshire Building | 2017-07-18 09:45 | 50596.7029 | 299.988
Devonshire Building | 2017-07-18 10:00 | 50596.7679 | 259.992
Devonshire Building | 2017-07-18 10:15 | 50596.8329 | 259.992
Devonshire Building | 2017-07-18 10:30 | 50596.8979 | 259.992
Devonshire Building | 2017-07-18 10:45 | 50596.9629 | 259.992
Devonshire Building | 2017-07-18 11:00 | 50597.5379 | 2300.004
Devonshire Building | 2017-07-18 11:15 | 50597.5779 | 159.984
Devonshire Building | 2017-07-18 11:30 | 50597.6229 | 180
Devonshire Building | 2017-07-18 11:45 | 50597.6679 | 180
Devonshire Building | 2017-07-18 12:00 | 50597.7129 | 180
Devonshire Building | 2017-07-18 12:15 | 50597.7579 | 180
Devonshire Building | 2017-07-18 12:30 | 50597.7979 | 159.984
Devonshire Building | 2017-07-18 12:45 | 50597.8329 | 140.004
Devonshire Building | 2017-07-18 13:00 | 50598.3979 | 2260.008
Devonshire Building | 2017-07-18 13:15 | 50598.4379 | 159.984
Devonshire Building | 2017-07-18 13:30 | 50598.4729 | 140.004
Devonshire Building | 2017-07-18 13:45 | 50598.5329 | 240.012
Devonshire Building | 2017-07-18 14:00 | 50598.5729 | 159.984
Devonshire Building | 2017-07-18 14:15 | 50598.6279 | 219.996
Devonshire Building | 2017-07-18 14:30 | 50598.6629 | 140.004
Devonshire Building | 2017-07-18 14:45 | 50598.7079 | 180
Devonshire Building | 2017-07-18 15:00 | 50599.0529 | 1379.988
Devonshire Building | 2017-07-18 15:15 | 50599.3279 | 1100.016
Devonshire Building | 2017-07-18 15:30 | 50599.4329 | 420.012
Devonshire Building | 2017-07-18 15:45 | 50599.5779 | 579.996
Devonshire Building | 2017-07-18 16:00 | 50599.6879 | 439.992
Devonshire Building | 2017-07-18 16:15 | 50599.7829 | 380.016
Devonshire Building | 2017-07-18 16:30 | 50600.3379 | 2220.012
Devonshire Building | 2017-07-18 16:45 | 50600.4379 | 399.996
Devonshire Building | 2017-07-18 17:00 | 50600.4929 | 219.996
Devonshire Building | 2017-07-18 17:15 | 50600.5579 | 259.992
Devonshire Building | 2017-07-18 17:30 | 50600.6179 | 240.012
Devonshire Building | 2017-07-18 17:45 | 50600.6729 | 219.996
Devonshire Building | 2017-07-18 18:00 | 50600.7279 | 219.996
Devonshire Building | 2017-07-18 18:15 | 50600.7729 | 180
Devonshire Building | 2017-07-18 18:30 | 50600.8229 | 200.016
Devonshire Building | 2017-07-18 18:45 | 50600.8579 | 140.004
Devonshire Building | 2017-07-18 19:00 | 50600.8929 | 140.004
Devonshire Building | 2017-07-18 19:15 | 50600.9179 | 100.008
Devonshire Building | 2017-07-18 19:30 | 50600.9429 | 100.008
Devonshire Building | 2017-07-18 19:45 | 50600.9679 | 100.008
Devonshire Building | 2017-07-18 20:00 | 50600.9879 | 79.992
Devonshire Building | 2017-07-18 20:15 | 50601.0079 | 79.992
Devonshire Building | 2017-07-18 20:30 | 50601.0279 | 79.992
Devonshire Building | 2017-07-18 20:45 | 50601.0679 | 159.984
Devonshire Building | 2017-07-18 21:00 | 50601.0729 | 20.016
Devonshire Building | 2017-07-18 21:15 | 50601.0829 | 39.996
Devonshire Building | 2017-07-18 21:30 | 50601.0879 | 20.016
Devonshire Building | 2017-07-18 21:45 | 50601.0979 | 39.996
Devonshire Building | 2017-07-18 22:00 | 50601.1029 | 20.016
Devonshire Building | 2017-07-18 22:15 | 50601.1129 | 39.996
Devonshire Building | 2017-07-18 22:30 | 50601.1179 | 20.016
Devonshire Building | 2017-07-18 22:45 | 50601.1229 | 20.016
Devonshire Building | 2017-07-18 23:00 | 50601.1329 | 39.996
Devonshire Building | 2017-07-18 23:15 | 50601.1379 | 20.016
Devonshire Building | 2017-07-18 23:30 | 50601.1479 | 39.996
Devonshire Building | 2017-07-18 23:45 | 50601.1529 | 20.016
Devonshire Building | 2017-07-19 | 50601.1602 | 20.016
Devonshire Building | 2017-07-19 00:15 | 50601.1702 | 39.996
Devonshire Building | 2017-07-19 00:30 | 50601.1752 | 20.016
Devonshire Building | 2017-07-19 00:45 | 50601.1802 | 20.016
Devonshire Building | 2017-07-19 01:00 | 50601.1902 | 39.996
Devonshire Building | 2017-07-19 01:15 | 50601.1952 | 20.016
Devonshire Building | 2017-07-19 01:30 | 50601.2002 | 20.016
Devonshire Building | 2017-07-19 01:45 | 50601.2102 | 39.996
Devonshire Building | 2017-07-19 02:00 | 50601.2152 | 20.016
Devonshire Building | 2017-07-19 02:15 | 50601.2202 | 20.016
Devonshire Building | 2017-07-19 02:30 | 50601.2252 | 20.016
Devonshire Building | 2017-07-19 02:45 | 50601.2352 | 39.996
Devonshire Building | 2017-07-19 03:00 | 50601.2402 | 20.016
Devonshire Building | 2017-07-19 03:15 | 50601.2452 | 20.016
Devonshire Building | 2017-07-19 03:30 | 50601.2502 | 20.016
Devonshire Building | 2017-07-19 03:45 | 50601.2552 | 20.016
Devonshire Building | 2017-07-19 04:00 | 50601.2652 | 39.996
Devonshire Building | 2017-07-19 04:15 | 50601.2702 | 20.016
Devonshire Building | 2017-07-19 04:30 | 50601.2752 | 20.016
Devonshire Building | 2017-07-19 04:45 | 50601.3352 | 240.012
Devonshire Building | 2017-07-19 05:00 | 50601.7902 | 1820.016
Devonshire Building | 2017-07-19 05:15 | 50601.7952 | 20.016
Devonshire Building | 2017-07-19 05:30 | 50601.8002 | 20.016
Devonshire Building | 2017-07-19 05:45 | 50601.8102 | 39.996
Devonshire Building | 2017-07-19 06:00 | 50601.8152 | 20.016
Devonshire Building | 2017-07-19 06:15 | 50601.8202 | 20.016
Devonshire Building | 2017-07-19 06:30 | 50601.8302 | 39.996
Devonshire Building | 2017-07-19 06:45 | 50601.8402 | 39.996
Devonshire Building | 2017-07-19 07:00 | 50601.8552 | 60.012
Devonshire Building | 2017-07-19 07:15 | 50601.8602 | 20.016
Devonshire Building | 2017-07-19 07:30 | 50601.8752 | 60.012
Devonshire Building | 2017-07-19 07:45 | 50601.9102 | 140.004
Devonshire Building | 2017-07-19 08:00 | 50601.9402 | 119.988
Devonshire Building | 2017-07-19 08:15 | 50602.4702 | 2120.004
Devonshire Building | 2017-07-19 08:30 | 50602.5052 | 140.004
Devonshire Building | 2017-07-19 08:45 | 50602.5452 | 159.984
Devonshire Building | 2017-07-19 09:00 | 50602.5952 | 200.016
Devonshire Building | 2017-07-19 09:15 | 50602.6802 | 339.984
Devonshire Building | 2017-07-19 09:30 | 50603.1202 | 1760.004
Devonshire Building | 2017-07-19 09:45 | 50603.3902 | 1080
Devonshire Building | 2017-07-19 10:00 | 50603.4952 | 420.012
Devonshire Building | 2017-07-19 10:15 | 50603.5852 | 360
Devonshire Building | 2017-07-19 10:30 | 50603.6702 | 339.984
Devonshire Building | 2017-07-19 10:45 | 50603.7552 | 339.984
Devonshire Building | 2017-07-19 11:00 | 50603.8302 | 299.988
Devonshire Building | 2017-07-19 11:15 | 50604.4102 | 2319.984
Devonshire Building | 2017-07-19 11:30 | 50604.4702 | 240.012
Devonshire Building | 2017-07-19 11:45 | 50604.5252 | 219.996
Devonshire Building | 2017-07-19 12:00 | 50604.5752 | 200.016
Devonshire Building | 2017-07-19 12:15 | 50604.6252 | 200.016
Devonshire Building | 2017-07-19 12:30 | 50604.6752 | 200.016
Devonshire Building | 2017-07-19 12:45 | 50605.2102 | 2139.984
Devonshire Building | 2017-07-19 13:00 | 50605.2952 | 339.984
Devonshire Building | 2017-07-19 13:15 | 50605.3252 | 119.988
Devonshire Building | 2017-07-19 13:30 | 50605.3752 | 200.016
Devonshire Building | 2017-07-19 13:45 | 50605.4152 | 159.984
Devonshire Building | 2017-07-19 14:00 | 50605.4452 | 119.988
Devonshire Building | 2017-07-19 14:15 | 50605.8052 | 1440
Devonshire Building | 2017-07-19 14:30 | 50606.0552 | 1000.008
Devonshire Building | 2017-07-19 14:45 | 50606.0952 | 159.984
Devonshire Building | 2017-07-19 15:00 | 50606.1402 | 180
Devonshire Building | 2017-07-19 15:15 | 50606.1802 | 159.984
Devonshire Building | 2017-07-19 15:30 | 50606.2202 | 159.984
Devonshire Building | 2017-07-19 15:45 | 50606.2802 | 240.012
Devonshire Building | 2017-07-19 16:00 | 50606.8902 | 2440.008
Devonshire Building | 2017-07-19 16:15 | 50606.9902 | 399.996
Devonshire Building | 2017-07-19 16:30 | 50607.0852 | 380.016
Devonshire Building | 2017-07-19 16:45 | 50607.1652 | 320.004
Devonshire Building | 2017-07-19 17:00 | 50607.2352 | 280.008
Devonshire Building | 2017-07-19 17:15 | 50607.3002 | 259.992
Devonshire Building | 2017-07-19 17:30 | 50607.3702 | 280.008
Devonshire Building | 2017-07-19 17:45 | 50607.4302 | 240.012
Devonshire Building | 2017-07-19 18:00 | 50607.4952 | 259.992
Devonshire Building | 2017-07-19 18:15 | 50607.5502 | 219.996
Devonshire Building | 2017-07-19 18:30 | 50607.5952 | 180
Devonshire Building | 2017-07-19 18:45 | 50607.6302 | 140.004
Devonshire Building | 2017-07-19 19:00 | 50607.6652 | 140.004
Devonshire Building | 2017-07-19 19:15 | 50607.6952 | 119.988
Devonshire Building | 2017-07-19 19:30 | 50607.7202 | 100.008
Devonshire Building | 2017-07-19 19:45 | 50607.7402 | 79.992
Devonshire Building | 2017-07-19 20:00 | 50607.7602 | 79.992
Devonshire Building | 2017-07-19 20:15 | 50607.7802 | 79.992
Devonshire Building | 2017-07-19 20:30 | 50607.8002 | 79.992
Devonshire Building | 2017-07-19 20:45 | 50607.8402 | 159.984
Devonshire Building | 2017-07-19 21:00 | 50607.8452 | 20.016
Devonshire Building | 2017-07-19 21:15 | 50607.8552 | 39.996
Devonshire Building | 2017-07-19 21:30 | 50607.8602 | 20.016
Devonshire Building | 2017-07-19 21:45 | 50607.8702 | 39.996
Devonshire Building | 2017-07-19 22:00 | 50607.8752 | 20.016
Devonshire Building | 2017-07-19 22:15 | 50607.8852 | 39.996
Devonshire Building | 2017-07-19 22:30 | 50608.3902 | 2019.996
Devonshire Building | 2017-07-19 22:45 | 50608.4002 | 39.996
Devonshire Building | 2017-07-19 23:00 | 50608.4052 | 20.016
Devonshire Building | 2017-07-19 23:15 | 50608.4102 | 20.016
Devonshire Building | 2017-07-19 23:30 | 50608.4152 | 20.016
Devonshire Building | 2017-07-19 23:45 | 50608.4202 | 20.016
Devonshire Building | 2017-07-20 | 50608.4297 | 39.996
Devonshire Building | 2017-07-20 00:15 | 50608.4347 | 20.016
Devonshire Building | 2017-07-20 00:30 | 50608.4397 | 20.016
Devonshire Building | 2017-07-20 00:45 | 50608.4447 | 20.016
Devonshire Building | 2017-07-20 01:00 | 50608.4547 | 39.996
Devonshire Building | 2017-07-20 01:15 | 50608.4647 | 39.996
Devonshire Building | 2017-07-20 01:30 | 50608.4697 | 20.016
Devonshire Building | 2017-07-20 01:45 | 50608.4747 | 20.016
Devonshire Building | 2017-07-20 02:00 | 50608.4847 | 39.996
Devonshire Building | 2017-07-20 02:15 | 50608.4897 | 20.016
Devonshire Building | 2017-07-20 02:30 | 50608.4947 | 20.016
Devonshire Building | 2017-07-20 02:45 | 50608.4997 | 20.016
Devonshire Building | 2017-07-20 03:00 | 50608.5097 | 39.996
Devonshire Building | 2017-07-20 03:15 | 50608.5147 | 20.016
Devonshire Building | 2017-07-20 03:30 | 50608.5197 | 20.016
Devonshire Building | 2017-07-20 03:45 | 50608.5247 | 20.016
Devonshire Building | 2017-07-20 04:00 | 50608.5347 | 39.996
Devonshire Building | 2017-07-20 04:15 | 50608.5397 | 20.016
Devonshire Building | 2017-07-20 04:30 | 50608.5447 | 20.016
Devonshire Building | 2017-07-20 04:45 | 50608.5497 | 20.016
Devonshire Building | 2017-07-20 05:00 | 50608.5547 | 20.016
Devonshire Building | 2017-07-20 05:15 | 50608.5647 | 39.996
Devonshire Building | 2017-07-20 05:30 | 50608.5697 | 20.016
Devonshire Building | 2017-07-20 05:45 | 50608.5748 | 20.016
Devonshire Building | 2017-07-20 06:00 | 50608.5798 | 20.016
Devonshire Building | 2017-07-20 06:15 | 50608.5848 | 20.016
Devonshire Building | 2017-07-20 06:30 | 50608.5948 | 39.996
Devonshire Building | 2017-07-20 06:45 | 50608.6048 | 39.996
Devonshire Building | 2017-07-20 07:00 | 50608.6198 | 60.012
Devonshire Building | 2017-07-20 07:15 | 50608.6348 | 60.012
Devonshire Building | 2017-07-20 07:30 | 50608.6398 | 20.016
Devonshire Building | 2017-07-20 07:45 | 50608.6598 | 79.992
Devonshire Building | 2017-07-20 08:00 | 50608.6998 | 159.984
Devonshire Building | 2017-07-20 08:15 | 50609.2298 | 2120.004
Devonshire Building | 2017-07-20 08:30 | 50609.2598 | 119.988
Devonshire Building | 2017-07-20 08:45 | 50609.2898 | 119.988
Devonshire Building | 2017-07-20 09:00 | 50609.3248 | 140.004
Devonshire Building | 2017-07-20 09:15 | 50609.3748 | 200.016
Devonshire Building | 2017-07-20 09:30 | 50609.4448 | 280.008
Devonshire Building | 2017-07-20 09:45 | 50610.0748 | 2520
Devonshire Building | 2017-07-20 10:00 | 50610.1798 | 420.012
Devonshire Building | 2017-07-20 10:15 | 50610.2798 | 399.996
Devonshire Building | 2017-07-20 10:30 | 50610.3598 | 320.004
Devonshire Building | 2017-07-20 10:45 | 50610.4398 | 320.004
Devonshire Building | 2017-07-20 11:00 | 50610.5148 | 299.988
Devonshire Building | 2017-07-20 11:15 | 50610.5948 | 320.004
Devonshire Building | 2017-07-20 11:30 | 50611.1048 | 2040.012
Devonshire Building | 2017-07-20 11:45 | 50611.2498 | 579.996
Devonshire Building | 2017-07-20 12:00 | 50611.3248 | 299.988
Devonshire Building | 2017-07-20 12:15 | 50611.3948 | 280.008
Devonshire Building | 2017-07-20 12:30 | 50611.4598 | 259.992
Devonshire Building | 2017-07-20 12:45 | 50611.5248 | 259.992
Devonshire Building | 2017-07-20 13:00 | 50611.8248 | 1199.988
Devonshire Building | 2017-07-20 13:15 | 50612.1698 | 1379.988
Devonshire Building | 2017-07-20 13:30 | 50612.2198 | 200.016
Devonshire Building | 2017-07-20 13:45 | 50612.2748 | 219.996
Devonshire Building | 2017-07-20 14:00 | 50612.3248 | 200.016
Devonshire Building | 2017-07-20 14:15 | 50612.3798 | 219.996
Devonshire Building | 2017-07-20 14:30 | 50612.4298 | 200.016
Devonshire Building | 2017-07-20 14:45 | 50612.4748 | 180
Devonshire Building | 2017-07-20 15:00 | 50613.0398 | 2260.008
Devonshire Building | 2017-07-20 15:15 | 50613.1298 | 360
Devonshire Building | 2017-07-20 15:30 | 50613.2548 | 500.004
Devonshire Building | 2017-07-20 15:45 | 50613.3698 | 460.008
Devonshire Building | 2017-07-20 16:00 | 50613.4848 | 460.008
Devonshire Building | 2017-07-20 16:15 | 50613.5998 | 460.008
Devonshire Building | 2017-07-20 16:30 | 50613.6948 | 380.016
Devonshire Building | 2017-07-20 16:45 | 50613.7848 | 360
Devonshire Building | 2017-07-20 17:00 | 50613.8698 | 339.984
Devonshire Building | 2017-07-20 17:15 | 50614.4348 | 2260.008
Devonshire Building | 2017-07-20 17:30 | 50614.4848 | 200.016
Devonshire Building | 2017-07-20 17:45 | 50614.5398 | 219.996
Devonshire Building | 2017-07-20 18:00 | 50614.5898 | 200.016
Devonshire Building | 2017-07-20 18:15 | 50614.6298 | 159.984
Devonshire Building | 2017-07-20 18:30 | 50614.6648 | 140.004
Devonshire Building | 2017-07-20 18:45 | 50614.6898 | 100.008
Devonshire Building | 2017-07-20 19:00 | 50614.7198 | 119.988
Devonshire Building | 2017-07-20 19:15 | 50614.7448 | 100.008
Devonshire Building | 2017-07-20 19:30 | 50614.7648 | 79.992
Devonshire Building | 2017-07-20 19:45 | 50614.7848 | 79.992
Devonshire Building | 2017-07-20 20:00 | 50614.8048 | 79.992
Devonshire Building | 2017-07-20 20:15 | 50614.8198 | 60.012
Devonshire Building | 2017-07-20 20:30 | 50614.8398 | 79.992
Devonshire Building | 2017-07-20 20:45 | 50614.8648 | 100.008
Devonshire Building | 2017-07-20 21:00 | 50614.8748 | 39.996
Devonshire Building | 2017-07-20 21:15 | 50614.8848 | 39.996
Devonshire Building | 2017-07-20 21:30 | 50614.8948 | 39.996
Devonshire Building | 2017-07-20 21:45 | 50614.8998 | 20.016
Devonshire Building | 2017-07-20 22:00 | 50614.9098 | 39.996
Devonshire Building | 2017-07-20 22:15 | 50614.9198 | 39.996
Devonshire Building | 2017-07-20 22:30 | 50614.9298 | 39.996
Devonshire Building | 2017-07-20 22:45 | 50614.9348 | 20.016
Devonshire Building | 2017-07-20 23:00 | 50614.9448 | 39.996
Devonshire Building | 2017-07-20 23:15 | 50614.9548 | 39.996
Devonshire Building | 2017-07-20 23:30 | 50614.9598 | 20.016
Devonshire Building | 2017-07-20 23:45 | 50614.9698 | 39.996
Devonshire Building | 2017-07-21 | 50614.9805 | 39.996
Devonshire Building | 2017-07-21 00:15 | 50614.9855 | 20.016
Devonshire Building | 2017-07-21 00:30 | 50614.9955 | 39.996
Devonshire Building | 2017-07-21 00:45 | 50615.0055 | 39.996
Devonshire Building | 2017-07-21 01:00 | 50615.0105 | 20.016
Devonshire Building | 2017-07-21 01:15 | 50615.0205 | 39.996
Devonshire Building | 2017-07-21 01:30 | 50615.0305 | 39.996
Devonshire Building | 2017-07-21 01:45 | 50615.0555 | 100.008
Devonshire Building | 2017-07-21 02:00 | 50615.0805 | 100.008
Devonshire Building | 2017-07-21 02:15 | 50615.1055 | 100.008
Devonshire Building | 2017-07-21 02:30 | 50615.1305 | 100.008
Devonshire Building | 2017-07-21 02:45 | 50615.1505 | 79.992
Devonshire Building | 2017-07-21 03:00 | 50615.1755 | 100.008
Devonshire Building | 2017-07-21 03:15 | 50615.2005 | 100.008
Devonshire Building | 2017-07-21 03:30 | 50615.2255 | 100.008
Devonshire Building | 2017-07-21 03:45 | 50615.2405 | 60.012
Devonshire Building | 2017-07-21 04:00 | 50615.2505 | 39.996
Devonshire Building | 2017-07-21 04:15 | 50615.2555 | 20.016
Devonshire Building | 2017-07-21 04:30 | 50615.2655 | 39.996
Devonshire Building | 2017-07-21 04:45 | 50615.2705 | 20.016
Devonshire Building | 2017-07-21 05:00 | 50615.2755 | 20.016
Devonshire Building | 2017-07-21 05:15 | 50615.2855 | 39.996
Devonshire Building | 2017-07-21 05:30 | 50615.2905 | 20.016
Devonshire Building | 2017-07-21 05:45 | 50615.3005 | 39.996
Devonshire Building | 2017-07-21 06:00 | 50615.3055 | 20.016
Devonshire Building | 2017-07-21 06:15 | 50615.3155 | 39.996
Devonshire Building | 2017-07-21 06:30 | 50615.3205 | 20.016
Devonshire Building | 2017-07-21 06:45 | 50615.3305 | 39.996
Devonshire Building | 2017-07-21 07:00 | 50615.3405 | 39.996
Devonshire Building | 2017-07-21 07:15 | 50615.3455 | 20.016
Devonshire Building | 2017-07-21 07:30 | 50615.8605 | 2059.992
Devonshire Building | 2017-07-21 07:45 | 50615.8755 | 60.012
Devonshire Building | 2017-07-21 08:00 | 50615.8905 | 60.012
Devonshire Building | 2017-07-21 08:15 | 50615.9055 | 60.012
Devonshire Building | 2017-07-21 08:30 | 50615.9155 | 39.996
Devonshire Building | 2017-07-21 08:45 | 50615.9255 | 39.996
Devonshire Building | 2017-07-21 09:00 | 50615.9355 | 39.996
Devonshire Building | 2017-07-21 09:15 | 50615.9455 | 39.996
Devonshire Building | 2017-07-21 09:30 | 50615.9755 | 119.988
Devonshire Building | 2017-07-21 09:45 | 50616.5205 | 2180.016
Devonshire Building | 2017-07-21 10:00 | 50616.5655 | 180
Devonshire Building | 2017-07-21 10:15 | 50616.6355 | 280.008
Devonshire Building | 2017-07-21 10:30 | 50616.7055 | 280.008
Devonshire Building | 2017-07-21 10:45 | 50616.7705 | 259.992
Devonshire Building | 2017-07-21 11:00 | 50616.8305 | 240.012
Devonshire Building | 2017-07-21 11:15 | 50617.4005 | 2279.988
Devonshire Building | 2017-07-21 11:30 | 50617.4405 | 159.984
Devonshire Building | 2017-07-21 11:45 | 50617.4905 | 200.016
Devonshire Building | 2017-07-21 12:00 | 50617.5405 | 200.016
Devonshire Building | 2017-07-21 12:15 | 50617.5805 | 159.984
Devonshire Building | 2017-07-21 12:30 | 50617.6305 | 200.016
Devonshire Building | 2017-07-21 12:45 | 50617.9305 | 1199.988
Devonshire Building | 2017-07-21 13:00 | 50618.2455 | 1260
Devonshire Building | 2017-07-21 13:15 | 50618.2855 | 159.984
Devonshire Building | 2017-07-21 13:30 | 50618.3205 | 140.004
Devonshire Building | 2017-07-21 13:45 | 50618.3655 | 180
Devonshire Building | 2017-07-21 14:00 | 50618.4205 | 219.996
Devonshire Building | 2017-07-21 14:15 | 50618.4755 | 219.996
Devonshire Building | 2017-07-21 14:30 | 50618.5355 | 240.012
Devonshire Building | 2017-07-21 14:45 | 50618.5955 | 240.012
Devonshire Building | 2017-07-21 15:00 | 50619.1555 | 2239.992
Devonshire Building | 2017-07-21 15:15 | 50619.2455 | 360
Devonshire Building | 2017-07-21 15:30 | 50619.3355 | 360
Devonshire Building | 2017-07-21 15:45 | 50619.4305 | 380.016
Devonshire Building | 2017-07-21 16:00 | 50619.5055 | 299.988
Devonshire Building | 2017-07-21 16:15 | 50619.5805 | 299.988
Devonshire Building | 2017-07-21 16:30 | 50619.6505 | 280.008
Devonshire Building | 2017-07-21 16:45 | 50619.7105 | 240.012
Devonshire Building | 2017-07-21 17:00 | 50619.7655 | 219.996
Devonshire Building | 2017-07-21 17:15 | 50620.1555 | 1559.988
Devonshire Building | 2017-07-21 17:30 | 50620.3405 | 740.016
Devonshire Building | 2017-07-21 17:45 | 50620.3755 | 140.004
Devonshire Building | 2017-07-21 18:00 | 50620.4055 | 119.988
Devonshire Building | 2017-07-21 18:15 | 50620.4405 | 140.004
Devonshire Building | 2017-07-21 18:30 | 50620.4705 | 119.988
Devonshire Building | 2017-07-21 18:45 | 50620.4955 | 100.008
Devonshire Building | 2017-07-21 19:00 | 50620.5155 | 79.992
Devonshire Building | 2017-07-21 19:15 | 50620.5355 | 79.992
Devonshire Building | 2017-07-21 19:30 | 50620.5555 | 79.992
Devonshire Building | 2017-07-21 19:45 | 50620.5705 | 60.012
Devonshire Building | 2017-07-21 20:00 | 50620.5855 | 60.012
Devonshire Building | 2017-07-21 20:15 | 50620.6105 | 100.008
Devonshire Building | 2017-07-21 20:30 | 50620.6255 | 60.012
Devonshire Building | 2017-07-21 20:45 | 50620.6505 | 100.008
Devonshire Building | 2017-07-21 21:00 | 50620.6555 | 20.016
Devonshire Building | 2017-07-21 21:15 | 50620.6655 | 39.996
Devonshire Building | 2017-07-21 21:30 | 50620.6705 | 20.016
Devonshire Building | 2017-07-21 21:45 | 50620.6755 | 20.016
Devonshire Building | 2017-07-21 22:00 | 50620.6855 | 39.996
Devonshire Building | 2017-07-21 22:15 | 50620.6905 | 20.016
Devonshire Building | 2017-07-21 22:30 | 50620.6955 | 20.016
Devonshire Building | 2017-07-21 22:45 | 50620.7055 | 39.996
Devonshire Building | 2017-07-21 23:00 | 50620.7105 | 20.016
Devonshire Building | 2017-07-21 23:15 | 50620.7155 | 20.016
Devonshire Building | 2017-07-21 23:30 | 50620.7255 | 39.996
Devonshire Building | 2017-07-21 23:45 | 50620.7306 | 20.016
Devonshire Building | 2017-07-22 | 50620.7344 | 20.016
Devonshire Building | 2017-07-22 00:15 | 50620.7444 | 39.996
Devonshire Building | 2017-07-22 00:30 | 50620.7494 | 20.016
Devonshire Building | 2017-07-22 00:45 | 50620.7544 | 20.016
Devonshire Building | 2017-07-22 01:00 | 50620.7644 | 39.996
Devonshire Building | 2017-07-22 01:15 | 50620.7694 | 20.016
Devonshire Building | 2017-07-22 01:30 | 50620.7744 | 20.016
Devonshire Building | 2017-07-22 01:45 | 50620.7794 | 20.016
Devonshire Building | 2017-07-22 02:00 | 50620.7844 | 20.016
Devonshire Building | 2017-07-22 02:15 | 50620.7944 | 39.996
Devonshire Building | 2017-07-22 02:30 | 50620.7994 | 20.016
Devonshire Building | 2017-07-22 02:45 | 50620.8044 | 20.016
Devonshire Building | 2017-07-22 03:00 | 50620.8094 | 20.016
Devonshire Building | 2017-07-22 03:15 | 50620.8144 | 20.016
Devonshire Building | 2017-07-22 03:30 | 50620.8244 | 39.996
Devonshire Building | 2017-07-22 03:45 | 50620.8294 | 20.016
Devonshire Building | 2017-07-22 04:00 | 50620.8344 | 20.016
Devonshire Building | 2017-07-22 04:15 | 50620.8394 | 20.016
Devonshire Building | 2017-07-22 04:30 | 50620.8444 | 20.016
Devonshire Building | 2017-07-22 04:45 | 50620.8494 | 20.016
Devonshire Building | 2017-07-22 05:00 | 50620.8594 | 39.996
Devonshire Building | 2017-07-22 05:15 | 50620.8644 | 20.016
Devonshire Building | 2017-07-22 05:30 | 50620.8694 | 20.016
Devonshire Building | 2017-07-22 05:45 | 50620.8744 | 20.016
Devonshire Building | 2017-07-22 06:00 | 50620.8795 | 20.016
Devonshire Building | 2017-07-22 06:15 | 50620.8845 | 20.016
Devonshire Building | 2017-07-22 06:30 | 50620.8945 | 39.996
Devonshire Building | 2017-07-22 06:45 | 50620.8995 | 20.016
Devonshire Building | 2017-07-22 07:00 | 50620.9045 | 20.016
Devonshire Building | 2017-07-22 07:15 | 50620.9095 | 20.016
Devonshire Building | 2017-07-22 07:30 | 50620.9145 | 20.016
Devonshire Building | 2017-07-22 07:45 | 50620.9195 | 20.016
Devonshire Building | 2017-07-22 08:00 | 50620.9295 | 39.996
Devonshire Building | 2017-07-22 08:15 | 50620.9345 | 20.016
Devonshire Building | 2017-07-22 08:30 | 50620.9395 | 20.016
Devonshire Building | 2017-07-22 08:45 | 50620.9445 | 20.016
Devonshire Building | 2017-07-22 09:00 | 50620.9495 | 20.016
Devonshire Building | 2017-07-22 09:15 | 50620.9595 | 39.996
Devonshire Building | 2017-07-22 09:30 | 50620.9645 | 20.016
Devonshire Building | 2017-07-22 09:45 | 50620.9695 | 20.016
Devonshire Building | 2017-07-22 10:00 | 50620.9745 | 20.016
Devonshire Building | 2017-07-22 10:15 | 50620.9845 | 39.996
Devonshire Building | 2017-07-22 10:30 | 50620.9895 | 20.016
Devonshire Building | 2017-07-22 10:45 | 50621.4945 | 2019.996
Devonshire Building | 2017-07-22 11:00 | 50621.5045 | 39.996
Devonshire Building | 2017-07-22 11:15 | 50621.5095 | 20.016
Devonshire Building | 2017-07-22 11:30 | 50621.5195 | 39.996
Devonshire Building | 2017-07-22 11:45 | 50621.5295 | 39.996
Devonshire Building | 2017-07-22 12:00 | 50621.5395 | 39.996
Devonshire Building | 2017-07-22 12:15 | 50621.5495 | 39.996
Devonshire Building | 2017-07-22 12:30 | 50621.5595 | 39.996
Devonshire Building | 2017-07-22 12:45 | 50621.5695 | 39.996
Devonshire Building | 2017-07-22 13:00 | 50621.5795 | 39.996
Devonshire Building | 2017-07-22 13:15 | 50621.5945 | 60.012
Devonshire Building | 2017-07-22 13:30 | 50621.6095 | 60.012
Devonshire Building | 2017-07-22 13:45 | 50621.6395 | 119.988
Devonshire Building | 2017-07-22 14:00 | 50621.6695 | 119.988
Devonshire Building | 2017-07-22 14:15 | 50621.6995 | 119.988
Devonshire Building | 2017-07-22 14:30 | 50621.7295 | 119.988
Devonshire Building | 2017-07-22 14:45 | 50621.7545 | 100.008
Devonshire Building | 2017-07-22 15:00 | 50621.7845 | 119.988
Devonshire Building | 2017-07-22 15:15 | 50621.8145 | 119.988
Devonshire Building | 2017-07-22 15:30 | 50621.8395 | 100.008
Devonshire Building | 2017-07-22 15:45 | 50621.8695 | 119.988
Devonshire Building | 2017-07-22 16:00 | 50621.8795 | 39.996
Devonshire Building | 2017-07-22 16:15 | 50621.8895 | 39.996
Devonshire Building | 2017-07-22 16:30 | 50621.9045 | 60.012
Devonshire Building | 2017-07-22 16:45 | 50621.9145 | 39.996
Devonshire Building | 2017-07-22 17:00 | 50621.9245 | 39.996
Devonshire Building | 2017-07-22 17:15 | 50621.9345 | 39.996
Devonshire Building | 2017-07-22 17:30 | 50621.9445 | 39.996
Devonshire Building | 2017-07-22 17:45 | 50621.9545 | 39.996
Devonshire Building | 2017-07-22 18:00 | 50621.9645 | 39.996
Devonshire Building | 2017-07-22 18:15 | 50621.9745 | 39.996
Devonshire Building | 2017-07-22 18:30 | 50621.9845 | 39.996
Devonshire Building | 2017-07-22 18:45 | 50621.9945 | 39.996
Devonshire Building | 2017-07-22 19:00 | 50622.0095 | 60.012
Devonshire Building | 2017-07-22 19:15 | 50622.0195 | 39.996
Devonshire Building | 2017-07-22 19:30 | 50622.0295 | 39.996
Devonshire Building | 2017-07-22 19:45 | 50622.0395 | 39.996
Devonshire Building | 2017-07-22 20:00 | 50622.0545 | 60.012
Devonshire Building | 2017-07-22 20:15 | 50622.0645 | 39.996
Devonshire Building | 2017-07-22 20:30 | 50622.0745 | 39.996
Devonshire Building | 2017-07-22 20:45 | 50622.1045 | 119.988
Devonshire Building | 2017-07-22 21:00 | 50622.1145 | 39.996
Devonshire Building | 2017-07-22 21:15 | 50622.1245 | 39.996
Devonshire Building | 2017-07-22 21:30 | 50622.1295 | 20.016
Devonshire Building | 2017-07-22 21:45 | 50622.1395 | 39.996
Devonshire Building | 2017-07-22 22:00 | 50622.1495 | 39.996
Devonshire Building | 2017-07-22 22:15 | 50622.1595 | 39.996
Devonshire Building | 2017-07-22 22:30 | 50622.1695 | 39.996
Devonshire Building | 2017-07-22 22:45 | 50622.1795 | 39.996
Devonshire Building | 2017-07-22 23:00 | 50622.1895 | 39.996
Devonshire Building | 2017-07-22 23:15 | 50622.1995 | 39.996
Devonshire Building | 2017-07-22 23:30 | 50622.2045 | 20.016
Devonshire Building | 2017-07-22 23:45 | 50622.2145 | 39.996
Devonshire Building | 2017-07-23 | 50622.2266 | 39.996
Devonshire Building | 2017-07-23 00:15 | 50622.2366 | 39.996
Devonshire Building | 2017-07-23 00:30 | 50622.2466 | 39.996
Devonshire Building | 2017-07-23 00:45 | 50622.2566 | 39.996
Devonshire Building | 2017-07-23 01:00 | 50622.2616 | 20.016
Devonshire Building | 2017-07-23 01:15 | 50622.2716 | 39.996
Devonshire Building | 2017-07-23 01:30 | 50622.2816 | 39.996
Devonshire Building | 2017-07-23 01:45 | 50622.2916 | 39.996
Devonshire Building | 2017-07-23 02:00 | 50622.2966 | 20.016
Devonshire Building | 2017-07-23 02:15 | 50622.3066 | 39.996
Devonshire Building | 2017-07-23 02:30 | 50622.3166 | 39.996
Devonshire Building | 2017-07-23 02:45 | 50622.3266 | 39.996
Devonshire Building | 2017-07-23 03:00 | 50622.3366 | 39.996
Devonshire Building | 2017-07-23 03:15 | 50622.3416 | 20.016
Devonshire Building | 2017-07-23 03:30 | 50622.3516 | 39.996
Devonshire Building | 2017-07-23 03:45 | 50622.3616 | 39.996
Devonshire Building | 2017-07-23 04:00 | 50622.8166 | 1820.016
Devonshire Building | 2017-07-23 04:15 | 50622.8716 | 219.996
Devonshire Building | 2017-07-23 04:30 | 50622.8816 | 39.996
Devonshire Building | 2017-07-23 04:45 | 50622.8866 | 20.016
Devonshire Building | 2017-07-23 05:00 | 50622.8966 | 39.996
Devonshire Building | 2017-07-23 05:15 | 50622.9066 | 39.996
Devonshire Building | 2017-07-23 05:30 | 50622.9116 | 20.016
Devonshire Building | 2017-07-23 05:45 | 50622.9216 | 39.996
Devonshire Building | 2017-07-23 06:00 | 50622.9316 | 39.996
Devonshire Building | 2017-07-23 06:15 | 50622.9416 | 39.996
Devonshire Building | 2017-07-23 06:30 | 50622.9516 | 39.996
Devonshire Building | 2017-07-23 06:45 | 50622.9616 | 39.996
Devonshire Building | 2017-07-23 07:00 | 50622.9716 | 39.996
Devonshire Building | 2017-07-23 07:15 | 50622.9816 | 39.996
Devonshire Building | 2017-07-23 07:30 | 50622.9966 | 60.012
Devonshire Building | 2017-07-23 07:45 | 50623.0066 | 39.996
Devonshire Building | 2017-07-23 08:00 | 50623.0266 | 79.992
Devonshire Building | 2017-07-23 08:15 | 50623.0566 | 119.988
Devonshire Building | 2017-07-23 08:30 | 50623.0816 | 100.008
Devonshire Building | 2017-07-23 08:45 | 50623.1116 | 119.988
Devonshire Building | 2017-07-23 09:00 | 50623.1366 | 100.008
Devonshire Building | 2017-07-23 09:15 | 50623.1616 | 100.008
Devonshire Building | 2017-07-23 09:30 | 50623.1866 | 100.008
Devonshire Building | 2017-07-23 09:45 | 50623.2166 | 119.988
Devonshire Building | 2017-07-23 10:00 | 50623.2366 | 79.992
Devonshire Building | 2017-07-23 10:15 | 50623.2466 | 39.996
Devonshire Building | 2017-07-23 10:30 | 50623.2566 | 39.996
Devonshire Building | 2017-07-23 10:45 | 50623.2666 | 39.996
Devonshire Building | 2017-07-23 11:00 | 50623.2766 | 39.996
Devonshire Building | 2017-07-23 11:15 | 50623.2866 | 39.996
Devonshire Building | 2017-07-23 11:30 | 50623.2966 | 39.996
Devonshire Building | 2017-07-23 11:45 | 50623.3066 | 39.996
Devonshire Building | 2017-07-23 12:00 | 50623.3166 | 39.996
Devonshire Building | 2017-07-23 12:15 | 50623.3265 | 39.996
Devonshire Building | 2017-07-23 12:30 | 50623.3365 | 39.996
Devonshire Building | 2017-07-23 12:45 | 50623.3465 | 39.996
Devonshire Building | 2017-07-23 13:00 | 50623.3565 | 39.996
Devonshire Building | 2017-07-23 13:15 | 50623.3665 | 39.996
Devonshire Building | 2017-07-23 13:30 | 50623.3765 | 39.996
Devonshire Building | 2017-07-23 13:45 | 50623.3815 | 20.016
Devonshire Building | 2017-07-23 14:00 | 50623.3915 | 39.996
Devonshire Building | 2017-07-23 14:15 | 50623.4015 | 39.996
Devonshire Building | 2017-07-23 14:30 | 50623.4115 | 39.996
Devonshire Building | 2017-07-23 14:45 | 50623.4165 | 20.016
Devonshire Building | 2017-07-23 15:00 | 50623.4265 | 39.996
Devonshire Building | 2017-07-23 15:15 | 50623.4365 | 39.996
Devonshire Building | 2017-07-23 15:30 | 50623.4416 | 20.016
Devonshire Building | 2017-07-23 15:45 | 50623.4515 | 39.996
Devonshire Building | 2017-07-23 16:00 | 50623.4615 | 39.996
Devonshire Building | 2017-07-23 16:15 | 50623.4715 | 39.996
Devonshire Building | 2017-07-23 16:30 | 50623.4766 | 20.016
Devonshire Building | 2017-07-23 16:45 | 50623.4866 | 39.996
Devonshire Building | 2017-07-23 17:00 | 50623.4966 | 39.996
Devonshire Building | 2017-07-23 17:15 | 50623.5065 | 39.996
Devonshire Building | 2017-07-23 17:30 | 50623.5165 | 39.996
Devonshire Building | 2017-07-23 17:45 | 50623.5265 | 39.996
Devonshire Building | 2017-07-23 18:00 | 50623.5316 | 20.016
Devonshire Building | 2017-07-23 18:15 | 50623.5416 | 39.996
Devonshire Building | 2017-07-23 18:30 | 50623.5515 | 39.996
Devonshire Building | 2017-07-23 18:45 | 50623.5615 | 39.996
Devonshire Building | 2017-07-23 19:00 | 50623.5666 | 20.016
Devonshire Building | 2017-07-23 19:15 | 50623.5865 | 79.992
Devonshire Building | 2017-07-23 19:30 | 50624.0765 | 1959.984
Devonshire Building | 2017-07-23 19:45 | 50624.0865 | 39.996
Devonshire Building | 2017-07-23 20:00 | 50624.0915 | 20.016
Devonshire Building | 2017-07-23 20:15 | 50624.1015 | 39.996
Devonshire Building | 2017-07-23 20:30 | 50624.1066 | 20.016
Devonshire Building | 2017-07-23 20:45 | 50624.1216 | 60.012
Devonshire Building | 2017-07-23 21:00 | 50624.1316 | 39.996
Devonshire Building | 2017-07-23 21:15 | 50624.1366 | 20.016
Devonshire Building | 2017-07-23 21:30 | 50624.1416 | 20.016
Devonshire Building | 2017-07-23 21:45 | 50624.1516 | 39.996
Devonshire Building | 2017-07-23 22:00 | 50624.1566 | 20.016
Devonshire Building | 2017-07-23 22:15 | 50624.1666 | 39.996
Devonshire Building | 2017-07-23 22:30 | 50624.1766 | 39.996
Devonshire Building | 2017-07-23 22:45 | 50624.1816 | 20.016
Devonshire Building | 2017-07-23 23:00 | 50624.1916 | 39.996
Devonshire Building | 2017-07-23 23:15 | 50624.2016 | 39.996
Devonshire Building | 2017-07-23 23:30 | 50624.2116 | 39.996
Devonshire Building | 2017-07-23 23:45 | 50624.2166 | 20.016
Devonshire Building | 2017-07-24 | 50624.2266 | 39.996
Devonshire Building | 2017-07-24 00:15 | 50624.2366 | 39.996
Devonshire Building | 2017-07-24 00:30 | 50624.2466 | 39.996
Devonshire Building | 2017-07-24 00:45 | 50624.2516 | 20.016
Devonshire Building | 2017-07-24 01:00 | 50624.2616 | 39.996
Devonshire Building | 2017-07-24 01:15 | 50624.2716 | 39.996
Devonshire Building | 2017-07-24 01:30 | 50624.2766 | 20.016
Devonshire Building | 2017-07-24 01:45 | 50624.2866 | 39.996
Devonshire Building | 2017-07-24 02:00 | 50624.2966 | 39.996
Devonshire Building | 2017-07-24 02:15 | 50624.3016 | 20.016
Devonshire Building | 2017-07-24 02:30 | 50624.3116 | 39.996
Devonshire Building | 2017-07-24 02:45 | 50624.3166 | 20.016
Devonshire Building | 2017-07-24 03:00 | 50624.3266 | 39.996
Devonshire Building | 2017-07-24 03:15 | 50624.3316 | 20.016
Devonshire Building | 2017-07-24 03:30 | 50624.3416 | 39.996
Devonshire Building | 2017-07-24 03:45 | 50624.3466 | 20.016
Devonshire Building | 2017-07-24 04:00 | 50624.3566 | 39.996
Devonshire Building | 2017-07-24 04:15 | 50624.3616 | 20.016
Devonshire Building | 2017-07-24 04:30 | 50624.3716 | 39.996
Devonshire Building | 2017-07-24 04:45 | 50624.3766 | 20.016
Devonshire Building | 2017-07-24 05:00 | 50624.3866 | 39.996
Devonshire Building | 2017-07-24 05:15 | 50624.3916 | 20.016
Devonshire Building | 2017-07-24 05:30 | 50624.4016 | 39.996
Devonshire Building | 2017-07-24 05:45 | 50624.4066 | 20.016
Devonshire Building | 2017-07-24 06:00 | 50624.4166 | 39.996
Devonshire Building | 2017-07-24 06:15 | 50624.4216 | 20.016
Devonshire Building | 2017-07-24 06:30 | 50624.4516 | 119.988
Devonshire Building | 2017-07-24 06:45 | 50624.4566 | 20.016
Devonshire Building | 2017-07-24 07:00 | 50624.4666 | 39.996
Devonshire Building | 2017-07-24 07:15 | 50624.4816 | 60.012
Devonshire Building | 2017-07-24 07:30 | 50624.5016 | 79.992
Devonshire Building | 2017-07-24 07:45 | 50625.0416 | 2160
Devonshire Building | 2017-07-24 08:00 | 50625.0916 | 200.016
Devonshire Building | 2017-07-24 08:15 | 50625.1266 | 140.004
Devonshire Building | 2017-07-24 08:30 | 50625.1666 | 159.984
Devonshire Building | 2017-07-24 08:45 | 50625.2066 | 159.984
Devonshire Building | 2017-07-24 09:00 | 50625.2566 | 200.016
Devonshire Building | 2017-07-24 09:15 | 50625.4216 | 659.988
Devonshire Building | 2017-07-24 09:30 | 50626.0166 | 2379.996
Devonshire Building | 2017-07-24 09:45 | 50626.2916 | 1100.016
Devonshire Building | 2017-07-24 10:00 | 50626.5066 | 860.004
Devonshire Building | 2017-07-24 10:15 | 50626.6716 | 659.988
Devonshire Building | 2017-07-24 10:30 | 50627.2516 | 2319.984
Devonshire Building | 2017-07-24 10:45 | 50627.5466 | 1180.008
Devonshire Building | 2017-07-24 11:00 | 50627.6666 | 479.988
Devonshire Building | 2017-07-24 11:15 | 50627.7566 | 360
Devonshire Building | 2017-07-24 11:30 | 50627.8266 | 280.008
Devonshire Building | 2017-07-24 11:45 | 50627.8866 | 240.012
Devonshire Building | 2017-07-24 12:00 | 50627.9916 | 420.012
Devonshire Building | 2017-07-24 12:15 | 50628.4766 | 1940.004
Devonshire Building | 2017-07-24 12:30 | 50628.5066 | 119.988
Devonshire Building | 2017-07-24 12:45 | 50628.5516 | 180
Devonshire Building | 2017-07-24 13:00 | 50628.5866 | 140.004
Devonshire Building | 2017-07-24 13:15 | 50628.6266 | 159.984
Devonshire Building | 2017-07-24 13:30 | 50628.6816 | 219.996
Devonshire Building | 2017-07-24 13:45 | 50629.3166 | 2540.016
Devonshire Building | 2017-07-24 14:00 | 50629.4966 | 720
Devonshire Building | 2017-07-24 14:15 | 50629.6266 | 519.984
Devonshire Building | 2017-07-24 14:30 | 50629.7566 | 519.984
Devonshire Building | 2017-07-24 14:45 | 50629.8666 | 439.992
Devonshire Building | 2017-07-24 15:00 | 50629.9616 | 380.016
Devonshire Building | 2017-07-24 15:15 | 50630.5516 | 2360.016
Devonshire Building | 2017-07-24 15:30 | 50630.5916 | 159.984
Devonshire Building | 2017-07-24 15:45 | 50630.6366 | 180
Devonshire Building | 2017-07-24 16:00 | 50630.6766 | 159.984
Devonshire Building | 2017-07-24 16:15 | 50630.7216 | 180
Devonshire Building | 2017-07-24 16:30 | 50630.7666 | 180
Devonshire Building | 2017-07-24 16:45 | 50630.8116 | 180
Devonshire Building | 2017-07-24 17:00 | 50631.3516 | 2160
Devonshire Building | 2017-07-24 17:15 | 50631.3966 | 180
Devonshire Building | 2017-07-24 17:30 | 50631.4466 | 200.016
Devonshire Building | 2017-07-24 17:45 | 50631.4866 | 159.984
Devonshire Building | 2017-07-24 18:00 | 50631.5266 | 159.984
Devonshire Building | 2017-07-24 18:15 | 50631.5666 | 159.984
Devonshire Building | 2017-07-24 18:30 | 50631.6016 | 140.004
Devonshire Building | 2017-07-24 18:45 | 50631.6316 | 119.988
Devonshire Building | 2017-07-24 19:00 | 50631.6616 | 119.988
Devonshire Building | 2017-07-24 19:15 | 50631.6816 | 79.992
Devonshire Building | 2017-07-24 19:30 | 50631.7016 | 79.992
Devonshire Building | 2017-07-24 19:45 | 50631.7266 | 100.008
Devonshire Building | 2017-07-24 20:00 | 50631.7416 | 60.012
Devonshire Building | 2017-07-24 20:15 | 50631.7616 | 79.992
Devonshire Building | 2017-07-24 20:30 | 50631.7766 | 60.012
Devonshire Building | 2017-07-24 20:45 | 50631.8116 | 140.004
Devonshire Building | 2017-07-24 21:00 | 50631.8166 | 20.016
Devonshire Building | 2017-07-24 21:15 | 50631.8216 | 20.016
Devonshire Building | 2017-07-24 21:30 | 50631.8316 | 39.996
Devonshire Building | 2017-07-24 21:45 | 50631.8366 | 20.016
Devonshire Building | 2017-07-24 22:00 | 50631.8416 | 20.016
Devonshire Building | 2017-07-24 22:15 | 50631.8466 | 20.016
Devonshire Building | 2017-07-24 22:30 | 50631.8516 | 20.016
Devonshire Building | 2017-07-24 22:45 | 50631.8616 | 39.996
Devonshire Building | 2017-07-24 23:00 | 50631.8666 | 20.016
Devonshire Building | 2017-07-24 23:15 | 50631.8716 | 20.016
Devonshire Building | 2017-07-24 23:30 | 50631.8766 | 20.016
Devonshire Building | 2017-07-24 23:45 | 50631.8816 | 20.016
Devonshire Building | 2017-07-25 | 50631.8828 | 20.016
Devonshire Building | 2017-07-25 00:15 | 50631.8928 | 39.996
Devonshire Building | 2017-07-25 00:30 | 50631.8978 | 20.016
Devonshire Building | 2017-07-25 00:45 | 50631.9028 | 20.016
Devonshire Building | 2017-07-25 01:00 | 50631.9078 | 20.016
Devonshire Building | 2017-07-25 01:15 | 50631.9128 | 20.016
Devonshire Building | 2017-07-25 01:30 | 50631.9178 | 20.016
Devonshire Building | 2017-07-25 01:45 | 50631.9228 | 20.016
Devonshire Building | 2017-07-25 02:00 | 50631.9278 | 20.016
Devonshire Building | 2017-07-25 02:15 | 50631.9378 | 39.996
Devonshire Building | 2017-07-25 02:30 | 50631.9428 | 20.016
Devonshire Building | 2017-07-25 02:45 | 50631.9478 | 20.016
Devonshire Building | 2017-07-25 03:00 | 50631.9528 | 20.016
Devonshire Building | 2017-07-25 03:15 | 50631.9579 | 20.016
Devonshire Building | 2017-07-25 03:30 | 50631.9629 | 20.016
Devonshire Building | 2017-07-25 03:45 | 50631.9679 | 20.016
Devonshire Building | 2017-07-25 04:00 | 50631.9729 | 20.016
Devonshire Building | 2017-07-25 04:15 | 50631.9779 | 20.016
Devonshire Building | 2017-07-25 04:30 | 50631.9829 | 20.016
Devonshire Building | 2017-07-25 04:45 | 50631.9879 | 20.016
Devonshire Building | 2017-07-25 05:00 | 50631.9929 | 20.016
Devonshire Building | 2017-07-25 05:15 | 50631.9979 | 20.016
Devonshire Building | 2017-07-25 05:30 | 50632.0079 | 39.996
Devonshire Building | 2017-07-25 05:45 | 50632.0129 | 20.016
Devonshire Building | 2017-07-25 06:00 | 50632.0179 | 20.016
Devonshire Building | 2017-07-25 06:15 | 50632.0279 | 39.996
Devonshire Building | 2017-07-25 06:30 | 50632.2729 | 979.992
Devonshire Building | 2017-07-25 06:45 | 50632.5629 | 1159.992
Devonshire Building | 2017-07-25 07:00 | 50632.5679 | 20.016
Devonshire Building | 2017-07-25 07:15 | 50632.5779 | 39.996
Devonshire Building | 2017-07-25 07:30 | 50632.5879 | 39.996
Devonshire Building | 2017-07-25 07:45 | 50632.6179 | 119.988
Devonshire Building | 2017-07-25 08:00 | 50632.6479 | 119.988
Devonshire Building | 2017-07-25 08:15 | 50632.6829 | 140.004
Devonshire Building | 2017-07-25 08:30 | 50632.7329 | 200.016
Devonshire Building | 2017-07-25 08:45 | 50632.8029 | 280.008
Devonshire Building | 2017-07-25 09:00 | 50632.9879 | 740.016
Devonshire Building | 2017-07-25 09:15 | 50633.7079 | 2880
Devonshire Building | 2017-07-25 09:30 | 50633.8829 | 699.984
Devonshire Building | 2017-07-25 09:45 | 50633.9979 | 460.008
Devonshire Building | 2017-07-25 10:00 | 50634.1329 | 540
Devonshire Building | 2017-07-25 10:15 | 50634.7379 | 2419.992
Devonshire Building | 2017-07-25 10:30 | 50634.8029 | 259.992
Devonshire Building | 2017-07-25 10:45 | 50634.8629 | 240.012
Devonshire Building | 2017-07-25 11:00 | 50634.9179 | 219.996
Devonshire Building | 2017-07-25 11:15 | 50634.9679 | 200.016
Devonshire Building | 2017-07-25 11:30 | 50635.1979 | 920.016
Devonshire Building | 2017-07-25 11:45 | 50635.5829 | 1540.008
Devonshire Building | 2017-07-25 12:00 | 50635.6179 | 140.004
Devonshire Building | 2017-07-25 12:15 | 50635.6579 | 159.984
Devonshire Building | 2017-07-25 12:30 | 50635.6929 | 140.004
Devonshire Building | 2017-07-25 12:45 | 50635.7329 | 159.984
Devonshire Building | 2017-07-25 13:00 | 50635.7729 | 159.984
Devonshire Building | 2017-07-25 13:15 | 50636.3529 | 2319.984
Devonshire Building | 2017-07-25 13:30 | 50636.4179 | 259.992
Devonshire Building | 2017-07-25 13:45 | 50636.4829 | 259.992
Devonshire Building | 2017-07-25 14:00 | 50636.5479 | 259.992
Devonshire Building | 2017-07-25 14:15 | 50636.6079 | 240.012
Devonshire Building | 2017-07-25 14:30 | 50636.6629 | 219.996
Devonshire Building | 2017-07-25 14:45 | 50637.2679 | 2419.992
Devonshire Building | 2017-07-25 15:00 | 50637.3179 | 200.016
Devonshire Building | 2017-07-25 15:15 | 50637.3679 | 200.016
Devonshire Building | 2017-07-25 15:30 | 50637.4279 | 240.012
Devonshire Building | 2017-07-25 15:45 | 50637.4829 | 219.996
Devonshire Building | 2017-07-25 16:00 | 50637.5279 | 180
Devonshire Building | 2017-07-25 16:15 | 50638.1629 | 2540.016
Devonshire Building | 2017-07-25 16:30 | 50638.3829 | 879.984
Devonshire Building | 2017-07-25 16:45 | 50638.7479 | 1460.016
Devonshire Building | 2017-07-25 17:00 | 50639.0179 | 1080
Devonshire Building | 2017-07-25 17:15 | 50639.1729 | 619.992
Devonshire Building | 2017-07-25 17:30 | 50639.2679 | 380.016
Devonshire Building | 2017-07-25 17:45 | 50639.3329 | 259.992
Devonshire Building | 2017-07-25 18:00 | 50639.3779 | 180
Devonshire Building | 2017-07-25 18:15 | 50639.4279 | 200.016
Devonshire Building | 2017-07-25 18:30 | 50639.4679 | 159.984
Devonshire Building | 2017-07-25 18:45 | 50639.5129 | 180
Devonshire Building | 2017-07-25 19:00 | 50639.5429 | 119.988
Devonshire Building | 2017-07-25 19:15 | 50639.5729 | 119.988
Devonshire Building | 2017-07-25 19:30 | 50639.5979 | 100.008
Devonshire Building | 2017-07-25 19:45 | 50639.6179 | 79.992
Devonshire Building | 2017-07-25 20:00 | 50639.6379 | 79.992
Devonshire Building | 2017-07-25 20:15 | 50639.6579 | 79.992
Devonshire Building | 2017-07-25 20:30 | 50639.6779 | 79.992
Devonshire Building | 2017-07-25 20:45 | 50639.7129 | 140.004
Devonshire Building | 2017-07-25 21:00 | 50639.7179 | 20.016
Devonshire Building | 2017-07-25 21:15 | 50639.7229 | 20.016
Devonshire Building | 2017-07-25 21:30 | 50639.7279 | 20.016
Devonshire Building | 2017-07-25 21:45 | 50640.2329 | 2019.996
Devonshire Building | 2017-07-25 22:00 | 50640.2379 | 20.016
Devonshire Building | 2017-07-25 22:15 | 50640.2429 | 20.016
Devonshire Building | 2017-07-25 22:30 | 50640.2479 | 20.016
Devonshire Building | 2017-07-25 22:45 | 50640.2529 | 20.016
Devonshire Building | 2017-07-25 23:00 | 50640.2579 | 20.016
Devonshire Building | 2017-07-25 23:15 | 50640.2629 | 20.016
Devonshire Building | 2017-07-25 23:30 | 50640.2679 | 20.016
Devonshire Building | 2017-07-25 23:45 | 50640.2729 | 20.016
Devonshire Building | 2017-07-26 | 50640.2812 | 20.016
Devonshire Building | 2017-07-26 00:15 | 50640.2912 | 39.996
Devonshire Building | 2017-07-26 00:30 | 50640.2963 | 20.016
Devonshire Building | 2017-07-26 00:45 | 50640.3013 | 20.016
Devonshire Building | 2017-07-26 01:00 | 50640.3063 | 20.016
Devonshire Building | 2017-07-26 01:15 | 50640.3113 | 20.016
Devonshire Building | 2017-07-26 01:30 | 50640.3163 | 20.016
Devonshire Building | 2017-07-26 01:45 | 50640.3213 | 20.016
Devonshire Building | 2017-07-26 02:00 | 50640.3263 | 20.016
Devonshire Building | 2017-07-26 02:15 | 50640.3313 | 20.016
Devonshire Building | 2017-07-26 02:30 | 50640.3363 | 20.016
Devonshire Building | 2017-07-26 02:45 | 50640.3413 | 20.016
Devonshire Building | 2017-07-26 03:00 | 50640.3463 | 20.016
Devonshire Building | 2017-07-26 03:15 | 50640.3513 | 20.016
Devonshire Building | 2017-07-26 03:30 | 50640.3563 | 20.016
Devonshire Building | 2017-07-26 03:45 | 50640.3663 | 39.996
Devonshire Building | 2017-07-26 04:00 | 50640.3713 | 20.016
Devonshire Building | 2017-07-26 04:15 | 50640.3763 | 20.016
Devonshire Building | 2017-07-26 04:30 | 50640.3813 | 20.016
Devonshire Building | 2017-07-26 04:45 | 50640.3863 | 20.016
Devonshire Building | 2017-07-26 05:00 | 50640.3913 | 20.016
Devonshire Building | 2017-07-26 05:15 | 50640.3963 | 20.016
Devonshire Building | 2017-07-26 05:30 | 50640.4013 | 20.016
Devonshire Building | 2017-07-26 05:45 | 50640.4113 | 39.996
Devonshire Building | 2017-07-26 06:00 | 50640.4163 | 20.016
Devonshire Building | 2017-07-26 06:15 | 50640.4263 | 39.996
Devonshire Building | 2017-07-26 06:30 | 50640.4413 | 60.012
Devonshire Building | 2017-07-26 06:45 | 50640.4463 | 20.016
Devonshire Building | 2017-07-26 07:00 | 50640.4613 | 60.012
Devonshire Building | 2017-07-26 07:15 | 50640.5013 | 159.984
Devonshire Building | 2017-07-26 07:30 | 50640.5563 | 219.996
Devonshire Building | 2017-07-26 07:45 | 50640.6313 | 299.988
Devonshire Building | 2017-07-26 08:00 | 50640.7263 | 380.016
Devonshire Building | 2017-07-26 08:15 | 50641.3063 | 2319.984
Devonshire Building | 2017-07-26 08:30 | 50641.4013 | 380.016
Devonshire Building | 2017-07-26 08:45 | 50641.5063 | 420.012
Devonshire Building | 2017-07-26 09:00 | 50641.6063 | 399.996
Devonshire Building | 2017-07-26 09:15 | 50641.7013 | 380.016
Devonshire Building | 2017-07-26 09:30 | 50642.3063 | 2419.992
Devonshire Building | 2017-07-26 09:45 | 50642.3763 | 280.008
Devonshire Building | 2017-07-26 10:00 | 50642.4513 | 299.988
Devonshire Building | 2017-07-26 10:15 | 50642.5163 | 259.992
Devonshire Building | 2017-07-26 10:30 | 50642.5763 | 240.012
Devonshire Building | 2017-07-26 10:45 | 50642.6263 | 200.016
Devonshire Building | 2017-07-26 11:00 | 50643.2013 | 2300.004
Devonshire Building | 2017-07-26 11:15 | 50643.2713 | 280.008
Devonshire Building | 2017-07-26 11:30 | 50643.3214 | 200.016
Devonshire Building | 2017-07-26 11:45 | 50643.3763 | 219.996
Devonshire Building | 2017-07-26 12:00 | 50643.4163 | 159.984
Devonshire Building | 2017-07-26 12:15 | 50643.4664 | 200.016
Devonshire Building | 2017-07-26 12:30 | 50644.0363 | 2279.988
Devonshire Building | 2017-07-26 12:45 | 50644.0763 | 159.984
Devonshire Building | 2017-07-26 13:00 | 50644.1313 | 219.996
Devonshire Building | 2017-07-26 13:15 | 50644.1813 | 200.016
Devonshire Building | 2017-07-26 13:30 | 50644.2463 | 259.992
Devonshire Building | 2017-07-26 13:45 | 50644.2813 | 140.004
Devonshire Building | 2017-07-26 14:00 | 50644.3213 | 159.984
Devonshire Building | 2017-07-26 14:15 | 50644.8813 | 2239.992
Devonshire Building | 2017-07-26 14:30 | 50644.9113 | 119.988
Devonshire Building | 2017-07-26 14:45 | 50644.9463 | 140.004
Devonshire Building | 2017-07-26 15:00 | 50644.9813 | 140.004
Devonshire Building | 2017-07-26 15:15 | 50645.0163 | 140.004
Devonshire Building | 2017-07-26 15:30 | 50645.0513 | 140.004
Devonshire Building | 2017-07-26 15:45 | 50645.6463 | 2379.996
Devonshire Building | 2017-07-26 16:00 | 50645.6813 | 140.004
Devonshire Building | 2017-07-26 16:15 | 50645.7213 | 159.984
Devonshire Building | 2017-07-26 16:30 | 50645.7563 | 140.004
Devonshire Building | 2017-07-26 16:45 | 50645.8213 | 259.992
Devonshire Building | 2017-07-26 17:00 | 50645.8513 | 119.988
Devonshire Building | 2017-07-26 17:15 | 50645.8863 | 140.004
Devonshire Building | 2017-07-26 17:30 | 50645.9163 | 119.988
Devonshire Building | 2017-07-26 17:45 | 50645.9463 | 119.988
Devonshire Building | 2017-07-26 18:00 | 50645.9763 | 119.988
Devonshire Building | 2017-07-26 18:15 | 50646.0013 | 100.008
Devonshire Building | 2017-07-26 18:30 | 50646.0363 | 140.004
Devonshire Building | 2017-07-26 18:45 | 50646.0613 | 100.008
Devonshire Building | 2017-07-26 19:00 | 50646.5813 | 2080.008
Devonshire Building | 2017-07-26 19:15 | 50646.6063 | 100.008
Devonshire Building | 2017-07-26 19:30 | 50646.6213 | 60.012
Devonshire Building | 2017-07-26 19:45 | 50646.6413 | 79.992
Devonshire Building | 2017-07-26 20:00 | 50646.6613 | 79.992
Devonshire Building | 2017-07-26 20:15 | 50646.6763 | 60.012
Devonshire Building | 2017-07-26 20:30 | 50646.6963 | 79.992
Devonshire Building | 2017-07-26 20:45 | 50646.7263 | 119.988
Devonshire Building | 2017-07-26 21:00 | 50646.7413 | 60.012
Devonshire Building | 2017-07-26 21:15 | 50646.7563 | 60.012
Devonshire Building | 2017-07-26 21:30 | 50646.7763 | 79.992
Devonshire Building | 2017-07-26 21:45 | 50646.7913 | 60.012
Devonshire Building | 2017-07-26 22:00 | 50646.8063 | 60.012
Devonshire Building | 2017-07-26 22:15 | 50646.8163 | 39.996
Devonshire Building | 2017-07-26 22:30 | 50646.8313 | 60.012
Devonshire Building | 2017-07-26 22:45 | 50646.8463 | 60.012
Devonshire Building | 2017-07-26 23:00 | 50646.8613 | 60.012
Devonshire Building | 2017-07-26 23:15 | 50646.8764 | 60.012
Devonshire Building | 2017-07-26 23:30 | 50646.8914 | 60.012
Devonshire Building | 2017-07-26 23:45 | 50646.9014 | 39.996
Devonshire Building | 2017-07-27 | 50646.9141 | 60.012
Devonshire Building | 2017-07-27 00:15 | 50646.9291 | 60.012
Devonshire Building | 2017-07-27 00:30 | 50646.9391 | 39.996
Devonshire Building | 2017-07-27 00:45 | 50646.9541 | 60.012
Devonshire Building | 2017-07-27 01:00 | 50646.9641 | 39.996
Devonshire Building | 2017-07-27 01:15 | 50646.9791 | 60.012
Devonshire Building | 2017-07-27 01:30 | 50646.9941 | 60.012
Devonshire Building | 2017-07-27 01:45 | 50647.0241 | 119.988
Devonshire Building | 2017-07-27 02:00 | 50647.0491 | 100.008
Devonshire Building | 2017-07-27 02:15 | 50647.0791 | 119.988
Devonshire Building | 2017-07-27 02:30 | 50647.1091 | 119.988
Devonshire Building | 2017-07-27 02:45 | 50647.1341 | 100.008
Devonshire Building | 2017-07-27 03:00 | 50647.1641 | 119.988
Devonshire Building | 2017-07-27 03:15 | 50647.1941 | 119.988
Devonshire Building | 2017-07-27 03:30 | 50647.2191 | 100.008
Devonshire Building | 2017-07-27 03:45 | 50647.2491 | 119.988
Devonshire Building | 2017-07-27 04:00 | 50647.2641 | 60.012
Devonshire Building | 2017-07-27 04:15 | 50647.2741 | 39.996
Devonshire Building | 2017-07-27 04:30 | 50647.2841 | 39.996
Devonshire Building | 2017-07-27 04:45 | 50647.2991 | 60.012
Devonshire Building | 2017-07-27 05:00 | 50647.3091 | 39.996
Devonshire Building | 2017-07-27 05:15 | 50647.3241 | 60.012
Devonshire Building | 2017-07-27 05:30 | 50647.3341 | 39.996
Devonshire Building | 2017-07-27 05:45 | 50647.3491 | 60.012
Devonshire Building | 2017-07-27 06:00 | 50647.3591 | 39.996
Devonshire Building | 2017-07-27 06:15 | 50647.3791 | 79.992
Devonshire Building | 2017-07-27 06:30 | 50647.3891 | 39.996
Devonshire Building | 2017-07-27 06:45 | 50647.4041 | 60.012
Devonshire Building | 2017-07-27 07:00 | 50647.6241 | 879.984
Devonshire Building | 2017-07-27 07:15 | 50647.9291 | 1220.004
Devonshire Building | 2017-07-27 07:30 | 50647.9391 | 39.996
Devonshire Building | 2017-07-27 07:45 | 50647.9491 | 39.996
Devonshire Building | 2017-07-27 08:00 | 50647.9691 | 79.992
Devonshire Building | 2017-07-27 08:15 | 50647.9791 | 39.996
Devonshire Building | 2017-07-27 08:30 | 50647.9991 | 79.992
Devonshire Building | 2017-07-27 08:45 | 50648.0141 | 60.012
Devonshire Building | 2017-07-27 09:00 | 50648.0241 | 39.996
Devonshire Building | 2017-07-27 09:15 | 50648.5741 | 2199.996
Devonshire Building | 2017-07-27 09:30 | 50648.5891 | 60.012
Devonshire Building | 2017-07-27 09:45 | 50648.6191 | 119.988
Devonshire Building | 2017-07-27 10:00 | 50648.6541 | 140.004
Devonshire Building | 2017-07-27 10:15 | 50648.6841 | 119.988
Devonshire Building | 2017-07-27 10:30 | 50648.8391 | 619.992
Devonshire Building | 2017-07-27 10:45 | 50649.2691 | 1720.008
Devonshire Building | 2017-07-27 11:00 | 50649.3091 | 159.984
Devonshire Building | 2017-07-27 11:15 | 50649.3541 | 180
Devonshire Building | 2017-07-27 11:30 | 50649.4041 | 200.016
Devonshire Building | 2017-07-27 11:45 | 50649.4591 | 219.996
Devonshire Building | 2017-07-27 12:00 | 50649.5141 | 219.996
Devonshire Building | 2017-07-27 12:15 | 50650.0791 | 2260.008
Devonshire Building | 2017-07-27 12:30 | 50650.1341 | 219.996
Devonshire Building | 2017-07-27 12:45 | 50650.1891 | 219.996
Devonshire Building | 2017-07-27 13:00 | 50650.2691 | 320.004
Devonshire Building | 2017-07-27 13:15 | 50650.4941 | 900
Devonshire Building | 2017-07-27 13:30 | 50650.6841 | 759.996
Devonshire Building | 2017-07-27 13:45 | 50650.8991 | 860.004
Devonshire Building | 2017-07-27 14:00 | 50651.5941 | 2779.992
Devonshire Building | 2017-07-27 14:15 | 50651.714 | 479.988
Devonshire Building | 2017-07-27 14:30 | 50651.8091 | 380.016
Devonshire Building | 2017-07-27 14:45 | 50651.8891 | 320.004
Devonshire Building | 2017-07-27 15:00 | 50651.9491 | 240.012
Devonshire Building | 2017-07-27 15:15 | 50652.0141 | 259.992
Devonshire Building | 2017-07-27 15:30 | 50652.0641 | 200.016
Devonshire Building | 2017-07-27 15:45 | 50652.1391 | 299.988
Devonshire Building | 2017-07-27 16:00 | 50652.2691 | 519.984
Devonshire Building | 2017-07-27 16:15 | 50652.9241 | 2620.008
Devonshire Building | 2017-07-27 16:30 | 50653.0291 | 420.012
Devonshire Building | 2017-07-27 16:45 | 50653.1141 | 339.984
Devonshire Building | 2017-07-27 17:00 | 50653.1691 | 219.996
Devonshire Building | 2017-07-27 17:15 | 50653.2191 | 200.016
Devonshire Building | 2017-07-27 17:30 | 50653.2591 | 159.984
Devonshire Building | 2017-07-27 17:45 | 50653.2941 | 140.004
Devonshire Building | 2017-07-27 18:00 | 50653.324 | 119.988
Devonshire Building | 2017-07-27 18:15 | 50653.3491 | 100.008
Devonshire Building | 2017-07-27 18:30 | 50653.3741 | 100.008
Devonshire Building | 2017-07-27 18:45 | 50653.3941 | 79.992
Devonshire Building | 2017-07-27 19:00 | 50653.4191 | 100.008
Devonshire Building | 2017-07-27 19:15 | 50653.4341 | 60.012
Devonshire Building | 2017-07-27 19:30 | 50653.4541 | 79.992
Devonshire Building | 2017-07-27 19:45 | 50653.4691 | 60.012
Devonshire Building | 2017-07-27 20:00 | 50653.4891 | 79.992
Devonshire Building | 2017-07-27 20:15 | 50653.5041 | 60.012
Devonshire Building | 2017-07-27 20:30 | 50653.5191 | 60.012
Devonshire Building | 2017-07-27 20:45 | 50653.5541 | 140.004
Devonshire Building | 2017-07-27 21:00 | 50653.5641 | 39.996
Devonshire Building | 2017-07-27 21:15 | 50653.5691 | 20.016
Devonshire Building | 2017-07-27 21:30 | 50653.5741 | 20.016
Devonshire Building | 2017-07-27 21:45 | 50653.5791 | 20.016
Devonshire Building | 2017-07-27 22:00 | 50653.5841 | 20.016
Devonshire Building | 2017-07-27 22:15 | 50653.5941 | 39.996
Devonshire Building | 2017-07-27 22:30 | 50653.5991 | 20.016
Devonshire Building | 2017-07-27 22:45 | 50653.6391 | 159.984
Devonshire Building | 2017-07-27 23:00 | 50654.1191 | 1919.988
Devonshire Building | 2017-07-27 23:15 | 50654.1241 | 20.016
Devonshire Building | 2017-07-27 23:30 | 50654.1291 | 20.016
Devonshire Building | 2017-07-27 23:45 | 50654.1341 | 20.016
Devonshire Building | 2017-07-28 | 50654.1406 | 20.016
Devonshire Building | 2017-07-28 00:15 | 50654.1456 | 20.016
Devonshire Building | 2017-07-28 00:30 | 50654.1556 | 39.996
Devonshire Building | 2017-07-28 00:45 | 50654.1606 | 20.016
Devonshire Building | 2017-07-28 01:00 | 50654.1656 | 20.016
Devonshire Building | 2017-07-28 01:15 | 50654.1706 | 20.016
Devonshire Building | 2017-07-28 01:30 | 50654.1756 | 20.016
Devonshire Building | 2017-07-28 01:45 | 50654.1807 | 20.016
Devonshire Building | 2017-07-28 02:00 | 50654.1907 | 39.996
Devonshire Building | 2017-07-28 02:15 | 50654.1957 | 20.016
Devonshire Building | 2017-07-28 02:30 | 50654.2007 | 20.016
Devonshire Building | 2017-07-28 02:45 | 50654.2057 | 20.016
Devonshire Building | 2017-07-28 03:00 | 50654.2107 | 20.016
Devonshire Building | 2017-07-28 03:15 | 50654.2207 | 39.996
Devonshire Building | 2017-07-28 03:30 | 50654.2257 | 20.016
Devonshire Building | 2017-07-28 03:45 | 50654.2307 | 20.016
Devonshire Building | 2017-07-28 04:00 | 50654.2357 | 20.016
Devonshire Building | 2017-07-28 04:15 | 50654.2457 | 39.996
Devonshire Building | 2017-07-28 04:30 | 50654.2507 | 20.016
Devonshire Building | 2017-07-28 04:45 | 50654.2557 | 20.016
Devonshire Building | 2017-07-28 05:00 | 50654.2607 | 20.016
Devonshire Building | 2017-07-28 05:15 | 50654.2707 | 39.996
Devonshire Building | 2017-07-28 05:30 | 50654.2757 | 20.016
Devonshire Building | 2017-07-28 05:45 | 50654.2857 | 39.996
Devonshire Building | 2017-07-28 06:00 | 50654.2907 | 20.016
Devonshire Building | 2017-07-28 06:15 | 50654.3007 | 39.996
Devonshire Building | 2017-07-28 06:30 | 50654.3207 | 79.992
Devonshire Building | 2017-07-28 06:45 | 50654.3307 | 39.996
Devonshire Building | 2017-07-28 07:00 | 50654.3407 | 39.996
Devonshire Building | 2017-07-28 07:15 | 50654.3557 | 60.012
Devonshire Building | 2017-07-28 07:30 | 50654.3657 | 39.996
Devonshire Building | 2017-07-28 07:45 | 50654.3957 | 119.988
Devonshire Building | 2017-07-28 08:00 | 50654.4307 | 140.004
Devonshire Building | 2017-07-28 08:15 | 50654.9857 | 2220.012
Devonshire Building | 2017-07-28 08:30 | 50655.0307 | 180
Devonshire Building | 2017-07-28 08:45 | 50655.0807 | 200.016
Devonshire Building | 2017-07-28 09:00 | 50655.1407 | 240.012
Devonshire Building | 2017-07-28 09:15 | 50655.2007 | 240.012
Devonshire Building | 2017-07-28 09:30 | 50655.2607 | 240.012
Devonshire Building | 2017-07-28 09:45 | 50655.6757 | 1659.996
Devonshire Building | 2017-07-28 10:00 | 50655.9857 | 1239.984
Devonshire Building | 2017-07-28 10:15 | 50656.1057 | 479.988
Devonshire Building | 2017-07-28 10:30 | 50656.2057 | 399.996
Devonshire Building | 2017-07-28 10:45 | 50656.3107 | 420.012
Devonshire Building | 2017-07-28 11:00 | 50656.4257 | 460.008
Devonshire Building | 2017-07-28 11:15 | 50656.5157 | 360
Devonshire Building | 2017-07-28 11:30 | 50656.6057 | 360
Devonshire Building | 2017-07-28 11:45 | 50657.2407 | 2540.016
Devonshire Building | 2017-07-28 12:00 | 50657.3307 | 360
Devonshire Building | 2017-07-28 12:15 | 50657.4207 | 360
Devonshire Building | 2017-07-28 12:30 | 50657.5007 | 320.004
Devonshire Building | 2017-07-28 12:45 | 50657.6007 | 399.996
Devonshire Building | 2017-07-28 13:00 | 50657.7057 | 420.012
Devonshire Building | 2017-07-28 13:15 | 50657.8157 | 439.992
Devonshire Building | 2017-07-28 13:30 | 50658.4207 | 2419.992
Devonshire Building | 2017-07-28 13:45 | 50658.5007 | 320.004
Devonshire Building | 2017-07-28 14:00 | 50658.5757 | 299.988
Devonshire Building | 2017-07-28 14:15 | 50658.6357 | 240.012
Devonshire Building | 2017-07-28 14:30 | 50658.6907 | 219.996
Devonshire Building | 2017-07-28 14:45 | 50658.7407 | 200.016
Devonshire Building | 2017-07-28 15:00 | 50658.7907 | 200.016
Devonshire Building | 2017-07-28 15:15 | 50658.8407 | 200.016
Devonshire Building | 2017-07-28 15:30 | 50659.4307 | 2360.016
Devonshire Building | 2017-07-28 15:45 | 50659.5107 | 320.004
Devonshire Building | 2017-07-28 16:00 | 50659.5857 | 299.988
Devonshire Building | 2017-07-28 16:15 | 50659.6557 | 280.008
Devonshire Building | 2017-07-28 16:30 | 50659.7257 | 280.008
Devonshire Building | 2017-07-28 16:45 | 50659.7957 | 280.008
Devonshire Building | 2017-07-28 17:00 | 50659.8657 | 280.008
Devonshire Building | 2017-07-28 17:15 | 50659.9257 | 240.012
Devonshire Building | 2017-07-28 17:30 | 50659.9807 | 219.996
Devonshire Building | 2017-07-28 17:45 | 50660.0307 | 200.016
Devonshire Building | 2017-07-28 18:00 | 50660.0707 | 159.984
Devonshire Building | 2017-07-28 18:15 | 50660.1057 | 140.004
Devonshire Building | 2017-07-28 18:30 | 50660.1407 | 140.004
Devonshire Building | 2017-07-28 18:45 | 50660.1707 | 119.988
Devonshire Building | 2017-07-28 19:00 | 50660.2007 | 119.988
Devonshire Building | 2017-07-28 19:15 | 50660.2207 | 79.992
Devonshire Building | 2017-07-28 19:30 | 50660.2407 | 79.992
Devonshire Building | 2017-07-28 19:45 | 50660.2607 | 79.992
Devonshire Building | 2017-07-28 20:00 | 50660.2807 | 79.992
Devonshire Building | 2017-07-28 20:15 | 50660.2957 | 60.012
Devonshire Building | 2017-07-28 20:30 | 50660.3157 | 79.992
Devonshire Building | 2017-07-28 20:45 | 50660.3507 | 140.004
Devonshire Building | 2017-07-28 21:00 | 50660.3557 | 20.016
Devonshire Building | 2017-07-28 21:15 | 50660.3657 | 39.996
Devonshire Building | 2017-07-28 21:30 | 50660.3707 | 20.016
Devonshire Building | 2017-07-28 21:45 | 50660.3807 | 39.996
Devonshire Building | 2017-07-28 22:00 | 50660.7457 | 1460.016
Devonshire Building | 2017-07-28 22:15 | 50660.8757 | 519.984
Devonshire Building | 2017-07-28 22:30 | 50660.8807 | 20.016
Devonshire Building | 2017-07-28 22:45 | 50660.8857 | 20.016
Devonshire Building | 2017-07-28 23:00 | 50660.8957 | 39.996
Devonshire Building | 2017-07-28 23:15 | 50660.9007 | 20.016
Devonshire Building | 2017-07-28 23:30 | 50660.9057 | 20.016
Devonshire Building | 2017-07-28 23:45 | 50660.9107 | 20.016
Devonshire Building | 2017-07-29 | 50660.9141 | 20.016
Devonshire Building | 2017-07-29 00:15 | 50660.9191 | 20.016
Devonshire Building | 2017-07-29 00:30 | 50660.9291 | 39.996
Devonshire Building | 2017-07-29 00:45 | 50660.9341 | 20.016
Devonshire Building | 2017-07-29 01:00 | 50660.9391 | 20.016
Devonshire Building | 2017-07-29 01:15 | 50660.9441 | 20.016
Devonshire Building | 2017-07-29 01:30 | 50660.9491 | 20.016
Devonshire Building | 2017-07-29 01:45 | 50660.9641 | 60.012
Devonshire Building | 2017-07-29 02:00 | 50660.9891 | 100.008
Devonshire Building | 2017-07-29 02:15 | 50661.0091 | 79.992
Devonshire Building | 2017-07-29 02:30 | 50661.0341 | 100.008
Devonshire Building | 2017-07-29 02:45 | 50661.0541 | 79.992
Devonshire Building | 2017-07-29 03:00 | 50661.0791 | 100.008
Devonshire Building | 2017-07-29 03:15 | 50661.0991 | 79.992
Devonshire Building | 2017-07-29 03:30 | 50661.1241 | 100.008
Devonshire Building | 2017-07-29 03:45 | 50661.1291 | 20.016
Devonshire Building | 2017-07-29 04:00 | 50661.1341 | 20.016
Devonshire Building | 2017-07-29 04:15 | 50661.1441 | 39.996
Devonshire Building | 2017-07-29 04:30 | 50661.1491 | 20.016
Devonshire Building | 2017-07-29 04:45 | 50661.1541 | 20.016
Devonshire Building | 2017-07-29 05:00 | 50661.1591 | 20.016
Devonshire Building | 2017-07-29 05:15 | 50661.1691 | 39.996
Devonshire Building | 2017-07-29 05:30 | 50661.1741 | 20.016
Devonshire Building | 2017-07-29 05:45 | 50661.1791 | 20.016
Devonshire Building | 2017-07-29 06:00 | 50661.1841 | 20.016
Devonshire Building | 2017-07-29 06:15 | 50661.1941 | 39.996
Devonshire Building | 2017-07-29 06:30 | 50661.1991 | 20.016
Devonshire Building | 2017-07-29 06:45 | 50661.2041 | 20.016
Devonshire Building | 2017-07-29 07:00 | 50661.2091 | 20.016
Devonshire Building | 2017-07-29 07:15 | 50661.2191 | 39.996
Devonshire Building | 2017-07-29 07:30 | 50661.2241 | 20.016
Devonshire Building | 2017-07-29 07:45 | 50661.2291 | 20.016
Devonshire Building | 2017-07-29 08:00 | 50661.2341 | 20.016
Devonshire Building | 2017-07-29 08:15 | 50661.2441 | 39.996
Devonshire Building | 2017-07-29 08:30 | 50661.2491 | 20.016
Devonshire Building | 2017-07-29 08:45 | 50661.2541 | 20.016
Devonshire Building | 2017-07-29 09:00 | 50661.2641 | 39.996
Devonshire Building | 2017-07-29 09:15 | 50661.2691 | 20.016
Devonshire Building | 2017-07-29 09:30 | 50661.2791 | 39.996
Devonshire Building | 2017-07-29 09:45 | 50661.2841 | 20.016
Devonshire Building | 2017-07-29 10:00 | 50661.2941 | 39.996
Devonshire Building | 2017-07-29 10:15 | 50661.2992 | 20.016
Devonshire Building | 2017-07-29 10:30 | 50661.3092 | 39.996
Devonshire Building | 2017-07-29 10:45 | 50661.3192 | 39.996
Devonshire Building | 2017-07-29 11:00 | 50661.3242 | 20.016
Devonshire Building | 2017-07-29 11:15 | 50661.3342 | 39.996
Devonshire Building | 2017-07-29 11:30 | 50661.3442 | 39.996
Devonshire Building | 2017-07-29 11:45 | 50661.3542 | 39.996
Devonshire Building | 2017-07-29 12:00 | 50661.3592 | 20.016
Devonshire Building | 2017-07-29 12:15 | 50661.3692 | 39.996
Devonshire Building | 2017-07-29 12:30 | 50661.3792 | 39.996
Devonshire Building | 2017-07-29 12:45 | 50661.3892 | 39.996
Devonshire Building | 2017-07-29 13:00 | 50661.3992 | 39.996
Devonshire Building | 2017-07-29 13:15 | 50661.4091 | 39.996
Devonshire Building | 2017-07-29 13:30 | 50661.4191 | 39.996
Devonshire Building | 2017-07-29 13:45 | 50661.4342 | 60.012
Devonshire Building | 2017-07-29 14:00 | 50661.4442 | 39.996
Devonshire Building | 2017-07-29 14:15 | 50661.6891 | 979.992
Devonshire Building | 2017-07-29 14:30 | 50661.9591 | 1080
Devonshire Building | 2017-07-29 14:45 | 50661.9791 | 79.992
Devonshire Building | 2017-07-29 15:00 | 50661.9941 | 60.012
Devonshire Building | 2017-07-29 15:15 | 50662.0092 | 60.012
Devonshire Building | 2017-07-29 15:30 | 50662.0292 | 79.992
Devonshire Building | 2017-07-29 15:45 | 50662.0491 | 79.992
Devonshire Building | 2017-07-29 16:00 | 50662.0691 | 79.992
Devonshire Building | 2017-07-29 16:15 | 50662.0891 | 79.992
Devonshire Building | 2017-07-29 16:30 | 50662.1091 | 79.992
Devonshire Building | 2017-07-29 16:45 | 50662.1291 | 79.992
Devonshire Building | 2017-07-29 17:00 | 50662.1491 | 79.992
Devonshire Building | 2017-07-29 17:15 | 50662.1691 | 79.992
Devonshire Building | 2017-07-29 17:30 | 50662.1891 | 79.992
Devonshire Building | 2017-07-29 17:45 | 50662.2041 | 60.012
Devonshire Building | 2017-07-29 18:00 | 50662.2241 | 79.992
Devonshire Building | 2017-07-29 18:15 | 50662.2391 | 60.012
Devonshire Building | 2017-07-29 18:30 | 50662.2541 | 60.012
Devonshire Building | 2017-07-29 18:45 | 50662.2691 | 60.012
Devonshire Building | 2017-07-29 19:00 | 50662.2841 | 60.012
Devonshire Building | 2017-07-29 19:15 | 50662.2992 | 60.012
Devonshire Building | 2017-07-29 19:30 | 50662.3142 | 60.012
Devonshire Building | 2017-07-29 19:45 | 50662.3392 | 100.008
Devonshire Building | 2017-07-29 20:00 | 50662.3692 | 119.988
Devonshire Building | 2017-07-29 20:15 | 50662.3991 | 119.988
Devonshire Building | 2017-07-29 20:30 | 50662.4291 | 119.988
Devonshire Building | 2017-07-29 20:45 | 50662.4691 | 159.984
Devonshire Building | 2017-07-29 21:00 | 50662.4941 | 100.008
Devonshire Building | 2017-07-29 21:15 | 50662.5191 | 100.008
Devonshire Building | 2017-07-29 21:30 | 50662.5441 | 100.008
Devonshire Building | 2017-07-29 21:45 | 50662.5592 | 60.012
Devonshire Building | 2017-07-29 22:00 | 50662.5692 | 39.996
Devonshire Building | 2017-07-29 22:15 | 50662.5791 | 39.996
Devonshire Building | 2017-07-29 22:30 | 50662.5842 | 20.016
Devonshire Building | 2017-07-29 22:45 | 50662.5942 | 39.996
Devonshire Building | 2017-07-29 23:00 | 50662.6042 | 39.996
Devonshire Building | 2017-07-29 23:15 | 50662.6092 | 20.016
Devonshire Building | 2017-07-29 23:30 | 50662.6192 | 39.996
Devonshire Building | 2017-07-29 23:45 | 50662.6292 | 39.996
Devonshire Building | 2017-07-30 | 50662.6328 | 20.016
Devonshire Building | 2017-07-30 00:15 | 50662.6428 | 39.996
Devonshire Building | 2017-07-30 00:30 | 50662.6528 | 39.996
Devonshire Building | 2017-07-30 00:45 | 50662.6578 | 20.016
Devonshire Building | 2017-07-30 01:00 | 50662.6678 | 39.996
Devonshire Building | 2017-07-30 01:15 | 50662.6728 | 20.016
Devonshire Building | 2017-07-30 01:30 | 50662.6828 | 39.996
Devonshire Building | 2017-07-30 01:45 | 50662.6928 | 39.996
Devonshire Building | 2017-07-30 02:00 | 50662.6978 | 20.016
Devonshire Building | 2017-07-30 02:15 | 50662.7078 | 39.996
Devonshire Building | 2017-07-30 02:30 | 50662.7128 | 20.016
Devonshire Building | 2017-07-30 02:45 | 50662.7228 | 39.996
Devonshire Building | 2017-07-30 03:00 | 50662.7278 | 20.016
Devonshire Building | 2017-07-30 03:15 | 50662.7378 | 39.996
Devonshire Building | 2017-07-30 03:30 | 50662.7428 | 20.016
Devonshire Building | 2017-07-30 03:45 | 50662.7528 | 39.996
Devonshire Building | 2017-07-30 04:00 | 50662.7628 | 39.996
Devonshire Building | 2017-07-30 04:15 | 50662.7678 | 20.016
Devonshire Building | 2017-07-30 04:30 | 50662.7778 | 39.996
Devonshire Building | 2017-07-30 04:45 | 50662.7828 | 20.016
Devonshire Building | 2017-07-30 05:00 | 50662.7928 | 39.996
Devonshire Building | 2017-07-30 05:15 | 50662.7978 | 20.016
Devonshire Building | 2017-07-30 05:30 | 50662.8078 | 39.996
Devonshire Building | 2017-07-30 05:45 | 50662.8128 | 20.016
Devonshire Building | 2017-07-30 06:00 | 50662.8228 | 39.996
Devonshire Building | 2017-07-30 06:15 | 50662.8278 | 20.016
Devonshire Building | 2017-07-30 06:30 | 50662.8378 | 39.996
Devonshire Building | 2017-07-30 06:45 | 50662.8428 | 20.016
Devonshire Building | 2017-07-30 07:00 | 50663.0078 | 659.988
Devonshire Building | 2017-07-30 07:15 | 50663.3578 | 1400.004
Devonshire Building | 2017-07-30 07:30 | 50663.3628 | 20.016
Devonshire Building | 2017-07-30 07:45 | 50663.3728 | 39.996
Devonshire Building | 2017-07-30 08:00 | 50663.3778 | 20.016
Devonshire Building | 2017-07-30 08:15 | 50663.3878 | 39.996
Devonshire Building | 2017-07-30 08:30 | 50663.3929 | 20.016
Devonshire Building | 2017-07-30 08:45 | 50663.4028 | 39.996
Devonshire Building | 2017-07-30 09:00 | 50663.4128 | 39.996
Devonshire Building | 2017-07-30 09:15 | 50663.4179 | 20.016
Devonshire Building | 2017-07-30 09:30 | 50663.4279 | 39.996
Devonshire Building | 2017-07-30 09:45 | 50663.4379 | 39.996
Devonshire Building | 2017-07-30 10:00 | 50663.4478 | 39.996
Devonshire Building | 2017-07-30 10:15 | 50663.4578 | 39.996
Devonshire Building | 2017-07-30 10:30 | 50663.4678 | 39.996
Devonshire Building | 2017-07-30 10:45 | 50663.4778 | 39.996
Devonshire Building | 2017-07-30 11:00 | 50663.4878 | 39.996
Devonshire Building | 2017-07-30 11:15 | 50663.4978 | 39.996
Devonshire Building | 2017-07-30 11:30 | 50663.5078 | 39.996
Devonshire Building | 2017-07-30 11:45 | 50663.5178 | 39.996
Devonshire Building | 2017-07-30 12:00 | 50663.5328 | 60.012
Devonshire Building | 2017-07-30 12:15 | 50663.5428 | 39.996
Devonshire Building | 2017-07-30 12:30 | 50663.5528 | 39.996
Devonshire Building | 2017-07-30 12:45 | 50663.5628 | 39.996
Devonshire Building | 2017-07-30 13:00 | 50663.5728 | 39.996
Devonshire Building | 2017-07-30 13:15 | 50663.5828 | 39.996
Devonshire Building | 2017-07-30 13:30 | 50663.5928 | 39.996
Devonshire Building | 2017-07-30 13:45 | 50663.6028 | 39.996
Devonshire Building | 2017-07-30 14:00 | 50663.6128 | 39.996
Devonshire Building | 2017-07-30 14:15 | 50663.6228 | 39.996
Devonshire Building | 2017-07-30 14:30 | 50663.6328 | 39.996
Devonshire Building | 2017-07-30 14:45 | 50663.6478 | 60.012
Devonshire Building | 2017-07-30 15:00 | 50663.6578 | 39.996
Devonshire Building | 2017-07-30 15:15 | 50663.6628 | 20.016
Devonshire Building | 2017-07-30 15:30 | 50663.6728 | 39.996
Devonshire Building | 2017-07-30 15:45 | 50663.6828 | 39.996
Devonshire Building | 2017-07-30 16:00 | 50663.6928 | 39.996
Devonshire Building | 2017-07-30 16:15 | 50663.6978 | 20.016
Devonshire Building | 2017-07-30 16:30 | 50663.7128 | 60.012
Devonshire Building | 2017-07-30 16:45 | 50663.7428 | 119.988
Devonshire Building | 2017-07-30 17:00 | 50663.7678 | 100.008
Devonshire Building | 2017-07-30 17:15 | 50663.7928 | 100.008
Devonshire Building | 2017-07-30 17:30 | 50663.8128 | 79.992
Devonshire Building | 2017-07-30 17:45 | 50663.8378 | 100.008
Devonshire Building | 2017-07-30 18:00 | 50663.8628 | 100.008
Devonshire Building | 2017-07-30 18:15 | 50663.8879 | 100.008
Devonshire Building | 2017-07-30 18:30 | 50663.9029 | 60.012
Devonshire Building | 2017-07-30 18:45 | 50663.9129 | 39.996
Devonshire Building | 2017-07-30 19:00 | 50663.9229 | 39.996
Devonshire Building | 2017-07-30 19:15 | 50663.9329 | 39.996
Devonshire Building | 2017-07-30 19:30 | 50664.4379 | 2019.996
Devonshire Building | 2017-07-30 19:45 | 50664.4429 | 20.016
Devonshire Building | 2017-07-30 20:00 | 50664.4529 | 39.996
Devonshire Building | 2017-07-30 20:15 | 50664.4579 | 20.016
Devonshire Building | 2017-07-30 20:30 | 50664.4679 | 39.996
Devonshire Building | 2017-07-30 20:45 | 50664.4829 | 60.012
Devonshire Building | 2017-07-30 21:00 | 50664.4879 | 20.016
Devonshire Building | 2017-07-30 21:15 | 50664.4979 | 39.996
Devonshire Building | 2017-07-30 21:30 | 50664.5079 | 39.996
Devonshire Building | 2017-07-30 21:45 | 50664.5129 | 20.016
Devonshire Building | 2017-07-30 22:00 | 50664.5229 | 39.996
Devonshire Building | 2017-07-30 22:15 | 50664.5329 | 39.996
Devonshire Building | 2017-07-30 22:30 | 50664.5429 | 39.996
Devonshire Building | 2017-07-30 22:45 | 50664.5529 | 39.996
Devonshire Building | 2017-07-30 23:00 | 50664.5629 | 39.996
Devonshire Building | 2017-07-30 23:15 | 50664.5729 | 39.996
Devonshire Building | 2017-07-30 23:30 | 50664.5829 | 39.996
Devonshire Building | 2017-07-30 23:45 | 50664.5979 | 60.012
Devonshire Building | 2017-07-31 | 50664.6094 | 39.996
Devonshire Building | 2017-07-31 00:15 | 50664.6194 | 39.996
Devonshire Building | 2017-07-31 00:30 | 50664.6294 | 39.996
Devonshire Building | 2017-07-31 00:45 | 50664.6344 | 20.016
Devonshire Building | 2017-07-31 01:00 | 50664.6444 | 39.996
Devonshire Building | 2017-07-31 01:15 | 50664.6544 | 39.996
Devonshire Building | 2017-07-31 01:30 | 50664.6644 | 39.996
Devonshire Building | 2017-07-31 01:45 | 50664.6744 | 39.996
Devonshire Building | 2017-07-31 02:00 | 50664.6844 | 39.996
Devonshire Building | 2017-07-31 02:15 | 50664.6944 | 39.996
Devonshire Building | 2017-07-31 02:30 | 50664.6994 | 20.016
Devonshire Building | 2017-07-31 02:45 | 50664.7094 | 39.996
Devonshire Building | 2017-07-31 03:00 | 50664.7194 | 39.996
Devonshire Building | 2017-07-31 03:15 | 50664.7294 | 39.996
Devonshire Building | 2017-07-31 03:30 | 50664.7344 | 20.016
Devonshire Building | 2017-07-31 03:45 | 50664.7444 | 39.996
Devonshire Building | 2017-07-31 04:00 | 50664.7544 | 39.996
Devonshire Building | 2017-07-31 04:15 | 50664.7594 | 20.016
Devonshire Building | 2017-07-31 04:30 | 50664.7694 | 39.996
Devonshire Building | 2017-07-31 04:45 | 50664.7794 | 39.996
Devonshire Building | 2017-07-31 05:00 | 50664.7844 | 20.016
Devonshire Building | 2017-07-31 05:15 | 50664.8044 | 79.992
Devonshire Building | 2017-07-31 05:30 | 50664.8144 | 39.996
Devonshire Building | 2017-07-31 05:45 | 50664.8244 | 39.996
Devonshire Building | 2017-07-31 06:00 | 50664.8294 | 20.016
Devonshire Building | 2017-07-31 06:15 | 50664.8444 | 60.012
Devonshire Building | 2017-07-31 06:30 | 50664.8544 | 39.996
Devonshire Building | 2017-07-31 06:45 | 50664.8644 | 39.996
Devonshire Building | 2017-07-31 07:00 | 50664.8744 | 39.996
Devonshire Building | 2017-07-31 07:15 | 50664.8894 | 60.012
Devonshire Building | 2017-07-31 07:30 | 50665.4094 | 2080.008
Devonshire Building | 2017-07-31 07:45 | 50665.4344 | 100.008
Devonshire Building | 2017-07-31 08:00 | 50665.4644 | 119.988
Devonshire Building | 2017-07-31 08:15 | 50665.5044 | 159.984
Devonshire Building | 2017-07-31 08:30 | 50665.5494 | 180
Devonshire Building | 2017-07-31 08:45 | 50665.6294 | 320.004
Devonshire Building | 2017-07-31 09:00 | 50665.7244 | 380.016
Devonshire Building | 2017-07-31 09:15 | 50666.0144 | 1159.992
Devonshire Building | 2017-07-31 09:30 | 50666.4444 | 1720.008
Devonshire Building | 2017-07-31 09:45 | 50666.5244 | 320.004
Devonshire Building | 2017-07-31 10:00 | 50666.6094 | 339.984
Devonshire Building | 2017-07-31 10:15 | 50666.6894 | 320.004
Devonshire Building | 2017-07-31 10:30 | 50666.7744 | 339.984
Devonshire Building | 2017-07-31 10:45 | 50667.3844 | 2440.008
Devonshire Building | 2017-07-31 11:00 | 50667.4294 | 180
Devonshire Building | 2017-07-31 11:15 | 50667.4744 | 180
Devonshire Building | 2017-07-31 11:30 | 50667.5244 | 200.016
Devonshire Building | 2017-07-31 11:45 | 50667.5694 | 180
Devonshire Building | 2017-07-31 12:00 | 50667.8344 | 1059.984
Devonshire Building | 2017-07-31 12:15 | 50668.1844 | 1400.004
Devonshire Building | 2017-07-31 12:30 | 50668.2344 | 200.016
Devonshire Building | 2017-07-31 12:45 | 50668.2844 | 200.016
Devonshire Building | 2017-07-31 13:00 | 50668.3344 | 200.016
Devonshire Building | 2017-07-31 13:15 | 50668.3894 | 219.996
Devonshire Building | 2017-07-31 13:30 | 50668.4344 | 180
Devonshire Building | 2017-07-31 13:45 | 50668.9644 | 2120.004
Devonshire Building | 2017-07-31 14:00 | 50669.0044 | 159.984
Devonshire Building | 2017-07-31 14:15 | 50669.0394 | 140.004
Devonshire Building | 2017-07-31 14:30 | 50669.0794 | 159.984
Devonshire Building | 2017-07-31 14:45 | 50669.1244 | 180
Devonshire Building | 2017-07-31 15:00 | 50669.1594 | 140.004
Devonshire Building | 2017-07-31 15:15 | 50669.1994 | 159.984
Devonshire Building | 2017-07-31 15:30 | 50669.7444 | 2180.016
Devonshire Building | 2017-07-31 15:45 | 50669.7844 | 159.984
Devonshire Building | 2017-07-31 16:00 | 50669.8244 | 159.984
Devonshire Building | 2017-07-31 16:15 | 50669.8644 | 159.984
Devonshire Building | 2017-07-31 16:30 | 50669.9044 | 159.984
Devonshire Building | 2017-07-31 16:45 | 50669.9494 | 180
Devonshire Building | 2017-07-31 17:00 | 50669.9894 | 159.984
Devonshire Building | 2017-07-31 17:15 | 50670.0244 | 140.004
Devonshire Building | 2017-07-31 17:30 | 50670.0544 | 119.988
Devonshire Building | 2017-07-31 17:45 | 50670.0894 | 140.004
Devonshire Building | 2017-07-31 18:00 | 50670.1194 | 119.988
Devonshire Building | 2017-07-31 18:15 | 50670.1494 | 119.988
Devonshire Building | 2017-07-31 18:30 | 50670.6694 | 2080.008
Devonshire Building | 2017-07-31 18:45 | 50670.6844 | 60.012
Devonshire Building | 2017-07-31 19:00 | 50670.6994 | 60.012
Devonshire Building | 2017-07-31 19:15 | 50670.7094 | 39.996
Devonshire Building | 2017-07-31 19:30 | 50670.7244 | 60.012
Devonshire Building | 2017-07-31 19:45 | 50670.7394 | 60.012
Devonshire Building | 2017-07-31 20:00 | 50670.7544 | 60.012
Devonshire Building | 2017-07-31 20:15 | 50670.7694 | 60.012
Devonshire Building | 2017-07-31 20:30 | 50670.7844 | 60.012
Devonshire Building | 2017-07-31 20:45 | 50670.8094 | 100.008
Devonshire Building | 2017-07-31 21:00 | 50670.8194 | 39.996
Devonshire Building | 2017-07-31 21:15 | 50670.8344 | 60.012
Devonshire Building | 2017-07-31 21:30 | 50670.8444 | 39.996
Devonshire Building | 2017-07-31 21:45 | 50670.8544 | 39.996
Devonshire Building | 2017-07-31 22:00 | 50670.8694 | 60.012
Devonshire Building | 2017-07-31 22:15 | 50670.8794 | 39.996
Devonshire Building | 2017-07-31 22:30 | 50670.8894 | 39.996
Devonshire Building | 2017-07-31 22:45 | 50670.8994 | 39.996
Devonshire Building | 2017-07-31 23:00 | 50670.9144 | 60.012
Devonshire Building | 2017-07-31 23:15 | 50670.9244 | 39.996
Devonshire Building | 2017-07-31 23:30 | 50670.9344 | 39.996
Devonshire Building | 2017-07-31 23:45 | 50670.9444 | 39.996
Devonshire Building | 2017-08-01 | 50670.9531 | 39.996
Devonshire Building | 2017-08-01 00:15 | 50670.9631 | 39.996
Devonshire Building | 2017-08-01 00:30 | 50670.9731 | 39.996
Devonshire Building | 2017-08-01 00:45 | 50670.9831 | 39.996
Devonshire Building | 2017-08-01 01:00 | 50670.9931 | 39.996
Devonshire Building | 2017-08-01 01:15 | 50671.0031 | 39.996
Devonshire Building | 2017-08-01 01:30 | 50671.0131 | 39.996
Devonshire Building | 2017-08-01 01:45 | 50671.0231 | 39.996
Devonshire Building | 2017-08-01 02:00 | 50671.0331 | 39.996
Devonshire Building | 2017-08-01 02:15 | 50671.0431 | 39.996
Devonshire Building | 2017-08-01 02:30 | 50671.0481 | 20.016
Devonshire Building | 2017-08-01 02:45 | 50671.0581 | 39.996
Devonshire Building | 2017-08-01 03:00 | 50671.0681 | 39.996
Devonshire Building | 2017-08-01 03:15 | 50671.0781 | 39.996
Devonshire Building | 2017-08-01 03:30 | 50671.0881 | 39.996
Devonshire Building | 2017-08-01 03:45 | 50671.0931 | 20.016
Devonshire Building | 2017-08-01 04:00 | 50671.1031 | 39.996
Devonshire Building | 2017-08-01 04:15 | 50671.1131 | 39.996
Devonshire Building | 2017-08-01 04:30 | 50671.1181 | 20.016
Devonshire Building | 2017-08-01 04:45 | 50671.1281 | 39.996
Devonshire Building | 2017-08-01 05:00 | 50671.1431 | 60.012
Devonshire Building | 2017-08-01 05:15 | 50671.1531 | 39.996
Devonshire Building | 2017-08-01 05:30 | 50671.1581 | 20.016
Devonshire Building | 2017-08-01 05:45 | 50671.1681 | 39.996
Devonshire Building | 2017-08-01 06:00 | 50671.1781 | 39.996
Devonshire Building | 2017-08-01 06:15 | 50671.1931 | 60.012
Devonshire Building | 2017-08-01 06:30 | 50671.2031 | 39.996
Devonshire Building | 2017-08-01 06:45 | 50671.2131 | 39.996
Devonshire Building | 2017-08-01 07:00 | 50671.2281 | 60.012
Devonshire Building | 2017-08-01 07:15 | 50671.2381 | 39.996
Devonshire Building | 2017-08-01 07:30 | 50671.7631 | 2099.988
Devonshire Building | 2017-08-01 07:45 | 50671.7881 | 100.008
Devonshire Building | 2017-08-01 08:00 | 50671.8281 | 159.984
Devonshire Building | 2017-08-01 08:15 | 50671.8681 | 159.984
Devonshire Building | 2017-08-01 08:30 | 50671.9131 | 180
Devonshire Building | 2017-08-01 08:45 | 50671.9581 | 180
Devonshire Building | 2017-08-01 09:00 | 50672.0081 | 200.016
Devonshire Building | 2017-08-01 09:15 | 50672.5781 | 2279.988
Devonshire Building | 2017-08-01 09:30 | 50672.6481 | 280.008
Devonshire Building | 2017-08-01 09:45 | 50672.7081 | 240.012
Devonshire Building | 2017-08-01 10:00 | 50672.7831 | 299.988
Devonshire Building | 2017-08-01 10:15 | 50672.8431 | 240.012
Devonshire Building | 2017-08-01 10:30 | 50673.4081 | 2260.008
Devonshire Building | 2017-08-01 10:45 | 50673.4831 | 299.988
Devonshire Building | 2017-08-01 11:00 | 50673.5631 | 320.004
Devonshire Building | 2017-08-01 11:15 | 50673.6331 | 280.008
Devonshire Building | 2017-08-01 11:30 | 50673.7031 | 280.008
Devonshire Building | 2017-08-01 11:45 | 50673.8831 | 720
Devonshire Building | 2017-08-01 12:00 | 50674.3531 | 1879.992
Devonshire Building | 2017-08-01 12:15 | 50674.4031 | 200.016
Devonshire Building | 2017-08-01 12:30 | 50674.4481 | 180
Devonshire Building | 2017-08-01 12:45 | 50674.4931 | 180
Devonshire Building | 2017-08-01 13:00 | 50674.5431 | 200.016
Devonshire Building | 2017-08-01 13:15 | 50675.0931 | 2199.996
Devonshire Building | 2017-08-01 13:30 | 50675.1231 | 119.988
Devonshire Building | 2017-08-01 13:45 | 50675.1631 | 159.984
Devonshire Building | 2017-08-01 14:00 | 50675.1981 | 140.004
Devonshire Building | 2017-08-01 14:15 | 50675.2431 | 180
Devonshire Building | 2017-08-01 14:30 | 50675.2981 | 219.996
Devonshire Building | 2017-08-01 14:45 | 50675.3631 | 259.992
Devonshire Building | 2017-08-01 15:00 | 50675.7131 | 1400.004
Devonshire Building | 2017-08-01 15:15 | 50676.0031 | 1159.992
Devonshire Building | 2017-08-01 15:30 | 50676.0631 | 240.012
Devonshire Building | 2017-08-01 15:45 | 50676.1231 | 240.012
Devonshire Building | 2017-08-01 16:00 | 50676.1831 | 240.012
Devonshire Building | 2017-08-01 16:15 | 50676.2431 | 240.012
Devonshire Building | 2017-08-01 16:30 | 50676.6681 | 1699.992
Devonshire Building | 2017-08-01 16:45 | 50676.8431 | 699.984
Devonshire Building | 2017-08-01 17:00 | 50676.8781 | 140.004
Devonshire Building | 2017-08-01 17:15 | 50676.9131 | 140.004
Devonshire Building | 2017-08-01 17:30 | 50676.9481 | 140.004
Devonshire Building | 2017-08-01 17:45 | 50676.9831 | 140.004
Devonshire Building | 2017-08-01 18:00 | 50677.0081 | 100.008
Devonshire Building | 2017-08-01 18:15 | 50677.0331 | 100.008
Devonshire Building | 2017-08-01 18:30 | 50677.0581 | 100.008
Devonshire Building | 2017-08-01 18:45 | 50677.0781 | 79.992
Devonshire Building | 2017-08-01 19:00 | 50677.1081 | 119.988
Devonshire Building | 2017-08-01 19:15 | 50677.1231 | 60.012
Devonshire Building | 2017-08-01 19:30 | 50677.1381 | 60.012
Devonshire Building | 2017-08-01 19:45 | 50677.1581 | 79.992
Devonshire Building | 2017-08-01 20:00 | 50677.1731 | 60.012
Devonshire Building | 2017-08-01 20:15 | 50677.1882 | 60.012
Devonshire Building | 2017-08-01 20:30 | 50677.1981 | 39.996
Devonshire Building | 2017-08-01 20:45 | 50677.2332 | 140.004
Devonshire Building | 2017-08-01 21:00 | 50677.2431 | 39.996
Devonshire Building | 2017-08-01 21:15 | 50677.2482 | 20.016
Devonshire Building | 2017-08-01 21:30 | 50677.2582 | 39.996
Devonshire Building | 2017-08-01 21:45 | 50677.2632 | 20.016
Devonshire Building | 2017-08-01 22:00 | 50677.2682 | 20.016
Devonshire Building | 2017-08-01 22:15 | 50677.2782 | 39.996
Devonshire Building | 2017-08-01 22:30 | 50677.2832 | 20.016
Devonshire Building | 2017-08-01 22:45 | 50677.2882 | 20.016
Devonshire Building | 2017-08-01 23:00 | 50677.2982 | 39.996
Devonshire Building | 2017-08-01 23:15 | 50677.3032 | 20.016
Devonshire Building | 2017-08-01 23:30 | 50677.3082 | 20.016
Devonshire Building | 2017-08-01 23:45 | 50677.3182 | 39.996
Devonshire Building | 2017-08-02 | 50677.3242 | 20.016
Devonshire Building | 2017-08-02 00:15 | 50677.3292 | 20.016
Devonshire Building | 2017-08-02 00:30 | 50677.3392 | 39.996
Devonshire Building | 2017-08-02 00:45 | 50677.3442 | 20.016
Devonshire Building | 2017-08-02 01:00 | 50677.3492 | 20.016
Devonshire Building | 2017-08-02 01:15 | 50677.3592 | 39.996
Devonshire Building | 2017-08-02 01:30 | 50677.3642 | 20.016
Devonshire Building | 2017-08-02 01:45 | 50677.3692 | 20.016
Devonshire Building | 2017-08-02 02:00 | 50677.3742 | 20.016
Devonshire Building | 2017-08-02 02:15 | 50677.3842 | 39.996
Devonshire Building | 2017-08-02 02:30 | 50677.3892 | 20.016
Devonshire Building | 2017-08-02 02:45 | 50677.3942 | 20.016
Devonshire Building | 2017-08-02 03:00 | 50677.8542 | 1839.996
Devonshire Building | 2017-08-02 03:15 | 50677.9092 | 219.996
Devonshire Building | 2017-08-02 03:30 | 50677.9143 | 20.016
Devonshire Building | 2017-08-02 03:45 | 50677.9193 | 20.016
Devonshire Building | 2017-08-02 04:00 | 50677.9243 | 20.016
Devonshire Building | 2017-08-02 04:15 | 50677.9293 | 20.016
Devonshire Building | 2017-08-02 04:30 | 50677.9393 | 39.996
Devonshire Building | 2017-08-02 04:45 | 50677.9443 | 20.016
Devonshire Building | 2017-08-02 05:00 | 50677.9543 | 39.996
Devonshire Building | 2017-08-02 05:15 | 50677.9593 | 20.016
Devonshire Building | 2017-08-02 05:30 | 50677.9643 | 20.016
Devonshire Building | 2017-08-02 05:45 | 50677.9743 | 39.996
Devonshire Building | 2017-08-02 06:00 | 50677.9793 | 20.016
Devonshire Building | 2017-08-02 06:15 | 50677.9893 | 39.996
Devonshire Building | 2017-08-02 06:30 | 50677.9943 | 20.016
Devonshire Building | 2017-08-02 06:45 | 50678.0043 | 39.996
Devonshire Building | 2017-08-02 07:00 | 50678.0143 | 39.996
Devonshire Building | 2017-08-02 07:15 | 50678.0243 | 39.996
Devonshire Building | 2017-08-02 07:30 | 50678.0343 | 39.996
Devonshire Building | 2017-08-02 07:45 | 50678.0643 | 119.988
Devonshire Building | 2017-08-02 08:00 | 50678.1043 | 159.984
Devonshire Building | 2017-08-02 08:15 | 50678.7243 | 2480.004
Devonshire Building | 2017-08-02 08:30 | 50678.8643 | 560.016
Devonshire Building | 2017-08-02 08:45 | 50679.0143 | 600.012
Devonshire Building | 2017-08-02 09:00 | 50679.1343 | 479.988
Devonshire Building | 2017-08-02 09:15 | 50679.2293 | 380.016
Devonshire Building | 2017-08-02 09:30 | 50679.3293 | 399.996
Devonshire Building | 2017-08-02 09:45 | 50679.4393 | 439.992
Devonshire Building | 2017-08-02 10:00 | 50680.0743 | 2540.016
Devonshire Building | 2017-08-02 10:15 | 50680.1943 | 479.988
Devonshire Building | 2017-08-02 10:30 | 50680.2843 | 360
Devonshire Building | 2017-08-02 10:45 | 50680.3643 | 320.004
Devonshire Building | 2017-08-02 11:00 | 50680.4393 | 299.988
Devonshire Building | 2017-08-02 11:15 | 50680.5093 | 280.008
Devonshire Building | 2017-08-02 11:30 | 50680.5743 | 259.992
Devonshire Building | 2017-08-02 11:45 | 50681.1493 | 2300.004
Devonshire Building | 2017-08-02 12:00 | 50681.1943 | 180
Devonshire Building | 2017-08-02 12:15 | 50681.2393 | 180
Devonshire Building | 2017-08-02 12:30 | 50681.2793 | 159.984
Devonshire Building | 2017-08-02 12:45 | 50681.3243 | 180
Devonshire Building | 2017-08-02 13:00 | 50681.6893 | 1460.016
Devonshire Building | 2017-08-02 13:15 | 50681.9343 | 979.992
Devonshire Building | 2017-08-02 13:30 | 50681.9743 | 159.984
Devonshire Building | 2017-08-02 13:45 | 50682.0093 | 140.004
Devonshire Building | 2017-08-02 14:00 | 50682.0493 | 159.984
Devonshire Building | 2017-08-02 14:15 | 50682.0843 | 140.004
Devonshire Building | 2017-08-02 14:30 | 50682.1143 | 119.988
Devonshire Building | 2017-08-02 14:45 | 50682.1493 | 140.004
Devonshire Building | 2017-08-02 15:00 | 50682.7093 | 2239.992
Devonshire Building | 2017-08-02 15:15 | 50682.7693 | 240.012
Devonshire Building | 2017-08-02 15:30 | 50682.8343 | 259.992
Devonshire Building | 2017-08-02 15:45 | 50682.8993 | 259.992
Devonshire Building | 2017-08-02 16:00 | 50682.9593 | 240.012
Devonshire Building | 2017-08-02 16:15 | 50683.0243 | 259.992
Devonshire Building | 2017-08-02 16:30 | 50683.1043 | 320.004
Devonshire Building | 2017-08-02 16:45 | 50683.6743 | 2279.988
Devonshire Building | 2017-08-02 17:00 | 50683.7493 | 299.988
Devonshire Building | 2017-08-02 17:15 | 50683.8193 | 280.008
Devonshire Building | 2017-08-02 17:30 | 50683.8743 | 219.996
Devonshire Building | 2017-08-02 17:45 | 50683.9243 | 200.016
Devonshire Building | 2017-08-02 18:00 | 50683.9643 | 159.984
Devonshire Building | 2017-08-02 18:15 | 50683.9993 | 140.004
Devonshire Building | 2017-08-02 18:30 | 50684.0293 | 119.988
Devonshire Building | 2017-08-02 18:45 | 50684.0643 | 140.004
Devonshire Building | 2017-08-02 19:00 | 50684.0893 | 100.008
Devonshire Building | 2017-08-02 19:15 | 50684.1143 | 100.008
Devonshire Building | 2017-08-02 19:30 | 50684.1343 | 79.992
Devonshire Building | 2017-08-02 19:45 | 50684.1593 | 100.008
Devonshire Building | 2017-08-02 20:00 | 50684.1793 | 79.992
Devonshire Building | 2017-08-02 20:15 | 50684.1943 | 60.012
Devonshire Building | 2017-08-02 20:30 | 50684.2143 | 79.992
Devonshire Building | 2017-08-02 20:45 | 50684.2493 | 140.004
Devonshire Building | 2017-08-02 21:00 | 50684.2593 | 39.996
Devonshire Building | 2017-08-02 21:15 | 50684.2643 | 20.016
Devonshire Building | 2017-08-02 21:30 | 50684.2743 | 39.996
Devonshire Building | 2017-08-02 21:45 | 50684.2793 | 20.016
Devonshire Building | 2017-08-02 22:00 | 50684.2893 | 39.996
Devonshire Building | 2017-08-02 22:15 | 50684.2993 | 39.996
Devonshire Building | 2017-08-02 22:30 | 50684.3043 | 20.016
Devonshire Building | 2017-08-02 22:45 | 50684.3143 | 39.996
Devonshire Building | 2017-08-02 23:00 | 50684.3193 | 20.016
Devonshire Building | 2017-08-02 23:15 | 50684.3293 | 39.996
Devonshire Building | 2017-08-02 23:30 | 50684.3393 | 39.996
Devonshire Building | 2017-08-02 23:45 | 50684.3443 | 20.016
Devonshire Building | 2017-08-03 | 50684.3555 | 39.996
Devonshire Building | 2017-08-03 00:15 | 50684.3605 | 20.016
Devonshire Building | 2017-08-03 00:30 | 50684.3705 | 39.996
Devonshire Building | 2017-08-03 00:45 | 50684.3755 | 20.016
Devonshire Building | 2017-08-03 01:00 | 50684.3855 | 39.996
Devonshire Building | 2017-08-03 01:15 | 50684.3905 | 20.016
Devonshire Building | 2017-08-03 01:30 | 50684.4005 | 39.996
Devonshire Building | 2017-08-03 01:45 | 50684.4055 | 20.016
Devonshire Building | 2017-08-03 02:00 | 50684.4155 | 39.996
Devonshire Building | 2017-08-03 02:15 | 50684.4205 | 20.016
Devonshire Building | 2017-08-03 02:30 | 50684.4305 | 39.996
Devonshire Building | 2017-08-03 02:45 | 50684.4355 | 20.016
Devonshire Building | 2017-08-03 03:00 | 50684.4455 | 39.996
Devonshire Building | 2017-08-03 03:15 | 50684.4505 | 20.016
Devonshire Building | 2017-08-03 03:30 | 50684.4605 | 39.996
Devonshire Building | 2017-08-03 03:45 | 50684.4655 | 20.016
Devonshire Building | 2017-08-03 04:00 | 50684.4705 | 20.016
Devonshire Building | 2017-08-03 04:15 | 50684.4805 | 39.996
Devonshire Building | 2017-08-03 04:30 | 50684.4855 | 20.016
Devonshire Building | 2017-08-03 04:45 | 50684.9755 | 1959.984
Devonshire Building | 2017-08-03 05:00 | 50685.0005 | 100.008
Devonshire Building | 2017-08-03 05:15 | 50685.0105 | 39.996
Devonshire Building | 2017-08-03 05:30 | 50685.0205 | 39.996
Devonshire Building | 2017-08-03 05:45 | 50685.0305 | 39.996
Devonshire Building | 2017-08-03 06:00 | 50685.0405 | 39.996
Devonshire Building | 2017-08-03 06:15 | 50685.0505 | 39.996
Devonshire Building | 2017-08-03 06:30 | 50685.0605 | 39.996
Devonshire Building | 2017-08-03 06:45 | 50685.0705 | 39.996
Devonshire Building | 2017-08-03 07:00 | 50685.0805 | 39.996
Devonshire Building | 2017-08-03 07:15 | 50685.1105 | 119.988
Devonshire Building | 2017-08-03 07:30 | 50685.1305 | 79.992
Devonshire Building | 2017-08-03 07:45 | 50685.1555 | 100.008
Devonshire Building | 2017-08-03 08:00 | 50685.1905 | 140.004
Devonshire Building | 2017-08-03 08:15 | 50685.2305 | 159.984
Devonshire Building | 2017-08-03 08:30 | 50685.2805 | 200.016
Devonshire Building | 2017-08-03 08:45 | 50685.6355 | 1419.984
Devonshire Building | 2017-08-03 09:00 | 50685.9455 | 1239.984
Devonshire Building | 2017-08-03 09:15 | 50686.0355 | 360
Devonshire Building | 2017-08-03 09:30 | 50686.1455 | 439.992
Devonshire Building | 2017-08-03 09:45 | 50686.3005 | 619.992
Devonshire Building | 2017-08-03 10:00 | 50686.4405 | 560.016
Devonshire Building | 2017-08-03 10:15 | 50686.5505 | 439.992
Devonshire Building | 2017-08-03 10:30 | 50686.6405 | 360
Devonshire Building | 2017-08-03 10:45 | 50687.1555 | 2059.992
Devonshire Building | 2017-08-03 11:00 | 50687.3155 | 640.008
Devonshire Building | 2017-08-03 11:15 | 50687.3955 | 320.004
Devonshire Building | 2017-08-03 11:30 | 50687.4555 | 240.012
Devonshire Building | 2017-08-03 11:45 | 50687.5205 | 259.992
Devonshire Building | 2017-08-03 12:00 | 50687.5955 | 299.988
Devonshire Building | 2017-08-03 12:15 | 50687.6855 | 360
Devonshire Building | 2017-08-03 12:30 | 50688.3205 | 2540.016
Devonshire Building | 2017-08-03 12:45 | 50688.4905 | 680.004
Devonshire Building | 2017-08-03 13:00 | 50688.6405 | 600.012
Devonshire Building | 2017-08-03 13:15 | 50688.7805 | 560.016
Devonshire Building | 2017-08-03 13:30 | 50688.9005 | 479.988
Devonshire Building | 2017-08-03 13:45 | 50689.0105 | 439.992
Devonshire Building | 2017-08-03 14:00 | 50689.1105 | 399.996
Devonshire Building | 2017-08-03 14:15 | 50689.7555 | 2580.012
Devonshire Building | 2017-08-03 14:30 | 50689.8755 | 479.988
Devonshire Building | 2017-08-03 14:45 | 50690.0055 | 519.984
Devonshire Building | 2017-08-03 15:00 | 50690.1205 | 460.008
Devonshire Building | 2017-08-03 15:15 | 50690.2305 | 439.992
Devonshire Building | 2017-08-03 15:30 | 50690.3255 | 380.016
Devonshire Building | 2017-08-03 15:45 | 50690.7555 | 1720.008
Devonshire Building | 2017-08-03 16:00 | 50690.9605 | 820.008
Devonshire Building | 2017-08-03 16:15 | 50690.9955 | 140.004
Devonshire Building | 2017-08-03 16:30 | 50691.0405 | 180
Devonshire Building | 2017-08-03 16:45 | 50691.0805 | 159.984
Devonshire Building | 2017-08-03 17:00 | 50691.1255 | 180
Devonshire Building | 2017-08-03 17:15 | 50691.1605 | 140.004
Devonshire Building | 2017-08-03 17:30 | 50691.2005 | 159.984
Devonshire Building | 2017-08-03 17:45 | 50691.2355 | 140.004
Devonshire Building | 2017-08-03 18:00 | 50691.2705 | 140.004
Devonshire Building | 2017-08-03 18:15 | 50691.3055 | 140.004
Devonshire Building | 2017-08-03 18:30 | 50691.3355 | 119.988
Devonshire Building | 2017-08-03 18:45 | 50691.3655 | 119.988
Devonshire Building | 2017-08-03 19:00 | 50691.4005 | 140.004
Devonshire Building | 2017-08-03 19:15 | 50691.4255 | 100.008
Devonshire Building | 2017-08-03 19:30 | 50691.4505 | 100.008
Devonshire Building | 2017-08-03 19:45 | 50691.4705 | 79.992
Devonshire Building | 2017-08-03 20:00 | 50691.4905 | 79.992
Devonshire Building | 2017-08-03 20:15 | 50691.5805 | 360
Devonshire Building | 2017-08-03 20:30 | 50692.0105 | 1720.008
Devonshire Building | 2017-08-03 20:45 | 50692.0255 | 60.012
Devonshire Building | 2017-08-03 21:00 | 50692.0355 | 39.996
Devonshire Building | 2017-08-03 21:15 | 50692.0405 | 20.016
Devonshire Building | 2017-08-03 21:30 | 50692.0455 | 20.016
Devonshire Building | 2017-08-03 21:45 | 50692.0505 | 20.016
Devonshire Building | 2017-08-03 22:00 | 50692.0555 | 20.016
Devonshire Building | 2017-08-03 22:15 | 50692.0605 | 20.016
Devonshire Building | 2017-08-03 22:30 | 50692.0655 | 20.016
Devonshire Building | 2017-08-03 22:45 | 50692.0705 | 20.016
Devonshire Building | 2017-08-03 23:00 | 50692.0755 | 20.016
Devonshire Building | 2017-08-03 23:15 | 50692.0855 | 39.996
Devonshire Building | 2017-08-03 23:30 | 50692.0905 | 20.016
Devonshire Building | 2017-08-03 23:45 | 50692.0955 | 20.016
Devonshire Building | 2017-08-04 | 50692.1016 | 20.016
Devonshire Building | 2017-08-04 00:15 | 50692.1066 | 20.016
Devonshire Building | 2017-08-04 00:30 | 50692.1116 | 20.016
Devonshire Building | 2017-08-04 00:45 | 50692.1166 | 20.016
Devonshire Building | 2017-08-04 01:00 | 50692.1216 | 20.016
Devonshire Building | 2017-08-04 01:15 | 50692.1316 | 39.996
Devonshire Building | 2017-08-04 01:30 | 50692.1366 | 20.016
Devonshire Building | 2017-08-04 01:45 | 50692.1416 | 20.016
Devonshire Building | 2017-08-04 02:00 | 50692.1466 | 20.016
Devonshire Building | 2017-08-04 02:15 | 50692.1516 | 20.016
Devonshire Building | 2017-08-04 02:30 | 50692.1566 | 20.016
Devonshire Building | 2017-08-04 02:45 | 50692.1666 | 39.996
Devonshire Building | 2017-08-04 03:00 | 50692.1716 | 20.016
Devonshire Building | 2017-08-04 03:15 | 50692.1766 | 20.016
Devonshire Building | 2017-08-04 03:30 | 50692.1816 | 20.016
Devonshire Building | 2017-08-04 03:45 | 50692.1866 | 20.016
Devonshire Building | 2017-08-04 04:00 | 50692.1916 | 20.016
Devonshire Building | 2017-08-04 04:15 | 50692.1966 | 20.016
Devonshire Building | 2017-08-04 04:30 | 50692.2016 | 20.016
Devonshire Building | 2017-08-04 04:45 | 50692.2066 | 20.016
Devonshire Building | 2017-08-04 05:00 | 50692.2166 | 39.996
Devonshire Building | 2017-08-04 05:15 | 50692.2216 | 20.016
Devonshire Building | 2017-08-04 05:30 | 50692.2266 | 20.016
Devonshire Building | 2017-08-04 05:45 | 50692.2366 | 39.996
Devonshire Building | 2017-08-04 06:00 | 50692.2416 | 20.016
Devonshire Building | 2017-08-04 06:15 | 50692.2516 | 39.996
Devonshire Building | 2017-08-04 06:30 | 50692.2616 | 39.996
Devonshire Building | 2017-08-04 06:45 | 50692.2766 | 60.012
Devonshire Building | 2017-08-04 07:00 | 50692.3016 | 100.008
Devonshire Building | 2017-08-04 07:15 | 50692.3366 | 140.004
Devonshire Building | 2017-08-04 07:30 | 50692.4066 | 280.008
Devonshire Building | 2017-08-04 07:45 | 50692.9466 | 2160
Devonshire Building | 2017-08-04 08:00 | 50693.0416 | 380.016
Devonshire Building | 2017-08-04 08:15 | 50693.1367 | 380.016
Devonshire Building | 2017-08-04 08:30 | 50693.2216 | 339.984
Devonshire Building | 2017-08-04 08:45 | 50693.2966 | 299.988
Devonshire Building | 2017-08-04 09:00 | 50693.3666 | 280.008
Devonshire Building | 2017-08-04 09:15 | 50693.4416 | 299.988
Devonshire Building | 2017-08-04 09:30 | 50693.5166 | 299.988
Devonshire Building | 2017-08-04 09:45 | 50693.5916 | 299.988
Devonshire Building | 2017-08-04 10:00 | 50694.2016 | 2440.008
Devonshire Building | 2017-08-04 10:15 | 50694.2866 | 339.984
Devonshire Building | 2017-08-04 10:30 | 50694.3566 | 280.008
Devonshire Building | 2017-08-04 10:45 | 50694.4166 | 240.012
Devonshire Building | 2017-08-04 11:00 | 50694.4766 | 240.012
Devonshire Building | 2017-08-04 11:15 | 50694.5266 | 200.016
Devonshire Building | 2017-08-04 11:30 | 50694.8566 | 1320.012
Devonshire Building | 2017-08-04 11:45 | 50695.1366 | 1119.996
Devonshire Building | 2017-08-04 12:00 | 50695.1716 | 140.004
Devonshire Building | 2017-08-04 12:15 | 50695.2116 | 159.984
Devonshire Building | 2017-08-04 12:30 | 50695.2566 | 180
Devonshire Building | 2017-08-04 12:45 | 50695.2966 | 159.984
Devonshire Building | 2017-08-04 13:00 | 50695.3316 | 140.004
Devonshire Building | 2017-08-04 13:15 | 50695.3766 | 180
Devonshire Building | 2017-08-04 13:30 | 50695.9516 | 2300.004
Devonshire Building | 2017-08-04 13:45 | 50695.9866 | 140.004
Devonshire Building | 2017-08-04 14:00 | 50696.0216 | 140.004
Devonshire Building | 2017-08-04 14:15 | 50696.0616 | 159.984
Devonshire Building | 2017-08-04 14:30 | 50696.0916 | 119.988
Devonshire Building | 2017-08-04 14:45 | 50696.1266 | 140.004
Devonshire Building | 2017-08-04 15:00 | 50696.1666 | 159.984
Devonshire Building | 2017-08-04 15:15 | 50696.2266 | 240.012
Devonshire Building | 2017-08-04 15:30 | 50696.8216 | 2379.996
Devonshire Building | 2017-08-04 15:45 | 50696.8616 | 159.984
Devonshire Building | 2017-08-04 16:00 | 50696.8966 | 140.004
Devonshire Building | 2017-08-04 16:15 | 50696.9366 | 159.984
Devonshire Building | 2017-08-04 16:30 | 50696.9766 | 159.984
Devonshire Building | 2017-08-04 16:45 | 50697.0116 | 140.004
Devonshire Building | 2017-08-04 17:00 | 50697.0666 | 219.996
Devonshire Building | 2017-08-04 17:15 | 50697.1316 | 259.992
Devonshire Building | 2017-08-04 17:30 | 50697.1966 | 259.992
Devonshire Building | 2017-08-04 17:45 | 50697.2566 | 240.012
Devonshire Building | 2017-08-04 18:00 | 50697.3166 | 240.012
Devonshire Building | 2017-08-04 18:15 | 50697.3816 | 259.992
Devonshire Building | 2017-08-04 18:30 | 50697.4416 | 240.012
Devonshire Building | 2017-08-04 18:45 | 50697.4916 | 200.016
Devonshire Building | 2017-08-04 19:00 | 50697.5416 | 200.016
Devonshire Building | 2017-08-04 19:15 | 50697.6016 | 240.012
Devonshire Building | 2017-08-04 19:30 | 50698.1066 | 2019.996
Devonshire Building | 2017-08-04 19:45 | 50698.1316 | 100.008
Devonshire Building | 2017-08-04 20:00 | 50698.1566 | 100.008
Devonshire Building | 2017-08-04 20:15 | 50698.1816 | 100.008
Devonshire Building | 2017-08-04 20:30 | 50698.2066 | 100.008
Devonshire Building | 2017-08-04 20:45 | 50698.2416 | 140.004
Devonshire Building | 2017-08-04 21:00 | 50698.2567 | 60.012
Devonshire Building | 2017-08-04 21:15 | 50698.2717 | 60.012
Devonshire Building | 2017-08-04 21:30 | 50698.2917 | 79.992
Devonshire Building | 2017-08-04 21:45 | 50698.3067 | 60.012
Devonshire Building | 2017-08-04 22:00 | 50698.3217 | 60.012
Devonshire Building | 2017-08-04 22:15 | 50698.3367 | 60.012
Devonshire Building | 2017-08-04 22:30 | 50698.3517 | 60.012
Devonshire Building | 2017-08-04 22:45 | 50698.3667 | 60.012
Devonshire Building | 2017-08-04 23:00 | 50698.3817 | 60.012
Devonshire Building | 2017-08-04 23:15 | 50698.3967 | 60.012
Devonshire Building | 2017-08-04 23:30 | 50698.4117 | 60.012
Devonshire Building | 2017-08-04 23:45 | 50698.4267 | 60.012
Devonshire Building | 2017-08-05 | 50698.4336 | 39.996
Devonshire Building | 2017-08-05 00:15 | 50698.4486 | 60.012
Devonshire Building | 2017-08-05 00:30 | 50698.4636 | 60.012
Devonshire Building | 2017-08-05 00:45 | 50698.4736 | 39.996
Devonshire Building | 2017-08-05 01:00 | 50698.4886 | 60.012
Devonshire Building | 2017-08-05 01:15 | 50698.4986 | 39.996
Devonshire Building | 2017-08-05 01:30 | 50698.5136 | 60.012
Devonshire Building | 2017-08-05 01:45 | 50698.5236 | 39.996
Devonshire Building | 2017-08-05 02:00 | 50698.5336 | 39.996
Devonshire Building | 2017-08-05 02:15 | 50698.5486 | 60.012
Devonshire Building | 2017-08-05 02:30 | 50698.5586 | 39.996
Devonshire Building | 2017-08-05 02:45 | 50698.5686 | 39.996
Devonshire Building | 2017-08-05 03:00 | 50698.5786 | 39.996
Devonshire Building | 2017-08-05 03:15 | 50698.5886 | 39.996
Devonshire Building | 2017-08-05 03:30 | 50698.6036 | 60.012
Devonshire Building | 2017-08-05 03:45 | 50698.6136 | 39.996
Devonshire Building | 2017-08-05 04:00 | 50698.6236 | 39.996
Devonshire Building | 2017-08-05 04:15 | 50698.6336 | 39.996
Devonshire Building | 2017-08-05 04:30 | 50698.6436 | 39.996
Devonshire Building | 2017-08-05 04:45 | 50698.6536 | 39.996
Devonshire Building | 2017-08-05 05:00 | 50698.6636 | 39.996
Devonshire Building | 2017-08-05 05:15 | 50698.6736 | 39.996
Devonshire Building | 2017-08-05 05:30 | 50698.6836 | 39.996
Devonshire Building | 2017-08-05 05:45 | 50698.6936 | 39.996
Devonshire Building | 2017-08-05 06:00 | 50698.7036 | 39.996
Devonshire Building | 2017-08-05 06:15 | 50698.7136 | 39.996
Devonshire Building | 2017-08-05 06:30 | 50698.7236 | 39.996
Devonshire Building | 2017-08-05 06:45 | 50698.7336 | 39.996
Devonshire Building | 2017-08-05 07:00 | 50698.7436 | 39.996
Devonshire Building | 2017-08-05 07:15 | 50698.7536 | 39.996
Devonshire Building | 2017-08-05 07:30 | 50698.7636 | 39.996
Devonshire Building | 2017-08-05 07:45 | 50698.7886 | 100.008
Devonshire Building | 2017-08-05 08:00 | 50698.8136 | 100.008
Devonshire Building | 2017-08-05 08:15 | 50698.8386 | 100.008
Devonshire Building | 2017-08-05 08:30 | 50698.8636 | 100.008
Devonshire Building | 2017-08-05 08:45 | 50698.8936 | 119.988
Devonshire Building | 2017-08-05 09:00 | 50698.9186 | 100.008
Devonshire Building | 2017-08-05 09:15 | 50698.9436 | 100.008
Devonshire Building | 2017-08-05 09:30 | 50698.9686 | 100.008
Devonshire Building | 2017-08-05 09:45 | 50698.9886 | 79.992
Devonshire Building | 2017-08-05 10:00 | 50698.9936 | 20.016
Devonshire Building | 2017-08-05 10:15 | 50699.0036 | 39.996
Devonshire Building | 2017-08-05 10:30 | 50699.5086 | 2019.996
Devonshire Building | 2017-08-05 10:45 | 50699.5136 | 20.016
Devonshire Building | 2017-08-05 11:00 | 50699.5186 | 20.016
Devonshire Building | 2017-08-05 11:15 | 50699.5236 | 20.016
Devonshire Building | 2017-08-05 11:30 | 50699.5336 | 39.996
Devonshire Building | 2017-08-05 11:45 | 50699.5386 | 20.016
Devonshire Building | 2017-08-05 12:00 | 50699.5436 | 20.016
Devonshire Building | 2017-08-05 12:15 | 50699.5486 | 20.016
Devonshire Building | 2017-08-05 12:30 | 50699.5536 | 20.016
Devonshire Building | 2017-08-05 12:45 | 50699.5586 | 20.016
Devonshire Building | 2017-08-05 13:00 | 50699.5636 | 20.016
Devonshire Building | 2017-08-05 13:15 | 50699.5686 | 20.016
Devonshire Building | 2017-08-05 13:30 | 50699.5736 | 20.016
Devonshire Building | 2017-08-05 13:45 | 50699.5836 | 39.996
Devonshire Building | 2017-08-05 14:00 | 50699.5886 | 20.016
Devonshire Building | 2017-08-05 14:15 | 50699.5986 | 39.996
Devonshire Building | 2017-08-05 14:30 | 50699.6036 | 20.016
Devonshire Building | 2017-08-05 14:45 | 50699.6086 | 20.016
Devonshire Building | 2017-08-05 15:00 | 50699.6137 | 20.016
Devonshire Building | 2017-08-05 15:15 | 50699.6237 | 39.996
Devonshire Building | 2017-08-05 15:30 | 50699.6287 | 20.016
Devonshire Building | 2017-08-05 15:45 | 50699.6337 | 20.016
Devonshire Building | 2017-08-05 16:00 | 50699.6437 | 39.996
Devonshire Building | 2017-08-05 16:15 | 50699.6487 | 20.016
Devonshire Building | 2017-08-05 16:30 | 50699.6587 | 39.996
Devonshire Building | 2017-08-05 16:45 | 50699.6637 | 20.016
Devonshire Building | 2017-08-05 17:00 | 50699.6687 | 20.016
Devonshire Building | 2017-08-05 17:15 | 50699.6737 | 20.016
Devonshire Building | 2017-08-05 17:30 | 50699.6837 | 39.996
Devonshire Building | 2017-08-05 17:45 | 50699.6887 | 20.016
Devonshire Building | 2017-08-05 18:00 | 50699.6937 | 20.016
Devonshire Building | 2017-08-05 18:15 | 50699.7037 | 39.996
Devonshire Building | 2017-08-05 18:30 | 50699.7087 | 20.016
Devonshire Building | 2017-08-05 18:45 | 50699.7137 | 20.016
Devonshire Building | 2017-08-05 19:00 | 50699.7187 | 20.016
Devonshire Building | 2017-08-05 19:15 | 50699.7237 | 20.016
Devonshire Building | 2017-08-05 19:30 | 50699.7337 | 39.996
Devonshire Building | 2017-08-05 19:45 | 50699.7387 | 20.016
Devonshire Building | 2017-08-05 20:00 | 50699.7437 | 20.016
Devonshire Building | 2017-08-05 20:15 | 50699.7487 | 20.016
Devonshire Building | 2017-08-05 20:30 | 50699.7537 | 20.016
Devonshire Building | 2017-08-05 20:45 | 50699.7837 | 119.988
Devonshire Building | 2017-08-05 21:00 | 50699.7887 | 20.016
Devonshire Building | 2017-08-05 21:15 | 50699.7987 | 39.996
Devonshire Building | 2017-08-05 21:30 | 50699.8087 | 39.996
Devonshire Building | 2017-08-05 21:45 | 50699.8137 | 20.016
Devonshire Building | 2017-08-05 22:00 | 50699.8187 | 20.016
Devonshire Building | 2017-08-05 22:15 | 50699.8287 | 39.996
Devonshire Building | 2017-08-05 22:30 | 50699.8337 | 20.016
Devonshire Building | 2017-08-05 22:45 | 50699.8387 | 20.016
Devonshire Building | 2017-08-05 23:00 | 50699.8487 | 39.996
Devonshire Building | 2017-08-05 23:15 | 50699.8537 | 20.016
Devonshire Building | 2017-08-05 23:30 | 50699.8587 | 20.016
Devonshire Building | 2017-08-05 23:45 | 50699.8687 | 39.996
Devonshire Building | 2017-08-06 | 50699.875 | 20.016
Devonshire Building | 2017-08-06 00:15 | 50699.88 | 20.016
Devonshire Building | 2017-08-06 00:30 | 50699.885 | 20.016
Devonshire Building | 2017-08-06 00:45 | 50699.895 | 39.996
Devonshire Building | 2017-08-06 01:00 | 50699.9 | 20.016
Devonshire Building | 2017-08-06 01:15 | 50700.41 | 2040.012
Devonshire Building | 2017-08-06 01:30 | 50700.415 | 20.016
Devonshire Building | 2017-08-06 01:45 | 50700.425 | 39.996
Devonshire Building | 2017-08-06 02:00 | 50700.43 | 20.016
Devonshire Building | 2017-08-06 02:15 | 50700.435 | 20.016
Devonshire Building | 2017-08-06 02:30 | 50700.445 | 39.996
Devonshire Building | 2017-08-06 02:45 | 50700.45 | 20.016
Devonshire Building | 2017-08-06 03:00 | 50700.46 | 39.996
Devonshire Building | 2017-08-06 03:15 | 50700.465 | 20.016
Devonshire Building | 2017-08-06 03:30 | 50700.475 | 39.996
Devonshire Building | 2017-08-06 03:45 | 50700.48 | 20.016
Devonshire Building | 2017-08-06 04:00 | 50700.49 | 39.996
Devonshire Building | 2017-08-06 04:15 | 50700.5 | 39.996
Devonshire Building | 2017-08-06 04:30 | 50700.51 | 39.996
Devonshire Building | 2017-08-06 04:45 | 50700.52 | 39.996
Devonshire Building | 2017-08-06 05:00 | 50700.53 | 39.996
Devonshire Building | 2017-08-06 05:15 | 50700.54 | 39.996
Devonshire Building | 2017-08-06 05:30 | 50700.55 | 39.996
Devonshire Building | 2017-08-06 05:45 | 50700.56 | 39.996
Devonshire Building | 2017-08-06 06:00 | 50700.57 | 39.996
Devonshire Building | 2017-08-06 06:15 | 50700.575 | 20.016
Devonshire Building | 2017-08-06 06:30 | 50700.585 | 39.996
Devonshire Building | 2017-08-06 06:45 | 50700.595 | 39.996
Devonshire Building | 2017-08-06 07:00 | 50700.605 | 39.996
Devonshire Building | 2017-08-06 07:15 | 50700.615 | 39.996
Devonshire Building | 2017-08-06 07:30 | 50700.625 | 39.996
Devonshire Building | 2017-08-06 07:45 | 50700.645 | 79.992
Devonshire Building | 2017-08-06 08:00 | 50700.67 | 100.008
Devonshire Building | 2017-08-06 08:15 | 50700.695 | 100.008
Devonshire Building | 2017-08-06 08:30 | 50700.72 | 100.008
Devonshire Building | 2017-08-06 08:45 | 50700.745 | 100.008
Devonshire Building | 2017-08-06 09:00 | 50700.77 | 100.008
Devonshire Building | 2017-08-06 09:15 | 50700.795 | 100.008
Devonshire Building | 2017-08-06 09:30 | 50700.82 | 100.008
Devonshire Building | 2017-08-06 09:45 | 50700.83 | 39.996
Devonshire Building | 2017-08-06 10:00 | 50700.84 | 39.996
Devonshire Building | 2017-08-06 10:15 | 50700.85 | 39.996
Devonshire Building | 2017-08-06 10:30 | 50700.855 | 20.016
Devonshire Building | 2017-08-06 10:45 | 50700.865 | 39.996
Devonshire Building | 2017-08-06 11:00 | 50700.875 | 39.996
Devonshire Building | 2017-08-06 11:15 | 50700.88 | 20.016
Devonshire Building | 2017-08-06 11:30 | 50700.89 | 39.996
Devonshire Building | 2017-08-06 11:45 | 50700.895 | 20.016
Devonshire Building | 2017-08-06 12:00 | 50700.905 | 39.996
Devonshire Building | 2017-08-06 12:15 | 50700.915 | 39.996
Devonshire Building | 2017-08-06 12:30 | 50700.92 | 20.016
Devonshire Building | 2017-08-06 12:45 | 50700.93 | 39.996
Devonshire Building | 2017-08-06 13:00 | 50700.935 | 20.016
Devonshire Building | 2017-08-06 13:15 | 50700.945 | 39.996
Devonshire Building | 2017-08-06 13:30 | 50700.955 | 39.996
Devonshire Building | 2017-08-06 13:45 | 50700.96 | 20.016
Devonshire Building | 2017-08-06 14:00 | 50700.97 | 39.996
Devonshire Building | 2017-08-06 14:15 | 50700.9751 | 20.016
Devonshire Building | 2017-08-06 14:30 | 50700.9901 | 60.012
Devonshire Building | 2017-08-06 14:45 | 50701.0001 | 39.996
Devonshire Building | 2017-08-06 15:00 | 50701.0051 | 20.016
Devonshire Building | 2017-08-06 15:15 | 50701.0151 | 39.996
Devonshire Building | 2017-08-06 15:30 | 50701.0251 | 39.996
Devonshire Building | 2017-08-06 15:45 | 50701.0351 | 39.996
Devonshire Building | 2017-08-06 16:00 | 50701.0401 | 20.016
Devonshire Building | 2017-08-06 16:15 | 50701.0501 | 39.996
Devonshire Building | 2017-08-06 16:30 | 50701.0601 | 39.996
Devonshire Building | 2017-08-06 16:45 | 50701.0851 | 100.008
Devonshire Building | 2017-08-06 17:00 | 50701.5701 | 1940.004
Devonshire Building | 2017-08-06 17:15 | 50701.5851 | 60.012
Devonshire Building | 2017-08-06 17:30 | 50701.6001 | 60.012
Devonshire Building | 2017-08-06 17:45 | 50701.6201 | 79.992
Devonshire Building | 2017-08-06 18:00 | 50701.6351 | 60.012
Devonshire Building | 2017-08-06 18:15 | 50701.6551 | 79.992
Devonshire Building | 2017-08-06 18:30 | 50701.6751 | 79.992
Devonshire Building | 2017-08-06 18:45 | 50701.6951 | 79.992
Devonshire Building | 2017-08-06 19:00 | 50701.7151 | 79.992
Devonshire Building | 2017-08-06 19:15 | 50701.7351 | 79.992
Devonshire Building | 2017-08-06 19:30 | 50701.7551 | 79.992
Devonshire Building | 2017-08-06 19:45 | 50701.7751 | 79.992
Devonshire Building | 2017-08-06 20:00 | 50701.7901 | 60.012
Devonshire Building | 2017-08-06 20:15 | 50701.8101 | 79.992
Devonshire Building | 2017-08-06 20:30 | 50701.8251 | 60.012
Devonshire Building | 2017-08-06 20:45 | 50701.8501 | 100.008
Devonshire Building | 2017-08-06 21:00 | 50701.8651 | 60.012
Devonshire Building | 2017-08-06 21:15 | 50701.8801 | 60.012
Devonshire Building | 2017-08-06 21:30 | 50701.8901 | 39.996
Devonshire Building | 2017-08-06 21:45 | 50701.9051 | 60.012
Devonshire Building | 2017-08-06 22:00 | 50701.9151 | 39.996
Devonshire Building | 2017-08-06 22:15 | 50701.9251 | 39.996
Devonshire Building | 2017-08-06 22:30 | 50701.9401 | 60.012
Devonshire Building | 2017-08-06 22:45 | 50701.9501 | 39.996
Devonshire Building | 2017-08-06 23:00 | 50701.9651 | 60.012
Devonshire Building | 2017-08-06 23:15 | 50701.9751 | 39.996
Devonshire Building | 2017-08-06 23:30 | 50701.9851 | 39.996
Devonshire Building | 2017-08-06 23:45 | 50702.0001 | 60.012
Devonshire Building | 2017-08-07 | 50702.0078 | 39.996
Devonshire Building | 2017-08-07 00:15 | 50702.0178 | 39.996
Devonshire Building | 2017-08-07 00:30 | 50702.0278 | 39.996
Devonshire Building | 2017-08-07 00:45 | 50702.0428 | 60.012
Devonshire Building | 2017-08-07 01:00 | 50702.0528 | 39.996
Devonshire Building | 2017-08-07 01:15 | 50702.0628 | 39.996
Devonshire Building | 2017-08-07 01:30 | 50702.0778 | 60.012
Devonshire Building | 2017-08-07 01:45 | 50702.0878 | 39.996
Devonshire Building | 2017-08-07 02:00 | 50702.0978 | 39.996
Devonshire Building | 2017-08-07 02:15 | 50702.1128 | 60.012
Devonshire Building | 2017-08-07 02:30 | 50702.1228 | 39.996
Devonshire Building | 2017-08-07 02:45 | 50702.1328 | 39.996
Devonshire Building | 2017-08-07 03:00 | 50702.1428 | 39.996
Devonshire Building | 2017-08-07 03:15 | 50702.1528 | 39.996
Devonshire Building | 2017-08-07 03:30 | 50702.1678 | 60.012
Devonshire Building | 2017-08-07 03:45 | 50702.1778 | 39.996
Devonshire Building | 2017-08-07 04:00 | 50702.1878 | 39.996
Devonshire Building | 2017-08-07 04:15 | 50702.1978 | 39.996
Devonshire Building | 2017-08-07 04:30 | 50702.2078 | 39.996
Devonshire Building | 2017-08-07 04:45 | 50702.2178 | 39.996
Devonshire Building | 2017-08-07 05:00 | 50702.2328 | 60.012
Devonshire Building | 2017-08-07 05:15 | 50702.2428 | 39.996
Devonshire Building | 2017-08-07 05:30 | 50702.2528 | 39.996
Devonshire Building | 2017-08-07 05:45 | 50702.2678 | 60.012
Devonshire Building | 2017-08-07 06:00 | 50702.2778 | 39.996
Devonshire Building | 2017-08-07 06:15 | 50702.2928 | 60.012
Devonshire Building | 2017-08-07 06:30 | 50702.3078 | 60.012
Devonshire Building | 2017-08-07 06:45 | 50702.3228 | 60.012
Devonshire Building | 2017-08-07 07:00 | 50702.3328 | 39.996
Devonshire Building | 2017-08-07 07:15 | 50702.8428 | 2040.012
Devonshire Building | 2017-08-07 07:30 | 50702.8578 | 60.012
Devonshire Building | 2017-08-07 07:45 | 50702.8828 | 100.008
Devonshire Building | 2017-08-07 08:00 | 50702.9078 | 100.008
Devonshire Building | 2017-08-07 08:15 | 50702.9428 | 140.004
Devonshire Building | 2017-08-07 08:30 | 50702.9778 | 140.004
Devonshire Building | 2017-08-07 08:45 | 50703.0078 | 119.988
Devonshire Building | 2017-08-07 09:00 | 50703.0528 | 180
Devonshire Building | 2017-08-07 09:15 | 50703.1078 | 219.996
Devonshire Building | 2017-08-07 09:30 | 50703.7378 | 2520
Devonshire Building | 2017-08-07 09:45 | 50703.8478 | 439.992
Devonshire Building | 2017-08-07 10:00 | 50703.9778 | 519.984
Devonshire Building | 2017-08-07 10:15 | 50704.0828 | 420.012
Devonshire Building | 2017-08-07 10:30 | 50704.1628 | 320.004
Devonshire Building | 2017-08-07 10:45 | 50704.7428 | 2319.984
Devonshire Building | 2017-08-07 11:00 | 50704.7978 | 219.996
Devonshire Building | 2017-08-07 11:15 | 50704.8528 | 219.996
Devonshire Building | 2017-08-07 11:30 | 50704.9128 | 240.012
Devonshire Building | 2017-08-07 11:45 | 50704.9628 | 200.016
Devonshire Building | 2017-08-07 12:00 | 50705.0178 | 219.996
Devonshire Building | 2017-08-07 12:15 | 50705.0678 | 200.016
Devonshire Building | 2017-08-07 12:30 | 50705.6228 | 2220.012
Devonshire Building | 2017-08-07 12:45 | 50705.6828 | 240.012
Devonshire Building | 2017-08-07 13:00 | 50705.7378 | 219.996
Devonshire Building | 2017-08-07 13:15 | 50705.7928 | 219.996
Devonshire Building | 2017-08-07 13:30 | 50705.8428 | 200.016
Devonshire Building | 2017-08-07 13:45 | 50706.3828 | 2160
Devonshire Building | 2017-08-07 14:00 | 50706.4178 | 140.004
Devonshire Building | 2017-08-07 14:15 | 50706.4578 | 159.984
Devonshire Building | 2017-08-07 14:30 | 50706.4928 | 140.004
Devonshire Building | 2017-08-07 14:45 | 50706.5228 | 119.988
Devonshire Building | 2017-08-07 15:00 | 50706.5528 | 119.988
Devonshire Building | 2017-08-07 15:15 | 50706.7828 | 920.016
Devonshire Building | 2017-08-07 15:30 | 50707.1478 | 1460.016
Devonshire Building | 2017-08-07 15:45 | 50707.1778 | 119.988
Devonshire Building | 2017-08-07 16:00 | 50707.2278 | 200.016
Devonshire Building | 2017-08-07 16:15 | 50707.2678 | 159.984
Devonshire Building | 2017-08-07 16:30 | 50707.3128 | 180
Devonshire Building | 2017-08-07 16:45 | 50707.3578 | 180
Devonshire Building | 2017-08-07 17:00 | 50707.3928 | 140.004
Devonshire Building | 2017-08-07 17:15 | 50707.4328 | 159.984
Devonshire Building | 2017-08-07 17:30 | 50707.4678 | 140.004
Devonshire Building | 2017-08-07 17:45 | 50707.4978 | 119.988
Devonshire Building | 2017-08-07 18:00 | 50707.5328 | 140.004
Devonshire Building | 2017-08-07 18:15 | 50707.5678 | 140.004
Devonshire Building | 2017-08-07 18:30 | 50707.5928 | 100.008
Devonshire Building | 2017-08-07 18:45 | 50707.6228 | 119.988
Devonshire Building | 2017-08-07 19:00 | 50708.1428 | 2080.008
Devonshire Building | 2017-08-07 19:15 | 50708.1628 | 79.992
Devonshire Building | 2017-08-07 19:30 | 50708.1778 | 60.012
Devonshire Building | 2017-08-07 19:45 | 50708.1928 | 60.012
Devonshire Building | 2017-08-07 20:00 | 50708.2128 | 79.992
Devonshire Building | 2017-08-07 20:15 | 50708.2278 | 60.012
Devonshire Building | 2017-08-07 20:30 | 50708.2478 | 79.992
Devonshire Building | 2017-08-07 20:45 | 50708.2778 | 119.988
Devonshire Building | 2017-08-07 21:00 | 50708.2928 | 60.012
Devonshire Building | 2017-08-07 21:15 | 50708.3078 | 60.012
Devonshire Building | 2017-08-07 21:30 | 50708.3178 | 39.996
Devonshire Building | 2017-08-07 21:45 | 50708.3378 | 79.992
Devonshire Building | 2017-08-07 22:00 | 50708.3528 | 60.012
Devonshire Building | 2017-08-07 22:15 | 50708.3678 | 60.012
Devonshire Building | 2017-08-07 22:30 | 50708.3828 | 60.012
Devonshire Building | 2017-08-07 22:45 | 50708.3928 | 39.996
Devonshire Building | 2017-08-07 23:00 | 50708.4078 | 60.012
Devonshire Building | 2017-08-07 23:15 | 50708.4178 | 39.996
Devonshire Building | 2017-08-07 23:30 | 50708.4328 | 60.012
Devonshire Building | 2017-08-07 23:45 | 50708.4478 | 60.012
Devonshire Building | 2017-08-08 | 50708.4609 | 39.996
Devonshire Building | 2017-08-08 00:15 | 50708.4709 | 39.996
Devonshire Building | 2017-08-08 00:30 | 50708.4859 | 60.012
Devonshire Building | 2017-08-08 00:45 | 50708.4959 | 39.996
Devonshire Building | 2017-08-08 01:00 | 50708.5059 | 39.996
Devonshire Building | 2017-08-08 01:15 | 50708.5159 | 39.996
Devonshire Building | 2017-08-08 01:30 | 50708.5309 | 60.012
Devonshire Building | 2017-08-08 01:45 | 50708.5409 | 39.996
Devonshire Building | 2017-08-08 02:00 | 50708.5509 | 39.996
Devonshire Building | 2017-08-08 02:15 | 50708.5609 | 39.996
Devonshire Building | 2017-08-08 02:30 | 50708.5709 | 39.996
Devonshire Building | 2017-08-08 02:45 | 50708.5809 | 39.996
Devonshire Building | 2017-08-08 03:00 | 50708.5959 | 60.012
Devonshire Building | 2017-08-08 03:15 | 50708.6059 | 39.996
Devonshire Building | 2017-08-08 03:30 | 50708.6159 | 39.996
Devonshire Building | 2017-08-08 03:45 | 50708.6259 | 39.996
Devonshire Building | 2017-08-08 04:00 | 50708.6359 | 39.996
Devonshire Building | 2017-08-08 04:15 | 50708.6459 | 39.996
Devonshire Building | 2017-08-08 04:30 | 50708.6559 | 39.996
Devonshire Building | 2017-08-08 04:45 | 50708.6659 | 39.996
Devonshire Building | 2017-08-08 05:00 | 50708.6759 | 39.996
Devonshire Building | 2017-08-08 05:15 | 50708.6909 | 60.012
Devonshire Building | 2017-08-08 05:30 | 50708.7009 | 39.996
Devonshire Building | 2017-08-08 05:45 | 50708.7109 | 39.996
Devonshire Building | 2017-08-08 06:00 | 50708.7209 | 39.996
Devonshire Building | 2017-08-08 06:15 | 50708.7359 | 60.012
Devonshire Building | 2017-08-08 06:30 | 50708.7459 | 39.996
Devonshire Building | 2017-08-08 06:45 | 50708.7559 | 39.996
Devonshire Building | 2017-08-08 07:00 | 50708.7659 | 39.996
Devonshire Building | 2017-08-08 07:15 | 50709.2809 | 2059.992
Devonshire Building | 2017-08-08 07:30 | 50709.2909 | 39.996
Devonshire Building | 2017-08-08 07:45 | 50709.3159 | 100.008
Devonshire Building | 2017-08-08 08:00 | 50709.3409 | 100.008
Devonshire Building | 2017-08-08 08:15 | 50709.3709 | 119.988
Devonshire Building | 2017-08-08 08:30 | 50709.4009 | 119.988
Devonshire Building | 2017-08-08 08:45 | 50709.4259 | 100.008
Devonshire Building | 2017-08-08 09:00 | 50709.4509 | 100.008
Devonshire Building | 2017-08-08 09:15 | 50709.4959 | 180
Devonshire Building | 2017-08-08 09:30 | 50710.1759 | 2720.016
Devonshire Building | 2017-08-08 09:45 | 50710.4009 | 900
Devonshire Building | 2017-08-08 10:00 | 50710.5759 | 699.984
Devonshire Building | 2017-08-08 10:15 | 50710.7059 | 519.984
Devonshire Building | 2017-08-08 10:30 | 50710.8009 | 380.016
Devonshire Building | 2017-08-08 10:45 | 50710.8859 | 339.984
Devonshire Building | 2017-08-08 11:00 | 50711.4509 | 2260.008
Devonshire Building | 2017-08-08 11:15 | 50711.5709 | 479.988
Devonshire Building | 2017-08-08 11:30 | 50711.6359 | 259.992
Devonshire Building | 2017-08-08 11:45 | 50711.7059 | 280.008
Devonshire Building | 2017-08-08 12:00 | 50711.7959 | 360
Devonshire Building | 2017-08-08 12:15 | 50711.8909 | 380.016
Devonshire Building | 2017-08-08 12:30 | 50712.5259 | 2540.016
Devonshire Building | 2017-08-08 12:45 | 50712.6759 | 600.012
Devonshire Building | 2017-08-08 13:00 | 50712.8159 | 560.016
Devonshire Building | 2017-08-08 13:15 | 50712.9559 | 560.016
Devonshire Building | 2017-08-08 13:30 | 50713.0759 | 479.988
Devonshire Building | 2017-08-08 13:45 | 50713.1859 | 439.992
Devonshire Building | 2017-08-08 14:00 | 50713.7059 | 2080.008
Devonshire Building | 2017-08-08 14:15 | 50713.8659 | 640.008
Devonshire Building | 2017-08-08 14:30 | 50713.9509 | 339.984
Devonshire Building | 2017-08-08 14:45 | 50714.0409 | 360
Devonshire Building | 2017-08-08 15:00 | 50714.1509 | 439.992
Devonshire Building | 2017-08-08 15:15 | 50714.2759 | 500.004
Devonshire Building | 2017-08-08 15:30 | 50714.5759 | 1199.988
Devonshire Building | 2017-08-08 15:45 | 50715.0459 | 1879.992
Devonshire Building | 2017-08-08 16:00 | 50715.1409 | 380.016
Devonshire Building | 2017-08-08 16:15 | 50715.2209 | 320.004
Devonshire Building | 2017-08-08 16:30 | 50715.2909 | 280.008
Devonshire Building | 2017-08-08 16:45 | 50715.3459 | 219.996
Devonshire Building | 2017-08-08 17:00 | 50715.3959 | 200.016
Devonshire Building | 2017-08-08 17:15 | 50715.4359 | 159.984
Devonshire Building | 2017-08-08 17:30 | 50715.4709 | 140.004
Devonshire Building | 2017-08-08 17:45 | 50715.4959 | 100.008
Devonshire Building | 2017-08-08 18:00 | 50715.5209 | 100.008
Devonshire Building | 2017-08-08 18:15 | 50715.5409 | 79.992
Devonshire Building | 2017-08-08 18:30 | 50715.5609 | 79.992
Devonshire Building | 2017-08-08 18:45 | 50715.5809 | 79.992
Devonshire Building | 2017-08-08 19:00 | 50715.6009 | 79.992
Devonshire Building | 2017-08-08 19:15 | 50716.1059 | 2019.996
Devonshire Building | 2017-08-08 19:30 | 50716.1159 | 39.996
Devonshire Building | 2017-08-08 19:45 | 50716.1209 | 20.016
Devonshire Building | 2017-08-08 20:00 | 50716.1259 | 20.016
Devonshire Building | 2017-08-08 20:15 | 50716.1359 | 39.996
Devonshire Building | 2017-08-08 20:30 | 50716.1409 | 20.016
Devonshire Building | 2017-08-08 20:45 | 50716.1559 | 60.012
Devonshire Building | 2017-08-08 21:00 | 50716.161 | 20.016
Devonshire Building | 2017-08-08 21:15 | 50716.171 | 39.996
Devonshire Building | 2017-08-08 21:30 | 50716.176 | 20.016
Devonshire Building | 2017-08-08 21:45 | 50716.181 | 20.016
Devonshire Building | 2017-08-08 22:00 | 50716.186 | 20.016
Devonshire Building | 2017-08-08 22:15 | 50716.196 | 39.996
Devonshire Building | 2017-08-08 22:30 | 50716.201 | 20.016
Devonshire Building | 2017-08-08 22:45 | 50716.206 | 20.016
Devonshire Building | 2017-08-08 23:00 | 50716.211 | 20.016
Devonshire Building | 2017-08-08 23:15 | 50716.216 | 20.016
Devonshire Building | 2017-08-08 23:30 | 50716.226 | 39.996
Devonshire Building | 2017-08-08 23:45 | 50716.231 | 20.016
Devonshire Building | 2017-08-09 | 50716.2344 | 20.016
Devonshire Building | 2017-08-09 00:15 | 50716.2444 | 39.996
Devonshire Building | 2017-08-09 00:30 | 50716.2494 | 20.016
Devonshire Building | 2017-08-09 00:45 | 50716.2544 | 20.016
Devonshire Building | 2017-08-09 01:00 | 50716.2594 | 20.016
Devonshire Building | 2017-08-09 01:15 | 50716.2644 | 20.016
Devonshire Building | 2017-08-09 01:30 | 50716.2744 | 39.996
Devonshire Building | 2017-08-09 01:45 | 50716.2944 | 79.992
Devonshire Building | 2017-08-09 02:00 | 50716.3194 | 100.008
Devonshire Building | 2017-08-09 02:15 | 50716.3394 | 79.992
Devonshire Building | 2017-08-09 02:30 | 50716.3644 | 100.008
Devonshire Building | 2017-08-09 02:45 | 50716.3844 | 79.992
Devonshire Building | 2017-08-09 03:00 | 50716.4094 | 100.008
Devonshire Building | 2017-08-09 03:15 | 50716.4294 | 79.992
Devonshire Building | 2017-08-09 03:30 | 50716.4494 | 79.992
Devonshire Building | 2017-08-09 03:45 | 50716.4644 | 60.012
Devonshire Building | 2017-08-09 04:00 | 50716.4694 | 20.016
Devonshire Building | 2017-08-09 04:15 | 50716.4744 | 20.016
Devonshire Building | 2017-08-09 04:30 | 50716.4794 | 20.016
Devonshire Building | 2017-08-09 04:45 | 50716.4844 | 20.016
Devonshire Building | 2017-08-09 05:00 | 50716.4944 | 39.996
Devonshire Building | 2017-08-09 05:15 | 50716.4994 | 20.016
Devonshire Building | 2017-08-09 05:30 | 50716.5094 | 39.996
Devonshire Building | 2017-08-09 05:45 | 50716.5144 | 20.016
Devonshire Building | 2017-08-09 06:00 | 50716.5194 | 20.016
Devonshire Building | 2017-08-09 06:15 | 50716.5294 | 39.996
Devonshire Building | 2017-08-09 06:30 | 50716.5344 | 20.016
Devonshire Building | 2017-08-09 06:45 | 50716.5394 | 20.016
Devonshire Building | 2017-08-09 07:00 | 50716.8194 | 1119.996
Devonshire Building | 2017-08-09 07:15 | 50717.0544 | 939.996
Devonshire Building | 2017-08-09 07:30 | 50717.0694 | 60.012
Devonshire Building | 2017-08-09 07:45 | 50717.0844 | 60.012
Devonshire Building | 2017-08-09 08:00 | 50717.1094 | 100.008
Devonshire Building | 2017-08-09 08:15 | 50717.1294 | 79.992
Devonshire Building | 2017-08-09 08:30 | 50717.1494 | 79.992
Devonshire Building | 2017-08-09 08:45 | 50717.1744 | 100.008
Devonshire Building | 2017-08-09 09:00 | 50717.1994 | 100.008
Devonshire Building | 2017-08-09 09:15 | 50717.8294 | 2520
Devonshire Building | 2017-08-09 09:30 | 50717.9944 | 659.988
Devonshire Building | 2017-08-09 09:45 | 50718.1294 | 540
Devonshire Building | 2017-08-09 10:00 | 50718.2444 | 460.008
Devonshire Building | 2017-08-09 10:15 | 50718.3494 | 420.012
Devonshire Building | 2017-08-09 10:30 | 50718.4544 | 420.012
Devonshire Building | 2017-08-09 10:45 | 50719.0394 | 2340
Devonshire Building | 2017-08-09 11:00 | 50719.1444 | 420.012
Devonshire Building | 2017-08-09 11:15 | 50719.1894 | 180
Devonshire Building | 2017-08-09 11:30 | 50719.2344 | 180
Devonshire Building | 2017-08-09 11:45 | 50719.2844 | 200.016
Devonshire Building | 2017-08-09 12:00 | 50719.3294 | 180
Devonshire Building | 2017-08-09 12:15 | 50719.4344 | 420.012
Devonshire Building | 2017-08-09 12:30 | 50719.9094 | 1900.008
Devonshire Building | 2017-08-09 12:45 | 50719.9394 | 119.988
Devonshire Building | 2017-08-09 13:00 | 50719.9794 | 159.984
Devonshire Building | 2017-08-09 13:15 | 50720.0244 | 180
Devonshire Building | 2017-08-09 13:30 | 50720.0594 | 140.004
Devonshire Building | 2017-08-09 13:45 | 50720.1194 | 240.012
Devonshire Building | 2017-08-09 14:00 | 50720.1695 | 200.016
Devonshire Building | 2017-08-09 14:15 | 50720.2295 | 240.012
Devonshire Building | 2017-08-09 14:30 | 50720.7994 | 2279.988
Devonshire Building | 2017-08-09 14:45 | 50720.8595 | 240.012
Devonshire Building | 2017-08-09 15:00 | 50720.9245 | 259.992
Devonshire Building | 2017-08-09 15:15 | 50720.9894 | 259.992
Devonshire Building | 2017-08-09 15:30 | 50721.0495 | 240.012
Devonshire Building | 2017-08-09 15:45 | 50721.1145 | 259.992
Devonshire Building | 2017-08-09 16:00 | 50721.1594 | 180
Devonshire Building | 2017-08-09 16:15 | 50721.1994 | 159.984
Devonshire Building | 2017-08-09 16:30 | 50721.2594 | 240.012
Devonshire Building | 2017-08-09 16:45 | 50721.7795 | 2080.008
Devonshire Building | 2017-08-09 17:00 | 50721.7994 | 79.992
Devonshire Building | 2017-08-09 17:15 | 50721.8194 | 79.992
Devonshire Building | 2017-08-09 17:30 | 50721.8444 | 100.008
Devonshire Building | 2017-08-09 17:45 | 50721.8695 | 100.008
Devonshire Building | 2017-08-09 18:00 | 50721.8894 | 79.992
Devonshire Building | 2017-08-09 18:15 | 50721.9145 | 100.008
Devonshire Building | 2017-08-09 18:30 | 50721.9344 | 79.992
Devonshire Building | 2017-08-09 18:45 | 50721.9544 | 79.992
Devonshire Building | 2017-08-09 19:00 | 50721.9744 | 79.992
Devonshire Building | 2017-08-09 19:15 | 50721.9944 | 79.992
Devonshire Building | 2017-08-09 19:30 | 50722.0144 | 79.992
Devonshire Building | 2017-08-09 19:45 | 50722.0294 | 60.012
Devonshire Building | 2017-08-09 20:00 | 50722.0494 | 79.992
Devonshire Building | 2017-08-09 20:15 | 50722.0644 | 60.012
Devonshire Building | 2017-08-09 20:30 | 50722.0794 | 60.012
Devonshire Building | 2017-08-09 20:45 | 50722.1044 | 100.008
Devonshire Building | 2017-08-09 21:00 | 50722.1144 | 39.996
Devonshire Building | 2017-08-09 21:15 | 50722.1195 | 20.016
Devonshire Building | 2017-08-09 21:30 | 50722.1245 | 20.016
Devonshire Building | 2017-08-09 21:45 | 50722.1345 | 39.996
Devonshire Building | 2017-08-09 22:00 | 50722.1395 | 20.016
Devonshire Building | 2017-08-09 22:15 | 50722.1445 | 20.016
Devonshire Building | 2017-08-09 22:30 | 50722.1495 | 20.016
Devonshire Building | 2017-08-09 22:45 | 50722.1595 | 39.996
Devonshire Building | 2017-08-09 23:00 | 50722.1645 | 20.016
Devonshire Building | 2017-08-09 23:15 | 50722.1695 | 20.016
Devonshire Building | 2017-08-09 23:30 | 50722.1795 | 39.996
Devonshire Building | 2017-08-09 23:45 | 50722.1845 | 20.016
Devonshire Building | 2017-08-10 | 50722.1914 | 20.016
Devonshire Building | 2017-08-10 00:15 | 50722.1964 | 20.016
Devonshire Building | 2017-08-10 00:30 | 50722.2064 | 39.996
Devonshire Building | 2017-08-10 00:45 | 50722.2114 | 20.016
Devonshire Building | 2017-08-10 01:00 | 50722.2164 | 20.016
Devonshire Building | 2017-08-10 01:15 | 50722.2214 | 20.016
Devonshire Building | 2017-08-10 01:30 | 50722.2314 | 39.996
Devonshire Building | 2017-08-10 01:45 | 50722.2364 | 20.016
Devonshire Building | 2017-08-10 02:00 | 50722.2414 | 20.016
Devonshire Building | 2017-08-10 02:15 | 50722.2464 | 20.016
Devonshire Building | 2017-08-10 02:30 | 50722.2564 | 39.996
Devonshire Building | 2017-08-10 02:45 | 50722.2614 | 20.016
Devonshire Building | 2017-08-10 03:00 | 50722.2664 | 20.016
Devonshire Building | 2017-08-10 03:15 | 50722.2714 | 20.016
Devonshire Building | 2017-08-10 03:30 | 50722.2765 | 20.016
Devonshire Building | 2017-08-10 03:45 | 50722.2815 | 20.016
Devonshire Building | 2017-08-10 04:00 | 50722.2915 | 39.996
Devonshire Building | 2017-08-10 04:15 | 50722.2965 | 20.016
Devonshire Building | 2017-08-10 04:30 | 50722.3015 | 20.016
Devonshire Building | 2017-08-10 04:45 | 50722.3065 | 20.016
Devonshire Building | 2017-08-10 05:00 | 50722.3115 | 20.016
Devonshire Building | 2017-08-10 05:15 | 50722.3215 | 39.996
Devonshire Building | 2017-08-10 05:30 | 50722.3265 | 20.016
Devonshire Building | 2017-08-10 05:45 | 50722.3315 | 20.016
Devonshire Building | 2017-08-10 06:00 | 50722.3415 | 39.996
Devonshire Building | 2017-08-10 06:15 | 50722.3465 | 20.016
Devonshire Building | 2017-08-10 06:30 | 50722.3515 | 20.016
Devonshire Building | 2017-08-10 06:45 | 50722.8865 | 2139.984
Devonshire Building | 2017-08-10 07:00 | 50722.8965 | 39.996
Devonshire Building | 2017-08-10 07:15 | 50722.9065 | 39.996
Devonshire Building | 2017-08-10 07:30 | 50722.9165 | 39.996
Devonshire Building | 2017-08-10 07:45 | 50722.9265 | 39.996
Devonshire Building | 2017-08-10 08:00 | 50722.9665 | 159.984
Devonshire Building | 2017-08-10 08:15 | 50723.0265 | 240.012
Devonshire Building | 2017-08-10 08:30 | 50723.1015 | 299.988
Devonshire Building | 2017-08-10 08:45 | 50723.1865 | 339.984
Devonshire Building | 2017-08-10 09:00 | 50723.5415 | 1419.984
Devonshire Building | 2017-08-10 09:15 | 50723.9115 | 1479.996
Devonshire Building | 2017-08-10 09:30 | 50724.0215 | 439.992
Devonshire Building | 2017-08-10 09:45 | 50724.1315 | 439.992
Devonshire Building | 2017-08-10 10:00 | 50724.2315 | 399.996
Devonshire Building | 2017-08-10 10:15 | 50724.3115 | 320.004
Devonshire Building | 2017-08-10 10:30 | 50724.3765 | 259.992
Devonshire Building | 2017-08-10 10:45 | 50724.4315 | 219.996
Devonshire Building | 2017-08-10 11:00 | 50725.0265 | 2379.996
Devonshire Building | 2017-08-10 11:15 | 50725.0615 | 140.004
Devonshire Building | 2017-08-10 11:30 | 50725.1015 | 159.984
Devonshire Building | 2017-08-10 11:45 | 50725.1414 | 159.984
Devonshire Building | 2017-08-10 12:00 | 50725.1864 | 180
Devonshire Building | 2017-08-10 12:15 | 50725.2365 | 200.016
Devonshire Building | 2017-08-10 12:30 | 50725.5715 | 1339.992
Devonshire Building | 2017-08-10 12:45 | 50725.9115 | 1360.008
Devonshire Building | 2017-08-10 13:00 | 50726.0065 | 380.016
Devonshire Building | 2017-08-10 13:15 | 50726.0965 | 360
Devonshire Building | 2017-08-10 13:30 | 50726.1865 | 360
Devonshire Building | 2017-08-10 13:45 | 50726.2665 | 320.004
Devonshire Building | 2017-08-10 14:00 | 50726.3515 | 339.984
Devonshire Building | 2017-08-10 14:15 | 50726.4215 | 280.008
Devonshire Building | 2017-08-10 14:30 | 50726.9765 | 2220.012
Devonshire Building | 2017-08-10 14:45 | 50727.0465 | 280.008
Devonshire Building | 2017-08-10 15:00 | 50727.0965 | 200.016
Devonshire Building | 2017-08-10 15:15 | 50727.1465 | 200.016
Devonshire Building | 2017-08-10 15:30 | 50727.1915 | 180
Devonshire Building | 2017-08-10 15:45 | 50727.2465 | 219.996
Devonshire Building | 2017-08-10 16:00 | 50727.2965 | 200.016
Devonshire Building | 2017-08-10 16:15 | 50727.3865 | 360
Devonshire Building | 2017-08-10 16:30 | 50727.8765 | 1959.984
Devonshire Building | 2017-08-10 16:45 | 50727.9115 | 140.004
Devonshire Building | 2017-08-10 17:00 | 50727.9415 | 119.988
Devonshire Building | 2017-08-10 17:15 | 50727.9765 | 140.004
Devonshire Building | 2017-08-10 17:30 | 50728.0115 | 140.004
Devonshire Building | 2017-08-10 17:45 | 50728.0465 | 140.004
Devonshire Building | 2017-08-10 18:00 | 50728.0765 | 119.988
Devonshire Building | 2017-08-10 18:15 | 50728.1065 | 119.988
Devonshire Building | 2017-08-10 18:30 | 50728.1365 | 119.988
Devonshire Building | 2017-08-10 18:45 | 50728.1615 | 100.008
Devonshire Building | 2017-08-10 19:00 | 50728.1865 | 100.008
Devonshire Building | 2017-08-10 19:15 | 50728.2115 | 100.008
Devonshire Building | 2017-08-10 19:30 | 50728.2315 | 79.992
Devonshire Building | 2017-08-10 19:45 | 50728.2515 | 79.992
Devonshire Building | 2017-08-10 20:00 | 50728.2715 | 79.992
Devonshire Building | 2017-08-10 20:15 | 50728.2915 | 79.992
Devonshire Building | 2017-08-10 20:30 | 50728.3065 | 60.012
Devonshire Building | 2017-08-10 20:45 | 50728.3465 | 159.984
Devonshire Building | 2017-08-10 21:00 | 50728.3515 | 20.016
Devonshire Building | 2017-08-10 21:15 | 50728.3615 | 39.996
Devonshire Building | 2017-08-10 21:30 | 50728.3715 | 39.996
Devonshire Building | 2017-08-10 21:45 | 50728.3815 | 39.996
Devonshire Building | 2017-08-10 22:00 | 50728.3865 | 20.016
Devonshire Building | 2017-08-10 22:15 | 50728.3965 | 39.996
Devonshire Building | 2017-08-10 22:30 | 50728.4065 | 39.996
Devonshire Building | 2017-08-10 22:45 | 50728.4115 | 20.016
Devonshire Building | 2017-08-10 23:00 | 50728.4215 | 39.996
Devonshire Building | 2017-08-10 23:15 | 50728.4265 | 20.016
Devonshire Building | 2017-08-10 23:30 | 50728.4365 | 39.996
Devonshire Building | 2017-08-10 23:45 | 50728.4465 | 39.996
Devonshire Building | 2017-08-11 | 50728.4492 | 20.016
Devonshire Building | 2017-08-11 00:15 | 50728.4592 | 39.996
Devonshire Building | 2017-08-11 00:30 | 50728.4642 | 20.016
Devonshire Building | 2017-08-11 00:45 | 50728.4742 | 39.996
Devonshire Building | 2017-08-11 01:00 | 50728.4842 | 39.996
Devonshire Building | 2017-08-11 01:15 | 50728.4892 | 20.016
Devonshire Building | 2017-08-11 01:30 | 50728.4992 | 39.996
Devonshire Building | 2017-08-11 01:45 | 50728.5042 | 20.016
Devonshire Building | 2017-08-11 02:00 | 50728.5142 | 39.996
Devonshire Building | 2017-08-11 02:15 | 50728.5192 | 20.016
Devonshire Building | 2017-08-11 02:30 | 50728.5292 | 39.996
Devonshire Building | 2017-08-11 02:45 | 50728.5342 | 20.016
Devonshire Building | 2017-08-11 03:00 | 50728.5442 | 39.996
Devonshire Building | 2017-08-11 03:15 | 50728.5492 | 20.016
Devonshire Building | 2017-08-11 03:30 | 50728.5592 | 39.996
Devonshire Building | 2017-08-11 03:45 | 50728.5642 | 20.016
Devonshire Building | 2017-08-11 04:00 | 50729.0642 | 2000.016
Devonshire Building | 2017-08-11 04:15 | 50729.0692 | 20.016
Devonshire Building | 2017-08-11 04:30 | 50729.0792 | 39.996
Devonshire Building | 2017-08-11 04:45 | 50729.0892 | 39.996
Devonshire Building | 2017-08-11 05:00 | 50729.0992 | 39.996
Devonshire Building | 2017-08-11 05:15 | 50729.1042 | 20.016
Devonshire Building | 2017-08-11 05:30 | 50729.1142 | 39.996
Devonshire Building | 2017-08-11 05:45 | 50729.1242 | 39.996
Devonshire Building | 2017-08-11 06:00 | 50729.1342 | 39.996
Devonshire Building | 2017-08-11 06:15 | 50729.1442 | 39.996
Devonshire Building | 2017-08-11 06:30 | 50729.1592 | 60.012
Devonshire Building | 2017-08-11 06:45 | 50729.1743 | 60.012
Devonshire Building | 2017-08-11 07:00 | 50729.1842 | 39.996
Devonshire Building | 2017-08-11 07:15 | 50729.1993 | 60.012
Devonshire Building | 2017-08-11 07:30 | 50729.2193 | 79.992
Devonshire Building | 2017-08-11 07:45 | 50729.2543 | 140.004
Devonshire Building | 2017-08-11 08:00 | 50729.2842 | 119.988
Devonshire Building | 2017-08-11 08:15 | 50729.3242 | 159.984
Devonshire Building | 2017-08-11 08:30 | 50729.3642 | 159.984
Devonshire Building | 2017-08-11 08:45 | 50729.4142 | 200.016
Devonshire Building | 2017-08-11 09:00 | 50730.0242 | 2440.008
Devonshire Building | 2017-08-11 09:15 | 50730.0842 | 240.012
Devonshire Building | 2017-08-11 09:30 | 50730.1543 | 280.008
Devonshire Building | 2017-08-11 09:45 | 50730.2543 | 399.996
Devonshire Building | 2017-08-11 10:00 | 50730.3493 | 380.016
Devonshire Building | 2017-08-11 10:15 | 50730.9743 | 2499.984
Devonshire Building | 2017-08-11 10:30 | 50731.0543 | 320.004
Devonshire Building | 2017-08-11 10:45 | 50731.1292 | 299.988
Devonshire Building | 2017-08-11 11:00 | 50731.1893 | 240.012
Devonshire Building | 2017-08-11 11:15 | 50731.2493 | 240.012
Devonshire Building | 2017-08-11 11:30 | 50731.3243 | 299.988
Devonshire Building | 2017-08-11 11:45 | 50731.4092 | 339.984
Devonshire Building | 2017-08-11 12:00 | 50732.0042 | 2379.996
Devonshire Building | 2017-08-11 12:15 | 50732.0892 | 339.984
Devonshire Building | 2017-08-11 12:30 | 50732.2342 | 579.996
Devonshire Building | 2017-08-11 12:45 | 50732.3742 | 560.016
Devonshire Building | 2017-08-11 13:00 | 50732.4842 | 439.992
Devonshire Building | 2017-08-11 13:15 | 50732.5692 | 339.984
Devonshire Building | 2017-08-11 13:30 | 50732.6442 | 299.988
Devonshire Building | 2017-08-11 13:45 | 50733.2142 | 2279.988
Devonshire Building | 2017-08-11 14:00 | 50733.2642 | 200.016
Devonshire Building | 2017-08-11 14:15 | 50733.3142 | 200.016
Devonshire Building | 2017-08-11 14:30 | 50733.3692 | 219.996
Devonshire Building | 2017-08-11 14:45 | 50733.4142 | 180
Devonshire Building | 2017-08-11 15:00 | 50733.4592 | 180
Devonshire Building | 2017-08-11 15:15 | 50733.4992 | 159.984
Devonshire Building | 2017-08-11 15:30 | 50733.5392 | 159.984
Devonshire Building | 2017-08-11 15:45 | 50733.5792 | 159.984
Devonshire Building | 2017-08-11 16:00 | 50733.9492 | 1479.996
Devonshire Building | 2017-08-11 16:15 | 50734.1392 | 759.996
Devonshire Building | 2017-08-11 16:30 | 50734.1592 | 79.992
Devonshire Building | 2017-08-11 16:45 | 50734.1792 | 79.992
Devonshire Building | 2017-08-11 17:00 | 50734.1942 | 60.012
Devonshire Building | 2017-08-11 17:15 | 50734.2142 | 79.992
Devonshire Building | 2017-08-11 17:30 | 50734.2342 | 79.992
Devonshire Building | 2017-08-11 17:45 | 50734.2542 | 79.992
Devonshire Building | 2017-08-11 18:00 | 50734.2742 | 79.992
Devonshire Building | 2017-08-11 18:15 | 50734.2942 | 79.992
Devonshire Building | 2017-08-11 18:30 | 50734.3092 | 60.012
Devonshire Building | 2017-08-11 18:45 | 50734.3342 | 100.008
Devonshire Building | 2017-08-11 19:00 | 50734.3542 | 79.992
Devonshire Building | 2017-08-11 19:15 | 50734.3692 | 60.012
Devonshire Building | 2017-08-11 19:30 | 50734.3892 | 79.992
Devonshire Building | 2017-08-11 19:45 | 50734.4042 | 60.012
Devonshire Building | 2017-08-11 20:00 | 50734.4242 | 79.992
Devonshire Building | 2017-08-11 20:15 | 50734.4392 | 60.012
Devonshire Building | 2017-08-11 20:30 | 50734.9592 | 2080.008
Devonshire Building | 2017-08-11 20:45 | 50734.9842 | 100.008
Devonshire Building | 2017-08-11 21:00 | 50735.0042 | 79.992
Devonshire Building | 2017-08-11 21:15 | 50735.0192 | 60.012
Devonshire Building | 2017-08-11 21:30 | 50735.0392 | 79.992
Devonshire Building | 2017-08-11 21:45 | 50735.0592 | 79.992
Devonshire Building | 2017-08-11 22:00 | 50735.0792 | 79.992
Devonshire Building | 2017-08-11 22:15 | 50735.0992 | 79.992
Devonshire Building | 2017-08-11 22:30 | 50735.1192 | 79.992
Devonshire Building | 2017-08-11 22:45 | 50735.1392 | 79.992
Devonshire Building | 2017-08-11 23:00 | 50735.1592 | 79.992
Devonshire Building | 2017-08-11 23:15 | 50735.1792 | 79.992
Devonshire Building | 2017-08-11 23:30 | 50735.1992 | 79.992
Devonshire Building | 2017-08-11 23:45 | 50735.2142 | 60.012
Devonshire Building | 2017-08-12 | 50735.2344 | 79.992
Devonshire Building | 2017-08-12 00:15 | 50735.2494 | 60.012
Devonshire Building | 2017-08-12 00:30 | 50735.2644 | 60.012
Devonshire Building | 2017-08-12 00:45 | 50735.2844 | 79.992
Devonshire Building | 2017-08-12 01:00 | 50735.2994 | 60.012
Devonshire Building | 2017-08-12 01:15 | 50735.3144 | 60.012
Devonshire Building | 2017-08-12 01:30 | 50735.3294 | 60.012
Devonshire Building | 2017-08-12 01:45 | 50735.3444 | 60.012
Devonshire Building | 2017-08-12 02:00 | 50735.3594 | 60.012
Devonshire Building | 2017-08-12 02:15 | 50735.3744 | 60.012
Devonshire Building | 2017-08-12 02:30 | 50735.3894 | 60.012
Devonshire Building | 2017-08-12 02:45 | 50735.4044 | 60.012
Devonshire Building | 2017-08-12 03:00 | 50735.4194 | 60.012
Devonshire Building | 2017-08-12 03:15 | 50735.4294 | 39.996
Devonshire Building | 2017-08-12 03:30 | 50735.4444 | 60.012
Devonshire Building | 2017-08-12 03:45 | 50735.4594 | 60.012
Devonshire Building | 2017-08-12 04:00 | 50735.4744 | 60.012
Devonshire Building | 2017-08-12 04:15 | 50735.4844 | 39.996
Devonshire Building | 2017-08-12 04:30 | 50735.4994 | 60.012
Devonshire Building | 2017-08-12 04:45 | 50735.5144 | 60.012
Devonshire Building | 2017-08-12 05:00 | 50735.5244 | 39.996
Devonshire Building | 2017-08-12 05:15 | 50735.5394 | 60.012
Devonshire Building | 2017-08-12 05:30 | 50735.5544 | 60.012
Devonshire Building | 2017-08-12 05:45 | 50735.5644 | 39.996
Devonshire Building | 2017-08-12 06:00 | 50735.5794 | 60.012
Devonshire Building | 2017-08-12 06:15 | 50735.5894 | 39.996
Devonshire Building | 2017-08-12 06:30 | 50735.6044 | 60.012
Devonshire Building | 2017-08-12 06:45 | 50735.6144 | 39.996
Devonshire Building | 2017-08-12 07:00 | 50735.6294 | 60.012
Devonshire Building | 2017-08-12 07:15 | 50735.6394 | 39.996
Devonshire Building | 2017-08-12 07:30 | 50735.6494 | 39.996
Devonshire Building | 2017-08-12 07:45 | 50735.6694 | 79.992
Devonshire Building | 2017-08-12 08:00 | 50735.6994 | 119.988
Devonshire Building | 2017-08-12 08:15 | 50735.7244 | 100.008
Devonshire Building | 2017-08-12 08:30 | 50735.7544 | 119.988
Devonshire Building | 2017-08-12 08:45 | 50735.7794 | 100.008
Devonshire Building | 2017-08-12 09:00 | 50735.8094 | 119.988
Devonshire Building | 2017-08-12 09:15 | 50735.8344 | 100.008
Devonshire Building | 2017-08-12 09:30 | 50735.8644 | 119.988
Devonshire Building | 2017-08-12 09:45 | 50735.8894 | 100.008
Devonshire Building | 2017-08-12 10:00 | 50735.9144 | 100.008
Devonshire Building | 2017-08-12 10:15 | 50735.9294 | 60.012
Devonshire Building | 2017-08-12 10:30 | 50735.9394 | 39.996
Devonshire Building | 2017-08-12 10:45 | 50735.9494 | 39.996
Devonshire Building | 2017-08-12 11:00 | 50735.9594 | 39.996
Devonshire Building | 2017-08-12 11:15 | 50735.9744 | 60.012
Devonshire Building | 2017-08-12 11:30 | 50735.9844 | 39.996
Devonshire Building | 2017-08-12 11:45 | 50735.9944 | 39.996
Devonshire Building | 2017-08-12 12:00 | 50736.0094 | 60.012
Devonshire Building | 2017-08-12 12:15 | 50736.0194 | 39.996
Devonshire Building | 2017-08-12 12:30 | 50736.0294 | 39.996
Devonshire Building | 2017-08-12 12:45 | 50736.5344 | 2019.996
Devonshire Building | 2017-08-12 13:00 | 50736.5394 | 20.016
Devonshire Building | 2017-08-12 13:15 | 50736.5444 | 20.016
Devonshire Building | 2017-08-12 13:30 | 50736.5544 | 39.996
Devonshire Building | 2017-08-12 13:45 | 50736.5594 | 20.016
Devonshire Building | 2017-08-12 14:00 | 50736.5694 | 39.996
Devonshire Building | 2017-08-12 14:15 | 50736.5744 | 20.016
Devonshire Building | 2017-08-12 14:30 | 50736.5794 | 20.016
Devonshire Building | 2017-08-12 14:45 | 50736.5894 | 39.996
Devonshire Building | 2017-08-12 15:00 | 50736.5945 | 20.016
Devonshire Building | 2017-08-12 15:15 | 50736.5995 | 20.016
Devonshire Building | 2017-08-12 15:30 | 50736.6045 | 20.016
Devonshire Building | 2017-08-12 15:45 | 50736.6145 | 39.996
Devonshire Building | 2017-08-12 16:00 | 50736.6195 | 20.016
Devonshire Building | 2017-08-12 16:15 | 50736.6245 | 20.016
Devonshire Building | 2017-08-12 16:30 | 50736.6345 | 39.996
Devonshire Building | 2017-08-12 16:45 | 50736.6445 | 39.996
Devonshire Building | 2017-08-12 17:00 | 50736.6495 | 20.016
Devonshire Building | 2017-08-12 17:15 | 50736.6545 | 20.016
Devonshire Building | 2017-08-12 17:30 | 50736.6645 | 39.996
Devonshire Building | 2017-08-12 17:45 | 50736.6695 | 20.016
Devonshire Building | 2017-08-12 18:00 | 50736.6795 | 39.996
Devonshire Building | 2017-08-12 18:15 | 50736.6845 | 20.016
Devonshire Building | 2017-08-12 18:30 | 50736.6945 | 39.996
Devonshire Building | 2017-08-12 18:45 | 50736.6995 | 20.016
Devonshire Building | 2017-08-12 19:00 | 50736.7095 | 39.996
Devonshire Building | 2017-08-12 19:15 | 50736.7145 | 20.016
Devonshire Building | 2017-08-12 19:30 | 50736.7195 | 20.016
Devonshire Building | 2017-08-12 19:45 | 50736.7295 | 39.996
Devonshire Building | 2017-08-12 20:00 | 50736.7345 | 20.016
Devonshire Building | 2017-08-12 20:15 | 50736.7445 | 39.996
Devonshire Building | 2017-08-12 20:30 | 50736.7495 | 20.016
Devonshire Building | 2017-08-12 20:45 | 50736.7695 | 79.992
Devonshire Building | 2017-08-12 21:00 | 50736.7795 | 39.996
Devonshire Building | 2017-08-12 21:15 | 50736.7845 | 20.016
Devonshire Building | 2017-08-12 21:30 | 50736.7945 | 39.996
Devonshire Building | 2017-08-12 21:45 | 50736.7995 | 20.016
Devonshire Building | 2017-08-12 22:00 | 50736.8095 | 39.996
Devonshire Building | 2017-08-12 22:15 | 50736.8195 | 39.996
Devonshire Building | 2017-08-12 22:30 | 50736.8245 | 20.016
Devonshire Building | 2017-08-12 22:45 | 50736.8345 | 39.996
Devonshire Building | 2017-08-12 23:00 | 50736.8395 | 20.016
Devonshire Building | 2017-08-12 23:15 | 50736.8495 | 39.996
Devonshire Building | 2017-08-12 23:30 | 50736.8595 | 39.996
Devonshire Building | 2017-08-12 23:45 | 50736.8645 | 20.016
Devonshire Building | 2017-08-13 | 50736.875 | 39.996
Devonshire Building | 2017-08-13 00:15 | 50736.88 | 20.016
Devonshire Building | 2017-08-13 00:30 | 50736.89 | 39.996
Devonshire Building | 2017-08-13 00:45 | 50736.895 | 20.016
Devonshire Building | 2017-08-13 01:00 | 50736.905 | 39.996
Devonshire Building | 2017-08-13 01:15 | 50736.91 | 20.016
Devonshire Building | 2017-08-13 01:30 | 50736.92 | 39.996
Devonshire Building | 2017-08-13 01:45 | 50736.93 | 39.996
Devonshire Building | 2017-08-13 02:00 | 50736.935 | 20.016
Devonshire Building | 2017-08-13 02:15 | 50736.945 | 39.996
Devonshire Building | 2017-08-13 02:30 | 50736.95 | 20.016
Devonshire Building | 2017-08-13 02:45 | 50736.96 | 39.996
Devonshire Building | 2017-08-13 03:00 | 50736.97 | 39.996
Devonshire Building | 2017-08-13 03:15 | 50736.98 | 39.996
Devonshire Building | 2017-08-13 03:30 | 50736.985 | 20.016
Devonshire Building | 2017-08-13 03:45 | 50736.995 | 39.996
Devonshire Building | 2017-08-13 04:00 | 50737.005 | 39.996
Devonshire Building | 2017-08-13 04:15 | 50737.015 | 39.996
Devonshire Building | 2017-08-13 04:30 | 50737.025 | 39.996
Devonshire Building | 2017-08-13 04:45 | 50737.035 | 39.996
Devonshire Building | 2017-08-13 05:00 | 50737.045 | 39.996
Devonshire Building | 2017-08-13 05:15 | 50737.055 | 39.996
Devonshire Building | 2017-08-13 05:30 | 50737.065 | 39.996
Devonshire Building | 2017-08-13 05:45 | 50737.075 | 39.996
Devonshire Building | 2017-08-13 06:00 | 50737.085 | 39.996
Devonshire Building | 2017-08-13 06:15 | 50737.095 | 39.996
Devonshire Building | 2017-08-13 06:30 | 50737.105 | 39.996
Devonshire Building | 2017-08-13 06:45 | 50737.115 | 39.996
Devonshire Building | 2017-08-13 07:00 | 50737.125 | 39.996
Devonshire Building | 2017-08-13 07:15 | 50737.135 | 39.996
Devonshire Building | 2017-08-13 07:30 | 50737.145 | 39.996
Devonshire Building | 2017-08-13 07:45 | 50737.16 | 60.012
Devonshire Building | 2017-08-13 08:00 | 50737.185 | 100.008
Devonshire Building | 2017-08-13 08:15 | 50737.7 | 2059.992
Devonshire Building | 2017-08-13 08:30 | 50737.74 | 159.984
Devonshire Building | 2017-08-13 08:45 | 50737.775 | 140.004
Devonshire Building | 2017-08-13 09:00 | 50737.805 | 119.988
Devonshire Building | 2017-08-13 09:15 | 50737.84 | 140.004
Devonshire Building | 2017-08-13 09:30 | 50737.875 | 140.004
Devonshire Building | 2017-08-13 09:45 | 50737.905 | 119.988
Devonshire Building | 2017-08-13 10:00 | 50737.925 | 79.992
Devonshire Building | 2017-08-13 10:15 | 50737.95 | 100.008
Devonshire Building | 2017-08-13 10:30 | 50737.97 | 79.992
Devonshire Building | 2017-08-13 10:45 | 50737.99 | 79.992
Devonshire Building | 2017-08-13 11:00 | 50738.01 | 79.992
Devonshire Building | 2017-08-13 11:15 | 50738.03 | 79.992
Devonshire Building | 2017-08-13 11:30 | 50738.045 | 60.012
Devonshire Building | 2017-08-13 11:45 | 50738.065 | 79.992
Devonshire Building | 2017-08-13 12:00 | 50738.08 | 60.012
Devonshire Building | 2017-08-13 12:15 | 50738.1 | 79.992
Devonshire Building | 2017-08-13 12:30 | 50738.115 | 60.012
Devonshire Building | 2017-08-13 12:45 | 50738.13 | 60.012
Devonshire Building | 2017-08-13 13:00 | 50738.145 | 60.012
Devonshire Building | 2017-08-13 13:15 | 50738.16 | 60.012
Devonshire Building | 2017-08-13 13:30 | 50738.175 | 60.012
Devonshire Building | 2017-08-13 13:45 | 50738.19 | 60.012
Devonshire Building | 2017-08-13 14:00 | 50738.205 | 60.012
Devonshire Building | 2017-08-13 14:15 | 50738.22 | 60.012
Devonshire Building | 2017-08-13 14:30 | 50738.235 | 60.012
Devonshire Building | 2017-08-13 14:45 | 50738.25 | 60.012
Devonshire Building | 2017-08-13 15:00 | 50738.26 | 39.996
Devonshire Building | 2017-08-13 15:15 | 50738.275 | 60.012
Devonshire Building | 2017-08-13 15:30 | 50738.285 | 39.996
Devonshire Building | 2017-08-13 15:45 | 50738.3 | 60.012
Devonshire Building | 2017-08-13 16:00 | 50738.315 | 60.012
Devonshire Building | 2017-08-13 16:15 | 50738.325 | 39.996
Devonshire Building | 2017-08-13 16:30 | 50738.34 | 60.012
Devonshire Building | 2017-08-13 16:45 | 50738.35 | 39.996
Devonshire Building | 2017-08-13 17:00 | 50738.365 | 60.012
Devonshire Building | 2017-08-13 17:15 | 50738.375 | 39.996
Devonshire Building | 2017-08-13 17:30 | 50738.385 | 39.996
Devonshire Building | 2017-08-13 17:45 | 50738.395 | 39.996
Devonshire Building | 2017-08-13 18:00 | 50738.41 | 60.012
Devonshire Building | 2017-08-13 18:15 | 50738.42 | 39.996
Devonshire Building | 2017-08-13 18:30 | 50738.43 | 39.996
Devonshire Building | 2017-08-13 18:45 | 50738.44 | 39.996
Devonshire Building | 2017-08-13 19:00 | 50738.45 | 39.996
Devonshire Building | 2017-08-13 19:15 | 50738.46 | 39.996
Devonshire Building | 2017-08-13 19:30 | 50738.47 | 39.996
Devonshire Building | 2017-08-13 19:45 | 50738.48 | 39.996
Devonshire Building | 2017-08-13 20:00 | 50738.49 | 39.996
Devonshire Building | 2017-08-13 20:15 | 50738.5 | 39.996
Devonshire Building | 2017-08-13 20:30 | 50738.515 | 60.012
Devonshire Building | 2017-08-13 20:45 | 50738.545 | 119.988
Devonshire Building | 2017-08-13 21:00 | 50738.55 | 20.016
Devonshire Building | 2017-08-13 21:15 | 50738.56 | 39.996
Devonshire Building | 2017-08-13 21:30 | 50738.565 | 20.016
Devonshire Building | 2017-08-13 21:45 | 50738.575 | 39.996
Devonshire Building | 2017-08-13 22:00 | 50738.58 | 20.016
Devonshire Building | 2017-08-13 22:15 | 50738.585 | 20.016
Devonshire Building | 2017-08-13 22:30 | 50738.595 | 39.996
Devonshire Building | 2017-08-13 22:45 | 50738.6 | 20.016
Devonshire Building | 2017-08-13 23:00 | 50738.61 | 39.996
Devonshire Building | 2017-08-13 23:15 | 50738.615 | 20.016
Devonshire Building | 2017-08-13 23:30 | 50738.625 | 39.996
Devonshire Building | 2017-08-13 23:45 | 50738.63 | 20.016
Devonshire Building | 2017-08-14 | 50738.6406 | 39.996
Devonshire Building | 2017-08-14 00:15 | 50738.6456 | 20.016
Devonshire Building | 2017-08-14 00:30 | 50738.6556 | 39.996
Devonshire Building | 2017-08-14 00:45 | 50738.6606 | 20.016
Devonshire Building | 2017-08-14 01:00 | 50738.6656 | 20.016
Devonshire Building | 2017-08-14 01:15 | 50738.6756 | 39.996
Devonshire Building | 2017-08-14 01:30 | 50738.6806 | 20.016
Devonshire Building | 2017-08-14 01:45 | 50738.6906 | 39.996
Devonshire Building | 2017-08-14 02:00 | 50738.7056 | 60.012
Devonshire Building | 2017-08-14 02:15 | 50739.1906 | 1940.004
Devonshire Building | 2017-08-14 02:30 | 50739.2006 | 39.996
Devonshire Building | 2017-08-14 02:45 | 50739.2057 | 20.016
Devonshire Building | 2017-08-14 03:00 | 50739.2156 | 39.996
Devonshire Building | 2017-08-14 03:15 | 50739.2207 | 20.016
Devonshire Building | 2017-08-14 03:30 | 50739.2307 | 39.996
Devonshire Building | 2017-08-14 03:45 | 50739.2357 | 20.016
Devonshire Building | 2017-08-14 04:00 | 50739.2457 | 39.996
Devonshire Building | 2017-08-14 04:15 | 50739.2507 | 20.016
Devonshire Building | 2017-08-14 04:30 | 50739.2607 | 39.996
Devonshire Building | 2017-08-14 04:45 | 50739.2657 | 20.016
Devonshire Building | 2017-08-14 05:00 | 50739.2757 | 39.996
Devonshire Building | 2017-08-14 05:15 | 50739.2857 | 39.996
Devonshire Building | 2017-08-14 05:30 | 50739.2957 | 39.996
Devonshire Building | 2017-08-14 05:45 | 50739.3057 | 39.996
Devonshire Building | 2017-08-14 06:00 | 50739.3207 | 60.012
Devonshire Building | 2017-08-14 06:15 | 50739.3407 | 79.992
Devonshire Building | 2017-08-14 06:30 | 50739.3507 | 39.996
Devonshire Building | 2017-08-14 06:45 | 50739.3607 | 39.996
Devonshire Building | 2017-08-14 07:00 | 50739.3707 | 39.996
Devonshire Building | 2017-08-14 07:15 | 50739.3907 | 79.992
Devonshire Building | 2017-08-14 07:30 | 50739.4107 | 79.992
Devonshire Building | 2017-08-14 07:45 | 50739.4707 | 240.012
Devonshire Building | 2017-08-14 08:00 | 50739.5457 | 299.988
Devonshire Building | 2017-08-14 08:15 | 50739.6306 | 339.984
Devonshire Building | 2017-08-14 08:30 | 50739.8856 | 1019.988
Devonshire Building | 2017-08-14 08:45 | 50740.3206 | 1739.988
Devonshire Building | 2017-08-14 09:00 | 50740.4206 | 399.996
Devonshire Building | 2017-08-14 09:15 | 50740.5256 | 420.012
Devonshire Building | 2017-08-14 09:30 | 50740.6356 | 439.992
Devonshire Building | 2017-08-14 09:45 | 50741.2706 | 2540.016
Devonshire Building | 2017-08-14 10:00 | 50741.3556 | 339.984
Devonshire Building | 2017-08-14 10:15 | 50741.4306 | 299.988
Devonshire Building | 2017-08-14 10:30 | 50741.5056 | 299.988
Devonshire Building | 2017-08-14 10:45 | 50741.5756 | 280.008
Devonshire Building | 2017-08-14 11:00 | 50741.6356 | 240.012
Devonshire Building | 2017-08-14 11:15 | 50742.2156 | 2319.984
Devonshire Building | 2017-08-14 11:30 | 50742.2606 | 180
Devonshire Building | 2017-08-14 11:45 | 50742.3056 | 180
Devonshire Building | 2017-08-14 12:00 | 50742.3556 | 200.016
Devonshire Building | 2017-08-14 12:15 | 50742.4056 | 200.016
Devonshire Building | 2017-08-14 12:30 | 50742.4556 | 200.016
Devonshire Building | 2017-08-14 12:45 | 50742.4956 | 159.984
Devonshire Building | 2017-08-14 13:00 | 50743.0956 | 2400.012
Devonshire Building | 2017-08-14 13:15 | 50743.1457 | 200.016
Devonshire Building | 2017-08-14 13:30 | 50743.2206 | 299.988
Devonshire Building | 2017-08-14 13:45 | 50743.2756 | 219.996
Devonshire Building | 2017-08-14 14:00 | 50743.3257 | 200.016
Devonshire Building | 2017-08-14 14:15 | 50743.3707 | 180
Devonshire Building | 2017-08-14 14:30 | 50743.4207 | 200.016
Devonshire Building | 2017-08-14 14:45 | 50743.4607 | 159.984
Devonshire Building | 2017-08-14 15:00 | 50743.5057 | 180
Devonshire Building | 2017-08-14 15:15 | 50744.0656 | 2239.992
Devonshire Building | 2017-08-14 15:30 | 50744.1056 | 159.984
Devonshire Building | 2017-08-14 15:45 | 50744.1557 | 200.016
Devonshire Building | 2017-08-14 16:00 | 50744.2106 | 219.996
Devonshire Building | 2017-08-14 16:15 | 50744.2907 | 320.004
Devonshire Building | 2017-08-14 16:30 | 50744.5057 | 860.004
Devonshire Building | 2017-08-14 16:45 | 50744.6407 | 540
Devonshire Building | 2017-08-14 17:00 | 50744.7307 | 360
Devonshire Building | 2017-08-14 17:15 | 50744.7907 | 240.012
Devonshire Building | 2017-08-14 17:30 | 50744.8357 | 180
Devonshire Building | 2017-08-14 17:45 | 50744.8707 | 140.004
Devonshire Building | 2017-08-14 18:00 | 50744.9057 | 140.004
Devonshire Building | 2017-08-14 18:15 | 50744.9357 | 119.988
Devonshire Building | 2017-08-14 18:30 | 50745.4407 | 2019.996
Devonshire Building | 2017-08-14 18:45 | 50745.4507 | 39.996
Devonshire Building | 2017-08-14 19:00 | 50745.4607 | 39.996
Devonshire Building | 2017-08-14 19:15 | 50745.4706 | 39.996
Devonshire Building | 2017-08-14 19:30 | 50745.4757 | 20.016
Devonshire Building | 2017-08-14 19:45 | 50745.4857 | 39.996
Devonshire Building | 2017-08-14 20:00 | 50745.4957 | 39.996
Devonshire Building | 2017-08-14 20:15 | 50745.5056 | 39.996
Devonshire Building | 2017-08-14 20:30 | 50745.5156 | 39.996
Devonshire Building | 2017-08-14 20:45 | 50745.5356 | 79.992
Devonshire Building | 2017-08-14 21:00 | 50745.5456 | 39.996
Devonshire Building | 2017-08-14 21:15 | 50745.5506 | 20.016
Devonshire Building | 2017-08-14 21:30 | 50745.5606 | 39.996
Devonshire Building | 2017-08-14 21:45 | 50745.5706 | 39.996
Devonshire Building | 2017-08-14 22:00 | 50745.5757 | 20.016
Devonshire Building | 2017-08-14 22:15 | 50745.5857 | 39.996
Devonshire Building | 2017-08-14 22:30 | 50745.5957 | 39.996
Devonshire Building | 2017-08-14 22:45 | 50745.6007 | 20.016
Devonshire Building | 2017-08-14 23:00 | 50745.6107 | 39.996
Devonshire Building | 2017-08-14 23:15 | 50745.6207 | 39.996
Devonshire Building | 2017-08-14 23:30 | 50745.6257 | 20.016
Devonshire Building | 2017-08-14 23:45 | 50745.6357 | 39.996
Devonshire Building | 2017-08-15 | 50745.6406 | 20.016
Devonshire Building | 2017-08-15 00:15 | 50745.6506 | 39.996
Devonshire Building | 2017-08-15 00:30 | 50745.6556 | 20.016
Devonshire Building | 2017-08-15 00:45 | 50745.6656 | 39.996
Devonshire Building | 2017-08-15 01:00 | 50745.6706 | 20.016
Devonshire Building | 2017-08-15 01:15 | 50745.6806 | 39.996
Devonshire Building | 2017-08-15 01:30 | 50745.6856 | 20.016
Devonshire Building | 2017-08-15 01:45 | 50745.6956 | 39.996
Devonshire Building | 2017-08-15 02:00 | 50745.7006 | 20.016
Devonshire Building | 2017-08-15 02:15 | 50745.7106 | 39.996
Devonshire Building | 2017-08-15 02:30 | 50745.7156 | 20.016
Devonshire Building | 2017-08-15 02:45 | 50745.7206 | 20.016
Devonshire Building | 2017-08-15 03:00 | 50745.7306 | 39.996
Devonshire Building | 2017-08-15 03:15 | 50745.7357 | 20.016
Devonshire Building | 2017-08-15 03:30 | 50745.7457 | 39.996
Devonshire Building | 2017-08-15 03:45 | 50745.7507 | 20.016
Devonshire Building | 2017-08-15 04:00 | 50745.7607 | 39.996
Devonshire Building | 2017-08-15 04:15 | 50745.7657 | 20.016
Devonshire Building | 2017-08-15 04:30 | 50745.7707 | 20.016
Devonshire Building | 2017-08-15 04:45 | 50745.7807 | 39.996
Devonshire Building | 2017-08-15 05:00 | 50745.7857 | 20.016
Devonshire Building | 2017-08-15 05:15 | 50745.7957 | 39.996
Devonshire Building | 2017-08-15 05:30 | 50745.8057 | 39.996
Devonshire Building | 2017-08-15 05:45 | 50745.8107 | 20.016
Devonshire Building | 2017-08-15 06:00 | 50745.8207 | 39.996
Devonshire Building | 2017-08-15 06:15 | 50745.8407 | 79.992
Devonshire Building | 2017-08-15 06:30 | 50745.8507 | 39.996
Devonshire Building | 2017-08-15 06:45 | 50745.8607 | 39.996
Devonshire Building | 2017-08-15 07:00 | 50745.8757 | 60.012
Devonshire Building | 2017-08-15 07:15 | 50746.3907 | 2059.992
Devonshire Building | 2017-08-15 07:30 | 50746.4407 | 200.016
Devonshire Building | 2017-08-15 07:45 | 50746.5107 | 280.008
Devonshire Building | 2017-08-15 08:00 | 50746.6057 | 380.016
Devonshire Building | 2017-08-15 08:15 | 50746.7007 | 380.016
Devonshire Building | 2017-08-15 08:30 | 50746.7907 | 360
Devonshire Building | 2017-08-15 08:45 | 50746.8707 | 320.004
Devonshire Building | 2017-08-15 09:00 | 50746.9507 | 320.004
Devonshire Building | 2017-08-15 09:15 | 50747.0307 | 320.004
Devonshire Building | 2017-08-15 09:30 | 50747.6357 | 2419.992
Devonshire Building | 2017-08-15 09:45 | 50747.6907 | 219.996
Devonshire Building | 2017-08-15 10:00 | 50747.7607 | 280.008
Devonshire Building | 2017-08-15 10:15 | 50747.8357 | 299.988
Devonshire Building | 2017-08-15 10:30 | 50747.9057 | 280.008
Devonshire Building | 2017-08-15 10:45 | 50747.9757 | 280.008
Devonshire Building | 2017-08-15 11:00 | 50748.6057 | 2520
Devonshire Building | 2017-08-15 11:15 | 50748.6657 | 240.012
Devonshire Building | 2017-08-15 11:30 | 50748.7207 | 219.996
Devonshire Building | 2017-08-15 11:45 | 50748.7757 | 219.996
Devonshire Building | 2017-08-15 12:00 | 50748.8307 | 219.996
Devonshire Building | 2017-08-15 12:15 | 50748.8807 | 200.016
Devonshire Building | 2017-08-15 12:30 | 50749.4607 | 2319.984
Devonshire Building | 2017-08-15 12:45 | 50749.4957 | 140.004
Devonshire Building | 2017-08-15 13:00 | 50749.5357 | 159.984
Devonshire Building | 2017-08-15 13:15 | 50749.5807 | 180
Devonshire Building | 2017-08-15 13:30 | 50749.6157 | 140.004
Devonshire Building | 2017-08-15 13:45 | 50749.6507 | 140.004
Devonshire Building | 2017-08-15 14:00 | 50749.6807 | 119.988
Devonshire Building | 2017-08-15 14:15 | 50750.1857 | 2019.996
Devonshire Building | 2017-08-15 14:30 | 50750.2857 | 399.996
Devonshire Building | 2017-08-15 14:45 | 50750.3357 | 200.016
Devonshire Building | 2017-08-15 15:00 | 50750.3807 | 180
Devonshire Building | 2017-08-15 15:15 | 50750.4207 | 159.984
Devonshire Building | 2017-08-15 15:30 | 50750.4707 | 200.016
Devonshire Building | 2017-08-15 15:45 | 50750.5407 | 280.008
Devonshire Building | 2017-08-15 16:00 | 50750.8857 | 1379.988
Devonshire Building | 2017-08-15 16:15 | 50751.2307 | 1379.988
Devonshire Building | 2017-08-15 16:30 | 50751.3057 | 299.988
Devonshire Building | 2017-08-15 16:45 | 50751.3707 | 259.992
Devonshire Building | 2017-08-15 17:00 | 50751.4307 | 240.012
Devonshire Building | 2017-08-15 17:15 | 50751.4757 | 180
Devonshire Building | 2017-08-15 17:30 | 50751.5157 | 159.984
Devonshire Building | 2017-08-15 17:45 | 50751.5507 | 140.004
Devonshire Building | 2017-08-15 18:00 | 50751.5807 | 119.988
Devonshire Building | 2017-08-15 18:15 | 50751.6107 | 119.988
Devonshire Building | 2017-08-15 18:30 | 50751.6357 | 100.008
Devonshire Building | 2017-08-15 18:45 | 50751.6607 | 100.008
Devonshire Building | 2017-08-15 19:00 | 50751.6807 | 79.992
Devonshire Building | 2017-08-15 19:15 | 50751.7007 | 79.992
Devonshire Building | 2017-08-15 19:30 | 50751.7207 | 79.992
Devonshire Building | 2017-08-15 19:45 | 50751.7407 | 79.992
Devonshire Building | 2017-08-15 20:00 | 50751.7557 | 60.012
Devonshire Building | 2017-08-15 20:15 | 50751.8457 | 360
Devonshire Building | 2017-08-15 20:30 | 50752.2807 | 1739.988
Devonshire Building | 2017-08-15 20:45 | 50752.3007 | 79.992
Devonshire Building | 2017-08-15 21:00 | 50752.3057 | 20.016
Devonshire Building | 2017-08-15 21:15 | 50752.3157 | 39.996
Devonshire Building | 2017-08-15 21:30 | 50752.3257 | 39.996
Devonshire Building | 2017-08-15 21:45 | 50752.3357 | 39.996
Devonshire Building | 2017-08-15 22:00 | 50752.3407 | 20.016
Devonshire Building | 2017-08-15 22:15 | 50752.3507 | 39.996
Devonshire Building | 2017-08-15 22:30 | 50752.3607 | 39.996
Devonshire Building | 2017-08-15 22:45 | 50752.3657 | 20.016
Devonshire Building | 2017-08-15 23:00 | 50752.3757 | 39.996
Devonshire Building | 2017-08-15 23:15 | 50752.3857 | 39.996
Devonshire Building | 2017-08-15 23:30 | 50752.3957 | 39.996
Devonshire Building | 2017-08-15 23:45 | 50752.4057 | 39.996
Devonshire Building | 2017-08-16 | 50752.4141 | 39.996
Devonshire Building | 2017-08-16 00:15 | 50752.4241 | 39.996
Devonshire Building | 2017-08-16 00:30 | 50752.4341 | 39.996
Devonshire Building | 2017-08-16 00:45 | 50752.4391 | 20.016
Devonshire Building | 2017-08-16 01:00 | 50752.4491 | 39.996
Devonshire Building | 2017-08-16 01:15 | 50752.4591 | 39.996
Devonshire Building | 2017-08-16 01:30 | 50752.4691 | 39.996
Devonshire Building | 2017-08-16 01:45 | 50752.4741 | 20.016
Devonshire Building | 2017-08-16 02:00 | 50752.4841 | 39.996
Devonshire Building | 2017-08-16 02:15 | 50752.4941 | 39.996
Devonshire Building | 2017-08-16 02:30 | 50752.4991 | 20.016
Devonshire Building | 2017-08-16 02:45 | 50752.5091 | 39.996
Devonshire Building | 2017-08-16 03:00 | 50752.5141 | 20.016
Devonshire Building | 2017-08-16 03:15 | 50752.5241 | 39.996
Devonshire Building | 2017-08-16 03:30 | 50752.5341 | 39.996
Devonshire Building | 2017-08-16 03:45 | 50752.5391 | 20.016
Devonshire Building | 2017-08-16 04:00 | 50752.5491 | 39.996
Devonshire Building | 2017-08-16 04:15 | 50752.5541 | 20.016
Devonshire Building | 2017-08-16 04:30 | 50752.5641 | 39.996
Devonshire Building | 2017-08-16 04:45 | 50752.5691 | 20.016
Devonshire Building | 2017-08-16 05:00 | 50752.5791 | 39.996
Devonshire Building | 2017-08-16 05:15 | 50752.5891 | 39.996
Devonshire Building | 2017-08-16 05:30 | 50752.5941 | 20.016
Devonshire Building | 2017-08-16 05:45 | 50752.6041 | 39.996
Devonshire Building | 2017-08-16 06:00 | 50752.6141 | 39.996
Devonshire Building | 2017-08-16 06:15 | 50752.6241 | 39.996
Devonshire Building | 2017-08-16 06:30 | 50752.6341 | 39.996
Devonshire Building | 2017-08-16 06:45 | 50752.6441 | 39.996
Devonshire Building | 2017-08-16 07:00 | 50752.6541 | 39.996
Devonshire Building | 2017-08-16 07:15 | 50752.6691 | 60.012
Devonshire Building | 2017-08-16 07:30 | 50752.6791 | 39.996
Devonshire Building | 2017-08-16 07:45 | 50752.7041 | 100.008
Devonshire Building | 2017-08-16 08:00 | 50753.2591 | 2220.012
Devonshire Building | 2017-08-16 08:15 | 50753.2991 | 159.984
Devonshire Building | 2017-08-16 08:30 | 50753.3491 | 200.016
Devonshire Building | 2017-08-16 08:45 | 50753.4141 | 259.992
Devonshire Building | 2017-08-16 09:00 | 50753.4991 | 339.984
Devonshire Building | 2017-08-16 09:15 | 50753.5941 | 380.016
Devonshire Building | 2017-08-16 09:30 | 50754.2291 | 2540.016
Devonshire Building | 2017-08-16 09:45 | 50754.4191 | 759.996
Devonshire Building | 2017-08-16 10:00 | 50754.6291 | 839.988
Devonshire Building | 2017-08-16 10:15 | 50754.7791 | 600.012
Devonshire Building | 2017-08-16 10:30 | 50754.8791 | 399.996
Devonshire Building | 2017-08-16 10:45 | 50754.9541 | 299.988
Devonshire Building | 2017-08-16 11:00 | 50755.5541 | 2400.012
Devonshire Building | 2017-08-16 11:15 | 50755.5841 | 119.988
Devonshire Building | 2017-08-16 11:30 | 50755.6191 | 140.004
Devonshire Building | 2017-08-16 11:45 | 50755.6541 | 140.004
Devonshire Building | 2017-08-16 12:00 | 50755.6891 | 140.004
Devonshire Building | 2017-08-16 12:15 | 50755.7291 | 159.984
Devonshire Building | 2017-08-16 12:30 | 50755.7591 | 119.988
Devonshire Building | 2017-08-16 12:45 | 50755.8041 | 180
Devonshire Building | 2017-08-16 13:00 | 50756.1891 | 1540.008
Devonshire Building | 2017-08-16 13:15 | 50756.4191 | 920.016
Devonshire Building | 2017-08-16 13:30 | 50756.4491 | 119.988
Devonshire Building | 2017-08-16 13:45 | 50756.4791 | 119.988
Devonshire Building | 2017-08-16 14:00 | 50756.5041 | 100.008
Devonshire Building | 2017-08-16 14:15 | 50756.5441 | 159.984
Devonshire Building | 2017-08-16 14:30 | 50756.5991 | 219.996
Devonshire Building | 2017-08-16 14:45 | 50756.7491 | 600.012
Devonshire Building | 2017-08-16 15:00 | 50756.8841 | 540
Devonshire Building | 2017-08-16 15:15 | 50757.5241 | 2559.996
Devonshire Building | 2017-08-16 15:30 | 50757.6341 | 439.992
Devonshire Building | 2017-08-16 15:45 | 50757.7441 | 439.992
Devonshire Building | 2017-08-16 16:00 | 50757.8341 | 360
Devonshire Building | 2017-08-16 16:15 | 50757.9091 | 299.988
Devonshire Building | 2017-08-16 16:30 | 50757.9641 | 219.996
Devonshire Building | 2017-08-16 16:45 | 50758.0091 | 180
Devonshire Building | 2017-08-16 17:00 | 50758.0491 | 159.984
Devonshire Building | 2017-08-16 17:15 | 50758.0791 | 119.988
Devonshire Building | 2017-08-16 17:30 | 50758.1091 | 119.988
Devonshire Building | 2017-08-16 17:45 | 50758.139 | 119.988
Devonshire Building | 2017-08-16 18:00 | 50758.159 | 79.992
Devonshire Building | 2017-08-16 18:15 | 50758.1841 | 100.008
Devonshire Building | 2017-08-16 18:30 | 50758.654 | 1879.992
Devonshire Building | 2017-08-16 18:45 | 50758.709 | 219.996
Devonshire Building | 2017-08-16 19:00 | 50758.719 | 39.996
Devonshire Building | 2017-08-16 19:15 | 50758.729 | 39.996
Devonshire Building | 2017-08-16 19:30 | 50758.739 | 39.996
Devonshire Building | 2017-08-16 19:45 | 50758.754 | 60.012
Devonshire Building | 2017-08-16 20:00 | 50758.779 | 100.008
Devonshire Building | 2017-08-16 20:15 | 50758.8041 | 100.008
Devonshire Building | 2017-08-16 20:30 | 50758.834 | 119.988
Devonshire Building | 2017-08-16 20:45 | 50758.869 | 140.004
Devonshire Building | 2017-08-16 21:00 | 50758.8941 | 100.008
Devonshire Building | 2017-08-16 21:15 | 50758.9191 | 100.008
Devonshire Building | 2017-08-16 21:30 | 50758.9441 | 100.008
Devonshire Building | 2017-08-16 21:45 | 50758.9541 | 39.996
Devonshire Building | 2017-08-16 22:00 | 50758.9641 | 39.996
Devonshire Building | 2017-08-16 22:15 | 50758.9741 | 39.996
Devonshire Building | 2017-08-16 22:30 | 50758.9841 | 39.996
Devonshire Building | 2017-08-16 22:45 | 50758.9941 | 39.996
Devonshire Building | 2017-08-16 23:00 | 50758.9991 | 20.016
Devonshire Building | 2017-08-16 23:15 | 50759.0091 | 39.996
Devonshire Building | 2017-08-16 23:30 | 50759.0191 | 39.996
Devonshire Building | 2017-08-16 23:45 | 50759.0241 | 20.016
Devonshire Building | 2017-08-17 | 50759.0352 | 39.996
Devonshire Building | 2017-08-17 00:15 | 50759.0452 | 39.996
Devonshire Building | 2017-08-17 00:30 | 50759.0502 | 20.016
Devonshire Building | 2017-08-17 00:45 | 50759.0602 | 39.996
Devonshire Building | 2017-08-17 01:00 | 50759.0652 | 20.016
Devonshire Building | 2017-08-17 01:15 | 50759.0752 | 39.996
Devonshire Building | 2017-08-17 01:30 | 50759.0802 | 20.016
Devonshire Building | 2017-08-17 01:45 | 50759.0902 | 39.996
Devonshire Building | 2017-08-17 02:00 | 50759.1002 | 39.996
Devonshire Building | 2017-08-17 02:15 | 50759.1052 | 20.016
Devonshire Building | 2017-08-17 02:30 | 50759.1152 | 39.996
Devonshire Building | 2017-08-17 02:45 | 50759.1202 | 20.016
Devonshire Building | 2017-08-17 03:00 | 50759.1302 | 39.996
Devonshire Building | 2017-08-17 03:15 | 50759.1402 | 39.996
Devonshire Building | 2017-08-17 03:30 | 50759.1452 | 20.016
Devonshire Building | 2017-08-17 03:45 | 50759.1552 | 39.996
Devonshire Building | 2017-08-17 04:00 | 50759.1652 | 39.996
Devonshire Building | 2017-08-17 04:15 | 50759.1702 | 20.016
Devonshire Building | 2017-08-17 04:30 | 50759.1802 | 39.996
Devonshire Building | 2017-08-17 04:45 | 50759.1902 | 39.996
Devonshire Building | 2017-08-17 05:00 | 50759.1952 | 20.016
Devonshire Building | 2017-08-17 05:15 | 50759.2052 | 39.996
Devonshire Building | 2017-08-17 05:30 | 50759.2152 | 39.996
Devonshire Building | 2017-08-17 05:45 | 50759.2252 | 39.996
Devonshire Building | 2017-08-17 06:00 | 50759.2352 | 39.996
Devonshire Building | 2017-08-17 06:15 | 50759.2502 | 60.012
Devonshire Building | 2017-08-17 06:30 | 50759.2602 | 39.996
Devonshire Building | 2017-08-17 06:45 | 50759.2802 | 79.992
Devonshire Building | 2017-08-17 07:00 | 50759.2902 | 39.996
Devonshire Building | 2017-08-17 07:15 | 50759.3052 | 60.012
Devonshire Building | 2017-08-17 07:30 | 50759.8352 | 2120.004
Devonshire Building | 2017-08-17 07:45 | 50759.8602 | 100.008
Devonshire Building | 2017-08-17 08:00 | 50759.8852 | 100.008
Devonshire Building | 2017-08-17 08:15 | 50759.9202 | 140.004
Devonshire Building | 2017-08-17 08:30 | 50759.9652 | 180
Devonshire Building | 2017-08-17 08:45 | 50760.0102 | 180
Devonshire Building | 2017-08-17 09:00 | 50760.0602 | 200.016
Devonshire Building | 2017-08-17 09:15 | 50760.2202 | 640.008
Devonshire Building | 2017-08-17 09:30 | 50760.7102 | 1959.984
Devonshire Building | 2017-08-17 09:45 | 50760.7702 | 240.012
Devonshire Building | 2017-08-17 10:00 | 50760.8402 | 280.008
Devonshire Building | 2017-08-17 10:15 | 50760.9052 | 259.992
Devonshire Building | 2017-08-17 10:30 | 50760.9702 | 259.992
Devonshire Building | 2017-08-17 10:45 | 50761.2002 | 920.016
Devonshire Building | 2017-08-17 11:00 | 50761.5852 | 1540.008
Devonshire Building | 2017-08-17 11:15 | 50761.6402 | 219.996
Devonshire Building | 2017-08-17 11:30 | 50761.6952 | 219.996
Devonshire Building | 2017-08-17 11:45 | 50761.7502 | 219.996
Devonshire Building | 2017-08-17 12:00 | 50761.8052 | 219.996
Devonshire Building | 2017-08-17 12:15 | 50761.8552 | 200.016
Devonshire Building | 2017-08-17 12:30 | 50761.9052 | 200.016
Devonshire Building | 2017-08-17 12:45 | 50762.4602 | 2220.012
Devonshire Building | 2017-08-17 13:00 | 50762.5052 | 180
Devonshire Building | 2017-08-17 13:15 | 50762.5552 | 200.016
Devonshire Building | 2017-08-17 13:30 | 50762.6052 | 200.016
Devonshire Building | 2017-08-17 13:45 | 50762.6702 | 259.992
Devonshire Building | 2017-08-17 14:00 | 50762.7402 | 280.008
Devonshire Building | 2017-08-17 14:15 | 50762.8052 | 259.992
Devonshire Building | 2017-08-17 14:30 | 50762.8652 | 240.012
Devonshire Building | 2017-08-17 14:45 | 50763.4452 | 2319.984
Devonshire Building | 2017-08-17 15:00 | 50763.5802 | 540
Devonshire Building | 2017-08-17 15:15 | 50763.7302 | 600.012
Devonshire Building | 2017-08-17 15:30 | 50763.8752 | 579.996
Devonshire Building | 2017-08-17 15:45 | 50764.1752 | 1199.988
Devonshire Building | 2017-08-17 16:00 | 50764.3752 | 799.992
Devonshire Building | 2017-08-17 16:15 | 50764.4902 | 460.008
Devonshire Building | 2017-08-17 16:30 | 50764.5652 | 299.988
Devonshire Building | 2017-08-17 16:45 | 50764.6252 | 240.012
Devonshire Building | 2017-08-17 17:00 | 50764.6752 | 200.016
Devonshire Building | 2017-08-17 17:15 | 50765.1952 | 2080.008
Devonshire Building | 2017-08-17 17:30 | 50765.2102 | 60.012
Devonshire Building | 2017-08-17 17:45 | 50765.2302 | 79.992
Devonshire Building | 2017-08-17 18:00 | 50765.2452 | 60.012
Devonshire Building | 2017-08-17 18:15 | 50765.2652 | 79.992
Devonshire Building | 2017-08-17 18:30 | 50765.2852 | 79.992
Devonshire Building | 2017-08-17 18:45 | 50765.3002 | 60.012
Devonshire Building | 2017-08-17 19:00 | 50765.3202 | 79.992
Devonshire Building | 2017-08-17 19:15 | 50765.3402 | 79.992
Devonshire Building | 2017-08-17 19:30 | 50765.3602 | 79.992
Devonshire Building | 2017-08-17 19:45 | 50765.3802 | 79.992
Devonshire Building | 2017-08-17 20:00 | 50765.4002 | 79.992
Devonshire Building | 2017-08-17 20:15 | 50765.4202 | 79.992
Devonshire Building | 2017-08-17 20:30 | 50765.4452 | 100.008
Devonshire Building | 2017-08-17 20:45 | 50765.5002 | 219.996
Devonshire Building | 2017-08-17 21:00 | 50765.5352 | 140.004
Devonshire Building | 2017-08-17 21:15 | 50765.5652 | 119.988
Devonshire Building | 2017-08-17 21:30 | 50765.6002 | 140.004
Devonshire Building | 2017-08-17 21:45 | 50765.6302 | 119.988
Devonshire Building | 2017-08-17 22:00 | 50765.6602 | 119.988
Devonshire Building | 2017-08-17 22:15 | 50765.6952 | 140.004
Devonshire Building | 2017-08-17 22:30 | 50765.7252 | 119.988
Devonshire Building | 2017-08-17 22:45 | 50765.7602 | 140.004
Devonshire Building | 2017-08-17 23:00 | 50765.7952 | 140.004
Devonshire Building | 2017-08-17 23:15 | 50765.8252 | 119.988
Devonshire Building | 2017-08-17 23:30 | 50765.8602 | 140.004
Devonshire Building | 2017-08-17 23:45 | 50765.8952 | 140.004
Devonshire Building | 2017-08-18 | 50765.9297 | 140.004
Devonshire Building | 2017-08-18 00:15 | 50765.9647 | 140.004
Devonshire Building | 2017-08-18 00:30 | 50765.9997 | 140.004
Devonshire Building | 2017-08-18 00:45 | 50766.0297 | 119.988
Devonshire Building | 2017-08-18 01:00 | 50766.5547 | 2099.988
Devonshire Building | 2017-08-18 01:15 | 50766.5847 | 119.988
Devonshire Building | 2017-08-18 01:30 | 50766.6147 | 119.988
Devonshire Building | 2017-08-18 01:45 | 50766.6497 | 140.004
Devonshire Building | 2017-08-18 02:00 | 50766.6847 | 140.004
Devonshire Building | 2017-08-18 02:15 | 50766.7147 | 119.988
Devonshire Building | 2017-08-18 02:30 | 50766.7497 | 140.004
Devonshire Building | 2017-08-18 02:45 | 50766.7847 | 140.004
Devonshire Building | 2017-08-18 03:00 | 50766.8147 | 119.988
Devonshire Building | 2017-08-18 03:15 | 50766.8497 | 140.004
Devonshire Building | 2017-08-18 03:30 | 50766.8797 | 119.988
Devonshire Building | 2017-08-18 03:45 | 50766.9097 | 119.988
Devonshire Building | 2017-08-18 04:00 | 50766.9397 | 119.988
Devonshire Building | 2017-08-18 04:15 | 50766.9697 | 119.988
Devonshire Building | 2017-08-18 04:30 | 50766.9947 | 100.008
Devonshire Building | 2017-08-18 04:45 | 50767.0247 | 119.988
Devonshire Building | 2017-08-18 05:00 | 50767.0547 | 119.988
Devonshire Building | 2017-08-18 05:15 | 50767.0847 | 119.988
Devonshire Building | 2017-08-18 05:30 | 50767.1097 | 100.008
Devonshire Building | 2017-08-18 05:45 | 50767.1397 | 119.988
Devonshire Building | 2017-08-18 06:00 | 50767.1697 | 119.988
Devonshire Building | 2017-08-18 06:15 | 50767.2047 | 140.004
Devonshire Building | 2017-08-18 06:30 | 50767.2347 | 119.988
Devonshire Building | 2017-08-18 06:45 | 50767.2597 | 100.008
Devonshire Building | 2017-08-18 07:00 | 50767.2897 | 119.988
Devonshire Building | 2017-08-18 07:15 | 50767.3247 | 140.004
Devonshire Building | 2017-08-18 07:30 | 50767.8797 | 2220.012
Devonshire Building | 2017-08-18 07:45 | 50767.9497 | 280.008
Devonshire Building | 2017-08-18 08:00 | 50768.0197 | 280.008
Devonshire Building | 2017-08-18 08:15 | 50768.0797 | 240.012
Devonshire Building | 2017-08-18 08:30 | 50768.1497 | 280.008
Devonshire Building | 2017-08-18 08:45 | 50768.2147 | 259.992
Devonshire Building | 2017-08-18 09:00 | 50768.2747 | 240.012
Devonshire Building | 2017-08-18 09:15 | 50768.3347 | 240.012
Devonshire Building | 2017-08-18 09:30 | 50768.5197 | 740.016
Devonshire Building | 2017-08-18 09:45 | 50768.9947 | 1900.008
Devonshire Building | 2017-08-18 10:00 | 50769.0547 | 240.012
Devonshire Building | 2017-08-18 10:15 | 50769.1297 | 299.988
Devonshire Building | 2017-08-18 10:30 | 50769.2597 | 519.984
Devonshire Building | 2017-08-18 10:45 | 50769.9747 | 2859.984
Devonshire Building | 2017-08-18 11:00 | 50770.2097 | 939.996
Devonshire Building | 2017-08-18 11:15 | 50770.3597 | 600.012
Devonshire Building | 2017-08-18 11:30 | 50770.4647 | 420.012
Devonshire Building | 2017-08-18 11:45 | 50770.5447 | 320.004
Devonshire Building | 2017-08-18 12:00 | 50770.6147 | 280.008
Devonshire Building | 2017-08-18 12:15 | 50770.6747 | 240.012
Devonshire Building | 2017-08-18 12:30 | 50771.2147 | 2160
Devonshire Building | 2017-08-18 12:45 | 50771.2497 | 140.004
Devonshire Building | 2017-08-18 13:00 | 50771.2847 | 140.004
Devonshire Building | 2017-08-18 13:15 | 50771.3247 | 159.984
Devonshire Building | 2017-08-18 13:30 | 50771.3847 | 240.012
Devonshire Building | 2017-08-18 13:45 | 50771.4547 | 280.008
Devonshire Building | 2017-08-18 14:00 | 50772.0797 | 2499.984
Devonshire Building | 2017-08-18 14:15 | 50772.1947 | 460.008
Devonshire Building | 2017-08-18 14:30 | 50772.3297 | 540
Devonshire Building | 2017-08-18 14:45 | 50772.4997 | 680.004
Devonshire Building | 2017-08-18 15:00 | 50772.6597 | 640.008
Devonshire Building | 2017-08-18 15:15 | 50772.7997 | 560.016
Devonshire Building | 2017-08-18 15:30 | 50773.1097 | 1239.984
Devonshire Building | 2017-08-18 15:45 | 50773.5097 | 1599.984
Devonshire Building | 2017-08-18 16:00 | 50773.5997 | 360
Devonshire Building | 2017-08-18 16:15 | 50773.6747 | 299.988
Devonshire Building | 2017-08-18 16:30 | 50773.7547 | 320.004
Devonshire Building | 2017-08-18 16:45 | 50773.8297 | 299.988
Devonshire Building | 2017-08-18 17:00 | 50773.9047 | 299.988
Devonshire Building | 2017-08-18 17:15 | 50773.9697 | 259.992
Devonshire Building | 2017-08-18 17:30 | 50774.0297 | 240.012
Devonshire Building | 2017-08-18 17:45 | 50774.0847 | 219.996
Devonshire Building | 2017-08-18 18:00 | 50774.1347 | 200.016
Devonshire Building | 2017-08-18 18:15 | 50774.2147 | 320.004
Devonshire Building | 2017-08-18 18:30 | 50774.6947 | 1919.988
Devonshire Building | 2017-08-18 18:45 | 50774.7147 | 79.992
Devonshire Building | 2017-08-18 19:00 | 50774.7347 | 79.992
Devonshire Building | 2017-08-18 19:15 | 50774.7597 | 100.008
Devonshire Building | 2017-08-18 19:30 | 50774.7797 | 79.992
Devonshire Building | 2017-08-18 19:45 | 50774.8047 | 100.008
Devonshire Building | 2017-08-18 20:00 | 50774.8247 | 79.992
Devonshire Building | 2017-08-18 20:15 | 50774.8497 | 100.008
Devonshire Building | 2017-08-18 20:30 | 50774.8697 | 79.992
Devonshire Building | 2017-08-18 20:45 | 50774.9047 | 140.004
Devonshire Building | 2017-08-18 21:00 | 50774.9297 | 100.008
Devonshire Building | 2017-08-18 21:15 | 50774.9547 | 100.008
Devonshire Building | 2017-08-18 21:30 | 50774.9797 | 100.008
Devonshire Building | 2017-08-18 21:45 | 50774.9997 | 79.992
Devonshire Building | 2017-08-18 22:00 | 50775.0247 | 100.008
Devonshire Building | 2017-08-18 22:15 | 50775.0447 | 79.992
Devonshire Building | 2017-08-18 22:30 | 50775.0697 | 100.008
Devonshire Building | 2017-08-18 22:45 | 50775.0897 | 79.992
Devonshire Building | 2017-08-18 23:00 | 50775.1147 | 100.008
Devonshire Building | 2017-08-18 23:15 | 50775.1347 | 79.992
Devonshire Building | 2017-08-18 23:30 | 50775.1597 | 100.008
Devonshire Building | 2017-08-18 23:45 | 50775.1797 | 79.992
Devonshire Building | 2017-08-19 | 50775.2031 | 100.008
Devonshire Building | 2017-08-19 00:15 | 50775.2281 | 100.008
Devonshire Building | 2017-08-19 00:30 | 50775.2531 | 100.008
Devonshire Building | 2017-08-19 00:45 | 50775.2831 | 119.988
Devonshire Building | 2017-08-19 01:00 | 50775.3081 | 100.008
Devonshire Building | 2017-08-19 01:15 | 50775.3331 | 100.008
Devonshire Building | 2017-08-19 01:30 | 50775.3581 | 100.008
Devonshire Building | 2017-08-19 01:45 | 50775.3881 | 119.988
Devonshire Building | 2017-08-19 02:00 | 50775.4131 | 100.008
Devonshire Building | 2017-08-19 02:15 | 50775.6931 | 1119.996
Devonshire Building | 2017-08-19 02:30 | 50775.9731 | 1119.996
Devonshire Building | 2017-08-19 02:45 | 50776.0081 | 140.004
Devonshire Building | 2017-08-19 03:00 | 50776.0481 | 159.984
Devonshire Building | 2017-08-19 03:15 | 50776.0931 | 180
Devonshire Building | 2017-08-19 03:30 | 50776.1331 | 159.984
Devonshire Building | 2017-08-19 03:45 | 50776.1731 | 159.984
Devonshire Building | 2017-08-19 04:00 | 50776.2131 | 159.984
Devonshire Building | 2017-08-19 04:15 | 50776.2481 | 140.004
Devonshire Building | 2017-08-19 04:30 | 50776.2831 | 140.004
Devonshire Building | 2017-08-19 04:45 | 50776.3181 | 140.004
Devonshire Building | 2017-08-19 05:00 | 50776.3531 | 140.004
Devonshire Building | 2017-08-19 05:15 | 50776.3881 | 140.004
Devonshire Building | 2017-08-19 05:30 | 50776.4231 | 140.004
Devonshire Building | 2017-08-19 05:45 | 50776.4531 | 119.988
Devonshire Building | 2017-08-19 06:00 | 50776.4881 | 140.004
Devonshire Building | 2017-08-19 06:15 | 50776.5181 | 119.988
Devonshire Building | 2017-08-19 06:30 | 50776.5481 | 119.988
Devonshire Building | 2017-08-19 06:45 | 50776.5781 | 119.988
Devonshire Building | 2017-08-19 07:00 | 50776.6081 | 119.988
Devonshire Building | 2017-08-19 07:15 | 50776.6381 | 119.988
Devonshire Building | 2017-08-19 07:30 | 50776.6681 | 119.988
Devonshire Building | 2017-08-19 07:45 | 50776.6981 | 119.988
Devonshire Building | 2017-08-19 08:00 | 50776.7281 | 119.988
Devonshire Building | 2017-08-19 08:15 | 50776.7581 | 119.988
Devonshire Building | 2017-08-19 08:30 | 50776.7881 | 119.988
Devonshire Building | 2017-08-19 08:45 | 50776.8181 | 119.988
Devonshire Building | 2017-08-19 09:00 | 50776.8431 | 100.008
Devonshire Building | 2017-08-19 09:15 | 50776.8731 | 119.988
Devonshire Building | 2017-08-19 09:30 | 50776.9031 | 119.988
Devonshire Building | 2017-08-19 09:45 | 50776.9331 | 119.988
Devonshire Building | 2017-08-19 10:00 | 50776.9581 | 100.008
Devonshire Building | 2017-08-19 10:15 | 50777.4931 | 2139.984
Devonshire Building | 2017-08-19 10:30 | 50777.5131 | 79.992
Devonshire Building | 2017-08-19 10:45 | 50777.5381 | 100.008
Devonshire Building | 2017-08-19 11:00 | 50777.5631 | 100.008
Devonshire Building | 2017-08-19 11:15 | 50777.5881 | 100.008
Devonshire Building | 2017-08-19 11:30 | 50777.6181 | 119.988
Devonshire Building | 2017-08-19 11:45 | 50777.6431 | 100.008
Devonshire Building | 2017-08-19 12:00 | 50777.6731 | 119.988
Devonshire Building | 2017-08-19 12:15 | 50777.6981 | 100.008
Devonshire Building | 2017-08-19 12:30 | 50777.7231 | 100.008
Devonshire Building | 2017-08-19 12:45 | 50777.7481 | 100.008
Devonshire Building | 2017-08-19 13:00 | 50777.7731 | 100.008
Devonshire Building | 2017-08-19 13:15 | 50777.7981 | 100.008
Devonshire Building | 2017-08-19 13:30 | 50777.8231 | 100.008
Devonshire Building | 2017-08-19 13:45 | 50777.8631 | 159.984
Devonshire Building | 2017-08-19 14:00 | 50777.9031 | 159.984
Devonshire Building | 2017-08-19 14:15 | 50777.9431 | 159.984
Devonshire Building | 2017-08-19 14:30 | 50777.9831 | 159.984
Devonshire Building | 2017-08-19 14:45 | 50778.0231 | 159.984
Devonshire Building | 2017-08-19 15:00 | 50778.0631 | 159.984
Devonshire Building | 2017-08-19 15:15 | 50778.1031 | 159.984
Devonshire Building | 2017-08-19 15:30 | 50778.1431 | 159.984
Devonshire Building | 2017-08-19 15:45 | 50778.1831 | 159.984
Devonshire Building | 2017-08-19 16:00 | 50778.2131 | 119.988
Devonshire Building | 2017-08-19 16:15 | 50778.2381 | 100.008
Devonshire Building | 2017-08-19 16:30 | 50778.2631 | 100.008
Devonshire Building | 2017-08-19 16:45 | 50778.2881 | 100.008
Devonshire Building | 2017-08-19 17:00 | 50778.3181 | 119.988
Devonshire Building | 2017-08-19 17:15 | 50778.3431 | 100.008
Devonshire Building | 2017-08-19 17:30 | 50778.3731 | 119.988
Devonshire Building | 2017-08-19 17:45 | 50778.3981 | 100.008
Devonshire Building | 2017-08-19 18:00 | 50778.9181 | 2080.008
Devonshire Building | 2017-08-19 18:15 | 50778.9531 | 140.004
Devonshire Building | 2017-08-19 18:30 | 50778.9931 | 159.984
Devonshire Building | 2017-08-19 18:45 | 50779.0331 | 159.984
Devonshire Building | 2017-08-19 19:00 | 50779.073 | 159.984
Devonshire Building | 2017-08-19 19:15 | 50779.113 | 159.984
Devonshire Building | 2017-08-19 19:30 | 50779.153 | 159.984
Devonshire Building | 2017-08-19 19:45 | 50779.188 | 140.004
Devonshire Building | 2017-08-19 20:00 | 50779.223 | 140.004
Devonshire Building | 2017-08-19 20:15 | 50779.258 | 140.004
Devonshire Building | 2017-08-19 20:30 | 50779.293 | 140.004
Devonshire Building | 2017-08-19 20:45 | 50779.343 | 200.016
Devonshire Building | 2017-08-19 21:00 | 50779.373 | 119.988
Devonshire Building | 2017-08-19 21:15 | 50779.403 | 119.988
Devonshire Building | 2017-08-19 21:30 | 50779.433 | 119.988
Devonshire Building | 2017-08-19 21:45 | 50779.463 | 119.988
Devonshire Building | 2017-08-19 22:00 | 50779.493 | 119.988
Devonshire Building | 2017-08-19 22:15 | 50779.523 | 119.988
Devonshire Building | 2017-08-19 22:30 | 50779.553 | 119.988
Devonshire Building | 2017-08-19 22:45 | 50779.583 | 119.988
Devonshire Building | 2017-08-19 23:00 | 50779.613 | 119.988
Devonshire Building | 2017-08-19 23:15 | 50779.643 | 119.988
Devonshire Building | 2017-08-19 23:30 | 50779.673 | 119.988
Devonshire Building | 2017-08-19 23:45 | 50779.703 | 119.988
Devonshire Building | 2017-08-20 | 50779.7344 | 119.988
Devonshire Building | 2017-08-20 00:15 | 50779.7644 | 119.988
Devonshire Building | 2017-08-20 00:30 | 50779.7944 | 119.988
Devonshire Building | 2017-08-20 00:45 | 50779.8244 | 119.988
Devonshire Building | 2017-08-20 01:00 | 50779.8544 | 119.988
Devonshire Building | 2017-08-20 01:15 | 50779.8844 | 119.988
Devonshire Building | 2017-08-20 01:30 | 50779.9144 | 119.988
Devonshire Building | 2017-08-20 01:45 | 50779.9394 | 100.008
Devonshire Building | 2017-08-20 02:00 | 50779.9694 | 119.988
Devonshire Building | 2017-08-20 02:15 | 50779.9994 | 119.988
Devonshire Building | 2017-08-20 02:30 | 50780.2044 | 820.008
Devonshire Building | 2017-08-20 02:45 | 50780.5494 | 1379.988
Devonshire Building | 2017-08-20 03:00 | 50780.5794 | 119.988
Devonshire Building | 2017-08-20 03:15 | 50780.6044 | 100.008
Devonshire Building | 2017-08-20 03:30 | 50780.6394 | 140.004
Devonshire Building | 2017-08-20 03:45 | 50780.6694 | 119.988
Devonshire Building | 2017-08-20 04:00 | 50780.6994 | 119.988
Devonshire Building | 2017-08-20 04:15 | 50780.7293 | 119.988
Devonshire Building | 2017-08-20 04:30 | 50780.7593 | 119.988
Devonshire Building | 2017-08-20 04:45 | 50780.7893 | 119.988
Devonshire Building | 2017-08-20 05:00 | 50780.8193 | 119.988
Devonshire Building | 2017-08-20 05:15 | 50780.8493 | 119.988
Devonshire Building | 2017-08-20 05:30 | 50780.8743 | 100.008
Devonshire Building | 2017-08-20 05:45 | 50780.9043 | 119.988
Devonshire Building | 2017-08-20 06:00 | 50780.9293 | 100.008
Devonshire Building | 2017-08-20 06:15 | 50780.9593 | 119.988
Devonshire Building | 2017-08-20 06:30 | 50780.9843 | 100.008
Devonshire Building | 2017-08-20 06:45 | 50781.0143 | 119.988
Devonshire Building | 2017-08-20 07:00 | 50781.0393 | 100.008
Devonshire Building | 2017-08-20 07:15 | 50781.0643 | 100.008
Devonshire Building | 2017-08-20 07:30 | 50781.0943 | 119.988
Devonshire Building | 2017-08-20 07:45 | 50781.1193 | 100.008
Devonshire Building | 2017-08-20 08:00 | 50781.1443 | 100.008
Devonshire Building | 2017-08-20 08:15 | 50781.1743 | 119.988
Devonshire Building | 2017-08-20 08:30 | 50781.1993 | 100.008
Devonshire Building | 2017-08-20 08:45 | 50781.2243 | 100.008
Devonshire Building | 2017-08-20 09:00 | 50781.2543 | 119.988
Devonshire Building | 2017-08-20 09:15 | 50781.2793 | 100.008
Devonshire Building | 2017-08-20 09:30 | 50781.3043 | 100.008
Devonshire Building | 2017-08-20 09:45 | 50781.3293 | 100.008
Devonshire Building | 2017-08-20 10:00 | 50781.3593 | 119.988
Devonshire Building | 2017-08-20 10:15 | 50781.3843 | 100.008
Devonshire Building | 2017-08-20 10:30 | 50781.4093 | 100.008
Devonshire Building | 2017-08-20 10:45 | 50781.4343 | 100.008
Devonshire Building | 2017-08-20 11:00 | 50781.4643 | 119.988
Devonshire Building | 2017-08-20 11:15 | 50781.4893 | 100.008
Devonshire Building | 2017-08-20 11:30 | 50781.5993 | 439.992
Devonshire Building | 2017-08-20 11:45 | 50782.0493 | 1800
Devonshire Building | 2017-08-20 12:00 | 50782.0743 | 100.008
Devonshire Building | 2017-08-20 12:15 | 50782.1093 | 140.004
Devonshire Building | 2017-08-20 12:30 | 50782.1393 | 119.988
Devonshire Building | 2017-08-20 12:45 | 50782.1743 | 140.004
Devonshire Building | 2017-08-20 13:00 | 50782.2093 | 140.004
Devonshire Building | 2017-08-20 13:15 | 50782.2443 | 140.004
Devonshire Building | 2017-08-20 13:30 | 50782.2793 | 140.004
Devonshire Building | 2017-08-20 13:45 | 50782.3293 | 200.016
Devonshire Building | 2017-08-20 14:00 | 50782.3794 | 200.016
Devonshire Building | 2017-08-20 14:15 | 50782.4244 | 180
Devonshire Building | 2017-08-20 14:30 | 50782.4694 | 180
Devonshire Building | 2017-08-20 14:45 | 50782.5244 | 219.996
Devonshire Building | 2017-08-20 15:00 | 50782.5694 | 180
Devonshire Building | 2017-08-20 15:15 | 50782.6144 | 180
Devonshire Building | 2017-08-20 15:30 | 50782.6594 | 180
Devonshire Building | 2017-08-20 15:45 | 50782.7094 | 200.016
Devonshire Building | 2017-08-20 16:00 | 50782.7444 | 140.004
Devonshire Building | 2017-08-20 16:15 | 50782.7744 | 119.988
Devonshire Building | 2017-08-20 16:30 | 50782.8044 | 119.988
Devonshire Building | 2017-08-20 16:45 | 50782.8343 | 119.988
Devonshire Building | 2017-08-20 17:00 | 50782.8643 | 119.988
Devonshire Building | 2017-08-20 17:15 | 50782.8993 | 140.004
Devonshire Building | 2017-08-20 17:30 | 50782.9343 | 140.004
Devonshire Building | 2017-08-20 17:45 | 50782.9643 | 119.988
Devonshire Building | 2017-08-20 18:00 | 50782.9993 | 140.004
Devonshire Building | 2017-08-20 18:15 | 50783.0293 | 119.988
Devonshire Building | 2017-08-20 18:30 | 50783.0593 | 119.988
Devonshire Building | 2017-08-20 18:45 | 50783.0893 | 119.988
Devonshire Building | 2017-08-20 19:00 | 50783.1193 | 119.988
Devonshire Building | 2017-08-20 19:15 | 50783.6443 | 2099.988
Devonshire Building | 2017-08-20 19:30 | 50783.6843 | 159.984
Devonshire Building | 2017-08-20 19:45 | 50783.7293 | 180
Devonshire Building | 2017-08-20 20:00 | 50783.7693 | 159.984
Devonshire Building | 2017-08-20 20:15 | 50783.8143 | 180
Devonshire Building | 2017-08-20 20:30 | 50783.8593 | 180
Devonshire Building | 2017-08-20 20:45 | 50783.9093 | 200.016
Devonshire Building | 2017-08-20 21:00 | 50783.9443 | 140.004
Devonshire Building | 2017-08-20 21:15 | 50783.9793 | 140.004
Devonshire Building | 2017-08-20 21:30 | 50784.0143 | 140.004
Devonshire Building | 2017-08-20 21:45 | 50784.0493 | 140.004
Devonshire Building | 2017-08-20 22:00 | 50784.0843 | 140.004
Devonshire Building | 2017-08-20 22:15 | 50784.1193 | 140.004
Devonshire Building | 2017-08-20 22:30 | 50784.1543 | 140.004
Devonshire Building | 2017-08-20 22:45 | 50784.1843 | 119.988
Devonshire Building | 2017-08-20 23:00 | 50784.2193 | 140.004
Devonshire Building | 2017-08-20 23:15 | 50784.2493 | 119.988
Devonshire Building | 2017-08-20 23:30 | 50784.2843 | 140.004
Devonshire Building | 2017-08-20 23:45 | 50784.3143 | 119.988
Devonshire Building | 2017-08-21 | 50784.3438 | 119.988
Devonshire Building | 2017-08-21 00:15 | 50784.3788 | 140.004
Devonshire Building | 2017-08-21 00:30 | 50784.4087 | 119.988
Devonshire Building | 2017-08-21 00:45 | 50784.4387 | 119.988
Devonshire Building | 2017-08-21 01:00 | 50784.4687 | 119.988
Devonshire Building | 2017-08-21 01:15 | 50784.5037 | 140.004
Devonshire Building | 2017-08-21 01:30 | 50784.5337 | 119.988
Devonshire Building | 2017-08-21 01:45 | 50784.5637 | 119.988
Devonshire Building | 2017-08-21 02:00 | 50784.5937 | 119.988
Devonshire Building | 2017-08-21 02:15 | 50784.6237 | 119.988
Devonshire Building | 2017-08-21 02:30 | 50784.6537 | 119.988
Devonshire Building | 2017-08-21 02:45 | 50784.6837 | 119.988
Devonshire Building | 2017-08-21 03:00 | 50784.7137 | 119.988
Devonshire Building | 2017-08-21 03:15 | 50784.7437 | 119.988
Devonshire Building | 2017-08-21 03:30 | 50784.7737 | 119.988
Devonshire Building | 2017-08-21 03:45 | 50784.8037 | 119.988
Devonshire Building | 2017-08-21 04:00 | 50785.3237 | 2080.008
Devonshire Building | 2017-08-21 04:15 | 50785.3487 | 100.008
Devonshire Building | 2017-08-21 04:30 | 50785.3737 | 100.008
Devonshire Building | 2017-08-21 04:45 | 50785.3987 | 100.008
Devonshire Building | 2017-08-21 05:00 | 50785.4237 | 100.008
Devonshire Building | 2017-08-21 05:15 | 50785.4537 | 119.988
Devonshire Building | 2017-08-21 05:30 | 50785.4787 | 100.008
Devonshire Building | 2017-08-21 05:45 | 50785.5087 | 119.988
Devonshire Building | 2017-08-21 06:00 | 50785.5337 | 100.008
Devonshire Building | 2017-08-21 06:15 | 50785.5587 | 100.008
Devonshire Building | 2017-08-21 06:30 | 50785.5937 | 140.004
Devonshire Building | 2017-08-21 06:45 | 50785.6287 | 140.004
Devonshire Building | 2017-08-21 07:00 | 50785.6637 | 140.004
Devonshire Building | 2017-08-21 07:15 | 50785.6987 | 140.004
Devonshire Building | 2017-08-21 07:30 | 50785.7437 | 180
Devonshire Building | 2017-08-21 07:45 | 50785.7887 | 180
Devonshire Building | 2017-08-21 08:00 | 50785.8437 | 219.996
Devonshire Building | 2017-08-21 08:15 | 50785.9437 | 399.996
Devonshire Building | 2017-08-21 08:30 | 50786.4587 | 2059.992
Devonshire Building | 2017-08-21 08:45 | 50786.5237 | 259.992
Devonshire Building | 2017-08-21 09:00 | 50786.5887 | 259.992
Devonshire Building | 2017-08-21 09:15 | 50786.6487 | 240.012
Devonshire Building | 2017-08-21 09:30 | 50786.7087 | 240.012
Devonshire Building | 2017-08-21 09:45 | 50786.7737 | 259.992
Devonshire Building | 2017-08-21 10:00 | 50787.3687 | 2379.996
Devonshire Building | 2017-08-21 10:15 | 50787.5037 | 540
Devonshire Building | 2017-08-21 10:30 | 50787.6087 | 420.012
Devonshire Building | 2017-08-21 10:45 | 50787.6987 | 360
Devonshire Building | 2017-08-21 11:00 | 50787.7887 | 360
Devonshire Building | 2017-08-21 11:15 | 50787.8687 | 320.004
Devonshire Building | 2017-08-21 11:30 | 50788.4687 | 2400.012
Devonshire Building | 2017-08-21 11:45 | 50788.5287 | 240.012
Devonshire Building | 2017-08-21 12:00 | 50788.5837 | 219.996
Devonshire Building | 2017-08-21 12:15 | 50788.6337 | 200.016
Devonshire Building | 2017-08-21 12:30 | 50788.6737 | 159.984
Devonshire Building | 2017-08-21 12:45 | 50788.7137 | 159.984
Devonshire Building | 2017-08-21 13:00 | 50788.7587 | 180
Devonshire Building | 2017-08-21 13:15 | 50789.3037 | 2180.016
Devonshire Building | 2017-08-21 13:30 | 50789.3287 | 100.008
Devonshire Building | 2017-08-21 13:45 | 50789.3587 | 119.988
Devonshire Building | 2017-08-21 14:00 | 50789.4437 | 339.984
Devonshire Building | 2017-08-21 14:15 | 50789.5387 | 380.016
Devonshire Building | 2017-08-21 14:30 | 50789.6237 | 339.984
Devonshire Building | 2017-08-21 14:45 | 50789.7137 | 360
Devonshire Building | 2017-08-21 15:00 | 50790.3037 | 2360.016
Devonshire Building | 2017-08-21 15:15 | 50790.3687 | 259.992
Devonshire Building | 2017-08-21 15:30 | 50790.4337 | 259.992
Devonshire Building | 2017-08-21 15:45 | 50790.4937 | 240.012
Devonshire Building | 2017-08-21 16:00 | 50790.5437 | 200.016
Devonshire Building | 2017-08-21 16:15 | 50790.5887 | 180
Devonshire Building | 2017-08-21 16:30 | 50791.1537 | 2260.008
Devonshire Building | 2017-08-21 16:45 | 50791.1787 | 100.008
Devonshire Building | 2017-08-21 17:00 | 50791.1987 | 79.992
Devonshire Building | 2017-08-21 17:15 | 50791.2237 | 100.008
Devonshire Building | 2017-08-21 17:30 | 50791.2487 | 100.008
Devonshire Building | 2017-08-21 17:45 | 50791.2737 | 100.008
Devonshire Building | 2017-08-21 18:00 | 50791.2987 | 100.008
Devonshire Building | 2017-08-21 18:15 | 50791.3287 | 119.988
Devonshire Building | 2017-08-21 18:30 | 50791.3537 | 100.008
Devonshire Building | 2017-08-21 18:45 | 50791.3737 | 79.992
Devonshire Building | 2017-08-21 19:00 | 50791.3987 | 100.008
Devonshire Building | 2017-08-21 19:15 | 50791.4187 | 79.992
Devonshire Building | 2017-08-21 19:30 | 50791.4437 | 100.008
Devonshire Building | 2017-08-21 19:45 | 50791.4637 | 79.992
Devonshire Building | 2017-08-21 20:00 | 50791.4837 | 79.992
Devonshire Building | 2017-08-21 20:15 | 50791.5037 | 79.992
Devonshire Building | 2017-08-21 20:30 | 50791.5187 | 60.012
Devonshire Building | 2017-08-21 20:45 | 50791.5587 | 159.984
Devonshire Building | 2017-08-21 21:00 | 50791.5687 | 39.996
Devonshire Building | 2017-08-21 21:15 | 50791.5787 | 39.996
Devonshire Building | 2017-08-21 21:30 | 50791.5887 | 39.996
Devonshire Building | 2017-08-21 21:45 | 50791.5987 | 39.996
Devonshire Building | 2017-08-21 22:00 | 50791.6087 | 39.996
Devonshire Building | 2017-08-21 22:15 | 50791.6137 | 20.016
Devonshire Building | 2017-08-21 22:30 | 50791.6237 | 39.996
Devonshire Building | 2017-08-21 22:45 | 50791.6337 | 39.996
Devonshire Building | 2017-08-21 23:00 | 50791.6437 | 39.996
Devonshire Building | 2017-08-21 23:15 | 50791.6537 | 39.996
Devonshire Building | 2017-08-21 23:30 | 50791.6937 | 159.984
Devonshire Building | 2017-08-21 23:45 | 50792.1687 | 1900.008
Devonshire Building | 2017-08-22 | 50792.1797 | 39.996
Devonshire Building | 2017-08-22 00:15 | 50792.1897 | 39.996
Devonshire Building | 2017-08-22 00:30 | 50792.1947 | 20.016
Devonshire Building | 2017-08-22 00:45 | 50792.2047 | 39.996
Devonshire Building | 2017-08-22 01:00 | 50792.2147 | 39.996
Devonshire Building | 2017-08-22 01:15 | 50792.2247 | 39.996
Devonshire Building | 2017-08-22 01:30 | 50792.2297 | 20.016
Devonshire Building | 2017-08-22 01:45 | 50792.2397 | 39.996
Devonshire Building | 2017-08-22 02:00 | 50792.2497 | 39.996
Devonshire Building | 2017-08-22 02:15 | 50792.2597 | 39.996
Devonshire Building | 2017-08-22 02:30 | 50792.2697 | 39.996
Devonshire Building | 2017-08-22 02:45 | 50792.2797 | 39.996
Devonshire Building | 2017-08-22 03:00 | 50792.2897 | 39.996
Devonshire Building | 2017-08-22 03:15 | 50792.2997 | 39.996
Devonshire Building | 2017-08-22 03:30 | 50792.3097 | 39.996
Devonshire Building | 2017-08-22 03:45 | 50792.3197 | 39.996
Devonshire Building | 2017-08-22 04:00 | 50792.3297 | 39.996
Devonshire Building | 2017-08-22 04:15 | 50792.3397 | 39.996
Devonshire Building | 2017-08-22 04:30 | 50792.3497 | 39.996
Devonshire Building | 2017-08-22 04:45 | 50792.3597 | 39.996
Devonshire Building | 2017-08-22 05:00 | 50792.3697 | 39.996
Devonshire Building | 2017-08-22 05:15 | 50792.3797 | 39.996
Devonshire Building | 2017-08-22 05:30 | 50792.3897 | 39.996
Devonshire Building | 2017-08-22 05:45 | 50792.3997 | 39.996
Devonshire Building | 2017-08-22 06:00 | 50792.4097 | 39.996
Devonshire Building | 2017-08-22 06:15 | 50792.4197 | 39.996
Devonshire Building | 2017-08-22 06:30 | 50792.4247 | 20.016
Devonshire Building | 2017-08-22 06:45 | 50792.4447 | 79.992
Devonshire Building | 2017-08-22 07:00 | 50792.4547 | 39.996
Devonshire Building | 2017-08-22 07:15 | 50792.7797 | 1299.996
Devonshire Building | 2017-08-22 07:30 | 50792.9997 | 879.984
Devonshire Building | 2017-08-22 07:45 | 50793.0397 | 159.984
Devonshire Building | 2017-08-22 08:00 | 50793.0747 | 140.004
Devonshire Building | 2017-08-22 08:15 | 50793.1097 | 140.004
Devonshire Building | 2017-08-22 08:30 | 50793.1447 | 140.004
Devonshire Building | 2017-08-22 08:45 | 50793.1847 | 159.984
Devonshire Building | 2017-08-22 09:00 | 50793.2397 | 219.996
Devonshire Building | 2017-08-22 09:15 | 50793.2947 | 219.996
Devonshire Building | 2017-08-22 09:30 | 50793.8897 | 2379.996
Devonshire Building | 2017-08-22 09:45 | 50793.9697 | 320.004
Devonshire Building | 2017-08-22 10:00 | 50794.0697 | 399.996
Devonshire Building | 2017-08-22 10:15 | 50794.1547 | 339.984
Devonshire Building | 2017-08-22 10:30 | 50794.2397 | 339.984
Devonshire Building | 2017-08-22 10:45 | 50794.8447 | 2419.992
Devonshire Building | 2017-08-22 11:00 | 50794.9047 | 240.012
Devonshire Building | 2017-08-22 11:15 | 50794.9697 | 259.992
Devonshire Building | 2017-08-22 11:30 | 50795.0347 | 259.992
Devonshire Building | 2017-08-22 11:45 | 50795.0947 | 240.012
Devonshire Building | 2017-08-22 12:00 | 50795.1497 | 219.996
Devonshire Building | 2017-08-22 12:15 | 50795.4997 | 1400.004
Devonshire Building | 2017-08-22 12:30 | 50795.7947 | 1180.008
Devonshire Building | 2017-08-22 12:45 | 50795.8447 | 200.016
Devonshire Building | 2017-08-22 13:00 | 50795.8897 | 180
Devonshire Building | 2017-08-22 13:15 | 50795.9397 | 200.016
Devonshire Building | 2017-08-22 13:30 | 50795.9847 | 180
Devonshire Building | 2017-08-22 13:45 | 50796.0447 | 240.012
Devonshire Building | 2017-08-22 14:00 | 50796.0847 | 159.984
Devonshire Building | 2017-08-22 14:15 | 50796.3547 | 1080
Devonshire Building | 2017-08-22 14:30 | 50796.6947 | 1360.008
Devonshire Building | 2017-08-22 14:45 | 50796.7297 | 140.004
Devonshire Building | 2017-08-22 15:00 | 50796.7647 | 140.004
Devonshire Building | 2017-08-22 15:15 | 50796.8047 | 159.984
Devonshire Building | 2017-08-22 15:30 | 50796.8497 | 180
Devonshire Building | 2017-08-22 15:45 | 50796.8847 | 140.004
Devonshire Building | 2017-08-22 16:00 | 50796.9147 | 119.988
Devonshire Building | 2017-08-22 16:15 | 50797.0697 | 619.992
Devonshire Building | 2017-08-22 16:30 | 50797.5347 | 1860.012
Devonshire Building | 2017-08-22 16:45 | 50797.5547 | 79.992
Devonshire Building | 2017-08-22 17:00 | 50797.5747 | 79.992
Devonshire Building | 2017-08-22 17:15 | 50797.5947 | 79.992
Devonshire Building | 2017-08-22 17:30 | 50797.6147 | 79.992
Devonshire Building | 2017-08-22 17:45 | 50797.6547 | 159.984
Devonshire Building | 2017-08-22 18:00 | 50797.6746 | 79.992
Devonshire Building | 2017-08-22 18:15 | 50797.6946 | 79.992
Devonshire Building | 2017-08-22 18:30 | 50797.7146 | 79.992
Devonshire Building | 2017-08-22 18:45 | 50797.7346 | 79.992
Devonshire Building | 2017-08-22 19:00 | 50797.7546 | 79.992
Devonshire Building | 2017-08-22 19:15 | 50797.7746 | 79.992
Devonshire Building | 2017-08-22 19:30 | 50797.7946 | 79.992
Devonshire Building | 2017-08-22 19:45 | 50797.8296 | 140.004
Devonshire Building | 2017-08-22 20:00 | 50797.8646 | 140.004
Devonshire Building | 2017-08-22 20:15 | 50797.8996 | 140.004
Devonshire Building | 2017-08-22 20:30 | 50797.9346 | 140.004
Devonshire Building | 2017-08-22 20:45 | 50797.9896 | 219.996
Devonshire Building | 2017-08-22 21:00 | 50798.0146 | 100.008
Devonshire Building | 2017-08-22 21:15 | 50798.0446 | 119.988
Devonshire Building | 2017-08-22 21:30 | 50798.0696 | 100.008
Devonshire Building | 2017-08-22 21:45 | 50798.1046 | 140.004
Devonshire Building | 2017-08-22 22:00 | 50798.1146 | 39.996
Devonshire Building | 2017-08-22 22:15 | 50798.1246 | 39.996
Devonshire Building | 2017-08-22 22:30 | 50798.1346 | 39.996
Devonshire Building | 2017-08-22 22:45 | 50798.1446 | 39.996
Devonshire Building | 2017-08-22 23:00 | 50798.1596 | 60.012
Devonshire Building | 2017-08-22 23:15 | 50798.6596 | 2000.016
Devonshire Building | 2017-08-22 23:30 | 50798.6696 | 39.996
Devonshire Building | 2017-08-22 23:45 | 50798.6796 | 39.996
Devonshire Building | 2017-08-23 | 50798.6875 | 39.996
Devonshire Building | 2017-08-23 00:15 | 50798.6975 | 39.996
Devonshire Building | 2017-08-23 00:30 | 50798.7075 | 39.996
Devonshire Building | 2017-08-23 00:45 | 50798.7175 | 39.996
Devonshire Building | 2017-08-23 01:00 | 50798.7275 | 39.996
Devonshire Building | 2017-08-23 01:15 | 50798.7375 | 39.996
Devonshire Building | 2017-08-23 01:30 | 50798.7475 | 39.996
Devonshire Building | 2017-08-23 01:45 | 50798.7575 | 39.996
Devonshire Building | 2017-08-23 02:00 | 50798.7675 | 39.996
Devonshire Building | 2017-08-23 02:15 | 50798.7775 | 39.996
Devonshire Building | 2017-08-23 02:30 | 50798.7925 | 60.012
Devonshire Building | 2017-08-23 02:45 | 50798.8025 | 39.996
Devonshire Building | 2017-08-23 03:00 | 50798.8125 | 39.996
Devonshire Building | 2017-08-23 03:15 | 50798.8275 | 60.012
Devonshire Building | 2017-08-23 03:30 | 50798.8375 | 39.996
Devonshire Building | 2017-08-23 03:45 | 50798.8475 | 39.996
Devonshire Building | 2017-08-23 04:00 | 50798.8575 | 39.996
Devonshire Building | 2017-08-23 04:15 | 50798.8675 | 39.996
Devonshire Building | 2017-08-23 04:30 | 50798.8775 | 39.996
Devonshire Building | 2017-08-23 04:45 | 50798.8875 | 39.996
Devonshire Building | 2017-08-23 05:00 | 50798.9025 | 60.012
Devonshire Building | 2017-08-23 05:15 | 50798.9125 | 39.996
Devonshire Building | 2017-08-23 05:30 | 50798.9225 | 39.996
Devonshire Building | 2017-08-23 05:45 | 50798.9325 | 39.996
Devonshire Building | 2017-08-23 06:00 | 50798.9425 | 39.996
Devonshire Building | 2017-08-23 06:15 | 50798.9575 | 60.012
Devonshire Building | 2017-08-23 06:30 | 50798.9675 | 39.996
Devonshire Building | 2017-08-23 06:45 | 50798.9775 | 39.996
Devonshire Building | 2017-08-23 07:00 | 50798.9875 | 39.996
Devonshire Building | 2017-08-23 07:15 | 50799.5275 | 2160
Devonshire Building | 2017-08-23 07:30 | 50799.5425 | 60.012
Devonshire Building | 2017-08-23 07:45 | 50799.5575 | 60.012
Devonshire Building | 2017-08-23 08:00 | 50799.5875 | 119.988
Devonshire Building | 2017-08-23 08:15 | 50799.6175 | 119.988
Devonshire Building | 2017-08-23 08:30 | 50799.6475 | 119.988
Devonshire Building | 2017-08-23 08:45 | 50799.6825 | 140.004
Devonshire Building | 2017-08-23 09:00 | 50799.7175 | 140.004
Devonshire Building | 2017-08-23 09:15 | 50799.7625 | 180
Devonshire Building | 2017-08-23 09:30 | 50800.3825 | 2480.004
Devonshire Building | 2017-08-23 09:45 | 50800.5475 | 659.988
Devonshire Building | 2017-08-23 10:00 | 50800.6825 | 540
Devonshire Building | 2017-08-23 10:15 | 50800.7875 | 420.012
Devonshire Building | 2017-08-23 10:30 | 50800.8825 | 380.016
Devonshire Building | 2017-08-23 10:45 | 50800.9675 | 339.984
Devonshire Building | 2017-08-23 11:00 | 50801.4825 | 2059.992
Devonshire Building | 2017-08-23 11:15 | 50801.6375 | 619.992
Devonshire Building | 2017-08-23 11:30 | 50801.7225 | 339.984
Devonshire Building | 2017-08-23 11:45 | 50801.7975 | 299.988
Devonshire Building | 2017-08-23 12:00 | 50801.8625 | 259.992
Devonshire Building | 2017-08-23 12:15 | 50801.9275 | 259.992
Devonshire Building | 2017-08-23 12:30 | 50801.9875 | 240.012
Devonshire Building | 2017-08-23 12:45 | 50802.5525 | 2260.008
Devonshire Building | 2017-08-23 13:00 | 50802.5825 | 119.988
Devonshire Building | 2017-08-23 13:15 | 50802.6225 | 159.984
Devonshire Building | 2017-08-23 13:30 | 50802.6625 | 159.984
Devonshire Building | 2017-08-23 13:45 | 50802.7125 | 200.016
Devonshire Building | 2017-08-23 14:00 | 50802.7625 | 200.016
Devonshire Building | 2017-08-23 14:15 | 50802.8225 | 240.012
Devonshire Building | 2017-08-23 14:30 | 50802.8775 | 219.996
Devonshire Building | 2017-08-23 14:45 | 50803.4825 | 2419.992
Devonshire Building | 2017-08-23 15:00 | 50803.5525 | 280.008
Devonshire Building | 2017-08-23 15:15 | 50803.6175 | 259.992
Devonshire Building | 2017-08-23 15:30 | 50803.6825 | 259.992
Devonshire Building | 2017-08-23 15:45 | 50803.7425 | 240.012
Devonshire Building | 2017-08-23 16:00 | 50803.8025 | 240.012
Devonshire Building | 2017-08-23 16:15 | 50804.1625 | 1440
Devonshire Building | 2017-08-23 16:30 | 50804.4025 | 960.012
Devonshire Building | 2017-08-23 16:45 | 50804.4425 | 159.984
Devonshire Building | 2017-08-23 17:00 | 50804.4875 | 180
Devonshire Building | 2017-08-23 17:15 | 50804.5275 | 159.984
Devonshire Building | 2017-08-23 17:30 | 50804.5675 | 159.984
Devonshire Building | 2017-08-23 17:45 | 50804.6025 | 140.004
Devonshire Building | 2017-08-23 18:00 | 50804.6375 | 140.004
Devonshire Building | 2017-08-23 18:15 | 50804.6675 | 119.988
Devonshire Building | 2017-08-23 18:30 | 50804.6975 | 119.988
Devonshire Building | 2017-08-23 18:45 | 50804.7275 | 119.988
Devonshire Building | 2017-08-23 19:00 | 50804.7525 | 100.008
Devonshire Building | 2017-08-23 19:15 | 50804.7725 | 79.992
Devonshire Building | 2017-08-23 19:30 | 50804.7975 | 100.008
Devonshire Building | 2017-08-23 19:45 | 50804.8175 | 79.992
Devonshire Building | 2017-08-23 20:00 | 50804.8375 | 79.992
Devonshire Building | 2017-08-23 20:15 | 50804.8575 | 79.992
Devonshire Building | 2017-08-23 20:30 | 50804.8775 | 79.992
Devonshire Building | 2017-08-23 20:45 | 50804.9175 | 159.984
Devonshire Building | 2017-08-23 21:00 | 50804.9225 | 20.016
Devonshire Building | 2017-08-23 21:15 | 50804.9325 | 39.996
Devonshire Building | 2017-08-23 21:30 | 50804.9375 | 20.016
Devonshire Building | 2017-08-23 21:45 | 50804.9475 | 39.996
Devonshire Building | 2017-08-23 22:00 | 50804.9525 | 20.016
Devonshire Building | 2017-08-23 22:15 | 50804.9575 | 20.016
Devonshire Building | 2017-08-23 22:30 | 50805.4725 | 2059.992
Devonshire Building | 2017-08-23 22:45 | 50805.4825 | 39.996
Devonshire Building | 2017-08-23 23:00 | 50805.4875 | 20.016
Devonshire Building | 2017-08-23 23:15 | 50805.4925 | 20.016
Devonshire Building | 2017-08-23 23:30 | 50805.5025 | 39.996
Devonshire Building | 2017-08-23 23:45 | 50805.5075 | 20.016
Devonshire Building | 2017-08-24 | 50805.5156 | 20.016
Devonshire Building | 2017-08-24 00:15 | 50805.5206 | 20.016
Devonshire Building | 2017-08-24 00:30 | 50805.5306 | 39.996
Devonshire Building | 2017-08-24 00:45 | 50805.5356 | 20.016
Devonshire Building | 2017-08-24 01:00 | 50805.5406 | 20.016
Devonshire Building | 2017-08-24 01:15 | 50805.5506 | 39.996
Devonshire Building | 2017-08-24 01:30 | 50805.5556 | 20.016
Devonshire Building | 2017-08-24 01:45 | 50805.5606 | 20.016
Devonshire Building | 2017-08-24 02:00 | 50805.5706 | 39.996
Devonshire Building | 2017-08-24 02:15 | 50805.5757 | 20.016
Devonshire Building | 2017-08-24 02:30 | 50805.5807 | 20.016
Devonshire Building | 2017-08-24 02:45 | 50805.5907 | 39.996
Devonshire Building | 2017-08-24 03:00 | 50805.5957 | 20.016
Devonshire Building | 2017-08-24 03:15 | 50805.6007 | 20.016
Devonshire Building | 2017-08-24 03:30 | 50805.6107 | 39.996
Devonshire Building | 2017-08-24 03:45 | 50805.6157 | 20.016
Devonshire Building | 2017-08-24 04:00 | 50805.6257 | 39.996
Devonshire Building | 2017-08-24 04:15 | 50805.6307 | 20.016
Devonshire Building | 2017-08-24 04:30 | 50805.6407 | 39.996
Devonshire Building | 2017-08-24 04:45 | 50805.6457 | 20.016
Devonshire Building | 2017-08-24 05:00 | 50805.6557 | 39.996
Devonshire Building | 2017-08-24 05:15 | 50805.6657 | 39.996
Devonshire Building | 2017-08-24 05:30 | 50805.6707 | 20.016
Devonshire Building | 2017-08-24 05:45 | 50805.6807 | 39.996
Devonshire Building | 2017-08-24 06:00 | 50805.6907 | 39.996
Devonshire Building | 2017-08-24 06:15 | 50805.6957 | 20.016
Devonshire Building | 2017-08-24 06:30 | 50805.7307 | 140.004
Devonshire Building | 2017-08-24 06:45 | 50806.2207 | 1959.984
Devonshire Building | 2017-08-24 07:00 | 50806.2357 | 60.012
Devonshire Building | 2017-08-24 07:15 | 50806.2507 | 60.012
Devonshire Building | 2017-08-24 07:30 | 50806.2657 | 60.012
Devonshire Building | 2017-08-24 07:45 | 50806.2757 | 39.996
Devonshire Building | 2017-08-24 08:00 | 50806.3007 | 100.008
Devonshire Building | 2017-08-24 08:15 | 50806.3157 | 60.012
Devonshire Building | 2017-08-24 08:30 | 50806.3457 | 119.988
Devonshire Building | 2017-08-24 08:45 | 50806.3807 | 140.004
Devonshire Building | 2017-08-24 09:00 | 50806.4207 | 159.984
Devonshire Building | 2017-08-24 09:15 | 50806.9907 | 2279.988
Devonshire Building | 2017-08-24 09:30 | 50807.0457 | 219.996
Devonshire Building | 2017-08-24 09:45 | 50807.1157 | 280.008
Devonshire Building | 2017-08-24 10:00 | 50807.1907 | 299.988
Devonshire Building | 2017-08-24 10:15 | 50807.2657 | 299.988
Devonshire Building | 2017-08-24 10:30 | 50807.3307 | 259.992
Devonshire Building | 2017-08-24 10:45 | 50807.4007 | 280.008
Devonshire Building | 2017-08-24 11:00 | 50808.0157 | 2459.988
Devonshire Building | 2017-08-24 11:15 | 50808.0757 | 240.012
Devonshire Building | 2017-08-24 11:30 | 50808.1307 | 219.996
Devonshire Building | 2017-08-24 11:45 | 50808.1907 | 240.012
Devonshire Building | 2017-08-24 12:00 | 50808.2407 | 200.016
Devonshire Building | 2017-08-24 12:15 | 50808.2757 | 140.004
Devonshire Building | 2017-08-24 12:30 | 50808.3107 | 140.004
Devonshire Building | 2017-08-24 12:45 | 50808.3507 | 159.984
Devonshire Building | 2017-08-24 13:00 | 50808.9007 | 2199.996
Devonshire Building | 2017-08-24 13:15 | 50808.9207 | 79.992
Devonshire Building | 2017-08-24 13:30 | 50808.9457 | 100.008
Devonshire Building | 2017-08-24 13:45 | 50808.9707 | 100.008
Devonshire Building | 2017-08-24 14:00 | 50809.0007 | 119.988
Devonshire Building | 2017-08-24 14:15 | 50809.0257 | 100.008
Devonshire Building | 2017-08-24 14:30 | 50809.0807 | 219.996
Devonshire Building | 2017-08-24 14:45 | 50809.5907 | 2040.012
Devonshire Building | 2017-08-24 15:00 | 50809.6107 | 79.992
Devonshire Building | 2017-08-24 15:15 | 50809.6307 | 79.992
Devonshire Building | 2017-08-24 15:30 | 50809.6607 | 119.988
Devonshire Building | 2017-08-24 15:45 | 50809.7007 | 159.984
Devonshire Building | 2017-08-24 16:00 | 50809.7607 | 240.012
Devonshire Building | 2017-08-24 16:15 | 50809.8107 | 200.016
Devonshire Building | 2017-08-24 16:30 | 50809.8657 | 219.996
Devonshire Building | 2017-08-24 16:45 | 50810.2157 | 1400.004
Devonshire Building | 2017-08-24 17:00 | 50810.4807 | 1059.984
Devonshire Building | 2017-08-24 17:15 | 50810.5207 | 159.984
Devonshire Building | 2017-08-24 17:30 | 50810.5607 | 159.984
Devonshire Building | 2017-08-24 17:45 | 50810.6007 | 159.984
Devonshire Building | 2017-08-24 18:00 | 50810.6357 | 140.004
Devonshire Building | 2017-08-24 18:15 | 50810.6707 | 140.004
Devonshire Building | 2017-08-24 18:30 | 50810.7007 | 119.988
Devonshire Building | 2017-08-24 18:45 | 50810.7307 | 119.988
Devonshire Building | 2017-08-24 19:00 | 50810.7606 | 119.988
Devonshire Building | 2017-08-24 19:15 | 50810.7857 | 100.008
Devonshire Building | 2017-08-24 19:30 | 50810.8107 | 100.008
Devonshire Building | 2017-08-24 19:45 | 50810.8307 | 79.992
Devonshire Building | 2017-08-24 20:00 | 50810.8557 | 100.008
Devonshire Building | 2017-08-24 20:15 | 50810.8757 | 79.992
Devonshire Building | 2017-08-24 20:30 | 50810.8956 | 79.992
Devonshire Building | 2017-08-24 20:45 | 50810.9356 | 159.984
Devonshire Building | 2017-08-24 21:00 | 50810.9456 | 39.996
Devonshire Building | 2017-08-24 21:15 | 50810.9556 | 39.996
Devonshire Building | 2017-08-24 21:30 | 50810.9656 | 39.996
Devonshire Building | 2017-08-24 21:45 | 50810.9756 | 39.996
Devonshire Building | 2017-08-24 22:00 | 50810.9856 | 39.996
Devonshire Building | 2017-08-24 22:15 | 50810.9956 | 39.996
Devonshire Building | 2017-08-24 22:30 | 50811.0056 | 39.996
Devonshire Building | 2017-08-24 22:45 | 50811.0156 | 39.996
Devonshire Building | 2017-08-24 23:00 | 50811.0306 | 60.012
Devonshire Building | 2017-08-24 23:15 | 50811.0406 | 39.996
Devonshire Building | 2017-08-24 23:30 | 50811.0506 | 39.996
Devonshire Building | 2017-08-24 23:45 | 50811.0606 | 39.996
Devonshire Building | 2017-08-25 | 50811.0703 | 39.996
Devonshire Building | 2017-08-25 00:15 | 50811.5803 | 2040.012
Devonshire Building | 2017-08-25 00:30 | 50811.5903 | 39.996
Devonshire Building | 2017-08-25 00:45 | 50811.5953 | 20.016
Devonshire Building | 2017-08-25 01:00 | 50811.6053 | 39.996
Devonshire Building | 2017-08-25 01:15 | 50811.6203 | 60.012
Devonshire Building | 2017-08-25 01:30 | 50811.6303 | 39.996
Devonshire Building | 2017-08-25 01:45 | 50811.6403 | 39.996
Devonshire Building | 2017-08-25 02:00 | 50811.6503 | 39.996
Devonshire Building | 2017-08-25 02:15 | 50811.6603 | 39.996
Devonshire Building | 2017-08-25 02:30 | 50811.6653 | 20.016
Devonshire Building | 2017-08-25 02:45 | 50811.6753 | 39.996
Devonshire Building | 2017-08-25 03:00 | 50811.6853 | 39.996
Devonshire Building | 2017-08-25 03:15 | 50811.7003 | 60.012
Devonshire Building | 2017-08-25 03:30 | 50811.7103 | 39.996
Devonshire Building | 2017-08-25 03:45 | 50811.7203 | 39.996
Devonshire Building | 2017-08-25 04:00 | 50811.7303 | 39.996
Devonshire Building | 2017-08-25 04:15 | 50811.7403 | 39.996
Devonshire Building | 2017-08-25 04:30 | 50811.7503 | 39.996
Devonshire Building | 2017-08-25 04:45 | 50811.7653 | 60.012
Devonshire Building | 2017-08-25 05:00 | 50811.7753 | 39.996
Devonshire Building | 2017-08-25 05:15 | 50811.7853 | 39.996
Devonshire Building | 2017-08-25 05:30 | 50811.7953 | 39.996
Devonshire Building | 2017-08-25 05:45 | 50811.8053 | 39.996
Devonshire Building | 2017-08-25 06:00 | 50811.8153 | 39.996
Devonshire Building | 2017-08-25 06:15 | 50811.8253 | 39.996
Devonshire Building | 2017-08-25 06:30 | 50811.8403 | 60.012
Devonshire Building | 2017-08-25 06:45 | 50811.8553 | 60.012
Devonshire Building | 2017-08-25 07:00 | 50812.0003 | 579.996
Devonshire Building | 2017-08-25 07:15 | 50812.3803 | 1519.992
Devonshire Building | 2017-08-25 07:30 | 50812.4003 | 79.992
Devonshire Building | 2017-08-25 07:45 | 50812.4403 | 159.984
Devonshire Building | 2017-08-25 08:00 | 50812.4853 | 180
Devonshire Building | 2017-08-25 08:15 | 50812.5403 | 219.996
Devonshire Building | 2017-08-25 08:30 | 50812.6353 | 380.016
Devonshire Building | 2017-08-25 08:45 | 50812.7303 | 380.016
Devonshire Building | 2017-08-25 09:00 | 50812.8203 | 360
Devonshire Building | 2017-08-25 09:15 | 50813.4253 | 2419.992
Devonshire Building | 2017-08-25 09:30 | 50813.5803 | 619.992
Devonshire Building | 2017-08-25 09:45 | 50813.8103 | 920.016
Devonshire Building | 2017-08-25 10:00 | 50813.9603 | 600.012
Devonshire Building | 2017-08-25 10:15 | 50814.0553 | 380.016
Devonshire Building | 2017-08-25 10:30 | 50814.1253 | 280.008
Devonshire Building | 2017-08-25 10:45 | 50814.1753 | 200.016
Devonshire Building | 2017-08-25 11:00 | 50814.6953 | 2080.008
Devonshire Building | 2017-08-25 11:15 | 50814.7503 | 219.996
Devonshire Building | 2017-08-25 11:30 | 50814.7653 | 60.012
Devonshire Building | 2017-08-25 11:45 | 50814.7903 | 100.008
Devonshire Building | 2017-08-25 12:00 | 50814.8053 | 60.012
Devonshire Building | 2017-08-25 12:15 | 50814.8253 | 79.992
Devonshire Building | 2017-08-25 12:30 | 50814.8503 | 100.008
Devonshire Building | 2017-08-25 12:45 | 50814.8703 | 79.992
Devonshire Building | 2017-08-25 13:00 | 50814.8903 | 79.992
Devonshire Building | 2017-08-25 13:15 | 50814.9103 | 79.992
Devonshire Building | 2017-08-25 13:30 | 50815.4603 | 2199.996
Devonshire Building | 2017-08-25 13:45 | 50815.4803 | 79.992
Devonshire Building | 2017-08-25 14:00 | 50815.4953 | 60.012
Devonshire Building | 2017-08-25 14:15 | 50815.5153 | 79.992
Devonshire Building | 2017-08-25 14:30 | 50815.5303 | 60.012
Devonshire Building | 2017-08-25 14:45 | 50815.5603 | 119.988
Devonshire Building | 2017-08-25 15:00 | 50815.5853 | 100.008
Devonshire Building | 2017-08-25 15:15 | 50815.6153 | 119.988
Devonshire Building | 2017-08-25 15:30 | 50815.7753 | 640.008
Devonshire Building | 2017-08-25 15:45 | 50816.2103 | 1739.988
Devonshire Building | 2017-08-25 16:00 | 50816.2903 | 320.004
Devonshire Building | 2017-08-25 16:15 | 50816.3953 | 420.012
Devonshire Building | 2017-08-25 16:30 | 50816.4953 | 399.996
Devonshire Building | 2017-08-25 16:45 | 50816.5803 | 339.984
Devonshire Building | 2017-08-25 17:00 | 50816.6553 | 299.988
Devonshire Building | 2017-08-25 17:15 | 50816.7253 | 280.008
Devonshire Building | 2017-08-25 17:30 | 50816.7953 | 280.008
Devonshire Building | 2017-08-25 17:45 | 50816.8653 | 280.008
Devonshire Building | 2017-08-25 18:00 | 50816.9253 | 240.012
Devonshire Building | 2017-08-25 18:15 | 50816.9753 | 200.016
Devonshire Building | 2017-08-25 18:30 | 50817.0203 | 180
Devonshire Building | 2017-08-25 18:45 | 50817.2103 | 759.996
Devonshire Building | 2017-08-25 19:00 | 50817.5603 | 1400.004
Devonshire Building | 2017-08-25 19:15 | 50817.5803 | 79.992
Devonshire Building | 2017-08-25 19:30 | 50817.6003 | 79.992
Devonshire Building | 2017-08-25 19:45 | 50817.6153 | 60.012
Devonshire Building | 2017-08-25 20:00 | 50817.6353 | 79.992
Devonshire Building | 2017-08-25 20:15 | 50817.6553 | 79.992
Devonshire Building | 2017-08-25 20:30 | 50817.6753 | 79.992
Devonshire Building | 2017-08-25 20:45 | 50817.7053 | 119.988
Devonshire Building | 2017-08-25 21:00 | 50817.7203 | 60.012
Devonshire Building | 2017-08-25 21:15 | 50817.7303 | 39.996
Devonshire Building | 2017-08-25 21:30 | 50817.7403 | 39.996
Devonshire Building | 2017-08-25 21:45 | 50817.7553 | 60.012
Devonshire Building | 2017-08-25 22:00 | 50817.7653 | 39.996
Devonshire Building | 2017-08-25 22:15 | 50817.7753 | 39.996
Devonshire Building | 2017-08-25 22:30 | 50817.7853 | 39.996
Devonshire Building | 2017-08-25 22:45 | 50817.7953 | 39.996
Devonshire Building | 2017-08-25 23:00 | 50817.8103 | 60.012
Devonshire Building | 2017-08-25 23:15 | 50817.8203 | 39.996
Devonshire Building | 2017-08-25 23:30 | 50817.8303 | 39.996
Devonshire Building | 2017-08-25 23:45 | 50817.8403 | 39.996
Devonshire Building | 2017-08-26 | 50817.8477 | 39.996
Devonshire Building | 2017-08-26 00:15 | 50817.8577 | 39.996
Devonshire Building | 2017-08-26 00:30 | 50817.8677 | 39.996
Devonshire Building | 2017-08-26 00:45 | 50817.8777 | 39.996
Devonshire Building | 2017-08-26 01:00 | 50817.8877 | 39.996
Devonshire Building | 2017-08-26 01:15 | 50817.8977 | 39.996
Devonshire Building | 2017-08-26 01:30 | 50817.9077 | 39.996
Devonshire Building | 2017-08-26 01:45 | 50817.9177 | 39.996
Devonshire Building | 2017-08-26 02:00 | 50817.9227 | 20.016
Devonshire Building | 2017-08-26 02:15 | 50817.9327 | 39.996
Devonshire Building | 2017-08-26 02:30 | 50817.9427 | 39.996
Devonshire Building | 2017-08-26 02:45 | 50817.9527 | 39.996
Devonshire Building | 2017-08-26 03:00 | 50817.9627 | 39.996
Devonshire Building | 2017-08-26 03:15 | 50818.4677 | 2019.996
Devonshire Building | 2017-08-26 03:30 | 50818.4777 | 39.996
Devonshire Building | 2017-08-26 03:45 | 50818.4877 | 39.996
Devonshire Building | 2017-08-26 04:00 | 50818.4976 | 39.996
Devonshire Building | 2017-08-26 04:15 | 50818.5076 | 39.996
Devonshire Building | 2017-08-26 04:30 | 50818.5176 | 39.996
Devonshire Building | 2017-08-26 04:45 | 50818.5276 | 39.996
Devonshire Building | 2017-08-26 05:00 | 50818.5376 | 39.996
Devonshire Building | 2017-08-26 05:15 | 50818.5476 | 39.996
Devonshire Building | 2017-08-26 05:30 | 50818.5576 | 39.996
Devonshire Building | 2017-08-26 05:45 | 50818.5676 | 39.996
Devonshire Building | 2017-08-26 06:00 | 50818.5776 | 39.996
Devonshire Building | 2017-08-26 06:15 | 50818.5926 | 60.012
Devonshire Building | 2017-08-26 06:30 | 50818.6026 | 39.996
Devonshire Building | 2017-08-26 06:45 | 50818.6176 | 60.012
Devonshire Building | 2017-08-26 07:00 | 50818.6276 | 39.996
Devonshire Building | 2017-08-26 07:15 | 50818.6376 | 39.996
Devonshire Building | 2017-08-26 07:30 | 50818.6526 | 60.012
Devonshire Building | 2017-08-26 07:45 | 50818.6726 | 79.992
Devonshire Building | 2017-08-26 08:00 | 50818.7026 | 119.988
Devonshire Building | 2017-08-26 08:15 | 50818.7276 | 100.008
Devonshire Building | 2017-08-26 08:30 | 50818.7526 | 100.008
Devonshire Building | 2017-08-26 08:45 | 50818.7826 | 119.988
Devonshire Building | 2017-08-26 09:00 | 50818.8076 | 100.008
Devonshire Building | 2017-08-26 09:15 | 50819.3326 | 2099.988
Devonshire Building | 2017-08-26 09:30 | 50819.3626 | 119.988
Devonshire Building | 2017-08-26 09:45 | 50819.3876 | 100.008
Devonshire Building | 2017-08-26 10:00 | 50819.4126 | 100.008
Devonshire Building | 2017-08-26 10:15 | 50819.4226 | 39.996
Devonshire Building | 2017-08-26 10:30 | 50819.4326 | 39.996
Devonshire Building | 2017-08-26 10:45 | 50819.4426 | 39.996
Devonshire Building | 2017-08-26 11:00 | 50819.4576 | 60.012
Devonshire Building | 2017-08-26 11:15 | 50819.4676 | 39.996
Devonshire Building | 2017-08-26 11:30 | 50819.4776 | 39.996
Devonshire Building | 2017-08-26 11:45 | 50819.4926 | 60.012
Devonshire Building | 2017-08-26 12:00 | 50819.5076 | 60.012
Devonshire Building | 2017-08-26 12:15 | 50819.5176 | 39.996
Devonshire Building | 2017-08-26 12:30 | 50819.5326 | 60.012
Devonshire Building | 2017-08-26 12:45 | 50819.5477 | 60.012
Devonshire Building | 2017-08-26 13:00 | 50819.5627 | 60.012
Devonshire Building | 2017-08-26 13:15 | 50819.5727 | 39.996
Devonshire Building | 2017-08-26 13:30 | 50819.5877 | 60.012
Devonshire Building | 2017-08-26 13:45 | 50819.5977 | 39.996
Devonshire Building | 2017-08-26 14:00 | 50819.6127 | 60.012
Devonshire Building | 2017-08-26 14:15 | 50819.6277 | 60.012
Devonshire Building | 2017-08-26 14:30 | 50819.6377 | 39.996
Devonshire Building | 2017-08-26 14:45 | 50819.6477 | 39.996
Devonshire Building | 2017-08-26 15:00 | 50819.6577 | 39.996
Devonshire Building | 2017-08-26 15:15 | 50819.6677 | 39.996
Devonshire Building | 2017-08-26 15:30 | 50819.6827 | 60.012
Devonshire Building | 2017-08-26 15:45 | 50820.1827 | 2000.016
Devonshire Building | 2017-08-26 16:00 | 50820.1977 | 60.012
Devonshire Building | 2017-08-26 16:15 | 50820.2077 | 39.996
Devonshire Building | 2017-08-26 16:30 | 50820.2227 | 60.012
Devonshire Building | 2017-08-26 16:45 | 50820.2327 | 39.996
Devonshire Building | 2017-08-26 17:00 | 50820.2477 | 60.012
Devonshire Building | 2017-08-26 17:15 | 50820.2627 | 60.012
Devonshire Building | 2017-08-26 17:30 | 50820.2727 | 39.996
Devonshire Building | 2017-08-26 17:45 | 50820.2927 | 79.992
Devonshire Building | 2017-08-26 18:00 | 50820.3077 | 60.012
Devonshire Building | 2017-08-26 18:15 | 50820.3227 | 60.012
Devonshire Building | 2017-08-26 18:30 | 50820.3377 | 60.012
Devonshire Building | 2017-08-26 18:45 | 50820.3527 | 60.012
Devonshire Building | 2017-08-26 19:00 | 50820.3677 | 60.012
Devonshire Building | 2017-08-26 19:15 | 50820.3777 | 39.996
Devonshire Building | 2017-08-26 19:30 | 50820.3927 | 60.012
Devonshire Building | 2017-08-26 19:45 | 50820.4077 | 60.012
Devonshire Building | 2017-08-26 20:00 | 50820.4227 | 60.012
Devonshire Building | 2017-08-26 20:15 | 50820.4377 | 60.012
Devonshire Building | 2017-08-26 20:30 | 50820.4477 | 39.996
Devonshire Building | 2017-08-26 20:45 | 50820.4827 | 140.004
Devonshire Building | 2017-08-26 21:00 | 50820.4977 | 60.012
Devonshire Building | 2017-08-26 21:15 | 50820.5077 | 39.996
Devonshire Building | 2017-08-26 21:30 | 50820.5227 | 60.012
Devonshire Building | 2017-08-26 21:45 | 50820.5327 | 39.996
Devonshire Building | 2017-08-26 22:00 | 50820.5427 | 39.996
Devonshire Building | 2017-08-26 22:15 | 50820.5577 | 60.012
Devonshire Building | 2017-08-26 22:30 | 50820.5677 | 39.996
Devonshire Building | 2017-08-26 22:45 | 50820.9077 | 1360.008
Devonshire Building | 2017-08-26 23:00 | 50821.0877 | 720
Devonshire Building | 2017-08-26 23:15 | 50821.0977 | 39.996
Devonshire Building | 2017-08-26 23:30 | 50821.1077 | 39.996
Devonshire Building | 2017-08-26 23:45 | 50821.1177 | 39.996
Devonshire Building | 2017-08-27 | 50821.1289 | 39.996
Devonshire Building | 2017-08-27 00:15 | 50821.1389 | 39.996
Devonshire Building | 2017-08-27 00:30 | 50821.1489 | 39.996
Devonshire Building | 2017-08-27 00:45 | 50821.1589 | 39.996
Devonshire Building | 2017-08-27 01:00 | 50821.1739 | 60.012
Devonshire Building | 2017-08-27 01:15 | 50821.1839 | 39.996
Devonshire Building | 2017-08-27 01:30 | 50821.1989 | 60.012
Devonshire Building | 2017-08-27 01:45 | 50821.2089 | 39.996
Devonshire Building | 2017-08-27 02:00 | 50821.2239 | 60.012
Devonshire Building | 2017-08-27 02:15 | 50821.2389 | 60.012
Devonshire Building | 2017-08-27 02:30 | 50821.2489 | 39.996
Devonshire Building | 2017-08-27 02:45 | 50821.2639 | 60.012
Devonshire Building | 2017-08-27 03:00 | 50821.2739 | 39.996
Devonshire Building | 2017-08-27 03:15 | 50821.2889 | 60.012
Devonshire Building | 2017-08-27 03:30 | 50821.2989 | 39.996
Devonshire Building | 2017-08-27 03:45 | 50821.3139 | 60.012
Devonshire Building | 2017-08-27 04:00 | 50821.3239 | 39.996
Devonshire Building | 2017-08-27 04:15 | 50821.3389 | 60.012
Devonshire Building | 2017-08-27 04:30 | 50821.3489 | 39.996
Devonshire Building | 2017-08-27 04:45 | 50821.3589 | 39.996
Devonshire Building | 2017-08-27 05:00 | 50821.3739 | 60.012
Devonshire Building | 2017-08-27 05:15 | 50821.3839 | 39.996
Devonshire Building | 2017-08-27 05:30 | 50821.3939 | 39.996
Devonshire Building | 2017-08-27 05:45 | 50821.4039 | 39.996
Devonshire Building | 2017-08-27 06:00 | 50821.4189 | 60.012
Devonshire Building | 2017-08-27 06:15 | 50821.4289 | 39.996
Devonshire Building | 2017-08-27 06:30 | 50821.4389 | 39.996
Devonshire Building | 2017-08-27 06:45 | 50821.4489 | 39.996
Devonshire Building | 2017-08-27 07:00 | 50821.4589 | 39.996
Devonshire Building | 2017-08-27 07:15 | 50821.4689 | 39.996
Devonshire Building | 2017-08-27 07:30 | 50821.4789 | 39.996
Devonshire Building | 2017-08-27 07:45 | 50821.9839 | 2019.996
Devonshire Building | 2017-08-27 08:00 | 50822.0089 | 100.008
Devonshire Building | 2017-08-27 08:15 | 50822.0339 | 100.008
Devonshire Building | 2017-08-27 08:30 | 50822.0639 | 119.988
Devonshire Building | 2017-08-27 08:45 | 50822.0889 | 100.008
Devonshire Building | 2017-08-27 09:00 | 50822.1139 | 100.008
Devonshire Building | 2017-08-27 09:15 | 50822.1389 | 100.008
Devonshire Building | 2017-08-27 09:30 | 50822.1639 | 100.008
Devonshire Building | 2017-08-27 09:45 | 50822.1889 | 100.008
Devonshire Building | 2017-08-27 10:00 | 50822.2139 | 100.008
Devonshire Building | 2017-08-27 10:15 | 50822.2239 | 39.996
Devonshire Building | 2017-08-27 10:30 | 50822.2339 | 39.996
Devonshire Building | 2017-08-27 10:45 | 50822.2439 | 39.996
Devonshire Building | 2017-08-27 11:00 | 50822.2589 | 60.012
Devonshire Building | 2017-08-27 11:15 | 50822.2739 | 60.012
Devonshire Building | 2017-08-27 11:30 | 50822.2889 | 60.012
Devonshire Building | 2017-08-27 11:45 | 50822.2989 | 39.996
Devonshire Building | 2017-08-27 12:00 | 50822.3139 | 60.012
Devonshire Building | 2017-08-27 12:15 | 50822.3239 | 39.996
Devonshire Building | 2017-08-27 12:30 | 50822.3389 | 60.012
Devonshire Building | 2017-08-27 12:45 | 50822.3539 | 60.012
Devonshire Building | 2017-08-27 13:00 | 50822.3639 | 39.996
Devonshire Building | 2017-08-27 13:15 | 50822.3789 | 60.012
Devonshire Building | 2017-08-27 13:30 | 50822.3889 | 39.996
Devonshire Building | 2017-08-27 13:45 | 50822.4039 | 60.012
Devonshire Building | 2017-08-27 14:00 | 50822.9289 | 2099.988
Devonshire Building | 2017-08-27 14:15 | 50822.9439 | 60.012
Devonshire Building | 2017-08-27 14:30 | 50822.9539 | 39.996
Devonshire Building | 2017-08-27 14:45 | 50822.9639 | 39.996
Devonshire Building | 2017-08-27 15:00 | 50822.9739 | 39.996
Devonshire Building | 2017-08-27 15:15 | 50822.9889 | 60.012
Devonshire Building | 2017-08-27 15:30 | 50822.9989 | 39.996
Devonshire Building | 2017-08-27 15:45 | 50823.014 | 60.012
Devonshire Building | 2017-08-27 16:00 | 50823.024 | 39.996
Devonshire Building | 2017-08-27 16:15 | 50823.0339 | 39.996
Devonshire Building | 2017-08-27 16:30 | 50823.049 | 60.012
Devonshire Building | 2017-08-27 16:45 | 50823.059 | 39.996
Devonshire Building | 2017-08-27 17:00 | 50823.074 | 60.012
Devonshire Building | 2017-08-27 17:15 | 50823.084 | 39.996
Devonshire Building | 2017-08-27 17:30 | 50823.099 | 60.012
Devonshire Building | 2017-08-27 17:45 | 50823.609 | 2040.012
Devonshire Building | 2017-08-27 18:00 | 50823.624 | 60.012
Devonshire Building | 2017-08-27 18:15 | 50823.634 | 39.996
Devonshire Building | 2017-08-27 18:30 | 50823.644 | 39.996
Devonshire Building | 2017-08-27 18:45 | 50823.659 | 60.012
Devonshire Building | 2017-08-27 19:00 | 50823.669 | 39.996
Devonshire Building | 2017-08-27 19:15 | 50823.679 | 39.996
Devonshire Building | 2017-08-27 19:30 | 50823.689 | 39.996
Devonshire Building | 2017-08-27 19:45 | 50823.704 | 60.012
Devonshire Building | 2017-08-27 20:00 | 50823.714 | 39.996
Devonshire Building | 2017-08-27 20:15 | 50823.729 | 60.012
Devonshire Building | 2017-08-27 20:30 | 50823.739 | 39.996
Devonshire Building | 2017-08-27 20:45 | 50823.774 | 140.004
Devonshire Building | 2017-08-27 21:00 | 50823.789 | 60.012
Devonshire Building | 2017-08-27 21:15 | 50823.804 | 60.012
Devonshire Building | 2017-08-27 21:30 | 50823.814 | 39.996
Devonshire Building | 2017-08-27 21:45 | 50823.829 | 60.012
Devonshire Building | 2017-08-27 22:00 | 50823.839 | 39.996
Devonshire Building | 2017-08-27 22:15 | 50823.854 | 60.012
Devonshire Building | 2017-08-27 22:30 | 50823.864 | 39.996
Devonshire Building | 2017-08-27 22:45 | 50824.379 | 2059.992
Devonshire Building | 2017-08-27 23:00 | 50824.389 | 39.996
Devonshire Building | 2017-08-27 23:15 | 50824.399 | 39.996
Devonshire Building | 2017-08-27 23:30 | 50824.409 | 39.996
Devonshire Building | 2017-08-27 23:45 | 50824.424 | 60.012
Devonshire Building | 2017-08-28 | 50824.4336 | 39.996
Devonshire Building | 2017-08-28 00:15 | 50824.4436 | 39.996
Devonshire Building | 2017-08-28 00:30 | 50824.4536 | 39.996
Devonshire Building | 2017-08-28 00:45 | 50824.4636 | 39.996
Devonshire Building | 2017-08-28 01:00 | 50824.4786 | 60.012
Devonshire Building | 2017-08-28 01:15 | 50824.4886 | 39.996
Devonshire Building | 2017-08-28 01:30 | 50824.5036 | 60.012
Devonshire Building | 2017-08-28 01:45 | 50824.5136 | 39.996
Devonshire Building | 2017-08-28 02:00 | 50824.5286 | 60.012
Devonshire Building | 2017-08-28 02:15 | 50824.5386 | 39.996
Devonshire Building | 2017-08-28 02:30 | 50824.5536 | 60.012
Devonshire Building | 2017-08-28 02:45 | 50824.5636 | 39.996
Devonshire Building | 2017-08-28 03:00 | 50824.5736 | 39.996
Devonshire Building | 2017-08-28 03:15 | 50824.5836 | 39.996
Devonshire Building | 2017-08-28 03:30 | 50824.5986 | 60.012
Devonshire Building | 2017-08-28 03:45 | 50824.6086 | 39.996
Devonshire Building | 2017-08-28 04:00 | 50824.6186 | 39.996
Devonshire Building | 2017-08-28 04:15 | 50824.9986 | 1519.992
Devonshire Building | 2017-08-28 04:30 | 50825.1286 | 519.984
Devonshire Building | 2017-08-28 04:45 | 50825.1386 | 39.996
Devonshire Building | 2017-08-28 05:00 | 50825.1486 | 39.996
Devonshire Building | 2017-08-28 05:15 | 50825.1586 | 39.996
Devonshire Building | 2017-08-28 05:30 | 50825.1686 | 39.996
Devonshire Building | 2017-08-28 05:45 | 50825.1786 | 39.996
Devonshire Building | 2017-08-28 06:00 | 50825.1886 | 39.996
Devonshire Building | 2017-08-28 06:15 | 50825.1986 | 39.996
Devonshire Building | 2017-08-28 06:30 | 50825.2086 | 39.996
Devonshire Building | 2017-08-28 06:45 | 50825.2186 | 39.996
Devonshire Building | 2017-08-28 07:00 | 50825.2336 | 60.012
Devonshire Building | 2017-08-28 07:15 | 50825.2436 | 39.996
Devonshire Building | 2017-08-28 07:30 | 50825.2536 | 39.996
Devonshire Building | 2017-08-28 07:45 | 50825.2736 | 79.992
Devonshire Building | 2017-08-28 08:00 | 50825.2986 | 100.008
Devonshire Building | 2017-08-28 08:15 | 50825.3286 | 119.988
Devonshire Building | 2017-08-28 08:30 | 50825.3536 | 100.008
Devonshire Building | 2017-08-28 08:45 | 50825.3786 | 100.008
Devonshire Building | 2017-08-28 09:00 | 50825.4086 | 119.988
Devonshire Building | 2017-08-28 09:15 | 50825.4336 | 100.008
Devonshire Building | 2017-08-28 09:30 | 50825.4586 | 100.008
Devonshire Building | 2017-08-28 09:45 | 50825.4886 | 119.988
Devonshire Building | 2017-08-28 10:00 | 50825.5036 | 60.012
Devonshire Building | 2017-08-28 10:15 | 50825.5136 | 39.996
Devonshire Building | 2017-08-28 10:30 | 50825.5286 | 60.012
Devonshire Building | 2017-08-28 10:45 | 50825.5386 | 39.996
Devonshire Building | 2017-08-28 11:00 | 50825.5486 | 39.996
Devonshire Building | 2017-08-28 11:15 | 50825.5586 | 39.996
Devonshire Building | 2017-08-28 11:30 | 50825.5686 | 39.996
Devonshire Building | 2017-08-28 11:45 | 50825.8736 | 1220.004
Devonshire Building | 2017-08-28 12:00 | 50826.0936 | 879.984
Devonshire Building | 2017-08-28 12:15 | 50826.1036 | 39.996
Devonshire Building | 2017-08-28 12:30 | 50826.1136 | 39.996
Devonshire Building | 2017-08-28 12:45 | 50826.1186 | 20.016
Devonshire Building | 2017-08-28 13:00 | 50826.1286 | 39.996
Devonshire Building | 2017-08-28 13:15 | 50826.1436 | 60.012
Devonshire Building | 2017-08-28 13:30 | 50826.1536 | 39.996
Devonshire Building | 2017-08-28 13:45 | 50826.1586 | 20.016
Devonshire Building | 2017-08-28 14:00 | 50826.1686 | 39.996
Devonshire Building | 2017-08-28 14:15 | 50826.1786 | 39.996
Devonshire Building | 2017-08-28 14:30 | 50826.1886 | 39.996
Devonshire Building | 2017-08-28 14:45 | 50826.1986 | 39.996
Devonshire Building | 2017-08-28 15:00 | 50826.2086 | 39.996
Devonshire Building | 2017-08-28 15:15 | 50826.2186 | 39.996
Devonshire Building | 2017-08-28 15:30 | 50826.2336 | 60.012
Devonshire Building | 2017-08-28 15:45 | 50826.2486 | 60.012
Devonshire Building | 2017-08-28 16:00 | 50826.2636 | 60.012
Devonshire Building | 2017-08-28 16:15 | 50826.2736 | 39.996
Devonshire Building | 2017-08-28 16:30 | 50826.2836 | 39.996
Devonshire Building | 2017-08-28 16:45 | 50826.2936 | 39.996
Devonshire Building | 2017-08-28 17:00 | 50826.3036 | 39.996
Devonshire Building | 2017-08-28 17:15 | 50826.3136 | 39.996
Devonshire Building | 2017-08-28 17:30 | 50826.8186 | 2019.996
Devonshire Building | 2017-08-28 17:45 | 50826.8286 | 39.996
Devonshire Building | 2017-08-28 18:00 | 50826.8386 | 39.996
Devonshire Building | 2017-08-28 18:15 | 50826.8486 | 39.996
Devonshire Building | 2017-08-28 18:30 | 50826.8536 | 20.016
Devonshire Building | 2017-08-28 18:45 | 50826.8636 | 39.996
Devonshire Building | 2017-08-28 19:00 | 50826.8736 | 39.996
Devonshire Building | 2017-08-28 19:15 | 50826.8836 | 39.996
Devonshire Building | 2017-08-28 19:30 | 50826.8936 | 39.996
Devonshire Building | 2017-08-28 19:45 | 50826.9036 | 39.996
Devonshire Building | 2017-08-28 20:00 | 50826.9136 | 39.996
Devonshire Building | 2017-08-28 20:15 | 50826.9286 | 60.012
Devonshire Building | 2017-08-28 20:30 | 50826.9386 | 39.996
Devonshire Building | 2017-08-28 20:45 | 50826.9736 | 140.004
Devonshire Building | 2017-08-28 21:00 | 50826.9836 | 39.996
Devonshire Building | 2017-08-28 21:15 | 50826.9986 | 60.012
Devonshire Building | 2017-08-28 21:30 | 50827.0086 | 39.996
Devonshire Building | 2017-08-28 21:45 | 50827.0186 | 39.996
Devonshire Building | 2017-08-28 22:00 | 50827.0336 | 60.012
Devonshire Building | 2017-08-28 22:15 | 50827.0436 | 39.996
Devonshire Building | 2017-08-28 22:30 | 50827.0536 | 39.996
Devonshire Building | 2017-08-28 22:45 | 50827.0636 | 39.996
Devonshire Building | 2017-08-28 23:00 | 50827.0786 | 60.012
Devonshire Building | 2017-08-28 23:15 | 50827.0886 | 39.996
Devonshire Building | 2017-08-28 23:30 | 50827.0986 | 39.996
Devonshire Building | 2017-08-28 23:45 | 50827.1086 | 39.996
Devonshire Building | 2017-08-29 | 50827.1211 | 39.996
Devonshire Building | 2017-08-29 00:15 | 50827.1311 | 39.996
Devonshire Building | 2017-08-29 00:30 | 50827.1511 | 79.992
Devonshire Building | 2017-08-29 00:45 | 50827.6461 | 1980
Devonshire Building | 2017-08-29 01:00 | 50827.6561 | 39.996
Devonshire Building | 2017-08-29 01:15 | 50827.6661 | 39.996
Devonshire Building | 2017-08-29 01:30 | 50827.6761 | 39.996
Devonshire Building | 2017-08-29 01:45 | 50827.6811 | 20.016
Devonshire Building | 2017-08-29 02:00 | 50827.6911 | 39.996
Devonshire Building | 2017-08-29 02:15 | 50827.7011 | 39.996
Devonshire Building | 2017-08-29 02:30 | 50827.7111 | 39.996
Devonshire Building | 2017-08-29 02:45 | 50827.7211 | 39.996
Devonshire Building | 2017-08-29 03:00 | 50827.7311 | 39.996
Devonshire Building | 2017-08-29 03:15 | 50827.7411 | 39.996
Devonshire Building | 2017-08-29 03:30 | 50827.7511 | 39.996
Devonshire Building | 2017-08-29 03:45 | 50827.7611 | 39.996
Devonshire Building | 2017-08-29 04:00 | 50827.7761 | 60.012
Devonshire Building | 2017-08-29 04:15 | 50827.7861 | 39.996
Devonshire Building | 2017-08-29 04:30 | 50827.7961 | 39.996
Devonshire Building | 2017-08-29 04:45 | 50827.8061 | 39.996
Devonshire Building | 2017-08-29 05:00 | 50827.8211 | 60.012
Devonshire Building | 2017-08-29 05:15 | 50827.8311 | 39.996
Devonshire Building | 2017-08-29 05:30 | 50827.8411 | 39.996
Devonshire Building | 2017-08-29 05:45 | 50827.8511 | 39.996
Devonshire Building | 2017-08-29 06:00 | 50827.8611 | 39.996
Devonshire Building | 2017-08-29 06:15 | 50827.8761 | 60.012
Devonshire Building | 2017-08-29 06:30 | 50827.8861 | 39.996
Devonshire Building | 2017-08-29 06:45 | 50827.9011 | 60.012
Devonshire Building | 2017-08-29 07:00 | 50827.9161 | 60.012
Devonshire Building | 2017-08-29 07:15 | 50828.4361 | 2080.008
Devonshire Building | 2017-08-29 07:30 | 50828.4461 | 39.996
Devonshire Building | 2017-08-29 07:45 | 50828.4711 | 100.008
Devonshire Building | 2017-08-29 08:00 | 50828.5211 | 200.016
Devonshire Building | 2017-08-29 08:15 | 50828.5511 | 119.988
Devonshire Building | 2017-08-29 08:30 | 50828.5811 | 119.988
Devonshire Building | 2017-08-29 08:45 | 50828.6211 | 159.984
Devonshire Building | 2017-08-29 09:00 | 50828.6611 | 159.984
Devonshire Building | 2017-08-29 09:15 | 50829.2361 | 2300.004
Devonshire Building | 2017-08-29 09:30 | 50829.2911 | 219.996
Devonshire Building | 2017-08-29 09:45 | 50829.3411 | 200.016
Devonshire Building | 2017-08-29 10:00 | 50829.3961 | 219.996
Devonshire Building | 2017-08-29 10:15 | 50829.4361 | 159.984
Devonshire Building | 2017-08-29 10:30 | 50829.9811 | 2180.016
Devonshire Building | 2017-08-29 10:45 | 50830.0911 | 439.992
Devonshire Building | 2017-08-29 11:00 | 50830.1661 | 299.988
Devonshire Building | 2017-08-29 11:15 | 50830.2311 | 259.992
Devonshire Building | 2017-08-29 11:30 | 50830.2961 | 259.992
Devonshire Building | 2017-08-29 11:45 | 50830.3461 | 200.016
Devonshire Building | 2017-08-29 12:00 | 50830.3961 | 200.016
Devonshire Building | 2017-08-29 12:15 | 50830.5661 | 680.004
Devonshire Building | 2017-08-29 12:30 | 50830.9961 | 1720.008
Devonshire Building | 2017-08-29 12:45 | 50831.0211 | 100.008
Devonshire Building | 2017-08-29 13:00 | 50831.0511 | 119.988
Devonshire Building | 2017-08-29 13:15 | 50831.0761 | 100.008
Devonshire Building | 2017-08-29 13:30 | 50831.1061 | 119.988
Devonshire Building | 2017-08-29 13:45 | 50831.1511 | 180
Devonshire Building | 2017-08-29 14:00 | 50831.1761 | 100.008
Devonshire Building | 2017-08-29 14:15 | 50831.2361 | 240.012
Devonshire Building | 2017-08-29 14:30 | 50831.7511 | 2059.992
Devonshire Building | 2017-08-29 14:45 | 50831.7661 | 60.012
Devonshire Building | 2017-08-29 15:00 | 50831.7811 | 60.012
Devonshire Building | 2017-08-29 15:15 | 50831.7961 | 60.012
Devonshire Building | 2017-08-29 15:30 | 50831.8111 | 60.012
Devonshire Building | 2017-08-29 15:45 | 50831.8261 | 60.012
Devonshire Building | 2017-08-29 16:00 | 50831.8461 | 79.992
Devonshire Building | 2017-08-29 16:15 | 50832.0011 | 619.992
Devonshire Building | 2017-08-29 16:30 | 50832.3811 | 1519.992
Devonshire Building | 2017-08-29 16:45 | 50832.3961 | 60.012
Devonshire Building | 2017-08-29 17:00 | 50832.4161 | 79.992
Devonshire Building | 2017-08-29 17:15 | 50832.4311 | 60.012
Devonshire Building | 2017-08-29 17:30 | 50832.4461 | 60.012
Devonshire Building | 2017-08-29 17:45 | 50832.4661 | 79.992
Devonshire Building | 2017-08-29 18:00 | 50832.4811 | 60.012
Devonshire Building | 2017-08-29 18:15 | 50832.4961 | 60.012
Devonshire Building | 2017-08-29 18:30 | 50832.5111 | 60.012
Devonshire Building | 2017-08-29 18:45 | 50832.5261 | 60.012
Devonshire Building | 2017-08-29 19:00 | 50832.5411 | 60.012
Devonshire Building | 2017-08-29 19:15 | 50832.5561 | 60.012
Devonshire Building | 2017-08-29 19:30 | 50832.5711 | 60.012
Devonshire Building | 2017-08-29 19:45 | 50832.5861 | 60.012
Devonshire Building | 2017-08-29 20:00 | 50832.6011 | 60.012
Devonshire Building | 2017-08-29 20:15 | 50832.6161 | 60.012
Devonshire Building | 2017-08-29 20:30 | 50832.6311 | 60.012
Devonshire Building | 2017-08-29 20:45 | 50832.6661 | 140.004
Devonshire Building | 2017-08-29 21:00 | 50832.6811 | 60.012
Devonshire Building | 2017-08-29 21:15 | 50832.6961 | 60.012
Devonshire Building | 2017-08-29 21:30 | 50832.7111 | 60.012
Devonshire Building | 2017-08-29 21:45 | 50832.7261 | 60.012
Devonshire Building | 2017-08-29 22:00 | 50832.7411 | 60.012
Devonshire Building | 2017-08-29 22:15 | 50832.7511 | 39.996
Devonshire Building | 2017-08-29 22:30 | 50832.7662 | 60.012
Devonshire Building | 2017-08-29 22:45 | 50833.1312 | 1460.016
Devonshire Building | 2017-08-29 23:00 | 50833.2912 | 640.008
Devonshire Building | 2017-08-29 23:15 | 50833.3062 | 60.012
Devonshire Building | 2017-08-29 23:30 | 50833.3162 | 39.996
Devonshire Building | 2017-08-29 23:45 | 50833.3262 | 39.996
Devonshire Building | 2017-08-30 | 50833.3398 | 60.012
Devonshire Building | 2017-08-30 00:15 | 50833.3498 | 39.996
Devonshire Building | 2017-08-30 00:30 | 50833.3648 | 60.012
Devonshire Building | 2017-08-30 00:45 | 50833.3798 | 60.012
Devonshire Building | 2017-08-30 01:00 | 50833.3948 | 60.012
Devonshire Building | 2017-08-30 01:15 | 50833.4099 | 60.012
Devonshire Building | 2017-08-30 01:30 | 50833.4249 | 60.012
Devonshire Building | 2017-08-30 01:45 | 50833.4399 | 60.012
Devonshire Building | 2017-08-30 02:00 | 50833.4549 | 60.012
Devonshire Building | 2017-08-30 02:15 | 50833.4699 | 60.012
Devonshire Building | 2017-08-30 02:30 | 50833.4849 | 60.012
Devonshire Building | 2017-08-30 02:45 | 50833.4999 | 60.012
Devonshire Building | 2017-08-30 03:00 | 50833.5149 | 60.012
Devonshire Building | 2017-08-30 03:15 | 50833.5249 | 39.996
Devonshire Building | 2017-08-30 03:30 | 50833.5399 | 60.012
Devonshire Building | 2017-08-30 03:45 | 50833.5549 | 60.012
Devonshire Building | 2017-08-30 04:00 | 50833.5699 | 60.012
Devonshire Building | 2017-08-30 04:15 | 50833.5799 | 39.996
Devonshire Building | 2017-08-30 04:30 | 50833.5949 | 60.012
Devonshire Building | 2017-08-30 04:45 | 50833.6049 | 39.996
Devonshire Building | 2017-08-30 05:00 | 50833.6199 | 60.012
Devonshire Building | 2017-08-30 05:15 | 50833.6299 | 39.996
Devonshire Building | 2017-08-30 05:30 | 50833.6449 | 60.012
Devonshire Building | 2017-08-30 05:45 | 50833.6549 | 39.996
Devonshire Building | 2017-08-30 06:00 | 50833.6699 | 60.012
Devonshire Building | 2017-08-30 06:15 | 50833.6799 | 39.996
Devonshire Building | 2017-08-30 06:30 | 50833.7199 | 159.984
Devonshire Building | 2017-08-30 06:45 | 50834.2249 | 2019.996
Devonshire Building | 2017-08-30 07:00 | 50834.2349 | 39.996
Devonshire Building | 2017-08-30 07:15 | 50834.2499 | 60.012
Devonshire Building | 2017-08-30 07:30 | 50834.2649 | 60.012
Devonshire Building | 2017-08-30 07:45 | 50834.2799 | 60.012
Devonshire Building | 2017-08-30 08:00 | 50834.3149 | 140.004
Devonshire Building | 2017-08-30 08:15 | 50834.3699 | 219.996
Devonshire Building | 2017-08-30 08:30 | 50834.4249 | 219.996
Devonshire Building | 2017-08-30 08:45 | 50834.4849 | 240.012
Devonshire Building | 2017-08-30 09:00 | 50835.0599 | 2300.004
Devonshire Building | 2017-08-30 09:15 | 50835.1349 | 299.988
Devonshire Building | 2017-08-30 09:30 | 50835.2099 | 299.988
Devonshire Building | 2017-08-30 09:45 | 50835.2999 | 360
Devonshire Building | 2017-08-30 10:00 | 50835.3699 | 280.008
Devonshire Building | 2017-08-30 10:15 | 50835.4199 | 200.016
Devonshire Building | 2017-08-30 10:30 | 50835.9849 | 2260.008
Devonshire Building | 2017-08-30 10:45 | 50836.0299 | 180
Devonshire Building | 2017-08-30 11:00 | 50836.0699 | 159.984
Devonshire Building | 2017-08-30 11:15 | 50836.1099 | 159.984
Devonshire Building | 2017-08-30 11:30 | 50836.1449 | 140.004
Devonshire Building | 2017-08-30 11:45 | 50836.3599 | 860.004
Devonshire Building | 2017-08-30 12:00 | 50836.7349 | 1500.012
Devonshire Building | 2017-08-30 12:15 | 50836.7699 | 140.004
Devonshire Building | 2017-08-30 12:30 | 50836.8149 | 180
Devonshire Building | 2017-08-30 12:45 | 50836.8699 | 219.996
Devonshire Building | 2017-08-30 13:00 | 50836.9349 | 259.992
Devonshire Building | 2017-08-30 13:15 | 50836.9999 | 259.992
Devonshire Building | 2017-08-30 13:30 | 50837.3549 | 1419.984
Devonshire Building | 2017-08-30 13:45 | 50837.7049 | 1400.004
Devonshire Building | 2017-08-30 14:00 | 50837.8299 | 500.004
Devonshire Building | 2017-08-30 14:15 | 50837.9399 | 439.992
Devonshire Building | 2017-08-30 14:30 | 50838.0299 | 360
Devonshire Building | 2017-08-30 14:45 | 50838.1199 | 360
Devonshire Building | 2017-08-30 15:00 | 50838.2099 | 360
Devonshire Building | 2017-08-30 15:15 | 50838.2949 | 339.984
Devonshire Building | 2017-08-30 15:30 | 50838.3799 | 339.984
Devonshire Building | 2017-08-30 15:45 | 50838.9499 | 2279.988
Devonshire Building | 2017-08-30 16:00 | 50839.0049 | 219.996
Devonshire Building | 2017-08-30 16:15 | 50839.0599 | 219.996
Devonshire Building | 2017-08-30 16:30 | 50839.1149 | 219.996
Devonshire Building | 2017-08-30 16:45 | 50839.1549 | 159.984
Devonshire Building | 2017-08-30 17:00 | 50839.1949 | 159.984
Devonshire Building | 2017-08-30 17:15 | 50839.2299 | 140.004
Devonshire Building | 2017-08-30 17:30 | 50839.2599 | 119.988
Devonshire Building | 2017-08-30 17:45 | 50839.2849 | 100.008
Devonshire Building | 2017-08-30 18:00 | 50839.3099 | 100.008
Devonshire Building | 2017-08-30 18:15 | 50839.3299 | 79.992
Devonshire Building | 2017-08-30 18:30 | 50839.3499 | 79.992
Devonshire Building | 2017-08-30 18:45 | 50839.3699 | 79.992
Devonshire Building | 2017-08-30 19:00 | 50839.3899 | 79.992
Devonshire Building | 2017-08-30 19:15 | 50839.4049 | 60.012
Devonshire Building | 2017-08-30 19:30 | 50839.4199 | 60.012
Devonshire Building | 2017-08-30 19:45 | 50839.4349 | 60.012
Devonshire Building | 2017-08-30 20:00 | 50839.4599 | 100.008
Devonshire Building | 2017-08-30 20:15 | 50839.9649 | 2019.996
Devonshire Building | 2017-08-30 20:30 | 50839.9849 | 79.992
Devonshire Building | 2017-08-30 20:45 | 50839.9999 | 60.012
Devonshire Building | 2017-08-30 21:00 | 50840.0099 | 39.996
Devonshire Building | 2017-08-30 21:15 | 50840.0149 | 20.016
Devonshire Building | 2017-08-30 21:30 | 50840.0199 | 20.016
Devonshire Building | 2017-08-30 21:45 | 50840.0299 | 39.996
Devonshire Building | 2017-08-30 22:00 | 50840.0349 | 20.016
Devonshire Building | 2017-08-30 22:15 | 50840.0399 | 20.016
Devonshire Building | 2017-08-30 22:30 | 50840.0449 | 20.016
Devonshire Building | 2017-08-30 22:45 | 50840.0549 | 39.996
Devonshire Building | 2017-08-30 23:00 | 50840.0599 | 20.016
Devonshire Building | 2017-08-30 23:15 | 50840.0649 | 20.016
Devonshire Building | 2017-08-30 23:30 | 50840.0699 | 20.016
Devonshire Building | 2017-08-30 23:45 | 50840.0799 | 39.996
Devonshire Building | 2017-08-31 | 50840.0859 | 20.016
Devonshire Building | 2017-08-31 00:15 | 50840.0909 | 20.016
Devonshire Building | 2017-08-31 00:30 | 50840.1009 | 39.996
Devonshire Building | 2017-08-31 00:45 | 50840.1059 | 20.016
Devonshire Building | 2017-08-31 01:00 | 50840.111 | 20.016
Devonshire Building | 2017-08-31 01:15 | 50840.1209 | 39.996
Devonshire Building | 2017-08-31 01:30 | 50840.126 | 20.016
Devonshire Building | 2017-08-31 01:45 | 50840.131 | 20.016
Devonshire Building | 2017-08-31 02:00 | 50840.141 | 39.996
Devonshire Building | 2017-08-31 02:15 | 50840.146 | 20.016
Devonshire Building | 2017-08-31 02:30 | 50840.151 | 20.016
Devonshire Building | 2017-08-31 02:45 | 50840.161 | 39.996
Devonshire Building | 2017-08-31 03:00 | 50840.166 | 20.016
Devonshire Building | 2017-08-31 03:15 | 50840.171 | 20.016
Devonshire Building | 2017-08-31 03:30 | 50840.681 | 2040.012
Devonshire Building | 2017-08-31 03:45 | 50840.691 | 39.996
Devonshire Building | 2017-08-31 04:00 | 50840.696 | 20.016
Devonshire Building | 2017-08-31 04:15 | 50840.706 | 39.996
Devonshire Building | 2017-08-31 04:30 | 50840.711 | 20.016
Devonshire Building | 2017-08-31 04:45 | 50840.721 | 39.996
Devonshire Building | 2017-08-31 05:00 | 50840.726 | 20.016
Devonshire Building | 2017-08-31 05:15 | 50840.736 | 39.996
Devonshire Building | 2017-08-31 05:30 | 50840.741 | 20.016
Devonshire Building | 2017-08-31 05:45 | 50840.746 | 20.016
Devonshire Building | 2017-08-31 06:00 | 50840.756 | 39.996
Devonshire Building | 2017-08-31 06:15 | 50840.761 | 20.016
Devonshire Building | 2017-08-31 06:30 | 50840.771 | 39.996
Devonshire Building | 2017-08-31 06:45 | 50840.781 | 39.996
Devonshire Building | 2017-08-31 07:00 | 50840.786 | 20.016
Devonshire Building | 2017-08-31 07:15 | 50840.796 | 39.996
Devonshire Building | 2017-08-31 07:30 | 50840.811 | 60.012
Devonshire Building | 2017-08-31 07:45 | 50840.831 | 79.992
Devonshire Building | 2017-08-31 08:00 | 50840.936 | 420.012
Devonshire Building | 2017-08-31 08:15 | 50841.406 | 1879.992
Devonshire Building | 2017-08-31 08:30 | 50841.446 | 159.984
Devonshire Building | 2017-08-31 08:45 | 50841.481 | 140.004
Devonshire Building | 2017-08-31 09:00 | 50841.516 | 140.004
Devonshire Building | 2017-08-31 09:15 | 50841.551 | 140.004
Devonshire Building | 2017-08-31 09:30 | 50841.586 | 140.004
Devonshire Building | 2017-08-31 09:45 | 50841.631 | 180
Devonshire Building | 2017-08-31 10:00 | 50841.676 | 180
Devonshire Building | 2017-08-31 10:15 | 50842.271 | 2379.996
Devonshire Building | 2017-08-31 10:30 | 50842.326 | 219.996
Devonshire Building | 2017-08-31 10:45 | 50842.386 | 240.012
Devonshire Building | 2017-08-31 11:00 | 50842.446 | 240.012
Devonshire Building | 2017-08-31 11:15 | 50842.501 | 219.996
Devonshire Building | 2017-08-31 11:30 | 50842.551 | 200.016
Devonshire Building | 2017-08-31 11:45 | 50842.606 | 219.996
Devonshire Building | 2017-08-31 12:00 | 50842.721 | 460.008
Devonshire Building | 2017-08-31 12:15 | 50843.201 | 1919.988
Devonshire Building | 2017-08-31 12:30 | 50843.236 | 140.004
Devonshire Building | 2017-08-31 12:45 | 50843.276 | 159.984
Devonshire Building | 2017-08-31 13:00 | 50843.316 | 159.984
Devonshire Building | 2017-08-31 13:15 | 50843.356 | 159.984
Devonshire Building | 2017-08-31 13:30 | 50843.391 | 140.004
Devonshire Building | 2017-08-31 13:45 | 50843.431 | 159.984
Devonshire Building | 2017-08-31 14:00 | 50843.466 | 140.004
Devonshire Building | 2017-08-31 14:15 | 50844.021 | 2220.012
Devonshire Building | 2017-08-31 14:30 | 50844.051 | 119.988
Devonshire Building | 2017-08-31 14:45 | 50844.081 | 119.988
Devonshire Building | 2017-08-31 15:00 | 50844.111 | 119.988
Devonshire Building | 2017-08-31 15:15 | 50844.151 | 159.984
Devonshire Building | 2017-08-31 15:30 | 50844.191 | 159.984
Devonshire Building | 2017-08-31 15:45 | 50844.231 | 159.984
Devonshire Building | 2017-08-31 16:00 | 50844.271 | 159.984
Devonshire Building | 2017-08-31 16:15 | 50844.826 | 2220.012
Devonshire Building | 2017-08-31 16:30 | 50844.886 | 240.012
Devonshire Building | 2017-08-31 16:45 | 50844.936 | 200.016
Devonshire Building | 2017-08-31 17:00 | 50844.981 | 180
Devonshire Building | 2017-08-31 17:15 | 50845.021 | 159.984
Devonshire Building | 2017-08-31 17:30 | 50845.061 | 159.984
Devonshire Building | 2017-08-31 17:45 | 50845.096 | 140.004
Devonshire Building | 2017-08-31 18:00 | 50845.131 | 140.004
Devonshire Building | 2017-08-31 18:15 | 50845.161 | 119.988
Devonshire Building | 2017-08-31 18:30 | 50845.191 | 119.988
Devonshire Building | 2017-08-31 18:45 | 50845.216 | 100.008
Devonshire Building | 2017-08-31 19:00 | 50845.241 | 100.008
Devonshire Building | 2017-08-31 19:15 | 50845.261 | 79.992
Devonshire Building | 2017-08-31 19:30 | 50845.281 | 79.992
Devonshire Building | 2017-08-31 19:45 | 50845.301 | 79.992
Devonshire Building | 2017-08-31 20:00 | 50845.321 | 79.992
Devonshire Building | 2017-08-31 20:15 | 50845.336 | 60.012
Devonshire Building | 2017-08-31 20:30 | 50845.356 | 79.992
Devonshire Building | 2017-08-31 20:45 | 50845.391 | 140.004
Devonshire Building | 2017-08-31 21:00 | 50845.401 | 39.996
Devonshire Building | 2017-08-31 21:15 | 50845.406 | 20.016
Devonshire Building | 2017-08-31 21:30 | 50845.416 | 39.996
Devonshire Building | 2017-08-31 21:45 | 50845.426 | 39.996
Devonshire Building | 2017-08-31 22:00 | 50845.436 | 39.996
Devonshire Building | 2017-08-31 22:15 | 50845.941 | 2019.996
Devonshire Building | 2017-08-31 22:30 | 50845.951 | 39.996
Devonshire Building | 2017-08-31 22:45 | 50845.956 | 20.016
Devonshire Building | 2017-08-31 23:00 | 50845.966 | 39.996
Devonshire Building | 2017-08-31 23:15 | 50845.971 | 20.016
Devonshire Building | 2017-08-31 23:30 | 50845.981 | 39.996
Devonshire Building | 2017-08-31 23:45 | 50845.986 | 20.016
Devonshire Building | 2017-09-01 | 50845.9961 | 39.996
Devonshire Building | 2017-09-01 00:15 | 50846.0011 | 20.016
Devonshire Building | 2017-09-01 00:30 | 50846.0111 | 39.996
Devonshire Building | 2017-09-01 00:45 | 50846.0161 | 20.016
Devonshire Building | 2017-09-01 01:00 | 50846.0261 | 39.996
Devonshire Building | 2017-09-01 01:15 | 50846.0311 | 20.016
Devonshire Building | 2017-09-01 01:30 | 50846.0411 | 39.996
Devonshire Building | 2017-09-01 01:45 | 50846.0461 | 20.016
Devonshire Building | 2017-09-01 02:00 | 50846.0561 | 39.996
Devonshire Building | 2017-09-01 02:15 | 50846.0611 | 20.016
Devonshire Building | 2017-09-01 02:30 | 50846.0711 | 39.996
Devonshire Building | 2017-09-01 02:45 | 50846.0761 | 20.016
Devonshire Building | 2017-09-01 03:00 | 50846.0861 | 39.996
Devonshire Building | 2017-09-01 03:15 | 50846.0961 | 39.996
Devonshire Building | 2017-09-01 03:30 | 50846.1011 | 20.016
Devonshire Building | 2017-09-01 03:45 | 50846.1111 | 39.996
Devonshire Building | 2017-09-01 04:00 | 50846.1161 | 20.016
Devonshire Building | 2017-09-01 04:15 | 50846.1261 | 39.996
Devonshire Building | 2017-09-01 04:30 | 50846.1311 | 20.016
Devonshire Building | 2017-09-01 04:45 | 50846.1411 | 39.996
Devonshire Building | 2017-09-01 05:00 | 50846.1461 | 20.016
Devonshire Building | 2017-09-01 05:15 | 50846.1561 | 39.996
Devonshire Building | 2017-09-01 05:30 | 50846.1611 | 20.016
Devonshire Building | 2017-09-01 05:45 | 50846.2911 | 519.984
Devonshire Building | 2017-09-01 06:00 | 50846.6861 | 1580.004
Devonshire Building | 2017-09-01 06:15 | 50846.6961 | 39.996
Devonshire Building | 2017-09-01 06:30 | 50846.7061 | 39.996
Devonshire Building | 2017-09-01 06:45 | 50846.7211 | 60.012
Devonshire Building | 2017-09-01 07:00 | 50846.7311 | 39.996
Devonshire Building | 2017-09-01 07:15 | 50846.7461 | 60.012
Devonshire Building | 2017-09-01 07:30 | 50846.7611 | 60.012
Devonshire Building | 2017-09-01 07:45 | 50846.7911 | 119.988
Devonshire Building | 2017-09-01 08:00 | 50846.8161 | 100.008
Devonshire Building | 2017-09-01 08:15 | 50846.8411 | 100.008
Devonshire Building | 2017-09-01 08:30 | 50846.8711 | 119.988
Devonshire Building | 2017-09-01 08:45 | 50847.4161 | 2180.016
Devonshire Building | 2017-09-01 09:00 | 50847.4511 | 140.004
Devonshire Building | 2017-09-01 09:15 | 50847.4911 | 159.984
Devonshire Building | 2017-09-01 09:30 | 50847.5311 | 159.984
Devonshire Building | 2017-09-01 09:45 | 50847.5711 | 159.984
Devonshire Building | 2017-09-01 10:00 | 50847.6161 | 180
Devonshire Building | 2017-09-01 10:15 | 50847.6461 | 119.988
Devonshire Building | 2017-09-01 10:30 | 50847.6761 | 119.988
Devonshire Building | 2017-09-01 10:45 | 50848.2311 | 2220.012
Devonshire Building | 2017-09-01 11:00 | 50848.2711 | 159.984
Devonshire Building | 2017-09-01 11:15 | 50848.3061 | 140.004
Devonshire Building | 2017-09-01 11:30 | 50848.3411 | 140.004
Devonshire Building | 2017-09-01 11:45 | 50848.3811 | 159.984
Devonshire Building | 2017-09-01 12:00 | 50848.4211 | 159.984
Devonshire Building | 2017-09-01 12:15 | 50848.4561 | 140.004
Devonshire Building | 2017-09-01 12:30 | 50848.4911 | 140.004
Devonshire Building | 2017-09-01 12:45 | 50848.7161 | 900
Devonshire Building | 2017-09-01 13:00 | 50849.0561 | 1360.008
Devonshire Building | 2017-09-01 13:15 | 50849.0961 | 159.984
Devonshire Building | 2017-09-01 13:30 | 50849.1261 | 119.988
Devonshire Building | 2017-09-01 13:45 | 50849.1611 | 140.004
Devonshire Building | 2017-09-01 14:00 | 50849.1961 | 140.004
Devonshire Building | 2017-09-01 14:15 | 50849.2261 | 119.988
Devonshire Building | 2017-09-01 14:30 | 50849.2561 | 119.988
Devonshire Building | 2017-09-01 14:45 | 50849.2861 | 119.988
Devonshire Building | 2017-09-01 15:00 | 50849.8261 | 2160
Devonshire Building | 2017-09-01 15:15 | 50849.8511 | 100.008
Devonshire Building | 2017-09-01 15:30 | 50849.8811 | 119.988
Devonshire Building | 2017-09-01 15:45 | 50849.9061 | 100.008
Devonshire Building | 2017-09-01 16:00 | 50849.9361 | 119.988
Devonshire Building | 2017-09-01 16:15 | 50849.9611 | 100.008
Devonshire Building | 2017-09-01 16:30 | 50849.9861 | 100.008
Devonshire Building | 2017-09-01 16:45 | 50850.0111 | 100.008
Devonshire Building | 2017-09-01 17:00 | 50850.0361 | 100.008
Devonshire Building | 2017-09-01 17:15 | 50850.0661 | 119.988
Devonshire Building | 2017-09-01 17:30 | 50850.0911 | 100.008
Devonshire Building | 2017-09-01 17:45 | 50850.1111 | 79.992
Devonshire Building | 2017-09-01 18:00 | 50850.1761 | 259.992
Devonshire Building | 2017-09-01 18:15 | 50850.6461 | 1879.992
Devonshire Building | 2017-09-01 18:30 | 50850.6661 | 79.992
Devonshire Building | 2017-09-01 18:45 | 50850.6811 | 60.012
Devonshire Building | 2017-09-01 19:00 | 50850.6961 | 60.012
Devonshire Building | 2017-09-01 19:15 | 50850.7161 | 79.992
Devonshire Building | 2017-09-01 19:30 | 50850.7311 | 60.012
Devonshire Building | 2017-09-01 19:45 | 50850.7511 | 79.992
Devonshire Building | 2017-09-01 20:00 | 50850.7711 | 79.992
Devonshire Building | 2017-09-01 20:15 | 50850.7911 | 79.992
Devonshire Building | 2017-09-01 20:30 | 50850.8061 | 60.012
Devonshire Building | 2017-09-01 20:45 | 50850.8411 | 140.004
Devonshire Building | 2017-09-01 21:00 | 50850.8561 | 60.012
Devonshire Building | 2017-09-01 21:15 | 50850.8661 | 39.996
Devonshire Building | 2017-09-01 21:30 | 50850.8811 | 60.012
Devonshire Building | 2017-09-01 21:45 | 50850.8911 | 39.996
Devonshire Building | 2017-09-01 22:00 | 50850.9011 | 39.996
Devonshire Building | 2017-09-01 22:15 | 50850.9161 | 60.012
Devonshire Building | 2017-09-01 22:30 | 50850.9261 | 39.996
Devonshire Building | 2017-09-01 22:45 | 50850.9411 | 60.012
Devonshire Building | 2017-09-01 23:00 | 50850.9511 | 39.996
Devonshire Building | 2017-09-01 23:15 | 50850.9611 | 39.996
Devonshire Building | 2017-09-01 23:30 | 50850.9711 | 39.996
Devonshire Building | 2017-09-01 23:45 | 50850.9861 | 60.012
Devonshire Building | 2017-09-02 | 50850.9961 | 39.996
Devonshire Building | 2017-09-02 00:15 | 50851.0061 | 39.996
Devonshire Building | 2017-09-02 00:30 | 50851.0161 | 39.996
Devonshire Building | 2017-09-02 00:45 | 50851.0261 | 39.996
Devonshire Building | 2017-09-02 01:00 | 50851.0361 | 39.996
Devonshire Building | 2017-09-02 01:15 | 50851.0511 | 60.012
Devonshire Building | 2017-09-02 01:30 | 50851.0611 | 39.996
Devonshire Building | 2017-09-02 01:45 | 50851.0711 | 39.996
Devonshire Building | 2017-09-02 02:00 | 50851.0811 | 39.996
Devonshire Building | 2017-09-02 02:15 | 50851.0911 | 39.996
Devonshire Building | 2017-09-02 02:30 | 50851.6061 | 2059.992
Devonshire Building | 2017-09-02 02:45 | 50851.6161 | 39.996
Devonshire Building | 2017-09-02 03:00 | 50851.6261 | 39.996
Devonshire Building | 2017-09-02 03:15 | 50851.6361 | 39.996
Devonshire Building | 2017-09-02 03:30 | 50851.6461 | 39.996
Devonshire Building | 2017-09-02 03:45 | 50851.6511 | 20.016
Devonshire Building | 2017-09-02 04:00 | 50851.6611 | 39.996
Devonshire Building | 2017-09-02 04:15 | 50851.6711 | 39.996
Devonshire Building | 2017-09-02 04:30 | 50851.6811 | 39.996
Devonshire Building | 2017-09-02 04:45 | 50851.6911 | 39.996
Devonshire Building | 2017-09-02 05:00 | 50851.7011 | 39.996
Devonshire Building | 2017-09-02 05:15 | 50851.7111 | 39.996
Devonshire Building | 2017-09-02 05:30 | 50851.7211 | 39.996
Devonshire Building | 2017-09-02 05:45 | 50851.7311 | 39.996
Devonshire Building | 2017-09-02 06:00 | 50851.7411 | 39.996
Devonshire Building | 2017-09-02 06:15 | 50851.7511 | 39.996
Devonshire Building | 2017-09-02 06:30 | 50851.7611 | 39.996
Devonshire Building | 2017-09-02 06:45 | 50851.7711 | 39.996
Devonshire Building | 2017-09-02 07:00 | 50851.7811 | 39.996
Devonshire Building | 2017-09-02 07:15 | 50851.7911 | 39.996
Devonshire Building | 2017-09-02 07:30 | 50851.8011 | 39.996
Devonshire Building | 2017-09-02 07:45 | 50851.8211 | 79.992
Devonshire Building | 2017-09-02 08:00 | 50851.8461 | 100.008
Devonshire Building | 2017-09-02 08:15 | 50851.8711 | 100.008
Devonshire Building | 2017-09-02 08:30 | 50851.8961 | 100.008
Devonshire Building | 2017-09-02 08:45 | 50851.9211 | 100.008
Devonshire Building | 2017-09-02 09:00 | 50851.9511 | 119.988
Devonshire Building | 2017-09-02 09:15 | 50851.9761 | 100.008
Devonshire Building | 2017-09-02 09:30 | 50852.0011 | 100.008
Devonshire Building | 2017-09-02 09:45 | 50852.0261 | 100.008
Devonshire Building | 2017-09-02 10:00 | 50852.0461 | 79.992
Devonshire Building | 2017-09-02 10:15 | 50852.0561 | 39.996
Devonshire Building | 2017-09-02 10:30 | 50852.0661 | 39.996
Devonshire Building | 2017-09-02 10:45 | 50852.0711 | 20.016
Devonshire Building | 2017-09-02 11:00 | 50852.5811 | 2040.012
Devonshire Building | 2017-09-02 11:15 | 50852.5911 | 39.996
Devonshire Building | 2017-09-02 11:30 | 50852.6011 | 39.996
Devonshire Building | 2017-09-02 11:45 | 50852.6111 | 39.996
Devonshire Building | 2017-09-02 12:00 | 50852.6211 | 39.996
Devonshire Building | 2017-09-02 12:15 | 50852.6311 | 39.996
Devonshire Building | 2017-09-02 12:30 | 50852.6411 | 39.996
Devonshire Building | 2017-09-02 12:45 | 50852.6461 | 20.016
Devonshire Building | 2017-09-02 13:00 | 50852.6561 | 39.996
Devonshire Building | 2017-09-02 13:15 | 50852.6661 | 39.996
Devonshire Building | 2017-09-02 13:30 | 50852.6761 | 39.996
Devonshire Building | 2017-09-02 13:45 | 50852.6861 | 39.996
Devonshire Building | 2017-09-02 14:00 | 50852.7011 | 60.012
Devonshire Building | 2017-09-02 14:15 | 50852.7111 | 39.996
Devonshire Building | 2017-09-02 14:30 | 50852.7211 | 39.996
Devonshire Building | 2017-09-02 14:45 | 50852.7311 | 39.996
Devonshire Building | 2017-09-02 15:00 | 50852.7411 | 39.996
Devonshire Building | 2017-09-02 15:15 | 50852.7561 | 60.012
Devonshire Building | 2017-09-02 15:30 | 50852.7661 | 39.996
Devonshire Building | 2017-09-02 15:45 | 50852.7761 | 39.996
Devonshire Building | 2017-09-02 16:00 | 50852.7861 | 39.996
Devonshire Building | 2017-09-02 16:15 | 50852.7961 | 39.996
Devonshire Building | 2017-09-02 16:30 | 50853.3061 | 2040.012
Devonshire Building | 2017-09-02 16:45 | 50853.3161 | 39.996
Devonshire Building | 2017-09-02 17:00 | 50853.3311 | 60.012
Devonshire Building | 2017-09-02 17:15 | 50853.3461 | 60.012
Devonshire Building | 2017-09-02 17:30 | 50853.3561 | 39.996
Devonshire Building | 2017-09-02 17:45 | 50853.3661 | 39.996
Devonshire Building | 2017-09-02 18:00 | 50853.3761 | 39.996
Devonshire Building | 2017-09-02 18:15 | 50853.3861 | 39.996
Devonshire Building | 2017-09-02 18:30 | 50853.3961 | 39.996
Devonshire Building | 2017-09-02 18:45 | 50853.4061 | 39.996
Devonshire Building | 2017-09-02 19:00 | 50853.4211 | 60.012
Devonshire Building | 2017-09-02 19:15 | 50853.4311 | 39.996
Devonshire Building | 2017-09-02 19:30 | 50853.4461 | 60.012
Devonshire Building | 2017-09-02 19:45 | 50853.4561 | 39.996
Devonshire Building | 2017-09-02 20:00 | 50853.4711 | 60.012
Devonshire Building | 2017-09-02 20:15 | 50853.4811 | 39.996
Devonshire Building | 2017-09-02 20:30 | 50853.4911 | 39.996
Devonshire Building | 2017-09-02 20:45 | 50853.5261 | 140.004
Devonshire Building | 2017-09-02 21:00 | 50853.5411 | 60.012
Devonshire Building | 2017-09-02 21:15 | 50853.5511 | 39.996
Devonshire Building | 2017-09-02 21:30 | 50853.5661 | 60.012
Devonshire Building | 2017-09-02 21:45 | 50853.5761 | 39.996
Devonshire Building | 2017-09-02 22:00 | 50853.5911 | 60.012
Devonshire Building | 2017-09-02 22:15 | 50853.6011 | 39.996
Devonshire Building | 2017-09-02 22:30 | 50853.6161 | 60.012
Devonshire Building | 2017-09-02 22:45 | 50853.6261 | 39.996
Devonshire Building | 2017-09-02 23:00 | 50853.6411 | 60.012
Devonshire Building | 2017-09-02 23:15 | 50853.6511 | 39.996
Devonshire Building | 2017-09-02 23:30 | 50854.0111 | 1440
Devonshire Building | 2017-09-02 23:45 | 50854.1811 | 680.004
Devonshire Building | 2017-09-03 | 50854.1875 | 39.996
Devonshire Building | 2017-09-03 00:15 | 50854.1975 | 39.996
Devonshire Building | 2017-09-03 00:30 | 50854.2075 | 39.996
Devonshire Building | 2017-09-03 00:45 | 50854.2175 | 39.996
Devonshire Building | 2017-09-03 01:00 | 50854.2275 | 39.996
Devonshire Building | 2017-09-03 01:15 | 50854.2425 | 60.012
Devonshire Building | 2017-09-03 01:30 | 50854.2525 | 39.996
Devonshire Building | 2017-09-03 01:45 | 50854.2625 | 39.996
Devonshire Building | 2017-09-03 02:00 | 50854.2775 | 60.012
Devonshire Building | 2017-09-03 02:15 | 50854.2925 | 60.012
Devonshire Building | 2017-09-03 02:30 | 50854.3025 | 39.996
Devonshire Building | 2017-09-03 02:45 | 50854.3175 | 60.012
Devonshire Building | 2017-09-03 03:00 | 50854.3325 | 60.012
Devonshire Building | 2017-09-03 03:15 | 50854.3425 | 39.996
Devonshire Building | 2017-09-03 03:30 | 50854.3575 | 60.012
Devonshire Building | 2017-09-03 03:45 | 50854.3725 | 60.012
Devonshire Building | 2017-09-03 04:00 | 50854.3825 | 39.996
Devonshire Building | 2017-09-03 04:15 | 50854.3975 | 60.012
Devonshire Building | 2017-09-03 04:30 | 50854.4075 | 39.996
Devonshire Building | 2017-09-03 04:45 | 50854.4225 | 60.012
Devonshire Building | 2017-09-03 05:00 | 50854.4325 | 39.996
Devonshire Building | 2017-09-03 05:15 | 50854.4425 | 39.996
Devonshire Building | 2017-09-03 05:30 | 50854.9525 | 2040.012
Devonshire Building | 2017-09-03 05:45 | 50854.9675 | 60.012
Devonshire Building | 2017-09-03 06:00 | 50854.9775 | 39.996
Devonshire Building | 2017-09-03 06:15 | 50854.9875 | 39.996
Devonshire Building | 2017-09-03 06:30 | 50854.9975 | 39.996
Devonshire Building | 2017-09-03 06:45 | 50855.0075 | 39.996
Devonshire Building | 2017-09-03 07:00 | 50855.0175 | 39.996
Devonshire Building | 2017-09-03 07:15 | 50855.0325 | 60.012
Devonshire Building | 2017-09-03 07:30 | 50855.0425 | 39.996
Devonshire Building | 2017-09-03 07:45 | 50855.0575 | 60.012
Devonshire Building | 2017-09-03 08:00 | 50855.0875 | 119.988
Devonshire Building | 2017-09-03 08:15 | 50855.1125 | 100.008
Devonshire Building | 2017-09-03 08:30 | 50855.1425 | 119.988
Devonshire Building | 2017-09-03 08:45 | 50855.1725 | 119.988
Devonshire Building | 2017-09-03 09:00 | 50855.1975 | 100.008
Devonshire Building | 2017-09-03 09:15 | 50855.2275 | 119.988
Devonshire Building | 2017-09-03 09:30 | 50855.2575 | 119.988
Devonshire Building | 2017-09-03 09:45 | 50855.2825 | 100.008
Devonshire Building | 2017-09-03 10:00 | 50855.3075 | 100.008
Devonshire Building | 2017-09-03 10:15 | 50855.3225 | 60.012
Devonshire Building | 2017-09-03 10:30 | 50855.3325 | 39.996
Devonshire Building | 2017-09-03 10:45 | 50855.3425 | 39.996
Devonshire Building | 2017-09-03 11:00 | 50855.3575 | 60.012
Devonshire Building | 2017-09-03 11:15 | 50855.3675 | 39.996
Devonshire Building | 2017-09-03 11:30 | 50855.3775 | 39.996
Devonshire Building | 2017-09-03 11:45 | 50855.3875 | 39.996
Devonshire Building | 2017-09-03 12:00 | 50855.4025 | 60.012
Devonshire Building | 2017-09-03 12:15 | 50855.4125 | 39.996
Devonshire Building | 2017-09-03 12:30 | 50855.9225 | 2040.012
Devonshire Building | 2017-09-03 12:45 | 50855.9325 | 39.996
Devonshire Building | 2017-09-03 13:00 | 50855.9425 | 39.996
Devonshire Building | 2017-09-03 13:15 | 50855.9525 | 39.996
Devonshire Building | 2017-09-03 13:30 | 50855.9625 | 39.996
Devonshire Building | 2017-09-03 13:45 | 50855.9725 | 39.996
Devonshire Building | 2017-09-03 14:00 | 50855.9825 | 39.996
Devonshire Building | 2017-09-03 14:15 | 50855.9975 | 60.012
Devonshire Building | 2017-09-03 14:30 | 50856.0075 | 39.996
Devonshire Building | 2017-09-03 14:45 | 50856.0175 | 39.996
Devonshire Building | 2017-09-03 15:00 | 50856.0275 | 39.996
Devonshire Building | 2017-09-03 15:15 | 50856.0375 | 39.996
Devonshire Building | 2017-09-03 15:30 | 50856.0525 | 60.012
Devonshire Building | 2017-09-03 15:45 | 50856.0625 | 39.996
Devonshire Building | 2017-09-03 16:00 | 50856.0775 | 60.012
Devonshire Building | 2017-09-03 16:15 | 50856.0875 | 39.996
Devonshire Building | 2017-09-03 16:30 | 50856.1025 | 60.012
Devonshire Building | 2017-09-03 16:45 | 50856.1175 | 60.012
Devonshire Building | 2017-09-03 17:00 | 50856.1275 | 39.996
Devonshire Building | 2017-09-03 17:15 | 50856.1375 | 39.996
Devonshire Building | 2017-09-03 17:30 | 50856.1525 | 60.012
Devonshire Building | 2017-09-03 17:45 | 50856.1625 | 39.996
Devonshire Building | 2017-09-03 18:00 | 50856.1775 | 60.012
Devonshire Building | 2017-09-03 18:15 | 50856.5975 | 1680.012
Devonshire Building | 2017-09-03 18:30 | 50856.7025 | 420.012
Devonshire Building | 2017-09-03 18:45 | 50856.7175 | 60.012
Devonshire Building | 2017-09-03 19:00 | 50856.7275 | 39.996
Devonshire Building | 2017-09-03 19:15 | 50856.7425 | 60.012
Devonshire Building | 2017-09-03 19:30 | 50856.7575 | 60.012
Devonshire Building | 2017-09-03 19:45 | 50856.7675 | 39.996
Devonshire Building | 2017-09-03 20:00 | 50856.7825 | 60.012
Devonshire Building | 2017-09-03 20:15 | 50856.7975 | 60.012
Devonshire Building | 2017-09-03 20:30 | 50856.8175 | 79.992
Devonshire Building | 2017-09-03 20:45 | 50856.8475 | 119.988
Devonshire Building | 2017-09-03 21:00 | 50856.8625 | 60.012
Devonshire Building | 2017-09-03 21:15 | 50856.8775 | 60.012
Devonshire Building | 2017-09-03 21:30 | 50856.8925 | 60.012
Devonshire Building | 2017-09-03 21:45 | 50856.9076 | 60.012
Devonshire Building | 2017-09-03 22:00 | 50856.9226 | 60.012
Devonshire Building | 2017-09-03 22:15 | 50856.9376 | 60.012
Devonshire Building | 2017-09-03 22:30 | 50856.9526 | 60.012
Devonshire Building | 2017-09-03 22:45 | 50856.9626 | 39.996
Devonshire Building | 2017-09-03 23:00 | 50856.9776 | 60.012
Devonshire Building | 2017-09-03 23:15 | 50856.9926 | 60.012
Devonshire Building | 2017-09-03 23:30 | 50857.0076 | 60.012
Devonshire Building | 2017-09-03 23:45 | 50857.0176 | 39.996
Devonshire Building | 2017-09-04 | 50857.0352 | 60.012
Devonshire Building | 2017-09-04 00:15 | 50857.0502 | 60.012
Devonshire Building | 2017-09-04 00:30 | 50857.0602 | 39.996
Devonshire Building | 2017-09-04 00:45 | 50857.0752 | 60.012
Devonshire Building | 2017-09-04 01:00 | 50857.0852 | 39.996
Devonshire Building | 2017-09-04 01:15 | 50857.5902 | 2019.996
Devonshire Building | 2017-09-04 01:30 | 50857.6002 | 39.996
Devonshire Building | 2017-09-04 01:45 | 50857.6202 | 79.992
Devonshire Building | 2017-09-04 02:00 | 50857.6452 | 100.008
Devonshire Building | 2017-09-04 02:15 | 50857.6752 | 119.988
Devonshire Building | 2017-09-04 02:30 | 50857.7002 | 100.008
Devonshire Building | 2017-09-04 02:45 | 50857.7302 | 119.988
Devonshire Building | 2017-09-04 03:00 | 50857.7552 | 100.008
Devonshire Building | 2017-09-04 03:15 | 50857.7852 | 119.988
Devonshire Building | 2017-09-04 03:30 | 50857.8102 | 100.008
Devonshire Building | 2017-09-04 03:45 | 50857.8352 | 100.008
Devonshire Building | 2017-09-04 04:00 | 50857.8502 | 60.012
Devonshire Building | 2017-09-04 04:15 | 50857.8602 | 39.996
Devonshire Building | 2017-09-04 04:30 | 50857.8752 | 60.012
Devonshire Building | 2017-09-04 04:45 | 50857.8852 | 39.996
Devonshire Building | 2017-09-04 05:00 | 50857.9002 | 60.012
Devonshire Building | 2017-09-04 05:15 | 50857.9102 | 39.996
Devonshire Building | 2017-09-04 05:30 | 50857.9252 | 60.012
Devonshire Building | 2017-09-04 05:45 | 50857.9352 | 39.996
Devonshire Building | 2017-09-04 06:00 | 50857.9502 | 60.012
Devonshire Building | 2017-09-04 06:15 | 50857.9602 | 39.996
Devonshire Building | 2017-09-04 06:30 | 50857.9702 | 39.996
Devonshire Building | 2017-09-04 06:45 | 50857.9852 | 60.012
Devonshire Building | 2017-09-04 07:00 | 50858.0102 | 100.008
Devonshire Building | 2017-09-04 07:15 | 50858.0252 | 60.012
Devonshire Building | 2017-09-04 07:30 | 50858.0502 | 100.008
Devonshire Building | 2017-09-04 07:45 | 50858.5952 | 2180.016
Devonshire Building | 2017-09-04 08:00 | 50858.6602 | 259.992
Devonshire Building | 2017-09-04 08:15 | 50858.7002 | 159.984
Devonshire Building | 2017-09-04 08:30 | 50858.7452 | 180
Devonshire Building | 2017-09-04 08:45 | 50858.7902 | 180
Devonshire Building | 2017-09-04 09:00 | 50858.8252 | 140.004
Devonshire Building | 2017-09-04 09:15 | 50858.9602 | 540
Devonshire Building | 2017-09-04 09:30 | 50859.3952 | 1739.988
Devonshire Building | 2017-09-04 09:45 | 50859.4252 | 119.988
Devonshire Building | 2017-09-04 10:00 | 50859.4602 | 140.004
Devonshire Building | 2017-09-04 10:15 | 50859.5052 | 180
Devonshire Building | 2017-09-04 10:30 | 50859.5652 | 240.012
Devonshire Building | 2017-09-04 10:45 | 50859.6302 | 259.992
Devonshire Building | 2017-09-04 11:00 | 50860.2452 | 2459.988
Devonshire Building | 2017-09-04 11:15 | 50860.3052 | 240.012
Devonshire Building | 2017-09-04 11:30 | 50860.4352 | 519.984
Devonshire Building | 2017-09-04 11:45 | 50860.5802 | 579.996
Devonshire Building | 2017-09-04 12:00 | 50860.6902 | 439.992
Devonshire Building | 2017-09-04 12:15 | 50860.7702 | 320.004
Devonshire Building | 2017-09-04 12:30 | 50860.8352 | 259.992
Devonshire Building | 2017-09-04 12:45 | 50861.3902 | 2220.012
Devonshire Building | 2017-09-04 13:00 | 50861.4302 | 159.984
Devonshire Building | 2017-09-04 13:15 | 50861.4652 | 140.004
Devonshire Building | 2017-09-04 13:30 | 50861.5002 | 140.004
Devonshire Building | 2017-09-04 13:45 | 50861.5402 | 159.984
Devonshire Building | 2017-09-04 14:00 | 50861.5752 | 140.004
Devonshire Building | 2017-09-04 14:15 | 50861.6052 | 119.988
Devonshire Building | 2017-09-04 14:30 | 50862.1252 | 2080.008
Devonshire Building | 2017-09-04 14:45 | 50862.1452 | 79.992
Devonshire Building | 2017-09-04 15:00 | 50862.1702 | 100.008
Devonshire Building | 2017-09-04 15:15 | 50862.1902 | 79.992
Devonshire Building | 2017-09-04 15:30 | 50862.2152 | 100.008
Devonshire Building | 2017-09-04 15:45 | 50862.2402 | 100.008
Devonshire Building | 2017-09-04 16:00 | 50862.2602 | 79.992
Devonshire Building | 2017-09-04 16:15 | 50862.7302 | 1879.992
Devonshire Building | 2017-09-04 16:30 | 50862.8352 | 420.012
Devonshire Building | 2017-09-04 16:45 | 50862.8552 | 79.992
Devonshire Building | 2017-09-04 17:00 | 50862.8752 | 79.992
Devonshire Building | 2017-09-04 17:15 | 50862.8952 | 79.992
Devonshire Building | 2017-09-04 17:30 | 50862.9152 | 79.992
Devonshire Building | 2017-09-04 17:45 | 50862.9352 | 79.992
Devonshire Building | 2017-09-04 18:00 | 50862.9602 | 100.008
Devonshire Building | 2017-09-04 18:15 | 50862.9752 | 60.012
Devonshire Building | 2017-09-04 18:30 | 50862.9952 | 79.992
Devonshire Building | 2017-09-04 18:45 | 50863.0152 | 79.992
Devonshire Building | 2017-09-04 19:00 | 50863.0352 | 79.992
Devonshire Building | 2017-09-04 19:15 | 50863.0502 | 60.012
Devonshire Building | 2017-09-04 19:30 | 50863.0702 | 79.992
Devonshire Building | 2017-09-04 19:45 | 50863.1002 | 119.988
Devonshire Building | 2017-09-04 20:00 | 50863.1352 | 140.004
Devonshire Building | 2017-09-04 20:15 | 50863.1652 | 119.988
Devonshire Building | 2017-09-04 20:30 | 50863.2002 | 140.004
Devonshire Building | 2017-09-04 20:45 | 50863.2502 | 200.016
Devonshire Building | 2017-09-04 21:00 | 50863.2802 | 119.988
Devonshire Building | 2017-09-04 21:15 | 50863.3052 | 100.008
Devonshire Building | 2017-09-04 21:30 | 50863.3352 | 119.988
Devonshire Building | 2017-09-04 21:45 | 50863.3551 | 79.992
Devonshire Building | 2017-09-04 22:00 | 50863.3702 | 60.012
Devonshire Building | 2017-09-04 22:15 | 50863.3802 | 39.996
Devonshire Building | 2017-09-04 22:30 | 50863.3901 | 39.996
Devonshire Building | 2017-09-04 22:45 | 50863.4001 | 39.996
Devonshire Building | 2017-09-04 23:00 | 50863.4101 | 39.996
Devonshire Building | 2017-09-04 23:15 | 50863.4201 | 39.996
Devonshire Building | 2017-09-04 23:30 | 50863.4301 | 39.996
Devonshire Building | 2017-09-04 23:45 | 50863.4401 | 39.996
Devonshire Building | 2017-09-05 | 50863.9453 | 2019.996
Devonshire Building | 2017-09-05 00:15 | 50863.9553 | 39.996
Devonshire Building | 2017-09-05 00:30 | 50863.9653 | 39.996
Devonshire Building | 2017-09-05 00:45 | 50863.9703 | 20.016
Devonshire Building | 2017-09-05 01:00 | 50863.9803 | 39.996
Devonshire Building | 2017-09-05 01:15 | 50863.9903 | 39.996
Devonshire Building | 2017-09-05 01:30 | 50864.0003 | 39.996
Devonshire Building | 2017-09-05 01:45 | 50864.0053 | 20.016
Devonshire Building | 2017-09-05 02:00 | 50864.0153 | 39.996
Devonshire Building | 2017-09-05 02:15 | 50864.0253 | 39.996
Devonshire Building | 2017-09-05 02:30 | 50864.0353 | 39.996
Devonshire Building | 2017-09-05 02:45 | 50864.0453 | 39.996
Devonshire Building | 2017-09-05 03:00 | 50864.0553 | 39.996
Devonshire Building | 2017-09-05 03:15 | 50864.0653 | 39.996
Devonshire Building | 2017-09-05 03:30 | 50864.0753 | 39.996
Devonshire Building | 2017-09-05 03:45 | 50864.0853 | 39.996
Devonshire Building | 2017-09-05 04:00 | 50864.0953 | 39.996
Devonshire Building | 2017-09-05 04:15 | 50864.1053 | 39.996
Devonshire Building | 2017-09-05 04:30 | 50864.1153 | 39.996
Devonshire Building | 2017-09-05 04:45 | 50864.1253 | 39.996
Devonshire Building | 2017-09-05 05:00 | 50864.1353 | 39.996
Devonshire Building | 2017-09-05 05:15 | 50864.1453 | 39.996
Devonshire Building | 2017-09-05 05:30 | 50864.1553 | 39.996
Devonshire Building | 2017-09-05 05:45 | 50864.1653 | 39.996
Devonshire Building | 2017-09-05 06:00 | 50864.1753 | 39.996
Devonshire Building | 2017-09-05 06:15 | 50864.1853 | 39.996
Devonshire Building | 2017-09-05 06:30 | 50864.1953 | 39.996
Devonshire Building | 2017-09-05 06:45 | 50864.2103 | 60.012
Devonshire Building | 2017-09-05 07:00 | 50864.2253 | 60.012
Devonshire Building | 2017-09-05 07:15 | 50864.2453 | 79.992
Devonshire Building | 2017-09-05 07:30 | 50864.2653 | 79.992
Devonshire Building | 2017-09-05 07:45 | 50864.8053 | 2160
Devonshire Building | 2017-09-05 08:00 | 50864.8453 | 159.984
Devonshire Building | 2017-09-05 08:15 | 50864.8803 | 140.004
Devonshire Building | 2017-09-05 08:30 | 50864.9203 | 159.984
Devonshire Building | 2017-09-05 08:45 | 50864.9603 | 159.984
Devonshire Building | 2017-09-05 09:00 | 50865.0003 | 159.984
Devonshire Building | 2017-09-05 09:15 | 50865.0403 | 159.984
Devonshire Building | 2017-09-05 09:30 | 50865.4553 | 1659.996
Devonshire Building | 2017-09-05 09:45 | 50865.6703 | 860.004
Devonshire Building | 2017-09-05 10:00 | 50865.7153 | 180
Devonshire Building | 2017-09-05 10:15 | 50865.7653 | 200.016
Devonshire Building | 2017-09-05 10:30 | 50865.8153 | 200.016
Devonshire Building | 2017-09-05 10:45 | 50866.2003 | 1540.008
Devonshire Building | 2017-09-05 11:00 | 50866.5353 | 1339.992
Devonshire Building | 2017-09-05 11:15 | 50866.5903 | 219.996
Devonshire Building | 2017-09-05 11:30 | 50866.6503 | 240.012
Devonshire Building | 2017-09-05 11:45 | 50866.7103 | 240.012
Devonshire Building | 2017-09-05 12:00 | 50866.7653 | 219.996
Devonshire Building | 2017-09-05 12:15 | 50866.8103 | 180
Devonshire Building | 2017-09-05 12:30 | 50867.1053 | 1180.008
Devonshire Building | 2017-09-05 12:45 | 50867.4253 | 1280.016
Devonshire Building | 2017-09-05 13:00 | 50867.4553 | 119.988
Devonshire Building | 2017-09-05 13:15 | 50867.4953 | 159.984
Devonshire Building | 2017-09-05 13:30 | 50867.5303 | 140.004
Devonshire Building | 2017-09-05 13:45 | 50867.5703 | 159.984
Devonshire Building | 2017-09-05 14:00 | 50867.6203 | 200.016
Devonshire Building | 2017-09-05 14:15 | 50867.6703 | 200.016
Devonshire Building | 2017-09-05 14:30 | 50867.9903 | 1280.016
Devonshire Building | 2017-09-05 14:45 | 50868.2703 | 1119.996
Devonshire Building | 2017-09-05 15:00 | 50868.3103 | 159.984
Devonshire Building | 2017-09-05 15:15 | 50868.3503 | 159.984
Devonshire Building | 2017-09-05 15:30 | 50868.3903 | 159.984
Devonshire Building | 2017-09-05 15:45 | 50868.4253 | 140.004
Devonshire Building | 2017-09-05 16:00 | 50868.4503 | 100.008
Devonshire Building | 2017-09-05 16:15 | 50868.4703 | 79.992
Devonshire Building | 2017-09-05 16:30 | 50868.7203 | 1000.008
Devonshire Building | 2017-09-05 16:45 | 50869.0103 | 1159.992
Devonshire Building | 2017-09-05 17:00 | 50869.0353 | 100.008
Devonshire Building | 2017-09-05 17:15 | 50869.0553 | 79.992
Devonshire Building | 2017-09-05 17:30 | 50869.0803 | 100.008
Devonshire Building | 2017-09-05 17:45 | 50869.1003 | 79.992
Devonshire Building | 2017-09-05 18:00 | 50869.1253 | 100.008
Devonshire Building | 2017-09-05 18:15 | 50869.1503 | 100.008
Devonshire Building | 2017-09-05 18:30 | 50869.1703 | 79.992
Devonshire Building | 2017-09-05 18:45 | 50869.1903 | 79.992
Devonshire Building | 2017-09-05 19:00 | 50869.2103 | 79.992
Devonshire Building | 2017-09-05 19:15 | 50869.2353 | 100.008
Devonshire Building | 2017-09-05 19:30 | 50869.2553 | 79.992
Devonshire Building | 2017-09-05 19:45 | 50869.2703 | 60.012
Devonshire Building | 2017-09-05 20:00 | 50869.2903 | 79.992
Devonshire Building | 2017-09-05 20:15 | 50869.3103 | 79.992
Devonshire Building | 2017-09-05 20:30 | 50869.3303 | 79.992
Devonshire Building | 2017-09-05 20:45 | 50869.3653 | 140.004
Devonshire Building | 2017-09-05 21:00 | 50869.3803 | 60.012
Devonshire Building | 2017-09-05 21:15 | 50869.3903 | 39.996
Devonshire Building | 2017-09-05 21:30 | 50869.4003 | 39.996
Devonshire Building | 2017-09-05 21:45 | 50869.4153 | 60.012
Devonshire Building | 2017-09-05 22:00 | 50869.4253 | 39.996
Devonshire Building | 2017-09-05 22:15 | 50869.6603 | 939.996
Devonshire Building | 2017-09-05 22:30 | 50869.9503 | 1159.992
Devonshire Building | 2017-09-05 22:45 | 50869.9603 | 39.996
Devonshire Building | 2017-09-05 23:00 | 50869.9703 | 39.996
Devonshire Building | 2017-09-05 23:15 | 50869.9803 | 39.996
Devonshire Building | 2017-09-05 23:30 | 50869.9903 | 39.996
Devonshire Building | 2017-09-05 23:45 | 50869.9953 | 20.016
Devonshire Building | 2017-09-06 | 50870.0039 | 39.996
Devonshire Building | 2017-09-06 00:15 | 50870.0139 | 39.996
Devonshire Building | 2017-09-06 00:30 | 50870.0239 | 39.996
Devonshire Building | 2017-09-06 00:45 | 50870.0339 | 39.996
Devonshire Building | 2017-09-06 01:00 | 50870.0489 | 60.012
Devonshire Building | 2017-09-06 01:15 | 50870.0589 | 39.996
Devonshire Building | 2017-09-06 01:30 | 50870.0689 | 39.996
Devonshire Building | 2017-09-06 01:45 | 50870.0789 | 39.996
Devonshire Building | 2017-09-06 02:00 | 50870.0939 | 60.012
Devonshire Building | 2017-09-06 02:15 | 50870.1039 | 39.996
Devonshire Building | 2017-09-06 02:30 | 50870.1139 | 39.996
Devonshire Building | 2017-09-06 02:45 | 50870.1239 | 39.996
Devonshire Building | 2017-09-06 03:00 | 50870.1339 | 39.996
Devonshire Building | 2017-09-06 03:15 | 50870.1439 | 39.996
Devonshire Building | 2017-09-06 03:30 | 50870.1539 | 39.996
Devonshire Building | 2017-09-06 03:45 | 50870.1639 | 39.996
Devonshire Building | 2017-09-06 04:00 | 50870.1739 | 39.996
Devonshire Building | 2017-09-06 04:15 | 50870.1839 | 39.996
Devonshire Building | 2017-09-06 04:30 | 50870.1939 | 39.996
Devonshire Building | 2017-09-06 04:45 | 50870.2039 | 39.996
Devonshire Building | 2017-09-06 05:00 | 50870.2139 | 39.996
Devonshire Building | 2017-09-06 05:15 | 50870.2239 | 39.996
Devonshire Building | 2017-09-06 05:30 | 50870.2339 | 39.996
Devonshire Building | 2017-09-06 05:45 | 50870.2539 | 79.992
Devonshire Building | 2017-09-06 06:00 | 50870.2689 | 60.012
Devonshire Building | 2017-09-06 06:15 | 50870.2789 | 39.996
Devonshire Building | 2017-09-06 06:30 | 50870.2889 | 39.996
Devonshire Building | 2017-09-06 06:45 | 50870.8089 | 2080.008
Devonshire Building | 2017-09-06 07:00 | 50870.8189 | 39.996
Devonshire Building | 2017-09-06 07:15 | 50870.8339 | 60.012
Devonshire Building | 2017-09-06 07:30 | 50870.8439 | 39.996
Devonshire Building | 2017-09-06 07:45 | 50870.8539 | 39.996
Devonshire Building | 2017-09-06 08:00 | 50870.8739 | 79.992
Devonshire Building | 2017-09-06 08:15 | 50870.8939 | 79.992
Devonshire Building | 2017-09-06 08:30 | 50870.9139 | 79.992
Devonshire Building | 2017-09-06 08:45 | 50870.9539 | 159.984
Devonshire Building | 2017-09-06 09:00 | 50871.0289 | 299.988
Devonshire Building | 2017-09-06 09:15 | 50871.5239 | 1980
Devonshire Building | 2017-09-06 09:30 | 50871.7189 | 780.012
Devonshire Building | 2017-09-06 09:45 | 50871.8039 | 339.984
Devonshire Building | 2017-09-06 10:00 | 50871.8889 | 339.984
Devonshire Building | 2017-09-06 10:15 | 50871.9639 | 299.988
Devonshire Building | 2017-09-06 10:30 | 50872.0389 | 299.988
Devonshire Building | 2017-09-06 10:45 | 50872.6539 | 2459.988
Devonshire Building | 2017-09-06 11:00 | 50872.7189 | 259.992
Devonshire Building | 2017-09-06 11:15 | 50872.7789 | 240.012
Devonshire Building | 2017-09-06 11:30 | 50872.8289 | 200.016
Devonshire Building | 2017-09-06 11:45 | 50872.8789 | 200.016
Devonshire Building | 2017-09-06 12:00 | 50872.9289 | 200.016
Devonshire Building | 2017-09-06 12:15 | 50873.1139 | 740.016
Devonshire Building | 2017-09-06 12:30 | 50873.5639 | 1800
Devonshire Building | 2017-09-06 12:45 | 50873.6289 | 259.992
Devonshire Building | 2017-09-06 13:00 | 50873.6839 | 219.996
Devonshire Building | 2017-09-06 13:15 | 50873.7389 | 219.996
Devonshire Building | 2017-09-06 13:30 | 50873.7939 | 219.996
Devonshire Building | 2017-09-06 13:45 | 50873.8439 | 200.016
Devonshire Building | 2017-09-06 14:00 | 50874.1139 | 1080
Devonshire Building | 2017-09-06 14:15 | 50874.4439 | 1320.012
Devonshire Building | 2017-09-06 14:30 | 50874.4739 | 119.988
Devonshire Building | 2017-09-06 14:45 | 50874.5089 | 140.004
Devonshire Building | 2017-09-06 15:00 | 50874.5389 | 119.988
Devonshire Building | 2017-09-06 15:15 | 50874.5739 | 140.004
Devonshire Building | 2017-09-06 15:30 | 50874.6089 | 140.004
Devonshire Building | 2017-09-06 15:45 | 50874.6389 | 119.988
Devonshire Building | 2017-09-06 16:00 | 50874.6689 | 119.988
Devonshire Building | 2017-09-06 16:15 | 50875.2289 | 2239.992
Devonshire Building | 2017-09-06 16:30 | 50875.2589 | 119.988
Devonshire Building | 2017-09-06 16:45 | 50875.2939 | 140.004
Devonshire Building | 2017-09-06 17:00 | 50875.3289 | 140.004
Devonshire Building | 2017-09-06 17:15 | 50875.3589 | 119.988
Devonshire Building | 2017-09-06 17:30 | 50875.3939 | 140.004
Devonshire Building | 2017-09-06 17:45 | 50875.4239 | 119.988
Devonshire Building | 2017-09-06 18:00 | 50875.4539 | 119.988
Devonshire Building | 2017-09-06 18:15 | 50875.4839 | 119.988
Devonshire Building | 2017-09-06 18:30 | 50875.5089 | 100.008
Devonshire Building | 2017-09-06 18:45 | 50875.5339 | 100.008
Devonshire Building | 2017-09-06 19:00 | 50875.5539 | 79.992
Devonshire Building | 2017-09-06 19:15 | 50875.5789 | 100.008
Devonshire Building | 2017-09-06 19:30 | 50875.5989 | 79.992
Devonshire Building | 2017-09-06 19:45 | 50875.6189 | 79.992
Devonshire Building | 2017-09-06 20:00 | 50875.6339 | 60.012
Devonshire Building | 2017-09-06 20:15 | 50875.6539 | 79.992
Devonshire Building | 2017-09-06 20:30 | 50875.6689 | 60.012
Devonshire Building | 2017-09-06 20:45 | 50875.7039 | 140.004
Devonshire Building | 2017-09-06 21:00 | 50875.7139 | 39.996
Devonshire Building | 2017-09-06 21:15 | 50875.7239 | 39.996
Devonshire Building | 2017-09-06 21:30 | 50875.7339 | 39.996
Devonshire Building | 2017-09-06 21:45 | 50875.7439 | 39.996
Devonshire Building | 2017-09-06 22:00 | 50875.7489 | 20.016
Devonshire Building | 2017-09-06 22:15 | 50875.7589 | 39.996
Devonshire Building | 2017-09-06 22:30 | 50875.7689 | 39.996
Devonshire Building | 2017-09-06 22:45 | 50875.7789 | 39.996
Devonshire Building | 2017-09-06 23:00 | 50875.7839 | 20.016
Devonshire Building | 2017-09-06 23:15 | 50875.7939 | 39.996
Devonshire Building | 2017-09-06 23:30 | 50875.8039 | 39.996
Devonshire Building | 2017-09-06 23:45 | 50875.8139 | 39.996
Devonshire Building | 2017-09-07 | 50875.8203 | 20.016
Devonshire Building | 2017-09-07 00:15 | 50876.3053 | 1940.004
Devonshire Building | 2017-09-07 00:30 | 50876.3303 | 100.008
Devonshire Building | 2017-09-07 00:45 | 50876.3403 | 39.996
Devonshire Building | 2017-09-07 01:00 | 50876.3503 | 39.996
Devonshire Building | 2017-09-07 01:15 | 50876.3553 | 20.016
Devonshire Building | 2017-09-07 01:30 | 50876.3653 | 39.996
Devonshire Building | 2017-09-07 01:45 | 50876.3703 | 20.016
Devonshire Building | 2017-09-07 02:00 | 50876.3803 | 39.996
Devonshire Building | 2017-09-07 02:15 | 50876.3903 | 39.996
Devonshire Building | 2017-09-07 02:30 | 50876.3953 | 20.016
Devonshire Building | 2017-09-07 02:45 | 50876.4053 | 39.996
Devonshire Building | 2017-09-07 03:00 | 50876.4103 | 20.016
Devonshire Building | 2017-09-07 03:15 | 50876.4203 | 39.996
Devonshire Building | 2017-09-07 03:30 | 50876.4303 | 39.996
Devonshire Building | 2017-09-07 03:45 | 50876.4353 | 20.016
Devonshire Building | 2017-09-07 04:00 | 50876.4453 | 39.996
Devonshire Building | 2017-09-07 04:15 | 50876.4553 | 39.996
Devonshire Building | 2017-09-07 04:30 | 50876.4653 | 39.996
Devonshire Building | 2017-09-07 04:45 | 50876.4703 | 20.016
Devonshire Building | 2017-09-07 05:00 | 50876.4803 | 39.996
Devonshire Building | 2017-09-07 05:15 | 50876.4903 | 39.996
Devonshire Building | 2017-09-07 05:30 | 50876.5003 | 39.996
Devonshire Building | 2017-09-07 05:45 | 50876.5053 | 20.016
Devonshire Building | 2017-09-07 06:00 | 50876.5153 | 39.996
Devonshire Building | 2017-09-07 06:15 | 50876.5253 | 39.996
Devonshire Building | 2017-09-07 06:30 | 50876.5303 | 20.016
Devonshire Building | 2017-09-07 06:45 | 50876.5403 | 39.996
Devonshire Building | 2017-09-07 07:00 | 50876.5503 | 39.996
Devonshire Building | 2017-09-07 07:15 | 50876.5603 | 39.996
Devonshire Building | 2017-09-07 07:30 | 50876.5703 | 39.996
Devonshire Building | 2017-09-07 07:45 | 50876.5853 | 60.012
Devonshire Building | 2017-09-07 08:00 | 50877.1153 | 2120.004
Devonshire Building | 2017-09-07 08:15 | 50877.1303 | 60.012
Devonshire Building | 2017-09-07 08:30 | 50877.1453 | 60.012
Devonshire Building | 2017-09-07 08:45 | 50877.1603 | 60.012
Devonshire Building | 2017-09-07 09:00 | 50877.1803 | 79.992
Devonshire Building | 2017-09-07 09:15 | 50877.2003 | 79.992
Devonshire Building | 2017-09-07 09:30 | 50877.7903 | 2360.016
Devonshire Building | 2017-09-07 09:45 | 50877.8303 | 159.984
Devonshire Building | 2017-09-07 10:00 | 50877.8703 | 159.984
Devonshire Building | 2017-09-07 10:15 | 50877.9153 | 180
Devonshire Building | 2017-09-07 10:30 | 50877.9703 | 219.996
Devonshire Building | 2017-09-07 10:45 | 50878.0553 | 339.984
Devonshire Building | 2017-09-07 11:00 | 50878.1303 | 299.988
Devonshire Building | 2017-09-07 11:15 | 50878.5953 | 1860.012
Devonshire Building | 2017-09-07 11:30 | 50878.7753 | 720
Devonshire Building | 2017-09-07 11:45 | 50878.8353 | 240.012
Devonshire Building | 2017-09-07 12:00 | 50878.8853 | 200.016
Devonshire Building | 2017-09-07 12:15 | 50878.9503 | 259.992
Devonshire Building | 2017-09-07 12:30 | 50879.0053 | 219.996
Devonshire Building | 2017-09-07 12:45 | 50879.0603 | 219.996
Devonshire Building | 2017-09-07 13:00 | 50879.1103 | 200.016
Devonshire Building | 2017-09-07 13:15 | 50879.6803 | 2279.988
Devonshire Building | 2017-09-07 13:30 | 50879.7153 | 140.004
Devonshire Building | 2017-09-07 13:45 | 50879.7503 | 140.004
Devonshire Building | 2017-09-07 14:00 | 50879.7903 | 159.984
Devonshire Building | 2017-09-07 14:15 | 50879.8253 | 140.004
Devonshire Building | 2017-09-07 14:30 | 50879.8653 | 159.984
Devonshire Building | 2017-09-07 14:45 | 50879.8853 | 79.992
Devonshire Building | 2017-09-07 15:00 | 50879.9053 | 79.992
Devonshire Building | 2017-09-07 15:15 | 50880.4403 | 2139.984
Devonshire Building | 2017-09-07 15:30 | 50880.4553 | 60.012
Devonshire Building | 2017-09-07 15:45 | 50880.4753 | 79.992
Devonshire Building | 2017-09-07 16:00 | 50880.4903 | 60.012
Devonshire Building | 2017-09-07 16:15 | 50880.5053 | 60.012
Devonshire Building | 2017-09-07 16:30 | 50880.5203 | 60.012
Devonshire Building | 2017-09-07 16:45 | 50880.5353 | 60.012
Devonshire Building | 2017-09-07 17:00 | 50880.5553 | 79.992
Devonshire Building | 2017-09-07 17:15 | 50881.0853 | 2120.004
Devonshire Building | 2017-09-07 17:30 | 50881.1103 | 100.008
Devonshire Building | 2017-09-07 17:45 | 50881.1303 | 79.992
Devonshire Building | 2017-09-07 18:00 | 50881.1503 | 79.992
Devonshire Building | 2017-09-07 18:15 | 50881.1703 | 79.992
Devonshire Building | 2017-09-07 18:30 | 50881.1903 | 79.992
Devonshire Building | 2017-09-07 18:45 | 50881.2153 | 100.008
Devonshire Building | 2017-09-07 19:00 | 50881.2353 | 79.992
Devonshire Building | 2017-09-07 19:15 | 50881.2553 | 79.992
Devonshire Building | 2017-09-07 19:30 | 50881.2753 | 79.992
Devonshire Building | 2017-09-07 19:45 | 50881.2903 | 60.012
Devonshire Building | 2017-09-07 20:00 | 50881.3103 | 79.992
Devonshire Building | 2017-09-07 20:15 | 50881.3303 | 79.992
Devonshire Building | 2017-09-07 20:30 | 50881.3453 | 60.012
Devonshire Building | 2017-09-07 20:45 | 50881.3853 | 159.984
Devonshire Building | 2017-09-07 21:00 | 50881.4003 | 60.012
Devonshire Building | 2017-09-07 21:15 | 50881.4203 | 79.992
Devonshire Building | 2017-09-07 21:30 | 50881.4353 | 60.012
Devonshire Building | 2017-09-07 21:45 | 50881.4503 | 60.012
Devonshire Building | 2017-09-07 22:00 | 50881.4653 | 60.012
Devonshire Building | 2017-09-07 22:15 | 50881.4803 | 60.012
Devonshire Building | 2017-09-07 22:30 | 50881.4953 | 60.012
Devonshire Building | 2017-09-07 22:45 | 50881.5103 | 60.012
Devonshire Building | 2017-09-07 23:00 | 50881.5203 | 39.996
Devonshire Building | 2017-09-07 23:15 | 50881.5353 | 60.012
Devonshire Building | 2017-09-07 23:30 | 50882.0403 | 2019.996
Devonshire Building | 2017-09-07 23:45 | 50882.0553 | 60.012
Devonshire Building | 2017-09-08 | 50882.0625 | 39.996
Devonshire Building | 2017-09-08 00:15 | 50882.0775 | 60.012
Devonshire Building | 2017-09-08 00:30 | 50882.0875 | 39.996
Devonshire Building | 2017-09-08 00:45 | 50882.1025 | 60.012
Devonshire Building | 2017-09-08 01:00 | 50882.1125 | 39.996
Devonshire Building | 2017-09-08 01:15 | 50882.1275 | 60.012
Devonshire Building | 2017-09-08 01:30 | 50882.1425 | 60.012
Devonshire Building | 2017-09-08 01:45 | 50882.1575 | 60.012
Devonshire Building | 2017-09-08 02:00 | 50882.1725 | 60.012
Devonshire Building | 2017-09-08 02:15 | 50882.1875 | 60.012
Devonshire Building | 2017-09-08 02:30 | 50882.1975 | 39.996
Devonshire Building | 2017-09-08 02:45 | 50882.2125 | 60.012
Devonshire Building | 2017-09-08 03:00 | 50882.2275 | 60.012
Devonshire Building | 2017-09-08 03:15 | 50882.2425 | 60.012
Devonshire Building | 2017-09-08 03:30 | 50882.2575 | 60.012
Devonshire Building | 2017-09-08 03:45 | 50882.2675 | 39.996
Devonshire Building | 2017-09-08 04:00 | 50882.2825 | 60.012
Devonshire Building | 2017-09-08 04:15 | 50882.2975 | 60.012
Devonshire Building | 2017-09-08 04:30 | 50882.3075 | 39.996
Devonshire Building | 2017-09-08 04:45 | 50882.3225 | 60.012
Devonshire Building | 2017-09-08 05:00 | 50882.3375 | 60.012
Devonshire Building | 2017-09-08 05:15 | 50882.3475 | 39.996
Devonshire Building | 2017-09-08 05:30 | 50882.3625 | 60.012
Devonshire Building | 2017-09-08 05:45 | 50882.3725 | 39.996
Devonshire Building | 2017-09-08 06:00 | 50882.3875 | 60.012
Devonshire Building | 2017-09-08 06:15 | 50882.3975 | 39.996
Devonshire Building | 2017-09-08 06:30 | 50882.4075 | 39.996
Devonshire Building | 2017-09-08 06:45 | 50882.4225 | 60.012
Devonshire Building | 2017-09-08 07:00 | 50882.7175 | 1180.008
Devonshire Building | 2017-09-08 07:15 | 50882.9675 | 1000.008
Devonshire Building | 2017-09-08 07:30 | 50882.9726 | 20.016
Devonshire Building | 2017-09-08 07:45 | 50882.9826 | 39.996
Devonshire Building | 2017-09-08 08:00 | 50883.0176 | 140.004
Devonshire Building | 2017-09-08 08:15 | 50883.0526 | 140.004
Devonshire Building | 2017-09-08 08:30 | 50883.0776 | 100.008
Devonshire Building | 2017-09-08 08:45 | 50883.1126 | 140.004
Devonshire Building | 2017-09-08 09:00 | 50883.1376 | 100.008
Devonshire Building | 2017-09-08 09:15 | 50883.1726 | 140.004
Devonshire Building | 2017-09-08 09:30 | 50883.7426 | 2279.988
Devonshire Building | 2017-09-08 09:45 | 50883.7876 | 180
Devonshire Building | 2017-09-08 10:00 | 50883.8276 | 159.984
Devonshire Building | 2017-09-08 10:15 | 50883.8526 | 100.008
Devonshire Building | 2017-09-08 10:30 | 50883.8876 | 140.004
Devonshire Building | 2017-09-08 10:45 | 50883.9326 | 180
Devonshire Building | 2017-09-08 11:00 | 50884.5326 | 2400.012
Devonshire Building | 2017-09-08 11:15 | 50884.6076 | 299.988
Devonshire Building | 2017-09-08 11:30 | 50884.6726 | 259.992
Devonshire Building | 2017-09-08 11:45 | 50884.7326 | 240.012
Devonshire Building | 2017-09-08 12:00 | 50884.7876 | 219.996
Devonshire Building | 2017-09-08 12:15 | 50884.8376 | 200.016
Devonshire Building | 2017-09-08 12:30 | 50884.8776 | 159.984
Devonshire Building | 2017-09-08 12:45 | 50885.1776 | 1199.988
Devonshire Building | 2017-09-08 13:00 | 50885.4425 | 1059.984
Devonshire Building | 2017-09-08 13:15 | 50885.4776 | 140.004
Devonshire Building | 2017-09-08 13:30 | 50885.5026 | 100.008
Devonshire Building | 2017-09-08 13:45 | 50885.5276 | 100.008
Devonshire Building | 2017-09-08 14:00 | 50885.5526 | 100.008
Devonshire Building | 2017-09-08 14:15 | 50885.5776 | 100.008
Devonshire Building | 2017-09-08 14:30 | 50885.6026 | 100.008
Devonshire Building | 2017-09-08 14:45 | 50886.1326 | 2120.004
Devonshire Building | 2017-09-08 15:00 | 50886.1526 | 79.992
Devonshire Building | 2017-09-08 15:15 | 50886.1776 | 100.008
Devonshire Building | 2017-09-08 15:30 | 50886.1976 | 79.992
Devonshire Building | 2017-09-08 15:45 | 50886.2226 | 100.008
Devonshire Building | 2017-09-08 16:00 | 50886.2426 | 79.992
Devonshire Building | 2017-09-08 16:15 | 50886.2626 | 79.992
Devonshire Building | 2017-09-08 16:30 | 50886.7976 | 2139.984
Devonshire Building | 2017-09-08 16:45 | 50886.8176 | 79.992
Devonshire Building | 2017-09-08 17:00 | 50886.8375 | 79.992
Devonshire Building | 2017-09-08 17:15 | 50886.8626 | 100.008
Devonshire Building | 2017-09-08 17:30 | 50886.8825 | 79.992
Devonshire Building | 2017-09-08 17:45 | 50886.9076 | 100.008
Devonshire Building | 2017-09-08 18:00 | 50886.9326 | 100.008
Devonshire Building | 2017-09-08 18:15 | 50886.9576 | 100.008
Devonshire Building | 2017-09-08 18:30 | 50887.0176 | 240.012
Devonshire Building | 2017-09-08 18:45 | 50887.0826 | 259.992
Devonshire Building | 2017-09-08 19:00 | 50887.1476 | 259.992
Devonshire Building | 2017-09-08 19:15 | 50887.2076 | 240.012
Devonshire Building | 2017-09-08 19:30 | 50887.2626 | 219.996
Devonshire Building | 2017-09-08 19:45 | 50887.3126 | 200.016
Devonshire Building | 2017-09-08 20:00 | 50887.3576 | 180
Devonshire Building | 2017-09-08 20:15 | 50887.3926 | 140.004
Devonshire Building | 2017-09-08 20:30 | 50887.4276 | 140.004
Devonshire Building | 2017-09-08 20:45 | 50887.4726 | 180
Devonshire Building | 2017-09-08 21:00 | 50887.4926 | 79.992
Devonshire Building | 2017-09-08 21:15 | 50887.5076 | 60.012
Devonshire Building | 2017-09-08 21:30 | 50887.5276 | 79.992
Devonshire Building | 2017-09-08 21:45 | 50887.5426 | 60.012
Devonshire Building | 2017-09-08 22:00 | 50887.5626 | 79.992
Devonshire Building | 2017-09-08 22:15 | 50887.5776 | 60.012
Devonshire Building | 2017-09-08 22:30 | 50887.5976 | 79.992
Devonshire Building | 2017-09-08 22:45 | 50887.6126 | 60.012
Devonshire Building | 2017-09-08 23:00 | 50887.6276 | 60.012
Devonshire Building | 2017-09-08 23:15 | 50887.6476 | 79.992
Devonshire Building | 2017-09-08 23:30 | 50888.1526 | 2019.996
Devonshire Building | 2017-09-08 23:45 | 50888.1626 | 39.996
Devonshire Building | 2017-09-09 | 50888.1758 | 39.996
Devonshire Building | 2017-09-09 00:15 | 50888.1858 | 39.996
Devonshire Building | 2017-09-09 00:30 | 50888.1958 | 39.996
Devonshire Building | 2017-09-09 00:45 | 50888.2058 | 39.996
Devonshire Building | 2017-09-09 01:00 | 50888.2158 | 39.996
Devonshire Building | 2017-09-09 01:15 | 50888.2258 | 39.996
Devonshire Building | 2017-09-09 01:30 | 50888.2358 | 39.996
Devonshire Building | 2017-09-09 01:45 | 50888.2458 | 39.996
Devonshire Building | 2017-09-09 02:00 | 50888.2558 | 39.996
Devonshire Building | 2017-09-09 02:15 | 50888.2658 | 39.996
Devonshire Building | 2017-09-09 02:30 | 50888.2758 | 39.996
Devonshire Building | 2017-09-09 02:45 | 50888.2908 | 60.012
Devonshire Building | 2017-09-09 03:00 | 50888.3008 | 39.996
Devonshire Building | 2017-09-09 03:15 | 50888.3108 | 39.996
Devonshire Building | 2017-09-09 03:30 | 50888.3208 | 39.996
Devonshire Building | 2017-09-09 03:45 | 50888.3308 | 39.996
Devonshire Building | 2017-09-09 04:00 | 50888.3458 | 60.012
Devonshire Building | 2017-09-09 04:15 | 50888.3558 | 39.996
Devonshire Building | 2017-09-09 04:30 | 50888.3658 | 39.996
Devonshire Building | 2017-09-09 04:45 | 50888.3758 | 39.996
Devonshire Building | 2017-09-09 05:00 | 50888.3858 | 39.996
Devonshire Building | 2017-09-09 05:15 | 50888.3958 | 39.996
Devonshire Building | 2017-09-09 05:30 | 50888.4058 | 39.996
Devonshire Building | 2017-09-09 05:45 | 50888.4158 | 39.996
Devonshire Building | 2017-09-09 06:00 | 50888.4208 | 20.016
Devonshire Building | 2017-09-09 06:15 | 50888.4308 | 39.996
Devonshire Building | 2017-09-09 06:30 | 50888.4408 | 39.996
Devonshire Building | 2017-09-09 06:45 | 50888.4508 | 39.996
Devonshire Building | 2017-09-09 07:00 | 50888.4608 | 39.996
Devonshire Building | 2017-09-09 07:15 | 50888.4708 | 39.996
Devonshire Building | 2017-09-09 07:30 | 50888.4758 | 20.016
Devonshire Building | 2017-09-09 07:45 | 50888.4908 | 60.012
Devonshire Building | 2017-09-09 08:00 | 50888.5208 | 119.988
Devonshire Building | 2017-09-09 08:15 | 50888.5458 | 100.008
Devonshire Building | 2017-09-09 08:30 | 50888.8108 | 1059.984
Devonshire Building | 2017-09-09 08:45 | 50889.0958 | 1140.012
Devonshire Building | 2017-09-09 09:00 | 50889.1208 | 100.008
Devonshire Building | 2017-09-09 09:15 | 50889.1458 | 100.008
Devonshire Building | 2017-09-09 09:30 | 50889.1708 | 100.008
Devonshire Building | 2017-09-09 09:45 | 50889.1958 | 100.008
Devonshire Building | 2017-09-09 10:00 | 50889.2208 | 100.008
Devonshire Building | 2017-09-09 10:15 | 50889.2258 | 20.016
Devonshire Building | 2017-09-09 10:30 | 50889.2358 | 39.996
Devonshire Building | 2017-09-09 10:45 | 50889.2458 | 39.996
Devonshire Building | 2017-09-09 11:00 | 50889.2558 | 39.996
Devonshire Building | 2017-09-09 11:15 | 50889.2658 | 39.996
Devonshire Building | 2017-09-09 11:30 | 50889.2758 | 39.996
Devonshire Building | 2017-09-09 11:45 | 50889.2858 | 39.996
Devonshire Building | 2017-09-09 12:00 | 50889.2958 | 39.996
Devonshire Building | 2017-09-09 12:15 | 50889.3058 | 39.996
Devonshire Building | 2017-09-09 12:30 | 50889.3158 | 39.996
Devonshire Building | 2017-09-09 12:45 | 50889.3308 | 60.012
Devonshire Building | 2017-09-09 13:00 | 50889.3408 | 39.996
Devonshire Building | 2017-09-09 13:15 | 50889.3508 | 39.996
Devonshire Building | 2017-09-09 13:30 | 50889.3608 | 39.996
Devonshire Building | 2017-09-09 13:45 | 50889.3708 | 39.996
Devonshire Building | 2017-09-09 14:00 | 50889.3808 | 39.996
Devonshire Building | 2017-09-09 14:15 | 50889.3908 | 39.996
Devonshire Building | 2017-09-09 14:30 | 50889.4008 | 39.996
Devonshire Building | 2017-09-09 14:45 | 50889.4108 | 39.996
Devonshire Building | 2017-09-09 15:00 | 50889.4258 | 60.012
Devonshire Building | 2017-09-09 15:15 | 50889.4358 | 39.996
Devonshire Building | 2017-09-09 15:30 | 50889.4458 | 39.996
Devonshire Building | 2017-09-09 15:45 | 50889.4558 | 39.996
Devonshire Building | 2017-09-09 16:00 | 50889.4658 | 39.996
Devonshire Building | 2017-09-09 16:15 | 50889.9658 | 2000.016
Devonshire Building | 2017-09-09 16:30 | 50889.9758 | 39.996
Devonshire Building | 2017-09-09 16:45 | 50889.9858 | 39.996
Devonshire Building | 2017-09-09 17:00 | 50890.0008 | 60.012
Devonshire Building | 2017-09-09 17:15 | 50890.0108 | 39.996
Devonshire Building | 2017-09-09 17:30 | 50890.0208 | 39.996
Devonshire Building | 2017-09-09 17:45 | 50890.0308 | 39.996
Devonshire Building | 2017-09-09 18:00 | 50890.0408 | 39.996
Devonshire Building | 2017-09-09 18:15 | 50890.0508 | 39.996
Devonshire Building | 2017-09-09 18:30 | 50890.0658 | 60.012
Devonshire Building | 2017-09-09 18:45 | 50890.0758 | 39.996
Devonshire Building | 2017-09-09 19:00 | 50890.0908 | 60.012
Devonshire Building | 2017-09-09 19:15 | 50890.1008 | 39.996
Devonshire Building | 2017-09-09 19:30 | 50890.1158 | 60.012
Devonshire Building | 2017-09-09 19:45 | 50890.1308 | 60.012
Devonshire Building | 2017-09-09 20:00 | 50890.1408 | 39.996
Devonshire Building | 2017-09-09 20:15 | 50890.1558 | 60.012
Devonshire Building | 2017-09-09 20:30 | 50890.1658 | 39.996
Devonshire Building | 2017-09-09 20:45 | 50890.1958 | 119.988
Devonshire Building | 2017-09-09 21:00 | 50890.2058 | 39.996
Devonshire Building | 2017-09-09 21:15 | 50890.2208 | 60.012
Devonshire Building | 2017-09-09 21:30 | 50890.2308 | 39.996
Devonshire Building | 2017-09-09 21:45 | 50890.2408 | 39.996
Devonshire Building | 2017-09-09 22:00 | 50890.2558 | 60.012
Devonshire Building | 2017-09-09 22:15 | 50890.2658 | 39.996
Devonshire Building | 2017-09-09 22:30 | 50890.2758 | 39.996
Devonshire Building | 2017-09-09 22:45 | 50890.2908 | 60.012
Devonshire Building | 2017-09-09 23:00 | 50890.3008 | 39.996
Devonshire Building | 2017-09-09 23:15 | 50890.3108 | 39.996
Devonshire Building | 2017-09-09 23:30 | 50890.3208 | 39.996
Devonshire Building | 2017-09-09 23:45 | 50890.3358 | 60.012
Devonshire Building | 2017-09-10 | 50890.3438 | 39.996
Devonshire Building | 2017-09-10 00:15 | 50890.3537 | 39.996
Devonshire Building | 2017-09-10 00:30 | 50890.3637 | 39.996
Devonshire Building | 2017-09-10 00:45 | 50890.3737 | 39.996
Devonshire Building | 2017-09-10 01:00 | 50890.3837 | 39.996
Devonshire Building | 2017-09-10 01:15 | 50890.3937 | 39.996
Devonshire Building | 2017-09-10 01:30 | 50890.4037 | 39.996
Devonshire Building | 2017-09-10 01:45 | 50890.4137 | 39.996
Devonshire Building | 2017-09-10 02:00 | 50890.4237 | 39.996
Devonshire Building | 2017-09-10 02:15 | 50890.9337 | 2040.012
Devonshire Building | 2017-09-10 02:30 | 50890.9437 | 39.996
Devonshire Building | 2017-09-10 02:45 | 50890.9537 | 39.996
Devonshire Building | 2017-09-10 03:00 | 50890.9637 | 39.996
Devonshire Building | 2017-09-10 03:15 | 50890.9737 | 39.996
Devonshire Building | 2017-09-10 03:30 | 50890.9837 | 39.996
Devonshire Building | 2017-09-10 03:45 | 50890.9937 | 39.996
Devonshire Building | 2017-09-10 04:00 | 50891.0037 | 39.996
Devonshire Building | 2017-09-10 04:15 | 50891.0137 | 39.996
Devonshire Building | 2017-09-10 04:30 | 50891.0237 | 39.996
Devonshire Building | 2017-09-10 04:45 | 50891.0337 | 39.996
Devonshire Building | 2017-09-10 05:00 | 50891.0487 | 60.012
Devonshire Building | 2017-09-10 05:15 | 50891.0587 | 39.996
Devonshire Building | 2017-09-10 05:30 | 50891.0737 | 60.012
Devonshire Building | 2017-09-10 05:45 | 50891.0837 | 39.996
Devonshire Building | 2017-09-10 06:00 | 50891.0987 | 60.012
Devonshire Building | 2017-09-10 06:15 | 50891.1087 | 39.996
Devonshire Building | 2017-09-10 06:30 | 50891.1187 | 39.996
Devonshire Building | 2017-09-10 06:45 | 50891.1337 | 60.012
Devonshire Building | 2017-09-10 07:00 | 50891.1437 | 39.996
Devonshire Building | 2017-09-10 07:15 | 50891.1537 | 39.996
Devonshire Building | 2017-09-10 07:30 | 50891.1687 | 60.012
Devonshire Building | 2017-09-10 07:45 | 50891.1887 | 79.992
Devonshire Building | 2017-09-10 08:00 | 50891.2137 | 100.008
Devonshire Building | 2017-09-10 08:15 | 50891.2437 | 119.988
Devonshire Building | 2017-09-10 08:30 | 50891.2687 | 100.008
Devonshire Building | 2017-09-10 08:45 | 50891.2987 | 119.988
Devonshire Building | 2017-09-10 09:00 | 50891.3237 | 100.008
Devonshire Building | 2017-09-10 09:15 | 50891.3487 | 100.008
Devonshire Building | 2017-09-10 09:30 | 50891.3787 | 119.988
Devonshire Building | 2017-09-10 09:45 | 50891.4037 | 100.008
Devonshire Building | 2017-09-10 10:00 | 50891.4337 | 119.988
Devonshire Building | 2017-09-10 10:15 | 50891.4437 | 39.996
Devonshire Building | 2017-09-10 10:30 | 50891.4537 | 39.996
Devonshire Building | 2017-09-10 10:45 | 50891.4637 | 39.996
Devonshire Building | 2017-09-10 11:00 | 50891.9687 | 2019.996
Devonshire Building | 2017-09-10 11:15 | 50891.9787 | 39.996
Devonshire Building | 2017-09-10 11:30 | 50891.9887 | 39.996
Devonshire Building | 2017-09-10 11:45 | 50891.9987 | 39.996
Devonshire Building | 2017-09-10 12:00 | 50892.0087 | 39.996
Devonshire Building | 2017-09-10 12:15 | 50892.0187 | 39.996
Devonshire Building | 2017-09-10 12:30 | 50892.0287 | 39.996
Devonshire Building | 2017-09-10 12:45 | 50892.0387 | 39.996
Devonshire Building | 2017-09-10 13:00 | 50892.0487 | 39.996
Devonshire Building | 2017-09-10 13:15 | 50892.0587 | 39.996
Devonshire Building | 2017-09-10 13:30 | 50892.0687 | 39.996
Devonshire Building | 2017-09-10 13:45 | 50892.0787 | 39.996
Devonshire Building | 2017-09-10 14:00 | 50892.0937 | 60.012
Devonshire Building | 2017-09-10 14:15 | 50892.1037 | 39.996
Devonshire Building | 2017-09-10 14:30 | 50892.1137 | 39.996
Devonshire Building | 2017-09-10 14:45 | 50892.1287 | 60.012
Devonshire Building | 2017-09-10 15:00 | 50892.1387 | 39.996
Devonshire Building | 2017-09-10 15:15 | 50892.1537 | 60.012
Devonshire Building | 2017-09-10 15:30 | 50892.1637 | 39.996
Devonshire Building | 2017-09-10 15:45 | 50892.1737 | 39.996
Devonshire Building | 2017-09-10 16:00 | 50892.1837 | 39.996
Devonshire Building | 2017-09-10 16:15 | 50892.1987 | 60.012
Devonshire Building | 2017-09-10 16:30 | 50892.2087 | 39.996
Devonshire Building | 2017-09-10 16:45 | 50892.2187 | 39.996
Devonshire Building | 2017-09-10 17:00 | 50892.2287 | 39.996
Devonshire Building | 2017-09-10 17:15 | 50892.2387 | 39.996
Devonshire Building | 2017-09-10 17:30 | 50892.2487 | 39.996
Devonshire Building | 2017-09-10 17:45 | 50892.2587 | 39.996
Devonshire Building | 2017-09-10 18:00 | 50892.2687 | 39.996
Devonshire Building | 2017-09-10 18:15 | 50892.2787 | 39.996
Devonshire Building | 2017-09-10 18:30 | 50892.2887 | 39.996
Devonshire Building | 2017-09-10 18:45 | 50892.2987 | 39.996
Devonshire Building | 2017-09-10 19:00 | 50892.3087 | 39.996
Devonshire Building | 2017-09-10 19:15 | 50892.3187 | 39.996
Devonshire Building | 2017-09-10 19:30 | 50892.7937 | 1900.008
Devonshire Building | 2017-09-10 19:45 | 50892.8387 | 180
Devonshire Building | 2017-09-10 20:00 | 50892.8487 | 39.996
Devonshire Building | 2017-09-10 20:15 | 50892.8587 | 39.996
Devonshire Building | 2017-09-10 20:30 | 50892.8687 | 39.996
Devonshire Building | 2017-09-10 20:45 | 50892.8887 | 79.992
Devonshire Building | 2017-09-10 21:00 | 50892.8987 | 39.996
Devonshire Building | 2017-09-10 21:15 | 50892.9087 | 39.996
Devonshire Building | 2017-09-10 21:30 | 50892.9187 | 39.996
Devonshire Building | 2017-09-10 21:45 | 50892.9287 | 39.996
Devonshire Building | 2017-09-10 22:00 | 50892.9437 | 60.012
Devonshire Building | 2017-09-10 22:15 | 50892.9537 | 39.996
Devonshire Building | 2017-09-10 22:30 | 50892.9637 | 39.996
Devonshire Building | 2017-09-10 22:45 | 50892.9787 | 60.012
Devonshire Building | 2017-09-10 23:00 | 50892.9887 | 39.996
Devonshire Building | 2017-09-10 23:15 | 50893.0037 | 60.012
Devonshire Building | 2017-09-10 23:30 | 50893.0137 | 39.996
Devonshire Building | 2017-09-10 23:45 | 50893.0287 | 60.012
Devonshire Building | 2017-09-11 | 50893.0391 | 39.996
Devonshire Building | 2017-09-11 00:15 | 50893.0491 | 39.996
Devonshire Building | 2017-09-11 00:30 | 50893.0641 | 60.012
Devonshire Building | 2017-09-11 00:45 | 50893.0741 | 39.996
Devonshire Building | 2017-09-11 01:00 | 50893.0841 | 39.996
Devonshire Building | 2017-09-11 01:15 | 50893.0991 | 60.012
Devonshire Building | 2017-09-11 01:30 | 50893.1091 | 39.996
Devonshire Building | 2017-09-11 01:45 | 50893.1191 | 39.996
Devonshire Building | 2017-09-11 02:00 | 50893.1291 | 39.996
Devonshire Building | 2017-09-11 02:15 | 50893.1391 | 39.996
Devonshire Building | 2017-09-11 02:30 | 50893.1541 | 60.012
Devonshire Building | 2017-09-11 02:45 | 50893.1641 | 39.996
Devonshire Building | 2017-09-11 03:00 | 50893.1741 | 39.996
Devonshire Building | 2017-09-11 03:15 | 50893.1841 | 39.996
Devonshire Building | 2017-09-11 03:30 | 50893.1941 | 39.996
Devonshire Building | 2017-09-11 03:45 | 50893.2041 | 39.996
Devonshire Building | 2017-09-11 04:00 | 50893.2141 | 39.996
Devonshire Building | 2017-09-11 04:15 | 50893.2241 | 39.996
Devonshire Building | 2017-09-11 04:30 | 50893.2341 | 39.996
Devonshire Building | 2017-09-11 04:45 | 50893.2441 | 39.996
Devonshire Building | 2017-09-11 05:00 | 50893.2541 | 39.996
Devonshire Building | 2017-09-11 05:15 | 50893.7591 | 2019.996
Devonshire Building | 2017-09-11 05:30 | 50893.7691 | 39.996
Devonshire Building | 2017-09-11 05:45 | 50893.779 | 39.996
Devonshire Building | 2017-09-11 06:00 | 50893.7941 | 60.012
Devonshire Building | 2017-09-11 06:15 | 50893.8041 | 39.996
Devonshire Building | 2017-09-11 06:30 | 50893.8141 | 39.996
Devonshire Building | 2017-09-11 06:45 | 50893.824 | 39.996
Devonshire Building | 2017-09-11 07:00 | 50893.844 | 79.992
Devonshire Building | 2017-09-11 07:15 | 50893.859 | 60.012
Devonshire Building | 2017-09-11 07:30 | 50893.8741 | 60.012
Devonshire Building | 2017-09-11 07:45 | 50893.8991 | 100.008
Devonshire Building | 2017-09-11 08:00 | 50893.9541 | 219.996
Devonshire Building | 2017-09-11 08:15 | 50894.0041 | 200.016
Devonshire Building | 2017-09-11 08:30 | 50894.5591 | 2220.012
Devonshire Building | 2017-09-11 08:45 | 50894.6191 | 240.012
Devonshire Building | 2017-09-11 09:00 | 50894.6791 | 240.012
Devonshire Building | 2017-09-11 09:15 | 50894.7491 | 280.008
Devonshire Building | 2017-09-11 09:30 | 50894.8141 | 259.992
Devonshire Building | 2017-09-11 09:45 | 50894.9141 | 399.996
Devonshire Building | 2017-09-11 10:00 | 50895.5141 | 2400.012
Devonshire Building | 2017-09-11 10:15 | 50895.5641 | 200.016
Devonshire Building | 2017-09-11 10:30 | 50895.6141 | 200.016
Devonshire Building | 2017-09-11 10:45 | 50895.6641 | 200.016
Devonshire Building | 2017-09-11 11:00 | 50896.0241 | 1440
Devonshire Building | 2017-09-11 11:15 | 50896.2791 | 1019.988
Devonshire Building | 2017-09-11 11:30 | 50896.3191 | 159.984
Devonshire Building | 2017-09-11 11:45 | 50896.3641 | 180
Devonshire Building | 2017-09-11 12:00 | 50896.4091 | 180
Devonshire Building | 2017-09-11 12:15 | 50896.4491 | 159.984
Devonshire Building | 2017-09-11 12:30 | 50897.0041 | 2220.012
Devonshire Building | 2017-09-11 12:45 | 50897.0391 | 140.004
Devonshire Building | 2017-09-11 13:00 | 50897.0791 | 159.984
Devonshire Building | 2017-09-11 13:15 | 50897.1191 | 159.984
Devonshire Building | 2017-09-11 13:30 | 50897.1491 | 119.988
Devonshire Building | 2017-09-11 13:45 | 50897.1841 | 140.004
Devonshire Building | 2017-09-11 14:00 | 50897.2191 | 140.004
Devonshire Building | 2017-09-11 14:15 | 50897.7791 | 2239.992
Devonshire Building | 2017-09-11 14:30 | 50897.8041 | 100.008
Devonshire Building | 2017-09-11 14:45 | 50897.8841 | 320.004
Devonshire Building | 2017-09-11 15:00 | 50897.9091 | 100.008
Devonshire Building | 2017-09-11 15:15 | 50897.9341 | 100.008
Devonshire Building | 2017-09-11 15:30 | 50897.9591 | 100.008
Devonshire Building | 2017-09-11 15:45 | 50897.9791 | 79.992
Devonshire Building | 2017-09-11 16:00 | 50898.5491 | 2279.988
Devonshire Building | 2017-09-11 16:15 | 50898.5741 | 100.008
Devonshire Building | 2017-09-11 16:30 | 50898.5941 | 79.992
Devonshire Building | 2017-09-11 16:45 | 50898.6241 | 119.988
Devonshire Building | 2017-09-11 17:00 | 50898.6441 | 79.992
Devonshire Building | 2017-09-11 17:15 | 50898.6691 | 100.008
Devonshire Building | 2017-09-11 17:30 | 50898.6941 | 100.008
Devonshire Building | 2017-09-11 17:45 | 50898.7141 | 79.992
Devonshire Building | 2017-09-11 18:00 | 50898.7391 | 100.008
Devonshire Building | 2017-09-11 18:15 | 50898.7591 | 79.992
Devonshire Building | 2017-09-11 18:30 | 50898.7841 | 100.008
Devonshire Building | 2017-09-11 18:45 | 50898.8041 | 79.992
Devonshire Building | 2017-09-11 19:00 | 50898.8241 | 79.992
Devonshire Building | 2017-09-11 19:15 | 50898.8441 | 79.992
Devonshire Building | 2017-09-11 19:30 | 50899.3691 | 2099.988
Devonshire Building | 2017-09-11 19:45 | 50899.3891 | 79.992
Devonshire Building | 2017-09-11 20:00 | 50899.4141 | 100.008
Devonshire Building | 2017-09-11 20:15 | 50899.4341 | 79.992
Devonshire Building | 2017-09-11 20:30 | 50899.4541 | 79.992
Devonshire Building | 2017-09-11 20:45 | 50899.4791 | 100.008
Devonshire Building | 2017-09-11 21:00 | 50899.4991 | 79.992
Devonshire Building | 2017-09-11 21:15 | 50899.5191 | 79.992
Devonshire Building | 2017-09-11 21:30 | 50899.539 | 79.992
Devonshire Building | 2017-09-11 21:45 | 50899.559 | 79.992
Devonshire Building | 2017-09-11 22:00 | 50899.579 | 79.992
Devonshire Building | 2017-09-11 22:15 | 50899.594 | 60.012
Devonshire Building | 2017-09-11 22:30 | 50899.614 | 79.992
Devonshire Building | 2017-09-11 22:45 | 50899.634 | 79.992
Devonshire Building | 2017-09-11 23:00 | 50899.654 | 79.992
Devonshire Building | 2017-09-11 23:15 | 50899.669 | 60.012
Devonshire Building | 2017-09-11 23:30 | 50899.684 | 60.012
Devonshire Building | 2017-09-11 23:45 | 50899.704 | 79.992
Devonshire Building | 2017-09-12 | 50899.7188 | 60.012
Devonshire Building | 2017-09-12 00:15 | 50899.7338 | 60.012
Devonshire Building | 2017-09-12 00:30 | 50899.7488 | 60.012
Devonshire Building | 2017-09-12 00:45 | 50899.7638 | 60.012
Devonshire Building | 2017-09-12 01:00 | 50899.7788 | 60.012
Devonshire Building | 2017-09-12 01:15 | 50899.7938 | 60.012
Devonshire Building | 2017-09-12 01:30 | 50899.8138 | 79.992
Devonshire Building | 2017-09-12 01:45 | 50899.8288 | 60.012
Devonshire Building | 2017-09-12 02:00 | 50899.8388 | 39.996
Devonshire Building | 2017-09-12 02:15 | 50899.8538 | 60.012
Devonshire Building | 2017-09-12 02:30 | 50899.8688 | 60.012
Devonshire Building | 2017-09-12 02:45 | 50899.8838 | 60.012
Devonshire Building | 2017-09-12 03:00 | 50899.8988 | 60.012
Devonshire Building | 2017-09-12 03:15 | 50899.9138 | 60.012
Devonshire Building | 2017-09-12 03:30 | 50899.9238 | 39.996
Devonshire Building | 2017-09-12 03:45 | 50899.9388 | 60.012
Devonshire Building | 2017-09-12 04:00 | 50899.9538 | 60.012
Devonshire Building | 2017-09-12 04:15 | 50899.9638 | 39.996
Devonshire Building | 2017-09-12 04:30 | 50899.9788 | 60.012
Devonshire Building | 2017-09-12 04:45 | 50899.9938 | 60.012
Devonshire Building | 2017-09-12 05:00 | 50900.0038 | 39.996
Devonshire Building | 2017-09-12 05:15 | 50900.5288 | 2099.988
Devonshire Building | 2017-09-12 05:30 | 50900.5338 | 20.016
Devonshire Building | 2017-09-12 05:45 | 50900.5438 | 39.996
Devonshire Building | 2017-09-12 06:00 | 50900.5538 | 39.996
Devonshire Building | 2017-09-12 06:15 | 50900.5588 | 20.016
Devonshire Building | 2017-09-12 06:30 | 50900.5688 | 39.996
Devonshire Building | 2017-09-12 06:45 | 50900.5788 | 39.996
Devonshire Building | 2017-09-12 07:00 | 50900.5838 | 20.016
Devonshire Building | 2017-09-12 07:15 | 50900.6038 | 79.992
Devonshire Building | 2017-09-12 07:30 | 50900.6188 | 60.012
Devonshire Building | 2017-09-12 07:45 | 50900.6438 | 100.008
Devonshire Building | 2017-09-12 08:00 | 50900.6888 | 180
Devonshire Building | 2017-09-12 08:15 | 50900.7138 | 100.008
Devonshire Building | 2017-09-12 08:30 | 50900.9388 | 900
Devonshire Building | 2017-09-12 08:45 | 50901.3088 | 1479.996
Devonshire Building | 2017-09-12 09:00 | 50901.3488 | 159.984
Devonshire Building | 2017-09-12 09:15 | 50901.3938 | 180
Devonshire Building | 2017-09-12 09:30 | 50901.4488 | 219.996
Devonshire Building | 2017-09-12 09:45 | 50902.1288 | 2720.016
Devonshire Building | 2017-09-12 10:00 | 50902.2388 | 439.992
Devonshire Building | 2017-09-12 10:15 | 50902.3338 | 380.016
Devonshire Building | 2017-09-12 10:30 | 50902.4088 | 299.988
Devonshire Building | 2017-09-12 10:45 | 50902.4688 | 240.012
Devonshire Building | 2017-09-12 11:00 | 50903.0838 | 2459.988
Devonshire Building | 2017-09-12 11:15 | 50903.1288 | 180
Devonshire Building | 2017-09-12 11:30 | 50903.1688 | 159.984
Devonshire Building | 2017-09-12 11:45 | 50903.2088 | 159.984
Devonshire Building | 2017-09-12 12:00 | 50903.6788 | 1879.992
Devonshire Building | 2017-09-12 12:15 | 50903.8938 | 860.004
Devonshire Building | 2017-09-12 12:30 | 50903.9338 | 159.984
Devonshire Building | 2017-09-12 12:45 | 50903.9738 | 159.984
Devonshire Building | 2017-09-12 13:00 | 50904.0138 | 159.984
Devonshire Building | 2017-09-12 13:15 | 50904.6188 | 2419.992
Devonshire Building | 2017-09-12 13:30 | 50904.6588 | 159.984
Devonshire Building | 2017-09-12 13:45 | 50904.7038 | 180
Devonshire Building | 2017-09-12 14:00 | 50904.7488 | 180
Devonshire Building | 2017-09-12 14:15 | 50904.7938 | 180
Devonshire Building | 2017-09-12 14:30 | 50904.8638 | 280.008
Devonshire Building | 2017-09-12 14:45 | 50904.9338 | 280.008
Devonshire Building | 2017-09-12 15:00 | 50905.5288 | 2379.996
Devonshire Building | 2017-09-12 15:15 | 50905.6088 | 320.004
Devonshire Building | 2017-09-12 15:30 | 50905.6788 | 280.008
Devonshire Building | 2017-09-12 15:45 | 50905.7588 | 320.004
Devonshire Building | 2017-09-12 16:00 | 50905.8238 | 259.992
Devonshire Building | 2017-09-12 16:15 | 50906.4088 | 2340
Devonshire Building | 2017-09-12 16:30 | 50906.4588 | 200.016
Devonshire Building | 2017-09-12 16:45 | 50906.5088 | 200.016
Devonshire Building | 2017-09-12 17:00 | 50906.5538 | 180
Devonshire Building | 2017-09-12 17:15 | 50906.5938 | 159.984
Devonshire Building | 2017-09-12 17:30 | 50906.6288 | 140.004
Devonshire Building | 2017-09-12 17:45 | 50906.6588 | 119.988
Devonshire Building | 2017-09-12 18:00 | 50906.6888 | 119.988
Devonshire Building | 2017-09-12 18:15 | 50906.7138 | 100.008
Devonshire Building | 2017-09-12 18:30 | 50906.7338 | 79.992
Devonshire Building | 2017-09-12 18:45 | 50906.7588 | 100.008
Devonshire Building | 2017-09-12 19:00 | 50906.7788 | 79.992
Devonshire Building | 2017-09-12 19:15 | 50906.7988 | 79.992
Devonshire Building | 2017-09-12 19:30 | 50906.8138 | 60.012
Devonshire Building | 2017-09-12 19:45 | 50906.8338 | 79.992
Devonshire Building | 2017-09-12 20:00 | 50906.8488 | 60.012
Devonshire Building | 2017-09-12 20:15 | 50906.8638 | 60.012
Devonshire Building | 2017-09-12 20:30 | 50907.0838 | 879.984
Devonshire Building | 2017-09-12 20:45 | 50907.4038 | 1280.016
Devonshire Building | 2017-09-12 21:00 | 50907.4088 | 20.016
Devonshire Building | 2017-09-12 21:15 | 50907.4188 | 39.996
Devonshire Building | 2017-09-12 21:30 | 50907.4238 | 20.016
Devonshire Building | 2017-09-12 21:45 | 50907.4338 | 39.996
Devonshire Building | 2017-09-12 22:00 | 50907.4438 | 39.996
Devonshire Building | 2017-09-12 22:15 | 50907.4488 | 20.016
Devonshire Building | 2017-09-12 22:30 | 50907.4588 | 39.996
Devonshire Building | 2017-09-12 22:45 | 50907.4638 | 20.016
Devonshire Building | 2017-09-12 23:00 | 50907.4738 | 39.996
Devonshire Building | 2017-09-12 23:15 | 50907.4788 | 20.016
Devonshire Building | 2017-09-12 23:30 | 50907.4888 | 39.996
Devonshire Building | 2017-09-12 23:45 | 50907.4938 | 20.016
Devonshire Building | 2017-09-13 | 50907.5039 | 39.996
Devonshire Building | 2017-09-13 00:15 | 50907.5139 | 39.996
Devonshire Building | 2017-09-13 00:30 | 50907.5189 | 20.016
Devonshire Building | 2017-09-13 00:45 | 50907.5289 | 39.996
Devonshire Building | 2017-09-13 01:00 | 50907.5389 | 39.996
Devonshire Building | 2017-09-13 01:15 | 50907.5439 | 20.016
Devonshire Building | 2017-09-13 01:30 | 50907.5539 | 39.996
Devonshire Building | 2017-09-13 01:45 | 50907.5639 | 39.996
Devonshire Building | 2017-09-13 02:00 | 50907.5689 | 20.016
Devonshire Building | 2017-09-13 02:15 | 50907.5789 | 39.996
Devonshire Building | 2017-09-13 02:30 | 50907.5889 | 39.996
Devonshire Building | 2017-09-13 02:45 | 50907.5939 | 20.016
Devonshire Building | 2017-09-13 03:00 | 50907.6039 | 39.996
Devonshire Building | 2017-09-13 03:15 | 50907.6089 | 20.016
Devonshire Building | 2017-09-13 03:30 | 50907.6189 | 39.996
Devonshire Building | 2017-09-13 03:45 | 50907.6289 | 39.996
Devonshire Building | 2017-09-13 04:00 | 50907.6339 | 20.016
Devonshire Building | 2017-09-13 04:15 | 50907.6439 | 39.996
Devonshire Building | 2017-09-13 04:30 | 50907.6489 | 20.016
Devonshire Building | 2017-09-13 04:45 | 50907.6589 | 39.996
Devonshire Building | 2017-09-13 05:00 | 50907.6639 | 20.016
Devonshire Building | 2017-09-13 05:15 | 50907.6739 | 39.996
Devonshire Building | 2017-09-13 05:30 | 50907.6839 | 39.996
Devonshire Building | 2017-09-13 05:45 | 50907.6939 | 39.996
Devonshire Building | 2017-09-13 06:00 | 50908.2039 | 2040.012
Devonshire Building | 2017-09-13 06:15 | 50908.2139 | 39.996
Devonshire Building | 2017-09-13 06:30 | 50908.2239 | 39.996
Devonshire Building | 2017-09-13 06:45 | 50908.2289 | 20.016
Devonshire Building | 2017-09-13 07:00 | 50908.2439 | 60.012
Devonshire Building | 2017-09-13 07:15 | 50908.2639 | 79.992
Devonshire Building | 2017-09-13 07:30 | 50908.2789 | 60.012
Devonshire Building | 2017-09-13 07:45 | 50908.3189 | 159.984
Devonshire Building | 2017-09-13 08:00 | 50908.3989 | 320.004
Devonshire Building | 2017-09-13 08:15 | 50908.4939 | 380.016
Devonshire Building | 2017-09-13 08:30 | 50909.1089 | 2459.988
Devonshire Building | 2017-09-13 08:45 | 50909.1939 | 339.984
Devonshire Building | 2017-09-13 09:00 | 50909.2839 | 360
Devonshire Building | 2017-09-13 09:15 | 50909.3639 | 320.004
Devonshire Building | 2017-09-13 09:30 | 50909.4339 | 280.008
Devonshire Building | 2017-09-13 09:45 | 50909.5039 | 280.008
Devonshire Building | 2017-09-13 10:00 | 50910.1739 | 2679.984
Devonshire Building | 2017-09-13 10:15 | 50910.2189 | 180
Devonshire Building | 2017-09-13 10:30 | 50910.2539 | 140.004
Devonshire Building | 2017-09-13 10:45 | 50910.2889 | 140.004
Devonshire Building | 2017-09-13 11:00 | 50910.8939 | 2419.992
Devonshire Building | 2017-09-13 11:15 | 50910.9389 | 180
Devonshire Building | 2017-09-13 11:30 | 50911.0039 | 259.992
Devonshire Building | 2017-09-13 11:45 | 50911.0689 | 259.992
Devonshire Building | 2017-09-13 12:00 | 50911.1289 | 240.012
Devonshire Building | 2017-09-13 12:15 | 50911.7189 | 2360.016
Devonshire Building | 2017-09-13 12:30 | 50911.7789 | 240.012
Devonshire Building | 2017-09-13 12:45 | 50911.8389 | 240.012
Devonshire Building | 2017-09-13 13:00 | 50911.8989 | 240.012
Devonshire Building | 2017-09-13 13:15 | 50911.9539 | 219.996
Devonshire Building | 2017-09-13 13:30 | 50912.3589 | 1620
Devonshire Building | 2017-09-13 13:45 | 50912.5739 | 860.004
Devonshire Building | 2017-09-13 14:00 | 50912.6189 | 180
Devonshire Building | 2017-09-13 14:15 | 50912.6589 | 159.984
Devonshire Building | 2017-09-13 14:30 | 50912.7039 | 180
Devonshire Building | 2017-09-13 14:45 | 50912.7439 | 159.984
Devonshire Building | 2017-09-13 15:00 | 50912.7889 | 180
Devonshire Building | 2017-09-13 15:15 | 50913.3989 | 2440.008
Devonshire Building | 2017-09-13 15:30 | 50913.4289 | 119.988
Devonshire Building | 2017-09-13 15:45 | 50913.4639 | 140.004
Devonshire Building | 2017-09-13 16:00 | 50913.4989 | 140.004
Devonshire Building | 2017-09-13 16:15 | 50913.5289 | 119.988
Devonshire Building | 2017-09-13 16:30 | 50913.5639 | 140.004
Devonshire Building | 2017-09-13 16:45 | 50913.6189 | 219.996
Devonshire Building | 2017-09-13 17:00 | 50913.6689 | 200.016
Devonshire Building | 2017-09-13 17:15 | 50913.7239 | 219.996
Devonshire Building | 2017-09-13 17:30 | 50914.2839 | 2239.992
Devonshire Building | 2017-09-13 17:45 | 50914.3389 | 219.996
Devonshire Building | 2017-09-13 18:00 | 50914.3939 | 219.996
Devonshire Building | 2017-09-13 18:15 | 50914.4539 | 240.012
Devonshire Building | 2017-09-13 18:30 | 50914.5039 | 200.016
Devonshire Building | 2017-09-13 18:45 | 50914.5489 | 180
Devonshire Building | 2017-09-13 19:00 | 50914.5839 | 140.004
Devonshire Building | 2017-09-13 19:15 | 50914.6139 | 119.988
Devonshire Building | 2017-09-13 19:30 | 50914.6439 | 119.988
Devonshire Building | 2017-09-13 19:45 | 50914.6689 | 100.008
Devonshire Building | 2017-09-13 20:00 | 50914.6939 | 100.008
Devonshire Building | 2017-09-13 20:15 | 50914.7139 | 79.992
Devonshire Building | 2017-09-13 20:30 | 50914.7389 | 100.008
Devonshire Building | 2017-09-13 20:45 | 50914.7689 | 119.988
Devonshire Building | 2017-09-13 21:00 | 50914.7789 | 39.996
Devonshire Building | 2017-09-13 21:15 | 50914.7939 | 60.012
Devonshire Building | 2017-09-13 21:30 | 50914.8039 | 39.996
Devonshire Building | 2017-09-13 21:45 | 50914.8139 | 39.996
Devonshire Building | 2017-09-13 22:00 | 50914.8239 | 39.996
Devonshire Building | 2017-09-13 22:15 | 50914.8339 | 39.996
Devonshire Building | 2017-09-13 22:30 | 50914.8439 | 39.996
Devonshire Building | 2017-09-13 22:45 | 50914.8589 | 60.012
Devonshire Building | 2017-09-13 23:00 | 50914.8689 | 39.996
Devonshire Building | 2017-09-13 23:15 | 50914.8789 | 39.996
Devonshire Building | 2017-09-13 23:30 | 50914.8889 | 39.996
Devonshire Building | 2017-09-13 23:45 | 50914.8989 | 39.996
Devonshire Building | 2017-09-14 | 50914.9102 | 39.996
Devonshire Building | 2017-09-14 00:15 | 50914.9202 | 39.996
Devonshire Building | 2017-09-14 00:30 | 50914.9302 | 39.996
Devonshire Building | 2017-09-14 00:45 | 50914.9402 | 39.996
Devonshire Building | 2017-09-14 01:00 | 50914.9502 | 39.996
Devonshire Building | 2017-09-14 01:15 | 50914.9602 | 39.996
Devonshire Building | 2017-09-14 01:30 | 50914.9702 | 39.996
Devonshire Building | 2017-09-14 01:45 | 50915.4952 | 2099.988
Devonshire Building | 2017-09-14 02:00 | 50915.5051 | 39.996
Devonshire Building | 2017-09-14 02:15 | 50915.5151 | 39.996
Devonshire Building | 2017-09-14 02:30 | 50915.5251 | 39.996
Devonshire Building | 2017-09-14 02:45 | 50915.5351 | 39.996
Devonshire Building | 2017-09-14 03:00 | 50915.5451 | 39.996
Devonshire Building | 2017-09-14 03:15 | 50915.5551 | 39.996
Devonshire Building | 2017-09-14 03:30 | 50915.5651 | 39.996
Devonshire Building | 2017-09-14 03:45 | 50915.5751 | 39.996
Devonshire Building | 2017-09-14 04:00 | 50915.5851 | 39.996
Devonshire Building | 2017-09-14 04:15 | 50915.5951 | 39.996
Devonshire Building | 2017-09-14 04:30 | 50915.6051 | 39.996
Devonshire Building | 2017-09-14 04:45 | 50915.6151 | 39.996
Devonshire Building | 2017-09-14 05:00 | 50915.6251 | 39.996
Devonshire Building | 2017-09-14 05:15 | 50915.6401 | 60.012
Devonshire Building | 2017-09-14 05:30 | 50915.6501 | 39.996
Devonshire Building | 2017-09-14 05:45 | 50915.6601 | 39.996
Devonshire Building | 2017-09-14 06:00 | 50915.6701 | 39.996
Devonshire Building | 2017-09-14 06:15 | 50915.6801 | 39.996
Devonshire Building | 2017-09-14 06:30 | 50915.6901 | 39.996
Devonshire Building | 2017-09-14 06:45 | 50915.7051 | 60.012
Devonshire Building | 2017-09-14 07:00 | 50915.7151 | 39.996
Devonshire Building | 2017-09-14 07:15 | 50915.7351 | 79.992
Devonshire Building | 2017-09-14 07:30 | 50915.7551 | 79.992
Devonshire Building | 2017-09-14 07:45 | 50916.2701 | 2059.992
Devonshire Building | 2017-09-14 08:00 | 50916.3151 | 180
Devonshire Building | 2017-09-14 08:15 | 50916.3501 | 140.004
Devonshire Building | 2017-09-14 08:30 | 50916.3851 | 140.004
Devonshire Building | 2017-09-14 08:45 | 50916.4151 | 119.988
Devonshire Building | 2017-09-14 09:00 | 50916.4451 | 119.988
Devonshire Building | 2017-09-14 09:15 | 50916.8151 | 1479.996
Devonshire Building | 2017-09-14 09:30 | 50917.0301 | 860.004
Devonshire Building | 2017-09-14 09:45 | 50917.0701 | 159.984
Devonshire Building | 2017-09-14 10:00 | 50917.1401 | 280.008
Devonshire Building | 2017-09-14 10:15 | 50917.2301 | 360
Devonshire Building | 2017-09-14 10:30 | 50917.7101 | 1919.988
Devonshire Building | 2017-09-14 10:45 | 50917.9451 | 939.996
Devonshire Building | 2017-09-14 11:00 | 50918.0451 | 399.996
Devonshire Building | 2017-09-14 11:15 | 50918.1401 | 380.016
Devonshire Building | 2017-09-14 11:30 | 50918.2301 | 360
Devonshire Building | 2017-09-14 11:45 | 50918.3101 | 320.004
Devonshire Building | 2017-09-14 12:00 | 50918.3801 | 280.008
Devonshire Building | 2017-09-14 12:15 | 50918.9801 | 2400.012
Devonshire Building | 2017-09-14 12:30 | 50919.0301 | 200.016
Devonshire Building | 2017-09-14 12:45 | 50919.0751 | 180
Devonshire Building | 2017-09-14 13:00 | 50919.1151 | 159.984
Devonshire Building | 2017-09-14 13:15 | 50919.1551 | 159.984
Devonshire Building | 2017-09-14 13:30 | 50919.1951 | 159.984
Devonshire Building | 2017-09-14 13:45 | 50919.7951 | 2400.012
Devonshire Building | 2017-09-14 14:00 | 50919.8451 | 200.016
Devonshire Building | 2017-09-14 14:15 | 50919.8951 | 200.016
Devonshire Building | 2017-09-14 14:30 | 50919.9501 | 219.996
Devonshire Building | 2017-09-14 14:45 | 50920.0001 | 200.016
Devonshire Building | 2017-09-14 15:00 | 50920.0551 | 219.996
Devonshire Building | 2017-09-14 15:15 | 50920.1051 | 200.016
Devonshire Building | 2017-09-14 15:30 | 50920.2451 | 560.016
Devonshire Building | 2017-09-14 15:45 | 50920.7801 | 2139.984
Devonshire Building | 2017-09-14 16:00 | 50920.8251 | 180
Devonshire Building | 2017-09-14 16:15 | 50920.8551 | 119.988
Devonshire Building | 2017-09-14 16:30 | 50920.8901 | 140.004
Devonshire Building | 2017-09-14 16:45 | 50920.9251 | 140.004
Devonshire Building | 2017-09-14 17:00 | 50920.9651 | 159.984
Devonshire Building | 2017-09-14 17:15 | 50921.0051 | 159.984
Devonshire Building | 2017-09-14 17:30 | 50921.0351 | 119.988
Devonshire Building | 2017-09-14 17:45 | 50921.0651 | 119.988
Devonshire Building | 2017-09-14 18:00 | 50921.1001 | 140.004
Devonshire Building | 2017-09-14 18:15 | 50921.1301 | 119.988
Devonshire Building | 2017-09-14 18:30 | 50921.1601 | 119.988
Devonshire Building | 2017-09-14 18:45 | 50921.6151 | 1820.016
Devonshire Building | 2017-09-14 19:00 | 50921.7101 | 380.016
Devonshire Building | 2017-09-14 19:15 | 50921.7301 | 79.992
Devonshire Building | 2017-09-14 19:30 | 50921.7551 | 100.008
Devonshire Building | 2017-09-14 19:45 | 50921.7801 | 100.008
Devonshire Building | 2017-09-14 20:00 | 50921.8051 | 100.008
Devonshire Building | 2017-09-14 20:15 | 50921.8301 | 100.008
Devonshire Building | 2017-09-14 20:30 | 50921.8551 | 100.008
Devonshire Building | 2017-09-14 20:45 | 50921.8851 | 119.988
Devonshire Building | 2017-09-14 21:00 | 50921.9001 | 60.012
Devonshire Building | 2017-09-14 21:15 | 50921.9201 | 79.992
Devonshire Building | 2017-09-14 21:30 | 50921.9351 | 60.012
Devonshire Building | 2017-09-14 21:45 | 50921.9501 | 60.012
Devonshire Building | 2017-09-14 22:00 | 50921.9701 | 79.992
Devonshire Building | 2017-09-14 22:15 | 50921.9851 | 60.012
Devonshire Building | 2017-09-14 22:30 | 50922.0001 | 60.012
Devonshire Building | 2017-09-14 22:45 | 50922.0151 | 60.012
Devonshire Building | 2017-09-14 23:00 | 50922.0301 | 60.012
Devonshire Building | 2017-09-14 23:15 | 50922.0452 | 60.012
Devonshire Building | 2017-09-14 23:30 | 50922.0602 | 60.012
Devonshire Building | 2017-09-14 23:45 | 50922.0752 | 60.012
Devonshire Building | 2017-09-15 | 50922.0898 | 60.012
Devonshire Building | 2017-09-15 00:15 | 50922.1048 | 60.012
Devonshire Building | 2017-09-15 00:30 | 50922.1198 | 60.012
Devonshire Building | 2017-09-15 00:45 | 50922.1348 | 60.012
Devonshire Building | 2017-09-15 01:00 | 50922.1499 | 60.012
Devonshire Building | 2017-09-15 01:15 | 50922.1649 | 60.012
Devonshire Building | 2017-09-15 01:30 | 50922.1749 | 39.996
Devonshire Building | 2017-09-15 01:45 | 50922.1899 | 60.012
Devonshire Building | 2017-09-15 02:00 | 50922.2049 | 60.012
Devonshire Building | 2017-09-15 02:15 | 50922.2199 | 60.012
Devonshire Building | 2017-09-15 02:30 | 50922.2349 | 60.012
Devonshire Building | 2017-09-15 02:45 | 50922.2449 | 39.996
Devonshire Building | 2017-09-15 03:00 | 50922.2599 | 60.012
Devonshire Building | 2017-09-15 03:15 | 50922.2749 | 60.012
Devonshire Building | 2017-09-15 03:30 | 50922.2849 | 39.996
Devonshire Building | 2017-09-15 03:45 | 50922.2999 | 60.012
Devonshire Building | 2017-09-15 04:00 | 50922.6399 | 1360.008
Devonshire Building | 2017-09-15 04:15 | 50922.8199 | 720
Devonshire Building | 2017-09-15 04:30 | 50922.8249 | 20.016
Devonshire Building | 2017-09-15 04:45 | 50922.8349 | 39.996
Devonshire Building | 2017-09-15 05:00 | 50922.8399 | 20.016
Devonshire Building | 2017-09-15 05:15 | 50922.8499 | 39.996
Devonshire Building | 2017-09-15 05:30 | 50922.8599 | 39.996
Devonshire Building | 2017-09-15 05:45 | 50922.8649 | 20.016
Devonshire Building | 2017-09-15 06:00 | 50922.8749 | 39.996
Devonshire Building | 2017-09-15 06:15 | 50922.8849 | 39.996
Devonshire Building | 2017-09-15 06:30 | 50922.8899 | 20.016
Devonshire Building | 2017-09-15 06:45 | 50922.8999 | 39.996
Devonshire Building | 2017-09-15 07:00 | 50922.9099 | 39.996
Devonshire Building | 2017-09-15 07:15 | 50922.9199 | 39.996
Devonshire Building | 2017-09-15 07:30 | 50922.9299 | 39.996
Devonshire Building | 2017-09-15 07:45 | 50922.9399 | 39.996
Devonshire Building | 2017-09-15 08:00 | 50922.9499 | 39.996
Devonshire Building | 2017-09-15 08:15 | 50922.9649 | 60.012
Devonshire Building | 2017-09-15 08:30 | 50923.2699 | 1220.004
Devonshire Building | 2017-09-15 08:45 | 50923.5099 | 960.012
Devonshire Building | 2017-09-15 09:00 | 50923.5299 | 79.992
Devonshire Building | 2017-09-15 09:15 | 50923.5599 | 119.988
Devonshire Building | 2017-09-15 09:30 | 50923.5749 | 60.012
Devonshire Building | 2017-09-15 09:45 | 50923.5949 | 79.992
Devonshire Building | 2017-09-15 10:00 | 50923.6199 | 100.008
Devonshire Building | 2017-09-15 10:15 | 50923.8699 | 1000.008
Devonshire Building | 2017-09-15 10:30 | 50924.2149 | 1379.988
Devonshire Building | 2017-09-15 10:45 | 50924.2549 | 159.984
Devonshire Building | 2017-09-15 11:00 | 50924.2949 | 159.984
Devonshire Building | 2017-09-15 11:15 | 50924.3399 | 180
Devonshire Building | 2017-09-15 11:30 | 50924.3799 | 159.984
Devonshire Building | 2017-09-15 11:45 | 50924.4599 | 320.004
Devonshire Building | 2017-09-15 12:00 | 50925.0399 | 2319.984
Devonshire Building | 2017-09-15 12:15 | 50925.1149 | 299.988
Devonshire Building | 2017-09-15 12:30 | 50925.1849 | 280.008
Devonshire Building | 2017-09-15 12:45 | 50925.2599 | 299.988
Devonshire Building | 2017-09-15 13:00 | 50925.3299 | 280.008
Devonshire Building | 2017-09-15 13:15 | 50925.3949 | 259.992
Devonshire Building | 2017-09-15 13:30 | 50925.4699 | 299.988
Devonshire Building | 2017-09-15 13:45 | 50925.5649 | 380.016
Devonshire Building | 2017-09-15 14:00 | 50925.6599 | 380.016
Devonshire Building | 2017-09-15 14:15 | 50925.7599 | 399.996
Devonshire Building | 2017-09-15 14:30 | 50926.3599 | 2400.012
Devonshire Building | 2017-09-15 14:45 | 50926.4399 | 320.004
Devonshire Building | 2017-09-15 15:00 | 50926.5199 | 320.004
Devonshire Building | 2017-09-15 15:15 | 50926.5949 | 299.988
Devonshire Building | 2017-09-15 15:30 | 50926.6549 | 240.012
Devonshire Building | 2017-09-15 15:45 | 50926.7099 | 219.996
Devonshire Building | 2017-09-15 16:00 | 50926.7549 | 180
Devonshire Building | 2017-09-15 16:15 | 50926.7849 | 119.988
Devonshire Building | 2017-09-15 16:30 | 50926.8149 | 119.988
Devonshire Building | 2017-09-15 16:45 | 50926.8449 | 119.988
Devonshire Building | 2017-09-15 17:00 | 50926.8699 | 100.008
Devonshire Building | 2017-09-15 17:15 | 50927.3899 | 2080.008
Devonshire Building | 2017-09-15 17:30 | 50927.4049 | 60.012
Devonshire Building | 2017-09-15 17:45 | 50927.4149 | 39.996
Devonshire Building | 2017-09-15 18:00 | 50927.4249 | 39.996
Devonshire Building | 2017-09-15 18:15 | 50927.4399 | 60.012
Devonshire Building | 2017-09-15 18:30 | 50927.4499 | 39.996
Devonshire Building | 2017-09-15 18:45 | 50927.4649 | 60.012
Devonshire Building | 2017-09-15 19:00 | 50927.4749 | 39.996
Devonshire Building | 2017-09-15 19:15 | 50927.4899 | 60.012
Devonshire Building | 2017-09-15 19:30 | 50927.4999 | 39.996
Devonshire Building | 2017-09-15 19:45 | 50927.5149 | 60.012
Devonshire Building | 2017-09-15 20:00 | 50927.5249 | 39.996
Devonshire Building | 2017-09-15 20:15 | 50927.5399 | 60.012
Devonshire Building | 2017-09-15 20:30 | 50927.5499 | 39.996
Devonshire Building | 2017-09-15 20:45 | 50927.5799 | 119.988
Devonshire Building | 2017-09-15 21:00 | 50927.5899 | 39.996
Devonshire Building | 2017-09-15 21:15 | 50927.5999 | 39.996
Devonshire Building | 2017-09-15 21:30 | 50927.6099 | 39.996
Devonshire Building | 2017-09-15 21:45 | 50927.6199 | 39.996
Devonshire Building | 2017-09-15 22:00 | 50927.6299 | 39.996
Devonshire Building | 2017-09-15 22:15 | 50927.6449 | 60.012
Devonshire Building | 2017-09-15 22:30 | 50927.6549 | 39.996
Devonshire Building | 2017-09-15 22:45 | 50927.6649 | 39.996
Devonshire Building | 2017-09-15 23:00 | 50927.6749 | 39.996
Devonshire Building | 2017-09-15 23:15 | 50927.6849 | 39.996
Devonshire Building | 2017-09-15 23:30 | 50927.6949 | 39.996
Devonshire Building | 2017-09-15 23:45 | 50927.7049 | 39.996
Devonshire Building | 2017-09-16 | 50927.7148 | 39.996
Devonshire Building | 2017-09-16 00:15 | 50927.7198 | 20.016
Devonshire Building | 2017-09-16 00:30 | 50927.7298 | 39.996
Devonshire Building | 2017-09-16 00:45 | 50927.7398 | 39.996
Devonshire Building | 2017-09-16 01:00 | 50927.7498 | 39.996
Devonshire Building | 2017-09-16 01:15 | 50927.7598 | 39.996
Devonshire Building | 2017-09-16 01:30 | 50927.7698 | 39.996
Devonshire Building | 2017-09-16 01:45 | 50927.7798 | 39.996
Devonshire Building | 2017-09-16 02:00 | 50927.7898 | 39.996
Devonshire Building | 2017-09-16 02:15 | 50928.2098 | 1680.012
Devonshire Building | 2017-09-16 02:30 | 50928.3098 | 399.996
Devonshire Building | 2017-09-16 02:45 | 50928.3198 | 39.996
Devonshire Building | 2017-09-16 03:00 | 50928.3298 | 39.996
Devonshire Building | 2017-09-16 03:15 | 50928.3398 | 39.996
Devonshire Building | 2017-09-16 03:30 | 50928.3498 | 39.996
Devonshire Building | 2017-09-16 03:45 | 50928.3548 | 20.016
Devonshire Building | 2017-09-16 04:00 | 50928.3648 | 39.996
Devonshire Building | 2017-09-16 04:15 | 50928.3748 | 39.996
Devonshire Building | 2017-09-16 04:30 | 50928.3848 | 39.996
Devonshire Building | 2017-09-16 04:45 | 50928.3948 | 39.996
Devonshire Building | 2017-09-16 05:00 | 50928.4048 | 39.996
Devonshire Building | 2017-09-16 05:15 | 50928.4148 | 39.996
Devonshire Building | 2017-09-16 05:30 | 50928.4298 | 60.012
Devonshire Building | 2017-09-16 05:45 | 50928.4398 | 39.996
Devonshire Building | 2017-09-16 06:00 | 50928.4498 | 39.996
Devonshire Building | 2017-09-16 06:15 | 50928.4648 | 60.012
Devonshire Building | 2017-09-16 06:30 | 50928.4748 | 39.996
Devonshire Building | 2017-09-16 06:45 | 50928.4848 | 39.996
Devonshire Building | 2017-09-16 07:00 | 50928.4998 | 60.012
Devonshire Building | 2017-09-16 07:15 | 50928.5098 | 39.996
Devonshire Building | 2017-09-16 07:30 | 50928.5248 | 60.012
Devonshire Building | 2017-09-16 07:45 | 50928.5348 | 39.996
Devonshire Building | 2017-09-16 08:00 | 50928.5448 | 39.996
Devonshire Building | 2017-09-16 08:15 | 50928.5548 | 39.996
Devonshire Building | 2017-09-16 08:30 | 50928.5648 | 39.996
Devonshire Building | 2017-09-16 08:45 | 50928.5748 | 39.996
Devonshire Building | 2017-09-16 09:00 | 50928.5848 | 39.996
Devonshire Building | 2017-09-16 09:15 | 50928.5948 | 39.996
Devonshire Building | 2017-09-16 09:30 | 50928.6098 | 60.012
Devonshire Building | 2017-09-16 09:45 | 50928.6198 | 39.996
Devonshire Building | 2017-09-16 10:00 | 50928.6298 | 39.996
Devonshire Building | 2017-09-16 10:15 | 50928.6398 | 39.996
Devonshire Building | 2017-09-16 10:30 | 50929.0398 | 1599.984
Devonshire Building | 2017-09-16 10:45 | 50929.1598 | 479.988
Devonshire Building | 2017-09-16 11:00 | 50929.1698 | 39.996
Devonshire Building | 2017-09-16 11:15 | 50929.1848 | 60.012
Devonshire Building | 2017-09-16 11:30 | 50929.1948 | 39.996
Devonshire Building | 2017-09-16 11:45 | 50929.2098 | 60.012
Devonshire Building | 2017-09-16 12:00 | 50929.2198 | 39.996
Devonshire Building | 2017-09-16 12:15 | 50929.2298 | 39.996
Devonshire Building | 2017-09-16 12:30 | 50929.2448 | 60.012
Devonshire Building | 2017-09-16 12:45 | 50929.2548 | 39.996
Devonshire Building | 2017-09-16 13:00 | 50929.2698 | 60.012
Devonshire Building | 2017-09-16 13:15 | 50929.2848 | 60.012
Devonshire Building | 2017-09-16 13:30 | 50929.2998 | 60.012
Devonshire Building | 2017-09-16 13:45 | 50929.3348 | 140.004
Devonshire Building | 2017-09-16 14:00 | 50929.3648 | 119.988
Devonshire Building | 2017-09-16 14:15 | 50929.3948 | 119.988
Devonshire Building | 2017-09-16 14:30 | 50929.4248 | 119.988
Devonshire Building | 2017-09-16 14:45 | 50929.4548 | 119.988
Devonshire Building | 2017-09-16 15:00 | 50929.4848 | 119.988
Devonshire Building | 2017-09-16 15:15 | 50929.5098 | 100.008
Devonshire Building | 2017-09-16 15:30 | 50929.5398 | 119.988
Devonshire Building | 2017-09-16 15:45 | 50929.5698 | 119.988
Devonshire Building | 2017-09-16 16:00 | 50929.5898 | 79.992
Devonshire Building | 2017-09-16 16:15 | 50930.1048 | 2059.992
Devonshire Building | 2017-09-16 16:30 | 50930.1198 | 60.012
Devonshire Building | 2017-09-16 16:45 | 50930.1298 | 39.996
Devonshire Building | 2017-09-16 17:00 | 50930.1448 | 60.012
Devonshire Building | 2017-09-16 17:15 | 50930.1548 | 39.996
Devonshire Building | 2017-09-16 17:30 | 50930.1698 | 60.012
Devonshire Building | 2017-09-16 17:45 | 50930.1798 | 39.996
Devonshire Building | 2017-09-16 18:00 | 50930.1948 | 60.012
Devonshire Building | 2017-09-16 18:15 | 50930.2048 | 39.996
Devonshire Building | 2017-09-16 18:30 | 50930.2198 | 60.012
Devonshire Building | 2017-09-16 18:45 | 50930.2348 | 60.012
Devonshire Building | 2017-09-16 19:00 | 50930.2498 | 60.012
Devonshire Building | 2017-09-16 19:15 | 50930.2648 | 60.012
Devonshire Building | 2017-09-16 19:30 | 50930.2798 | 60.012
Devonshire Building | 2017-09-16 19:45 | 50930.2948 | 60.012
Devonshire Building | 2017-09-16 20:00 | 50930.3048 | 39.996
Devonshire Building | 2017-09-16 20:15 | 50930.3198 | 60.012
Devonshire Building | 2017-09-16 20:30 | 50930.3348 | 60.012
Devonshire Building | 2017-09-16 20:45 | 50930.3648 | 119.988
Devonshire Building | 2017-09-16 21:00 | 50930.3798 | 60.012
Devonshire Building | 2017-09-16 21:15 | 50930.3949 | 60.012
Devonshire Building | 2017-09-16 21:30 | 50930.4048 | 39.996
Devonshire Building | 2017-09-16 21:45 | 50930.4199 | 60.012
Devonshire Building | 2017-09-16 22:00 | 50930.4299 | 39.996
Devonshire Building | 2017-09-16 22:15 | 50930.4449 | 60.012
Devonshire Building | 2017-09-16 22:30 | 50930.4599 | 60.012
Devonshire Building | 2017-09-16 22:45 | 50930.4699 | 39.996
Devonshire Building | 2017-09-16 23:00 | 50930.4799 | 39.996
Devonshire Building | 2017-09-16 23:15 | 50930.4949 | 60.012
Devonshire Building | 2017-09-16 23:30 | 50930.5049 | 39.996
Devonshire Building | 2017-09-16 23:45 | 50930.5199 | 60.012
Devonshire Building | 2017-09-17 | 50930.5312 | 39.996
Devonshire Building | 2017-09-17 00:15 | 50930.5412 | 39.996
Devonshire Building | 2017-09-17 00:30 | 50930.5512 | 39.996
Devonshire Building | 2017-09-17 00:45 | 50930.5663 | 60.012
Devonshire Building | 2017-09-17 01:00 | 50930.5762 | 39.996
Devonshire Building | 2017-09-17 01:15 | 50930.5862 | 39.996
Devonshire Building | 2017-09-17 01:30 | 50930.5962 | 39.996
Devonshire Building | 2017-09-17 01:45 | 50930.6113 | 60.012
Devonshire Building | 2017-09-17 02:00 | 50930.6212 | 39.996
Devonshire Building | 2017-09-17 02:15 | 50931.1262 | 2019.996
Devonshire Building | 2017-09-17 02:30 | 50931.1413 | 60.012
Devonshire Building | 2017-09-17 02:45 | 50931.1513 | 39.996
Devonshire Building | 2017-09-17 03:00 | 50931.1612 | 39.996
Devonshire Building | 2017-09-17 03:15 | 50931.1712 | 39.996
Devonshire Building | 2017-09-17 03:30 | 50931.1812 | 39.996
Devonshire Building | 2017-09-17 03:45 | 50931.1912 | 39.996
Devonshire Building | 2017-09-17 04:00 | 50931.2063 | 60.012
Devonshire Building | 2017-09-17 04:15 | 50931.2162 | 39.996
Devonshire Building | 2017-09-17 04:30 | 50931.2313 | 60.012
Devonshire Building | 2017-09-17 04:45 | 50931.2413 | 39.996
Devonshire Building | 2017-09-17 05:00 | 50931.2563 | 60.012
Devonshire Building | 2017-09-17 05:15 | 50931.2713 | 60.012
Devonshire Building | 2017-09-17 05:30 | 50931.2863 | 60.012
Devonshire Building | 2017-09-17 05:45 | 50931.3013 | 60.012
Devonshire Building | 2017-09-17 06:00 | 50931.3113 | 39.996
Devonshire Building | 2017-09-17 06:15 | 50931.3263 | 60.012
Devonshire Building | 2017-09-17 06:30 | 50931.3363 | 39.996
Devonshire Building | 2017-09-17 06:45 | 50931.3513 | 60.012
Devonshire Building | 2017-09-17 07:00 | 50931.3613 | 39.996
Devonshire Building | 2017-09-17 07:15 | 50931.3763 | 60.012
Devonshire Building | 2017-09-17 07:30 | 50931.3863 | 39.996
Devonshire Building | 2017-09-17 07:45 | 50931.4013 | 60.012
Devonshire Building | 2017-09-17 08:00 | 50931.4113 | 39.996
Devonshire Building | 2017-09-17 08:15 | 50931.4213 | 39.996
Devonshire Building | 2017-09-17 08:30 | 50931.4363 | 60.012
Devonshire Building | 2017-09-17 08:45 | 50931.4463 | 39.996
Devonshire Building | 2017-09-17 09:00 | 50931.4563 | 39.996
Devonshire Building | 2017-09-17 09:15 | 50931.4713 | 60.012
Devonshire Building | 2017-09-17 09:30 | 50931.4813 | 39.996
Devonshire Building | 2017-09-17 09:45 | 50931.4913 | 39.996
Devonshire Building | 2017-09-17 10:00 | 50931.5013 | 39.996
Devonshire Building | 2017-09-17 10:15 | 50931.5163 | 60.012
Devonshire Building | 2017-09-17 10:30 | 50931.5263 | 39.996
Devonshire Building | 2017-09-17 10:45 | 50931.5363 | 39.996
Devonshire Building | 2017-09-17 11:00 | 50931.5513 | 60.012
Devonshire Building | 2017-09-17 11:15 | 50931.5613 | 39.996
Devonshire Building | 2017-09-17 11:30 | 50932.0663 | 2019.996
Devonshire Building | 2017-09-17 11:45 | 50932.0763 | 39.996
Devonshire Building | 2017-09-17 12:00 | 50932.0863 | 39.996
Devonshire Building | 2017-09-17 12:15 | 50932.0963 | 39.996
Devonshire Building | 2017-09-17 12:30 | 50932.1063 | 39.996
Devonshire Building | 2017-09-17 12:45 | 50932.1163 | 39.996
Devonshire Building | 2017-09-17 13:00 | 50932.1263 | 39.996
Devonshire Building | 2017-09-17 13:15 | 50932.1363 | 39.996
Devonshire Building | 2017-09-17 13:30 | 50932.1513 | 60.012
Devonshire Building | 2017-09-17 13:45 | 50932.1763 | 100.008
Devonshire Building | 2017-09-17 14:00 | 50932.2063 | 119.988
Devonshire Building | 2017-09-17 14:15 | 50932.2363 | 119.988
Devonshire Building | 2017-09-17 14:30 | 50932.2613 | 100.008
Devonshire Building | 2017-09-17 14:45 | 50932.2913 | 119.988
Devonshire Building | 2017-09-17 15:00 | 50932.3213 | 119.988
Devonshire Building | 2017-09-17 15:15 | 50932.3513 | 119.988
Devonshire Building | 2017-09-17 15:30 | 50932.3813 | 119.988
Devonshire Building | 2017-09-17 15:45 | 50932.4063 | 100.008
Devonshire Building | 2017-09-17 16:00 | 50932.4263 | 79.992
Devonshire Building | 2017-09-17 16:15 | 50932.4413 | 60.012
Devonshire Building | 2017-09-17 16:30 | 50932.4513 | 39.996
Devonshire Building | 2017-09-17 16:45 | 50932.4663 | 60.012
Devonshire Building | 2017-09-17 17:00 | 50932.4763 | 39.996
Devonshire Building | 2017-09-17 17:15 | 50932.4913 | 60.012
Devonshire Building | 2017-09-17 17:30 | 50932.5013 | 39.996
Devonshire Building | 2017-09-17 17:45 | 50932.5113 | 39.996
Devonshire Building | 2017-09-17 18:00 | 50932.5263 | 60.012
Devonshire Building | 2017-09-17 18:15 | 50932.5363 | 39.996
Devonshire Building | 2017-09-17 18:30 | 50932.5463 | 39.996
Devonshire Building | 2017-09-17 18:45 | 50932.5563 | 39.996
Devonshire Building | 2017-09-17 19:00 | 50932.5713 | 60.012
Devonshire Building | 2017-09-17 19:15 | 50932.5813 | 39.996
Devonshire Building | 2017-09-17 19:30 | 50932.5913 | 39.996
Devonshire Building | 2017-09-17 19:45 | 50933.1013 | 2040.012
Devonshire Building | 2017-09-17 20:00 | 50933.1113 | 39.996
Devonshire Building | 2017-09-17 20:15 | 50933.1213 | 39.996
Devonshire Building | 2017-09-17 20:30 | 50933.1363 | 60.012
Devonshire Building | 2017-09-17 20:45 | 50933.1563 | 79.992
Devonshire Building | 2017-09-17 21:00 | 50933.1663 | 39.996
Devonshire Building | 2017-09-17 21:15 | 50933.1763 | 39.996
Devonshire Building | 2017-09-17 21:30 | 50933.1863 | 39.996
Devonshire Building | 2017-09-17 21:45 | 50933.1963 | 39.996
Devonshire Building | 2017-09-17 22:00 | 50933.2113 | 60.012
Devonshire Building | 2017-09-17 22:15 | 50933.2213 | 39.996
Devonshire Building | 2017-09-17 22:30 | 50933.2313 | 39.996
Devonshire Building | 2017-09-17 22:45 | 50933.2463 | 60.012
Devonshire Building | 2017-09-17 23:00 | 50933.2613 | 60.012
Devonshire Building | 2017-09-17 23:15 | 50933.2713 | 39.996
Devonshire Building | 2017-09-17 23:30 | 50933.2863 | 60.012
Devonshire Building | 2017-09-17 23:45 | 50933.2963 | 39.996
Devonshire Building | 2017-09-18 | 50933.3086 | 60.012
Devonshire Building | 2017-09-18 00:15 | 50933.3186 | 39.996
Devonshire Building | 2017-09-18 00:30 | 50933.3286 | 39.996
Devonshire Building | 2017-09-18 00:45 | 50933.3436 | 60.012
Devonshire Building | 2017-09-18 01:00 | 50933.3536 | 39.996
Devonshire Building | 2017-09-18 01:15 | 50933.3636 | 39.996
Devonshire Building | 2017-09-18 01:30 | 50933.3786 | 60.012
Devonshire Building | 2017-09-18 01:45 | 50933.3886 | 39.996
Devonshire Building | 2017-09-18 02:00 | 50933.3986 | 39.996
Devonshire Building | 2017-09-18 02:15 | 50933.4136 | 60.012
Devonshire Building | 2017-09-18 02:30 | 50933.4236 | 39.996
Devonshire Building | 2017-09-18 02:45 | 50933.4336 | 39.996
Devonshire Building | 2017-09-18 03:00 | 50933.4436 | 39.996
Devonshire Building | 2017-09-18 03:15 | 50933.4536 | 39.996
Devonshire Building | 2017-09-18 03:30 | 50933.4686 | 60.012
Devonshire Building | 2017-09-18 03:45 | 50933.4786 | 39.996
Devonshire Building | 2017-09-18 04:00 | 50933.4886 | 39.996
Devonshire Building | 2017-09-18 04:15 | 50933.4986 | 39.996
Devonshire Building | 2017-09-18 04:30 | 50933.5086 | 39.996
Devonshire Building | 2017-09-18 04:45 | 50933.5186 | 39.996
Devonshire Building | 2017-09-18 05:00 | 50933.5336 | 60.012
Devonshire Building | 2017-09-18 05:15 | 50933.5436 | 39.996
Devonshire Building | 2017-09-18 05:30 | 50933.9836 | 1760.004
Devonshire Building | 2017-09-18 05:45 | 50934.0786 | 380.016
Devonshire Building | 2017-09-18 06:00 | 50934.0886 | 39.996
Devonshire Building | 2017-09-18 06:15 | 50934.0986 | 39.996
Devonshire Building | 2017-09-18 06:30 | 50934.1086 | 39.996
Devonshire Building | 2017-09-18 06:45 | 50934.1186 | 39.996
Devonshire Building | 2017-09-18 07:00 | 50934.1386 | 79.992
Devonshire Building | 2017-09-18 07:15 | 50934.1536 | 60.012
Devonshire Building | 2017-09-18 07:30 | 50934.1686 | 60.012
Devonshire Building | 2017-09-18 07:45 | 50934.1936 | 100.008
Devonshire Building | 2017-09-18 08:00 | 50934.2186 | 100.008
Devonshire Building | 2017-09-18 08:15 | 50934.2636 | 180
Devonshire Building | 2017-09-18 08:30 | 50934.8186 | 2220.012
Devonshire Building | 2017-09-18 08:45 | 50934.8736 | 219.996
Devonshire Building | 2017-09-18 09:00 | 50934.9336 | 240.012
Devonshire Building | 2017-09-18 09:15 | 50934.9936 | 240.012
Devonshire Building | 2017-09-18 09:30 | 50935.0486 | 219.996
Devonshire Building | 2017-09-18 09:45 | 50935.2136 | 659.988
Devonshire Building | 2017-09-18 10:00 | 50935.7036 | 1959.984
Devonshire Building | 2017-09-18 10:15 | 50935.7586 | 219.996
Devonshire Building | 2017-09-18 10:30 | 50935.8086 | 200.016
Devonshire Building | 2017-09-18 10:45 | 50935.8636 | 219.996
Devonshire Building | 2017-09-18 11:00 | 50935.9136 | 200.016
Devonshire Building | 2017-09-18 11:15 | 50936.4836 | 2279.988
Devonshire Building | 2017-09-18 11:30 | 50936.5286 | 180
Devonshire Building | 2017-09-18 11:45 | 50936.5786 | 200.016
Devonshire Building | 2017-09-18 12:00 | 50936.6336 | 219.996
Devonshire Building | 2017-09-18 12:15 | 50936.6986 | 259.992
Devonshire Building | 2017-09-18 12:30 | 50937.2636 | 2260.008
Devonshire Building | 2017-09-18 12:45 | 50937.3436 | 320.004
Devonshire Building | 2017-09-18 13:00 | 50937.4086 | 259.992
Devonshire Building | 2017-09-18 13:15 | 50937.4736 | 259.992
Devonshire Building | 2017-09-18 13:30 | 50937.5336 | 240.012
Devonshire Building | 2017-09-18 13:45 | 50937.6086 | 299.988
Devonshire Building | 2017-09-18 14:00 | 50937.6936 | 339.984
Devonshire Building | 2017-09-18 14:15 | 50937.7636 | 280.008
Devonshire Building | 2017-09-18 14:30 | 50938.2036 | 1760.004
Devonshire Building | 2017-09-18 14:45 | 50938.4186 | 860.004
Devonshire Building | 2017-09-18 15:00 | 50938.4786 | 240.012
Devonshire Building | 2017-09-18 15:15 | 50938.5386 | 240.012
Devonshire Building | 2017-09-18 15:30 | 50938.5986 | 240.012
Devonshire Building | 2017-09-18 15:45 | 50938.6536 | 219.996
Devonshire Building | 2017-09-18 16:00 | 50939.2286 | 2300.004
Devonshire Building | 2017-09-18 16:15 | 50939.2686 | 159.984
Devonshire Building | 2017-09-18 16:30 | 50939.3036 | 140.004
Devonshire Building | 2017-09-18 16:45 | 50939.3436 | 159.984
Devonshire Building | 2017-09-18 17:00 | 50939.3786 | 140.004
Devonshire Building | 2017-09-18 17:15 | 50939.4186 | 159.984
Devonshire Building | 2017-09-18 17:30 | 50939.4536 | 140.004
Devonshire Building | 2017-09-18 17:45 | 50939.4836 | 119.988
Devonshire Building | 2017-09-18 18:00 | 50939.5136 | 119.988
Devonshire Building | 2017-09-18 18:15 | 50939.5436 | 119.988
Devonshire Building | 2017-09-18 18:30 | 50939.5686 | 100.008
Devonshire Building | 2017-09-18 18:45 | 50939.5936 | 100.008
Devonshire Building | 2017-09-18 19:00 | 50939.6136 | 79.992
Devonshire Building | 2017-09-18 19:15 | 50939.6336 | 79.992
Devonshire Building | 2017-09-18 19:30 | 50939.6536 | 79.992
Devonshire Building | 2017-09-18 19:45 | 50939.6736 | 79.992
Devonshire Building | 2017-09-18 20:00 | 50940.1436 | 1879.992
Devonshire Building | 2017-09-18 20:15 | 50940.2036 | 240.012
Devonshire Building | 2017-09-18 20:30 | 50940.2136 | 39.996
Devonshire Building | 2017-09-18 20:45 | 50940.2336 | 79.992
Devonshire Building | 2017-09-18 21:00 | 50940.2436 | 39.996
Devonshire Building | 2017-09-18 21:15 | 50940.2536 | 39.996
Devonshire Building | 2017-09-18 21:30 | 50940.2636 | 39.996
Devonshire Building | 2017-09-18 21:45 | 50940.2736 | 39.996
Devonshire Building | 2017-09-18 22:00 | 50940.2886 | 60.012
Devonshire Building | 2017-09-18 22:15 | 50940.2986 | 39.996
Devonshire Building | 2017-09-18 22:30 | 50940.3086 | 39.996
Devonshire Building | 2017-09-18 22:45 | 50940.3186 | 39.996
Devonshire Building | 2017-09-18 23:00 | 50940.3286 | 39.996
Devonshire Building | 2017-09-18 23:15 | 50940.3436 | 60.012
Devonshire Building | 2017-09-18 23:30 | 50940.3536 | 39.996
Devonshire Building | 2017-09-18 23:45 | 50940.3686 | 60.012
Devonshire Building | 2017-09-19 | 50940.3789 | 39.996
Devonshire Building | 2017-09-19 00:15 | 50940.3889 | 39.996
Devonshire Building | 2017-09-19 00:30 | 50940.3989 | 39.996
Devonshire Building | 2017-09-19 00:45 | 50940.4089 | 39.996
Devonshire Building | 2017-09-19 01:00 | 50940.4239 | 60.012
Devonshire Building | 2017-09-19 01:15 | 50940.4339 | 39.996
Devonshire Building | 2017-09-19 01:30 | 50940.4439 | 39.996
Devonshire Building | 2017-09-19 01:45 | 50940.4539 | 39.996
Devonshire Building | 2017-09-19 02:00 | 50940.4639 | 39.996
Devonshire Building | 2017-09-19 02:15 | 50940.4739 | 39.996
Devonshire Building | 2017-09-19 02:30 | 50940.4839 | 39.996
Devonshire Building | 2017-09-19 02:45 | 50940.4939 | 39.996
Devonshire Building | 2017-09-19 03:00 | 50940.5039 | 39.996
Devonshire Building | 2017-09-19 03:15 | 50940.5089 | 20.016
Devonshire Building | 2017-09-19 03:30 | 50940.5189 | 39.996
Devonshire Building | 2017-09-19 03:45 | 50940.5289 | 39.996
Devonshire Building | 2017-09-19 04:00 | 50940.9639 | 1739.988
Devonshire Building | 2017-09-19 04:15 | 50941.0539 | 360
Devonshire Building | 2017-09-19 04:30 | 50941.0639 | 39.996
Devonshire Building | 2017-09-19 04:45 | 50941.0739 | 39.996
Devonshire Building | 2017-09-19 05:00 | 50941.0839 | 39.996
Devonshire Building | 2017-09-19 05:15 | 50941.0939 | 39.996
Devonshire Building | 2017-09-19 05:30 | 50941.1089 | 60.012
Devonshire Building | 2017-09-19 05:45 | 50941.1189 | 39.996
Devonshire Building | 2017-09-19 06:00 | 50941.1289 | 39.996
Devonshire Building | 2017-09-19 06:15 | 50941.1389 | 39.996
Devonshire Building | 2017-09-19 06:30 | 50941.1489 | 39.996
Devonshire Building | 2017-09-19 06:45 | 50941.1639 | 60.012
Devonshire Building | 2017-09-19 07:00 | 50941.1839 | 79.992
Devonshire Building | 2017-09-19 07:15 | 50941.1989 | 60.012
Devonshire Building | 2017-09-19 07:30 | 50941.2139 | 60.012
Devonshire Building | 2017-09-19 07:45 | 50941.2289 | 60.012
Devonshire Building | 2017-09-19 08:00 | 50941.4139 | 740.016
Devonshire Building | 2017-09-19 08:15 | 50941.7939 | 1519.992
Devonshire Building | 2017-09-19 08:30 | 50941.8089 | 60.012
Devonshire Building | 2017-09-19 08:45 | 50941.8289 | 79.992
Devonshire Building | 2017-09-19 09:00 | 50941.8489 | 79.992
Devonshire Building | 2017-09-19 09:15 | 50941.8689 | 79.992
Devonshire Building | 2017-09-19 09:30 | 50941.8989 | 119.988
Devonshire Building | 2017-09-19 09:45 | 50942.4989 | 2400.012
Devonshire Building | 2017-09-19 10:00 | 50942.5539 | 219.996
Devonshire Building | 2017-09-19 10:15 | 50942.6039 | 200.016
Devonshire Building | 2017-09-19 10:30 | 50942.6589 | 219.996
Devonshire Building | 2017-09-19 10:45 | 50942.7039 | 180
Devonshire Building | 2017-09-19 11:00 | 50942.8089 | 420.012
Devonshire Building | 2017-09-19 11:15 | 50943.4539 | 2580.012
Devonshire Building | 2017-09-19 11:30 | 50943.4889 | 140.004
Devonshire Building | 2017-09-19 11:45 | 50943.5239 | 140.004
Devonshire Building | 2017-09-19 12:00 | 50943.5589 | 140.004
Devonshire Building | 2017-09-19 12:15 | 50943.5989 | 159.984
Devonshire Building | 2017-09-19 12:30 | 50943.6389 | 159.984
Devonshire Building | 2017-09-19 12:45 | 50944.2189 | 2319.984
Devonshire Building | 2017-09-19 13:00 | 50944.2589 | 159.984
Devonshire Building | 2017-09-19 13:15 | 50944.2889 | 119.988
Devonshire Building | 2017-09-19 13:30 | 50944.3239 | 140.004
Devonshire Building | 2017-09-19 13:45 | 50944.3739 | 200.016
Devonshire Building | 2017-09-19 14:00 | 50944.4239 | 200.016
Devonshire Building | 2017-09-19 14:15 | 50944.4739 | 200.016
Devonshire Building | 2017-09-19 14:30 | 50944.9589 | 1940.004
Devonshire Building | 2017-09-19 14:45 | 50945.0839 | 500.004
Devonshire Building | 2017-09-19 15:00 | 50945.1239 | 159.984
Devonshire Building | 2017-09-19 15:15 | 50945.1689 | 180
Devonshire Building | 2017-09-19 15:30 | 50945.2089 | 159.984
Devonshire Building | 2017-09-19 15:45 | 50945.2489 | 159.984
Devonshire Building | 2017-09-19 16:00 | 50945.2889 | 159.984
Devonshire Building | 2017-09-19 16:15 | 50945.8539 | 2260.008
Devonshire Building | 2017-09-19 16:30 | 50945.8739 | 79.992
Devonshire Building | 2017-09-19 16:45 | 50945.8939 | 79.992
Devonshire Building | 2017-09-19 17:00 | 50945.9239 | 119.988
Devonshire Building | 2017-09-19 17:15 | 50945.9539 | 119.988
Devonshire Building | 2017-09-19 17:30 | 50945.9839 | 119.988
Devonshire Building | 2017-09-19 17:45 | 50946.0439 | 240.012
Devonshire Building | 2017-09-19 18:00 | 50946.1039 | 240.012
Devonshire Building | 2017-09-19 18:15 | 50946.1639 | 240.012
Devonshire Building | 2017-09-19 18:30 | 50946.2189 | 219.996
Devonshire Building | 2017-09-19 18:45 | 50946.2689 | 200.016
Devonshire Building | 2017-09-19 19:00 | 50946.3139 | 180
Devonshire Building | 2017-09-19 19:15 | 50946.3589 | 180
Devonshire Building | 2017-09-19 19:30 | 50946.3989 | 159.984
Devonshire Building | 2017-09-19 19:45 | 50946.4339 | 140.004
Devonshire Building | 2017-09-19 20:00 | 50946.4639 | 119.988
Devonshire Building | 2017-09-19 20:15 | 50946.4939 | 119.988
Devonshire Building | 2017-09-19 20:30 | 50946.5189 | 100.008
Devonshire Building | 2017-09-19 20:45 | 50946.5639 | 180
Devonshire Building | 2017-09-19 21:00 | 50946.5789 | 60.012
Devonshire Building | 2017-09-19 21:15 | 50946.5939 | 60.012
Devonshire Building | 2017-09-19 21:30 | 50946.6089 | 60.012
Devonshire Building | 2017-09-19 21:45 | 50946.6239 | 60.012
Devonshire Building | 2017-09-19 22:00 | 50946.6389 | 60.012
Devonshire Building | 2017-09-19 22:15 | 50946.6539 | 60.012
Devonshire Building | 2017-09-19 22:30 | 50946.6689 | 60.012
Devonshire Building | 2017-09-19 22:45 | 50946.6789 | 39.996
Devonshire Building | 2017-09-19 23:00 | 50947.1989 | 2080.008
Devonshire Building | 2017-09-19 23:15 | 50947.2089 | 39.996
Devonshire Building | 2017-09-19 23:30 | 50947.2239 | 60.012
Devonshire Building | 2017-09-19 23:45 | 50947.2339 | 39.996
Devonshire Building | 2017-09-20 | 50947.2461 | 39.996
Devonshire Building | 2017-09-20 00:15 | 50947.2561 | 39.996
Devonshire Building | 2017-09-20 00:30 | 50947.2661 | 39.996
Devonshire Building | 2017-09-20 00:45 | 50947.2811 | 60.012
Devonshire Building | 2017-09-20 01:00 | 50947.2911 | 39.996
Devonshire Building | 2017-09-20 01:15 | 50947.3011 | 39.996
Devonshire Building | 2017-09-20 01:30 | 50947.3161 | 60.012
Devonshire Building | 2017-09-20 01:45 | 50947.3261 | 39.996
Devonshire Building | 2017-09-20 02:00 | 50947.3411 | 60.012
Devonshire Building | 2017-09-20 02:15 | 50947.3511 | 39.996
Devonshire Building | 2017-09-20 02:30 | 50947.3611 | 39.996
Devonshire Building | 2017-09-20 02:45 | 50947.3761 | 60.012
Devonshire Building | 2017-09-20 03:00 | 50947.3861 | 39.996
Devonshire Building | 2017-09-20 03:15 | 50947.3961 | 39.996
Devonshire Building | 2017-09-20 03:30 | 50947.4111 | 60.012
Devonshire Building | 2017-09-20 03:45 | 50947.4211 | 39.996
Devonshire Building | 2017-09-20 04:00 | 50947.4311 | 39.996
Devonshire Building | 2017-09-20 04:15 | 50947.4411 | 39.996
Devonshire Building | 2017-09-20 04:30 | 50947.4561 | 60.012
Devonshire Building | 2017-09-20 04:45 | 50947.4661 | 39.996
Devonshire Building | 2017-09-20 05:00 | 50947.4761 | 39.996
Devonshire Building | 2017-09-20 05:15 | 50947.4861 | 39.996
Devonshire Building | 2017-09-20 05:30 | 50947.4961 | 39.996
Devonshire Building | 2017-09-20 05:45 | 50947.5111 | 60.012
Devonshire Building | 2017-09-20 06:00 | 50947.5211 | 39.996
Devonshire Building | 2017-09-20 06:15 | 50947.5311 | 39.996
Devonshire Building | 2017-09-20 06:30 | 50947.5411 | 39.996
Devonshire Building | 2017-09-20 06:45 | 50948.0811 | 2160
Devonshire Building | 2017-09-20 07:00 | 50948.0911 | 39.996
Devonshire Building | 2017-09-20 07:15 | 50948.1061 | 60.012
Devonshire Building | 2017-09-20 07:30 | 50948.1211 | 60.012
Devonshire Building | 2017-09-20 07:45 | 50948.1611 | 159.984
Devonshire Building | 2017-09-20 08:00 | 50948.1761 | 60.012
Devonshire Building | 2017-09-20 08:15 | 50948.1911 | 60.012
Devonshire Building | 2017-09-20 08:30 | 50948.2161 | 100.008
Devonshire Building | 2017-09-20 08:45 | 50948.2511 | 140.004
Devonshire Building | 2017-09-20 09:00 | 50948.2861 | 140.004
Devonshire Building | 2017-09-20 09:15 | 50948.8711 | 2340
Devonshire Building | 2017-09-20 09:30 | 50948.9361 | 259.992
Devonshire Building | 2017-09-20 09:45 | 50949.0011 | 259.992
Devonshire Building | 2017-09-20 10:00 | 50949.0661 | 259.992
Devonshire Building | 2017-09-20 10:15 | 50949.1211 | 219.996
Devonshire Building | 2017-09-20 10:30 | 50949.1811 | 240.012
Devonshire Building | 2017-09-20 10:45 | 50949.7661 | 2340
Devonshire Building | 2017-09-20 11:00 | 50949.8161 | 200.016
Devonshire Building | 2017-09-20 11:15 | 50949.8761 | 240.012
Devonshire Building | 2017-09-20 11:30 | 50949.9461 | 280.008
Devonshire Building | 2017-09-20 11:45 | 50950.0111 | 259.992
Devonshire Building | 2017-09-20 12:00 | 50950.0761 | 259.992
Devonshire Building | 2017-09-20 12:15 | 50950.6361 | 2239.992
Devonshire Building | 2017-09-20 12:30 | 50950.7161 | 320.004
Devonshire Building | 2017-09-20 12:45 | 50950.7661 | 200.016
Devonshire Building | 2017-09-20 13:00 | 50950.8111 | 180
Devonshire Building | 2017-09-20 13:15 | 50950.8611 | 200.016
Devonshire Building | 2017-09-20 13:30 | 50950.9061 | 180
Devonshire Building | 2017-09-20 13:45 | 50950.9411 | 140.004
Devonshire Building | 2017-09-20 14:00 | 50951.0511 | 439.992
Devonshire Building | 2017-09-20 14:15 | 50951.5261 | 1900.008
Devonshire Building | 2017-09-20 14:30 | 50951.5461 | 79.992
Devonshire Building | 2017-09-20 14:45 | 50951.5761 | 119.988
Devonshire Building | 2017-09-20 15:00 | 50951.6061 | 119.988
Devonshire Building | 2017-09-20 15:15 | 50951.6361 | 119.988
Devonshire Building | 2017-09-20 15:30 | 50951.6711 | 140.004
Devonshire Building | 2017-09-20 15:45 | 50951.7111 | 159.984
Devonshire Building | 2017-09-20 16:00 | 50952.3211 | 2440.008
Devonshire Building | 2017-09-20 16:15 | 50952.3811 | 240.012
Devonshire Building | 2017-09-20 16:30 | 50952.4461 | 259.992
Devonshire Building | 2017-09-20 16:45 | 50952.5011 | 219.996
Devonshire Building | 2017-09-20 17:00 | 50952.5511 | 200.016
Devonshire Building | 2017-09-20 17:15 | 50952.5961 | 180
Devonshire Building | 2017-09-20 17:30 | 50952.6361 | 159.984
Devonshire Building | 2017-09-20 17:45 | 50952.6761 | 159.984
Devonshire Building | 2017-09-20 18:00 | 50952.7061 | 119.988
Devonshire Building | 2017-09-20 18:15 | 50952.7361 | 119.988
Devonshire Building | 2017-09-20 18:30 | 50952.7611 | 100.008
Devonshire Building | 2017-09-20 18:45 | 50952.7861 | 100.008
Devonshire Building | 2017-09-20 19:00 | 50953.3111 | 2099.988
Devonshire Building | 2017-09-20 19:15 | 50953.3211 | 39.996
Devonshire Building | 2017-09-20 19:30 | 50953.3361 | 60.012
Devonshire Building | 2017-09-20 19:45 | 50953.3511 | 60.012
Devonshire Building | 2017-09-20 20:00 | 50953.3611 | 39.996
Devonshire Building | 2017-09-20 20:15 | 50953.3761 | 60.012
Devonshire Building | 2017-09-20 20:30 | 50953.4011 | 100.008
Devonshire Building | 2017-09-20 20:45 | 50953.4261 | 100.008
Devonshire Building | 2017-09-20 21:00 | 50953.4361 | 39.996
Devonshire Building | 2017-09-20 21:15 | 50953.4511 | 60.012
Devonshire Building | 2017-09-20 21:30 | 50953.4611 | 39.996
Devonshire Building | 2017-09-20 21:45 | 50953.4761 | 60.012
Devonshire Building | 2017-09-20 22:00 | 50953.4861 | 39.996
Devonshire Building | 2017-09-20 22:15 | 50953.5011 | 60.012
Devonshire Building | 2017-09-20 22:30 | 50953.5111 | 39.996
Devonshire Building | 2017-09-20 22:45 | 50953.5211 | 39.996
Devonshire Building | 2017-09-20 23:00 | 50953.5361 | 60.012
Devonshire Building | 2017-09-20 23:15 | 50953.5461 | 39.996
Devonshire Building | 2017-09-20 23:30 | 50953.5561 | 39.996
Devonshire Building | 2017-09-20 23:45 | 50953.5661 | 39.996
Devonshire Building | 2017-09-21 | 50953.5742 | 39.996
Devonshire Building | 2017-09-21 00:15 | 50953.5892 | 60.012
Devonshire Building | 2017-09-21 00:30 | 50953.5992 | 39.996
Devonshire Building | 2017-09-21 00:45 | 50953.6092 | 39.996
Devonshire Building | 2017-09-21 01:00 | 50953.6192 | 39.996
Devonshire Building | 2017-09-21 01:15 | 50953.6292 | 39.996
Devonshire Building | 2017-09-21 01:30 | 50953.6392 | 39.996
Devonshire Building | 2017-09-21 01:45 | 50953.6492 | 39.996
Devonshire Building | 2017-09-21 02:00 | 50953.6592 | 39.996
Devonshire Building | 2017-09-21 02:15 | 50953.6692 | 39.996
Devonshire Building | 2017-09-21 02:30 | 50953.6792 | 39.996
Devonshire Building | 2017-09-21 02:45 | 50953.6892 | 39.996
Devonshire Building | 2017-09-21 03:00 | 50954.1892 | 2000.016
Devonshire Building | 2017-09-21 03:15 | 50954.2092 | 79.992
Devonshire Building | 2017-09-21 03:30 | 50954.2192 | 39.996
Devonshire Building | 2017-09-21 03:45 | 50954.2292 | 39.996
Devonshire Building | 2017-09-21 04:00 | 50954.2392 | 39.996
Devonshire Building | 2017-09-21 04:15 | 50954.2492 | 39.996
Devonshire Building | 2017-09-21 04:30 | 50954.2592 | 39.996
Devonshire Building | 2017-09-21 04:45 | 50954.2692 | 39.996
Devonshire Building | 2017-09-21 05:00 | 50954.2792 | 39.996
Devonshire Building | 2017-09-21 05:15 | 50954.2892 | 39.996
Devonshire Building | 2017-09-21 05:30 | 50954.2992 | 39.996
Devonshire Building | 2017-09-21 05:45 | 50954.3142 | 60.012
Devonshire Building | 2017-09-21 06:00 | 50954.3242 | 39.996
Devonshire Building | 2017-09-21 06:15 | 50954.3292 | 20.016
Devonshire Building | 2017-09-21 06:30 | 50954.3342 | 20.016
Devonshire Building | 2017-09-21 06:45 | 50954.3392 | 20.016
Devonshire Building | 2017-09-21 07:00 | 50954.3542 | 60.012
Devonshire Building | 2017-09-21 07:15 | 50954.3692 | 60.012
Devonshire Building | 2017-09-21 07:30 | 50954.3842 | 60.012
Devonshire Building | 2017-09-21 07:45 | 50954.4142 | 119.988
Devonshire Building | 2017-09-21 08:00 | 50954.8742 | 1839.996
Devonshire Building | 2017-09-21 08:15 | 50955.0192 | 579.996
Devonshire Building | 2017-09-21 08:30 | 50955.0592 | 159.984
Devonshire Building | 2017-09-21 08:45 | 50955.0942 | 140.004
Devonshire Building | 2017-09-21 09:00 | 50955.1292 | 140.004
Devonshire Building | 2017-09-21 09:15 | 50955.1692 | 159.984
Devonshire Building | 2017-09-21 09:30 | 50955.2342 | 259.992
Devonshire Building | 2017-09-21 09:45 | 50955.9242 | 2760.012
Devonshire Building | 2017-09-21 10:00 | 50956.0992 | 699.984
Devonshire Building | 2017-09-21 10:15 | 50956.2192 | 479.988
Devonshire Building | 2017-09-21 10:30 | 50956.3042 | 339.984
Devonshire Building | 2017-09-21 10:45 | 50956.3692 | 259.992
Devonshire Building | 2017-09-21 11:00 | 50956.8142 | 1779.984
Devonshire Building | 2017-09-21 11:15 | 50957.0242 | 839.988
Devonshire Building | 2017-09-21 11:30 | 50957.0492 | 100.008
Devonshire Building | 2017-09-21 11:45 | 50957.0792 | 119.988
Devonshire Building | 2017-09-21 12:00 | 50957.1092 | 119.988
Devonshire Building | 2017-09-21 12:15 | 50957.1692 | 240.012
Devonshire Building | 2017-09-21 12:30 | 50957.7842 | 2459.988
Devonshire Building | 2017-09-21 12:45 | 50957.8242 | 159.984
Devonshire Building | 2017-09-21 13:00 | 50957.8592 | 140.004
Devonshire Building | 2017-09-21 13:15 | 50957.9092 | 200.016
Devonshire Building | 2017-09-21 13:30 | 50957.9692 | 240.012
Devonshire Building | 2017-09-21 13:45 | 50958.5642 | 2379.996
Devonshire Building | 2017-09-21 14:00 | 50958.6692 | 420.012
Devonshire Building | 2017-09-21 14:15 | 50958.7592 | 360
Devonshire Building | 2017-09-21 14:30 | 50958.8392 | 320.004
Devonshire Building | 2017-09-21 14:45 | 50958.9042 | 259.992
Devonshire Building | 2017-09-21 15:00 | 50958.9642 | 240.012
Devonshire Building | 2017-09-21 15:15 | 50959.3492 | 1540.008
Devonshire Building | 2017-09-21 15:30 | 50959.6292 | 1119.996
Devonshire Building | 2017-09-21 15:45 | 50959.6642 | 140.004
Devonshire Building | 2017-09-21 16:00 | 50959.7092 | 180
Devonshire Building | 2017-09-21 16:15 | 50959.7492 | 159.984
Devonshire Building | 2017-09-21 16:30 | 50959.7892 | 159.984
Devonshire Building | 2017-09-21 16:45 | 50959.8242 | 140.004
Devonshire Building | 2017-09-21 17:00 | 50959.8592 | 140.004
Devonshire Building | 2017-09-21 17:15 | 50959.8892 | 119.988
Devonshire Building | 2017-09-21 17:30 | 50959.9192 | 119.988
Devonshire Building | 2017-09-21 17:45 | 50960.4642 | 2180.016
Devonshire Building | 2017-09-21 18:00 | 50960.4792 | 60.012
Devonshire Building | 2017-09-21 18:15 | 50960.4942 | 60.012
Devonshire Building | 2017-09-21 18:30 | 50960.5092 | 60.012
Devonshire Building | 2017-09-21 18:45 | 50960.5242 | 60.012
Devonshire Building | 2017-09-21 19:00 | 50960.5392 | 60.012
Devonshire Building | 2017-09-21 19:15 | 50960.5542 | 60.012
Devonshire Building | 2017-09-21 19:30 | 50960.5692 | 60.012
Devonshire Building | 2017-09-21 19:45 | 50960.5842 | 60.012
Devonshire Building | 2017-09-21 20:00 | 50960.5992 | 60.012
Devonshire Building | 2017-09-21 20:15 | 50960.6142 | 60.012
Devonshire Building | 2017-09-21 20:30 | 50960.6292 | 60.012
Devonshire Building | 2017-09-21 20:45 | 50960.6642 | 140.004
Devonshire Building | 2017-09-21 21:00 | 50960.6742 | 39.996
Devonshire Building | 2017-09-21 21:15 | 50960.6892 | 60.012
Devonshire Building | 2017-09-21 21:30 | 50960.6992 | 39.996
Devonshire Building | 2017-09-21 21:45 | 50960.7092 | 39.996
Devonshire Building | 2017-09-21 22:00 | 50960.7192 | 39.996
Devonshire Building | 2017-09-21 22:15 | 50960.7292 | 39.996
Devonshire Building | 2017-09-21 22:30 | 50960.7392 | 39.996
Devonshire Building | 2017-09-21 22:45 | 50960.7492 | 39.996
Devonshire Building | 2017-09-21 23:00 | 50960.7592 | 39.996
Devonshire Building | 2017-09-21 23:15 | 50960.7692 | 39.996
Devonshire Building | 2017-09-21 23:30 | 50960.7792 | 39.996
Devonshire Building | 2017-09-21 23:45 | 50960.7892 | 39.996
Devonshire Building | 2017-09-22 | 50960.8008 | 39.996
Devonshire Building | 2017-09-22 00:15 | 50960.8058 | 20.016
Devonshire Building | 2017-09-22 00:30 | 50960.8158 | 39.996
Devonshire Building | 2017-09-22 00:45 | 50960.8258 | 39.996
Devonshire Building | 2017-09-22 01:00 | 50960.8358 | 39.996
Devonshire Building | 2017-09-22 01:15 | 50961.2808 | 1779.984
Devonshire Building | 2017-09-22 01:30 | 50961.3608 | 320.004
Devonshire Building | 2017-09-22 01:45 | 50961.3708 | 39.996
Devonshire Building | 2017-09-22 02:00 | 50961.3808 | 39.996
Devonshire Building | 2017-09-22 02:15 | 50961.3908 | 39.996
Devonshire Building | 2017-09-22 02:30 | 50961.3958 | 20.016
Devonshire Building | 2017-09-22 02:45 | 50961.4058 | 39.996
Devonshire Building | 2017-09-22 03:00 | 50961.4158 | 39.996
Devonshire Building | 2017-09-22 03:15 | 50961.4258 | 39.996
Devonshire Building | 2017-09-22 03:30 | 50961.4308 | 20.016
Devonshire Building | 2017-09-22 03:45 | 50961.4408 | 39.996
Devonshire Building | 2017-09-22 04:00 | 50961.4508 | 39.996
Devonshire Building | 2017-09-22 04:15 | 50961.4608 | 39.996
Devonshire Building | 2017-09-22 04:30 | 50961.4708 | 39.996
Devonshire Building | 2017-09-22 04:45 | 50961.4808 | 39.996
Devonshire Building | 2017-09-22 05:00 | 50961.4908 | 39.996
Devonshire Building | 2017-09-22 05:15 | 50961.5008 | 39.996
Devonshire Building | 2017-09-22 05:30 | 50961.5108 | 39.996
Devonshire Building | 2017-09-22 05:45 | 50961.5208 | 39.996
Devonshire Building | 2017-09-22 06:00 | 50961.5308 | 39.996
Devonshire Building | 2017-09-22 06:15 | 50961.5408 | 39.996
Devonshire Building | 2017-09-22 06:30 | 50961.5508 | 39.996
Devonshire Building | 2017-09-22 06:45 | 50961.5608 | 39.996
Devonshire Building | 2017-09-22 07:00 | 50961.5758 | 60.012
Devonshire Building | 2017-09-22 07:15 | 50961.6608 | 339.984
Devonshire Building | 2017-09-22 07:30 | 50962.1208 | 1839.996
Devonshire Building | 2017-09-22 07:45 | 50962.1408 | 79.992
Devonshire Building | 2017-09-22 08:00 | 50962.1708 | 119.988
Devonshire Building | 2017-09-22 08:15 | 50962.2008 | 119.988
Devonshire Building | 2017-09-22 08:30 | 50962.2308 | 119.988
Devonshire Building | 2017-09-22 08:45 | 50962.2658 | 140.004
Devonshire Building | 2017-09-22 09:00 | 50962.3008 | 140.004
Devonshire Building | 2017-09-22 09:15 | 50962.3408 | 159.984
Devonshire Building | 2017-09-22 09:30 | 50962.3858 | 180
Devonshire Building | 2017-09-22 09:45 | 50962.9708 | 2340
Devonshire Building | 2017-09-22 10:00 | 50963.0208 | 200.016
Devonshire Building | 2017-09-22 10:15 | 50963.0658 | 180
Devonshire Building | 2017-09-22 10:30 | 50963.1058 | 159.984
Devonshire Building | 2017-09-22 10:45 | 50963.1658 | 240.012
Devonshire Building | 2017-09-22 11:00 | 50963.2358 | 280.008
Devonshire Building | 2017-09-22 11:15 | 50963.3008 | 259.992
Devonshire Building | 2017-09-22 11:30 | 50963.3658 | 259.992
Devonshire Building | 2017-09-22 11:45 | 50963.4358 | 280.008
Devonshire Building | 2017-09-22 12:00 | 50964.0308 | 2379.996
Devonshire Building | 2017-09-22 12:15 | 50964.1008 | 280.008
Devonshire Building | 2017-09-22 12:30 | 50964.1708 | 280.008
Devonshire Building | 2017-09-22 12:45 | 50964.2358 | 259.992
Devonshire Building | 2017-09-22 13:00 | 50964.3108 | 299.988
Devonshire Building | 2017-09-22 13:15 | 50964.3708 | 240.012
Devonshire Building | 2017-09-22 13:30 | 50964.4208 | 200.016
Devonshire Building | 2017-09-22 13:45 | 50964.4708 | 200.016
Devonshire Building | 2017-09-22 14:00 | 50964.5208 | 200.016
Devonshire Building | 2017-09-22 14:15 | 50965.0658 | 2180.016
Devonshire Building | 2017-09-22 14:30 | 50965.0908 | 100.008
Devonshire Building | 2017-09-22 14:45 | 50965.1208 | 119.988
Devonshire Building | 2017-09-22 15:00 | 50965.1458 | 100.008
Devonshire Building | 2017-09-22 15:15 | 50965.1808 | 140.004
Devonshire Building | 2017-09-22 15:30 | 50965.2108 | 119.988
Devonshire Building | 2017-09-22 15:45 | 50965.2358 | 100.008
Devonshire Building | 2017-09-22 16:00 | 50965.2958 | 240.012
Devonshire Building | 2017-09-22 16:15 | 50965.8008 | 2019.996
Devonshire Building | 2017-09-22 16:30 | 50965.8158 | 60.012
Devonshire Building | 2017-09-22 16:45 | 50965.8308 | 60.012
Devonshire Building | 2017-09-22 17:00 | 50965.8458 | 60.012
Devonshire Building | 2017-09-22 17:15 | 50965.8608 | 60.012
Devonshire Building | 2017-09-22 17:30 | 50965.8758 | 60.012
Devonshire Building | 2017-09-22 17:45 | 50965.8908 | 60.012
Devonshire Building | 2017-09-22 18:00 | 50965.9108 | 79.992
Devonshire Building | 2017-09-22 18:15 | 50965.9258 | 60.012
Devonshire Building | 2017-09-22 18:30 | 50965.9458 | 79.992
Devonshire Building | 2017-09-22 18:45 | 50965.9608 | 60.012
Devonshire Building | 2017-09-22 19:00 | 50965.9758 | 60.012
Devonshire Building | 2017-09-22 19:15 | 50965.9908 | 60.012
Devonshire Building | 2017-09-22 19:30 | 50966.0058 | 60.012
Devonshire Building | 2017-09-22 19:45 | 50966.0208 | 60.012
Devonshire Building | 2017-09-22 20:00 | 50966.0308 | 39.996
Devonshire Building | 2017-09-22 20:15 | 50966.0458 | 60.012
Devonshire Building | 2017-09-22 20:30 | 50966.0608 | 60.012
Devonshire Building | 2017-09-22 20:45 | 50966.5858 | 2099.988
Devonshire Building | 2017-09-22 21:00 | 50966.6008 | 60.012
Devonshire Building | 2017-09-22 21:15 | 50966.6158 | 60.012
Devonshire Building | 2017-09-22 21:30 | 50966.6258 | 39.996
Devonshire Building | 2017-09-22 21:45 | 50966.6408 | 60.012
Devonshire Building | 2017-09-22 22:00 | 50966.6508 | 39.996
Devonshire Building | 2017-09-22 22:15 | 50966.6658 | 60.012
Devonshire Building | 2017-09-22 22:30 | 50966.6808 | 60.012
Devonshire Building | 2017-09-22 22:45 | 50966.6908 | 39.996
Devonshire Building | 2017-09-22 23:00 | 50966.7058 | 60.012
Devonshire Building | 2017-09-22 23:15 | 50966.7208 | 60.012
Devonshire Building | 2017-09-22 23:30 | 50966.7358 | 60.012
Devonshire Building | 2017-09-22 23:45 | 50966.7508 | 60.012
Devonshire Building | 2017-09-23 | 50966.7656 | 60.012
Devonshire Building | 2017-09-23 00:15 | 50966.7756 | 39.996
Devonshire Building | 2017-09-23 00:30 | 50966.7906 | 60.012
Devonshire Building | 2017-09-23 00:45 | 50966.8056 | 60.012
Devonshire Building | 2017-09-23 01:00 | 50966.8156 | 39.996
Devonshire Building | 2017-09-23 01:15 | 50966.8306 | 60.012
Devonshire Building | 2017-09-23 01:30 | 50966.8456 | 60.012
Devonshire Building | 2017-09-23 01:45 | 50966.8556 | 39.996
Devonshire Building | 2017-09-23 02:00 | 50966.8706 | 60.012
Devonshire Building | 2017-09-23 02:15 | 50966.8806 | 39.996
Devonshire Building | 2017-09-23 02:30 | 50966.8956 | 60.012
Devonshire Building | 2017-09-23 02:45 | 50966.9056 | 39.996
Devonshire Building | 2017-09-23 03:00 | 50966.9206 | 60.012
Devonshire Building | 2017-09-23 03:15 | 50966.9306 | 39.996
Devonshire Building | 2017-09-23 03:30 | 50966.9456 | 60.012
Devonshire Building | 2017-09-23 03:45 | 50966.9556 | 39.996
Devonshire Building | 2017-09-23 04:00 | 50966.9656 | 39.996
Devonshire Building | 2017-09-23 04:15 | 50966.9806 | 60.012
Devonshire Building | 2017-09-23 04:30 | 50966.9906 | 39.996
Devonshire Building | 2017-09-23 04:45 | 50967.0006 | 39.996
Devonshire Building | 2017-09-23 05:00 | 50967.0106 | 39.996
Devonshire Building | 2017-09-23 05:15 | 50967.3356 | 1299.996
Devonshire Building | 2017-09-23 05:30 | 50967.5506 | 860.004
Devonshire Building | 2017-09-23 05:45 | 50967.5606 | 39.996
Devonshire Building | 2017-09-23 06:00 | 50967.5706 | 39.996
Devonshire Building | 2017-09-23 06:15 | 50967.5806 | 39.996
Devonshire Building | 2017-09-23 06:30 | 50967.5906 | 39.996
Devonshire Building | 2017-09-23 06:45 | 50967.6006 | 39.996
Devonshire Building | 2017-09-23 07:00 | 50967.6106 | 39.996
Devonshire Building | 2017-09-23 07:15 | 50967.6206 | 39.996
Devonshire Building | 2017-09-23 07:30 | 50967.6306 | 39.996
Devonshire Building | 2017-09-23 07:45 | 50967.6506 | 79.992
Devonshire Building | 2017-09-23 08:00 | 50967.6756 | 100.008
Devonshire Building | 2017-09-23 08:15 | 50967.7056 | 119.988
Devonshire Building | 2017-09-23 08:30 | 50967.7356 | 119.988
Devonshire Building | 2017-09-23 08:45 | 50967.7656 | 119.988
Devonshire Building | 2017-09-23 09:00 | 50967.7906 | 100.008
Devonshire Building | 2017-09-23 09:15 | 50967.8206 | 119.988
Devonshire Building | 2017-09-23 09:30 | 50967.8506 | 119.988
Devonshire Building | 2017-09-23 09:45 | 50967.8756 | 100.008
Devonshire Building | 2017-09-23 10:00 | 50967.9056 | 119.988
Devonshire Building | 2017-09-23 10:15 | 50967.9206 | 60.012
Devonshire Building | 2017-09-23 10:30 | 50967.9356 | 60.012
Devonshire Building | 2017-09-23 10:45 | 50967.9506 | 60.012
Devonshire Building | 2017-09-23 11:00 | 50967.9606 | 39.996
Devonshire Building | 2017-09-23 11:15 | 50968.4756 | 2059.992
Devonshire Building | 2017-09-23 11:30 | 50968.4906 | 60.012
Devonshire Building | 2017-09-23 11:45 | 50968.5056 | 60.012
Devonshire Building | 2017-09-23 12:00 | 50968.5156 | 39.996
Devonshire Building | 2017-09-23 12:15 | 50968.5306 | 60.012
Devonshire Building | 2017-09-23 12:30 | 50968.5406 | 39.996
Devonshire Building | 2017-09-23 12:45 | 50968.5506 | 39.996
Devonshire Building | 2017-09-23 13:00 | 50968.5656 | 60.012
Devonshire Building | 2017-09-23 13:15 | 50968.5756 | 39.996
Devonshire Building | 2017-09-23 13:30 | 50968.5906 | 60.012
Devonshire Building | 2017-09-23 13:45 | 50968.6006 | 39.996
Devonshire Building | 2017-09-23 14:00 | 50968.6156 | 60.012
Devonshire Building | 2017-09-23 14:15 | 50968.6306 | 60.012
Devonshire Building | 2017-09-23 14:30 | 50968.6406 | 39.996
Devonshire Building | 2017-09-23 14:45 | 50968.6556 | 60.012
Devonshire Building | 2017-09-23 15:00 | 50968.6656 | 39.996
Devonshire Building | 2017-09-23 15:15 | 50968.6807 | 60.012
Devonshire Building | 2017-09-23 15:30 | 50968.6957 | 60.012
Devonshire Building | 2017-09-23 15:45 | 50968.7057 | 39.996
Devonshire Building | 2017-09-23 16:00 | 50968.7207 | 60.012
Devonshire Building | 2017-09-23 16:15 | 50968.7307 | 39.996
Devonshire Building | 2017-09-23 16:30 | 50968.7457 | 60.012
Devonshire Building | 2017-09-23 16:45 | 50968.7557 | 39.996
Devonshire Building | 2017-09-23 17:00 | 50968.7657 | 39.996
Devonshire Building | 2017-09-23 17:15 | 50968.7807 | 60.012
Devonshire Building | 2017-09-23 17:30 | 50968.7907 | 39.996
Devonshire Building | 2017-09-23 17:45 | 50968.8007 | 39.996
Devonshire Building | 2017-09-23 18:00 | 50968.8107 | 39.996
Devonshire Building | 2017-09-23 18:15 | 50968.8257 | 60.012
Devonshire Building | 2017-09-23 18:30 | 50968.8357 | 39.996
Devonshire Building | 2017-09-23 18:45 | 50968.8457 | 39.996
Devonshire Building | 2017-09-23 19:00 | 50968.8557 | 39.996
Devonshire Building | 2017-09-23 19:15 | 50969.3807 | 2099.988
Devonshire Building | 2017-09-23 19:30 | 50969.3907 | 39.996
Devonshire Building | 2017-09-23 19:45 | 50969.4007 | 39.996
Devonshire Building | 2017-09-23 20:00 | 50969.4106 | 39.996
Devonshire Building | 2017-09-23 20:15 | 50969.4206 | 39.996
Devonshire Building | 2017-09-23 20:30 | 50969.4306 | 39.996
Devonshire Building | 2017-09-23 20:45 | 50969.4506 | 79.992
Devonshire Building | 2017-09-23 21:00 | 50969.4656 | 60.012
Devonshire Building | 2017-09-23 21:15 | 50969.4756 | 39.996
Devonshire Building | 2017-09-23 21:30 | 50969.4856 | 39.996
Devonshire Building | 2017-09-23 21:45 | 50969.4956 | 39.996
Devonshire Building | 2017-09-23 22:00 | 50969.5106 | 60.012
Devonshire Building | 2017-09-23 22:15 | 50969.5206 | 39.996
Devonshire Building | 2017-09-23 22:30 | 50969.5356 | 60.012
Devonshire Building | 2017-09-23 22:45 | 50969.5507 | 60.012
Devonshire Building | 2017-09-23 23:00 | 50969.5607 | 39.996
Devonshire Building | 2017-09-23 23:15 | 50969.5757 | 60.012
Devonshire Building | 2017-09-23 23:30 | 50969.5857 | 39.996
Devonshire Building | 2017-09-23 23:45 | 50969.6007 | 60.012
Devonshire Building | 2017-09-24 | 50969.6094 | 39.996
Devonshire Building | 2017-09-24 00:15 | 50969.6244 | 60.012
Devonshire Building | 2017-09-24 00:30 | 50969.6344 | 39.996
Devonshire Building | 2017-09-24 00:45 | 50969.6444 | 39.996
Devonshire Building | 2017-09-24 01:00 | 50969.6594 | 60.012
Devonshire Building | 2017-09-24 01:15 | 50969.6694 | 39.996
Devonshire Building | 2017-09-24 01:30 | 50969.6794 | 39.996
Devonshire Building | 2017-09-24 01:45 | 50969.6894 | 39.996
Devonshire Building | 2017-09-24 02:00 | 50969.7044 | 60.012
Devonshire Building | 2017-09-24 02:15 | 50969.7144 | 39.996
Devonshire Building | 2017-09-24 02:30 | 50970.2294 | 2059.992
Devonshire Building | 2017-09-24 02:45 | 50970.2394 | 39.996
Devonshire Building | 2017-09-24 03:00 | 50970.2494 | 39.996
Devonshire Building | 2017-09-24 03:15 | 50970.2594 | 39.996
Devonshire Building | 2017-09-24 03:30 | 50970.2694 | 39.996
Devonshire Building | 2017-09-24 03:45 | 50970.2794 | 39.996
Devonshire Building | 2017-09-24 04:00 | 50970.2844 | 20.016
Devonshire Building | 2017-09-24 04:15 | 50970.2944 | 39.996
Devonshire Building | 2017-09-24 04:30 | 50970.3044 | 39.996
Devonshire Building | 2017-09-24 04:45 | 50970.3144 | 39.996
Devonshire Building | 2017-09-24 05:00 | 50970.3244 | 39.996
Devonshire Building | 2017-09-24 05:15 | 50970.3344 | 39.996
Devonshire Building | 2017-09-24 05:30 | 50970.3494 | 60.012
Devonshire Building | 2017-09-24 05:45 | 50970.3594 | 39.996
Devonshire Building | 2017-09-24 06:00 | 50970.3694 | 39.996
Devonshire Building | 2017-09-24 06:15 | 50970.3844 | 60.012
Devonshire Building | 2017-09-24 06:30 | 50970.3944 | 39.996
Devonshire Building | 2017-09-24 06:45 | 50970.4044 | 39.996
Devonshire Building | 2017-09-24 07:00 | 50970.4194 | 60.012
Devonshire Building | 2017-09-24 07:15 | 50970.4294 | 39.996
Devonshire Building | 2017-09-24 07:30 | 50970.4394 | 39.996
Devonshire Building | 2017-09-24 07:45 | 50970.4544 | 60.012
Devonshire Building | 2017-09-24 08:00 | 50970.4794 | 100.008
Devonshire Building | 2017-09-24 08:15 | 50970.5094 | 119.988
Devonshire Building | 2017-09-24 08:30 | 50970.5344 | 100.008
Devonshire Building | 2017-09-24 08:45 | 50970.5594 | 100.008
Devonshire Building | 2017-09-24 09:00 | 50970.5844 | 100.008
Devonshire Building | 2017-09-24 09:15 | 50970.6144 | 119.988
Devonshire Building | 2017-09-24 09:30 | 50970.6394 | 100.008
Devonshire Building | 2017-09-24 09:45 | 50970.6644 | 100.008
Devonshire Building | 2017-09-24 10:00 | 50970.6894 | 100.008
Devonshire Building | 2017-09-24 10:15 | 50970.7044 | 60.012
Devonshire Building | 2017-09-24 10:30 | 50970.7094 | 20.016
Devonshire Building | 2017-09-24 10:45 | 50970.8844 | 699.984
Devonshire Building | 2017-09-24 11:00 | 50971.2344 | 1400.004
Devonshire Building | 2017-09-24 11:15 | 50971.2444 | 39.996
Devonshire Building | 2017-09-24 11:30 | 50971.2544 | 39.996
Devonshire Building | 2017-09-24 11:45 | 50971.2594 | 20.016
Devonshire Building | 2017-09-24 12:00 | 50971.2694 | 39.996
Devonshire Building | 2017-09-24 12:15 | 50971.2794 | 39.996
Devonshire Building | 2017-09-24 12:30 | 50971.2894 | 39.996
Devonshire Building | 2017-09-24 12:45 | 50971.2994 | 39.996
Devonshire Building | 2017-09-24 13:00 | 50971.3094 | 39.996
Devonshire Building | 2017-09-24 13:15 | 50971.3144 | 20.016
Devonshire Building | 2017-09-24 13:30 | 50971.3244 | 39.996
Devonshire Building | 2017-09-24 13:45 | 50971.3344 | 39.996
Devonshire Building | 2017-09-24 14:00 | 50971.3444 | 39.996
Devonshire Building | 2017-09-24 14:15 | 50971.3544 | 39.996
Devonshire Building | 2017-09-24 14:30 | 50971.3644 | 39.996
Devonshire Building | 2017-09-24 14:45 | 50971.3744 | 39.996
Devonshire Building | 2017-09-24 15:00 | 50971.3894 | 60.012
Devonshire Building | 2017-09-24 15:15 | 50971.3994 | 39.996
Devonshire Building | 2017-09-24 15:30 | 50971.4094 | 39.996
Devonshire Building | 2017-09-24 15:45 | 50971.4194 | 39.996
Devonshire Building | 2017-09-24 16:00 | 50971.4294 | 39.996
Devonshire Building | 2017-09-24 16:15 | 50971.4394 | 39.996
Devonshire Building | 2017-09-24 16:30 | 50971.4494 | 39.996
Devonshire Building | 2017-09-24 16:45 | 50971.4594 | 39.996
Devonshire Building | 2017-09-24 17:00 | 50971.4694 | 39.996
Devonshire Building | 2017-09-24 17:15 | 50971.4794 | 39.996
Devonshire Building | 2017-09-24 17:30 | 50971.4894 | 39.996
Devonshire Building | 2017-09-24 17:45 | 50971.8644 | 1500.012
Devonshire Building | 2017-09-24 18:00 | 50972.0044 | 560.016
Devonshire Building | 2017-09-24 18:15 | 50972.0144 | 39.996
Devonshire Building | 2017-09-24 18:30 | 50972.0244 | 39.996
Devonshire Building | 2017-09-24 18:45 | 50972.0344 | 39.996
Devonshire Building | 2017-09-24 19:00 | 50972.0444 | 39.996
Devonshire Building | 2017-09-24 19:15 | 50972.0544 | 39.996
Devonshire Building | 2017-09-24 19:30 | 50972.0644 | 39.996
Devonshire Building | 2017-09-24 19:45 | 50972.0744 | 39.996
Devonshire Building | 2017-09-24 20:00 | 50972.0844 | 39.996
Devonshire Building | 2017-09-24 20:15 | 50972.0944 | 39.996
Devonshire Building | 2017-09-24 20:30 | 50972.1044 | 39.996
Devonshire Building | 2017-09-24 20:45 | 50972.1294 | 100.008
Devonshire Building | 2017-09-24 21:00 | 50972.1444 | 60.012
Devonshire Building | 2017-09-24 21:15 | 50972.1544 | 39.996
Devonshire Building | 2017-09-24 21:30 | 50972.1694 | 60.012
Devonshire Building | 2017-09-24 21:45 | 50972.1794 | 39.996
Devonshire Building | 2017-09-24 22:00 | 50972.1894 | 39.996
Devonshire Building | 2017-09-24 22:15 | 50972.2044 | 60.012
Devonshire Building | 2017-09-24 22:30 | 50972.2144 | 39.996
Devonshire Building | 2017-09-24 22:45 | 50972.2244 | 39.996
Devonshire Building | 2017-09-24 23:00 | 50972.2394 | 60.012
Devonshire Building | 2017-09-24 23:15 | 50972.2494 | 39.996
Devonshire Building | 2017-09-24 23:30 | 50972.2594 | 39.996
Devonshire Building | 2017-09-24 23:45 | 50972.2694 | 39.996
Devonshire Building | 2017-09-25 | 50972.2812 | 39.996
Devonshire Building | 2017-09-25 00:15 | 50972.2912 | 39.996
Devonshire Building | 2017-09-25 00:30 | 50972.3063 | 60.012
Devonshire Building | 2017-09-25 00:45 | 50972.3163 | 39.996
Devonshire Building | 2017-09-25 01:00 | 50972.3262 | 39.996
Devonshire Building | 2017-09-25 01:15 | 50972.3362 | 39.996
Devonshire Building | 2017-09-25 01:30 | 50972.3462 | 39.996
Devonshire Building | 2017-09-25 01:45 | 50972.3562 | 39.996
Devonshire Building | 2017-09-25 02:00 | 50972.3662 | 39.996
Devonshire Building | 2017-09-25 02:15 | 50972.3762 | 39.996
Devonshire Building | 2017-09-25 02:30 | 50972.8812 | 2019.996
Devonshire Building | 2017-09-25 02:45 | 50972.8912 | 39.996
Devonshire Building | 2017-09-25 03:00 | 50972.9012 | 39.996
Devonshire Building | 2017-09-25 03:15 | 50972.9112 | 39.996
Devonshire Building | 2017-09-25 03:30 | 50972.9212 | 39.996
Devonshire Building | 2017-09-25 03:45 | 50972.9312 | 39.996
Devonshire Building | 2017-09-25 04:00 | 50972.9362 | 20.016
Devonshire Building | 2017-09-25 04:15 | 50972.9462 | 39.996
Devonshire Building | 2017-09-25 04:30 | 50972.9562 | 39.996
Devonshire Building | 2017-09-25 04:45 | 50972.9662 | 39.996
Devonshire Building | 2017-09-25 05:00 | 50972.9762 | 39.996
Devonshire Building | 2017-09-25 05:15 | 50972.9862 | 39.996
Devonshire Building | 2017-09-25 05:30 | 50972.9962 | 39.996
Devonshire Building | 2017-09-25 05:45 | 50973.0112 | 60.012
Devonshire Building | 2017-09-25 06:00 | 50973.0262 | 60.012
Devonshire Building | 2017-09-25 06:15 | 50973.0362 | 39.996
Devonshire Building | 2017-09-25 06:30 | 50973.0512 | 60.012
Devonshire Building | 2017-09-25 06:45 | 50973.0662 | 60.012
Devonshire Building | 2017-09-25 07:00 | 50973.0862 | 79.992
Devonshire Building | 2017-09-25 07:15 | 50973.1062 | 79.992
Devonshire Building | 2017-09-25 07:30 | 50973.1262 | 79.992
Devonshire Building | 2017-09-25 07:45 | 50973.6412 | 2059.992
Devonshire Building | 2017-09-25 08:00 | 50973.7212 | 320.004
Devonshire Building | 2017-09-25 08:15 | 50973.7562 | 140.004
Devonshire Building | 2017-09-25 08:30 | 50973.8312 | 299.988
Devonshire Building | 2017-09-25 08:45 | 50973.9062 | 299.988
Devonshire Building | 2017-09-25 09:00 | 50973.9412 | 140.004
Devonshire Building | 2017-09-25 09:15 | 50973.9712 | 119.988
Devonshire Building | 2017-09-25 09:30 | 50974.5562 | 2340
Devonshire Building | 2017-09-25 09:45 | 50974.6212 | 259.992
Devonshire Building | 2017-09-25 10:00 | 50974.7212 | 399.996
Devonshire Building | 2017-09-25 10:15 | 50974.8212 | 399.996
Devonshire Building | 2017-09-25 10:30 | 50974.9062 | 339.984
Devonshire Building | 2017-09-25 10:45 | 50975.0512 | 579.996
Devonshire Building | 2017-09-25 11:00 | 50975.7612 | 2840.004
Devonshire Building | 2017-09-25 11:15 | 50975.8362 | 299.988
Devonshire Building | 2017-09-25 11:30 | 50975.9212 | 339.984
Devonshire Building | 2017-09-25 11:45 | 50975.9912 | 280.008
Devonshire Building | 2017-09-25 12:00 | 50976.0612 | 280.008
Devonshire Building | 2017-09-25 12:15 | 50976.6812 | 2480.004
Devonshire Building | 2017-09-25 12:30 | 50976.7662 | 339.984
Devonshire Building | 2017-09-25 12:45 | 50976.8562 | 360
Devonshire Building | 2017-09-25 13:00 | 50976.9312 | 299.988
Devonshire Building | 2017-09-25 13:15 | 50976.9912 | 240.012
Devonshire Building | 2017-09-25 13:30 | 50977.0512 | 240.012
Devonshire Building | 2017-09-25 13:45 | 50977.1012 | 200.016
Devonshire Building | 2017-09-25 14:00 | 50977.1562 | 219.996
Devonshire Building | 2017-09-25 14:15 | 50977.7262 | 2279.988
Devonshire Building | 2017-09-25 14:30 | 50977.7662 | 159.984
Devonshire Building | 2017-09-25 14:45 | 50977.8262 | 240.012
Devonshire Building | 2017-09-25 15:00 | 50977.8762 | 200.016
Devonshire Building | 2017-09-25 15:15 | 50977.9312 | 219.996
Devonshire Building | 2017-09-25 15:30 | 50977.9912 | 240.012
Devonshire Building | 2017-09-25 15:45 | 50978.5562 | 2260.008
Devonshire Building | 2017-09-25 16:00 | 50978.6012 | 180
Devonshire Building | 2017-09-25 16:15 | 50978.6512 | 200.016
Devonshire Building | 2017-09-25 16:30 | 50978.6962 | 180
Devonshire Building | 2017-09-25 16:45 | 50978.7762 | 320.004
Devonshire Building | 2017-09-25 17:00 | 50978.8712 | 380.016
Devonshire Building | 2017-09-25 17:15 | 50979.0762 | 820.008
Devonshire Building | 2017-09-25 17:30 | 50979.2362 | 640.008
Devonshire Building | 2017-09-25 17:45 | 50979.3362 | 399.996
Devonshire Building | 2017-09-25 18:00 | 50979.4012 | 259.992
Devonshire Building | 2017-09-25 18:15 | 50979.4512 | 200.016
Devonshire Building | 2017-09-25 18:30 | 50979.4912 | 159.984
Devonshire Building | 2017-09-25 18:45 | 50979.5212 | 119.988
Devonshire Building | 2017-09-25 19:00 | 50979.5462 | 100.008
Devonshire Building | 2017-09-25 19:15 | 50979.5712 | 100.008
Devonshire Building | 2017-09-25 19:30 | 50979.9512 | 1519.992
Devonshire Building | 2017-09-25 19:45 | 50980.1062 | 619.992
Devonshire Building | 2017-09-25 20:00 | 50980.1162 | 39.996
Devonshire Building | 2017-09-25 20:15 | 50980.1262 | 39.996
Devonshire Building | 2017-09-25 20:30 | 50980.1312 | 20.016
Devonshire Building | 2017-09-25 20:45 | 50980.1512 | 79.992
Devonshire Building | 2017-09-25 21:00 | 50980.1562 | 20.016
Devonshire Building | 2017-09-25 21:15 | 50980.1662 | 39.996
Devonshire Building | 2017-09-25 21:30 | 50980.1762 | 39.996
Devonshire Building | 2017-09-25 21:45 | 50980.1812 | 20.016
Devonshire Building | 2017-09-25 22:00 | 50980.1912 | 39.996
Devonshire Building | 2017-09-25 22:15 | 50980.1962 | 20.016
Devonshire Building | 2017-09-25 22:30 | 50980.2062 | 39.996
Devonshire Building | 2017-09-25 22:45 | 50980.2162 | 39.996
Devonshire Building | 2017-09-25 23:00 | 50980.2212 | 20.016
Devonshire Building | 2017-09-25 23:15 | 50980.2312 | 39.996
Devonshire Building | 2017-09-25 23:30 | 50980.2412 | 39.996
Devonshire Building | 2017-09-25 23:45 | 50980.2512 | 39.996
Devonshire Building | 2017-09-26 | 50980.2539 | 20.016
Devonshire Building | 2017-09-26 00:15 | 50980.2639 | 39.996
Devonshire Building | 2017-09-26 00:30 | 50980.2739 | 39.996
Devonshire Building | 2017-09-26 00:45 | 50980.2789 | 20.016
Devonshire Building | 2017-09-26 01:00 | 50980.2889 | 39.996
Devonshire Building | 2017-09-26 01:15 | 50980.2939 | 20.016
Devonshire Building | 2017-09-26 01:30 | 50980.3039 | 39.996
Devonshire Building | 2017-09-26 01:45 | 50980.3089 | 20.016
Devonshire Building | 2017-09-26 02:00 | 50980.3189 | 39.996
Devonshire Building | 2017-09-26 02:15 | 50980.3239 | 20.016
Devonshire Building | 2017-09-26 02:30 | 50980.3339 | 39.996
Devonshire Building | 2017-09-26 02:45 | 50980.3389 | 20.016
Devonshire Building | 2017-09-26 03:00 | 50980.3489 | 39.996
Devonshire Building | 2017-09-26 03:15 | 50980.3539 | 20.016
Devonshire Building | 2017-09-26 03:30 | 50980.3639 | 39.996
Devonshire Building | 2017-09-26 03:45 | 50980.3689 | 20.016
Devonshire Building | 2017-09-26 04:00 | 50980.3789 | 39.996
Devonshire Building | 2017-09-26 04:15 | 50980.3839 | 20.016
Devonshire Building | 2017-09-26 04:30 | 50980.3889 | 20.016
Devonshire Building | 2017-09-26 04:45 | 50980.3989 | 39.996
Devonshire Building | 2017-09-26 05:00 | 50980.9039 | 2019.996
Devonshire Building | 2017-09-26 05:15 | 50980.9139 | 39.996
Devonshire Building | 2017-09-26 05:30 | 50980.9189 | 20.016
Devonshire Building | 2017-09-26 05:45 | 50980.9289 | 39.996
Devonshire Building | 2017-09-26 06:00 | 50980.9439 | 60.012
Devonshire Building | 2017-09-26 06:15 | 50980.9489 | 20.016
Devonshire Building | 2017-09-26 06:30 | 50980.9589 | 39.996
Devonshire Building | 2017-09-26 06:45 | 50980.9689 | 39.996
Devonshire Building | 2017-09-26 07:00 | 50980.9839 | 60.012
Devonshire Building | 2017-09-26 07:15 | 50980.9939 | 39.996
Devonshire Building | 2017-09-26 07:30 | 50981.0039 | 39.996
Devonshire Building | 2017-09-26 07:45 | 50981.0189 | 60.012
Devonshire Building | 2017-09-26 08:00 | 50981.0539 | 140.004
Devonshire Building | 2017-09-26 08:15 | 50981.0839 | 119.988
Devonshire Building | 2017-09-26 08:30 | 50981.3139 | 920.016
Devonshire Building | 2017-09-26 08:45 | 50981.6689 | 1419.984
Devonshire Building | 2017-09-26 09:00 | 50981.7089 | 159.984
Devonshire Building | 2017-09-26 09:15 | 50981.7489 | 159.984
Devonshire Building | 2017-09-26 09:30 | 50981.7939 | 180
Devonshire Building | 2017-09-26 09:45 | 50981.8439 | 200.016
Devonshire Building | 2017-09-26 10:00 | 50982.4839 | 2559.996
Devonshire Building | 2017-09-26 10:15 | 50982.5489 | 259.992
Devonshire Building | 2017-09-26 10:30 | 50982.6039 | 219.996
Devonshire Building | 2017-09-26 10:45 | 50982.6589 | 219.996
Devonshire Building | 2017-09-26 11:00 | 50982.7089 | 200.016
Devonshire Building | 2017-09-26 11:15 | 50982.7639 | 219.996
Devonshire Building | 2017-09-26 11:30 | 50982.8089 | 180
Devonshire Building | 2017-09-26 11:45 | 50983.3939 | 2340
Devonshire Building | 2017-09-26 12:00 | 50983.4489 | 219.996
Devonshire Building | 2017-09-26 12:15 | 50983.5289 | 320.004
Devonshire Building | 2017-09-26 12:30 | 50983.6239 | 380.016
Devonshire Building | 2017-09-26 12:45 | 50983.7289 | 420.012
Devonshire Building | 2017-09-26 13:00 | 50983.8339 | 420.012
Devonshire Building | 2017-09-26 13:15 | 50984.424 | 2360.016
Devonshire Building | 2017-09-26 13:30 | 50984.494 | 280.008
Devonshire Building | 2017-09-26 13:45 | 50984.559 | 259.992
Devonshire Building | 2017-09-26 14:00 | 50984.624 | 259.992
Devonshire Building | 2017-09-26 14:15 | 50984.674 | 200.016
Devonshire Building | 2017-09-26 14:30 | 50984.719 | 180
Devonshire Building | 2017-09-26 14:45 | 50984.764 | 180
Devonshire Building | 2017-09-26 15:00 | 50985.339 | 2300.004
Devonshire Building | 2017-09-26 15:15 | 50985.389 | 200.016
Devonshire Building | 2017-09-26 15:30 | 50985.454 | 259.992
Devonshire Building | 2017-09-26 15:45 | 50985.529 | 299.988
Devonshire Building | 2017-09-26 16:00 | 50985.599 | 280.008
Devonshire Building | 2017-09-26 16:15 | 50985.664 | 259.992
Devonshire Building | 2017-09-26 16:30 | 50985.719 | 219.996
Devonshire Building | 2017-09-26 16:45 | 50986.144 | 1699.992
Devonshire Building | 2017-09-26 17:00 | 50986.334 | 759.996
Devonshire Building | 2017-09-26 17:15 | 50986.369 | 140.004
Devonshire Building | 2017-09-26 17:30 | 50986.4089 | 159.984
Devonshire Building | 2017-09-26 17:45 | 50986.4439 | 140.004
Devonshire Building | 2017-09-26 18:00 | 50986.4739 | 119.988
Devonshire Building | 2017-09-26 18:15 | 50986.4989 | 100.008
Devonshire Building | 2017-09-26 18:30 | 50986.5239 | 100.008
Devonshire Building | 2017-09-26 18:45 | 50986.549 | 100.008
Devonshire Building | 2017-09-26 19:00 | 50986.574 | 100.008
Devonshire Building | 2017-09-26 19:15 | 50986.594 | 79.992
Devonshire Building | 2017-09-26 19:30 | 50986.6139 | 79.992
Devonshire Building | 2017-09-26 19:45 | 50986.629 | 60.012
Devonshire Building | 2017-09-26 20:00 | 50986.649 | 79.992
Devonshire Building | 2017-09-26 20:15 | 50986.664 | 60.012
Devonshire Building | 2017-09-26 20:30 | 50986.679 | 60.012
Devonshire Building | 2017-09-26 20:45 | 50986.714 | 140.004
Devonshire Building | 2017-09-26 21:00 | 50986.719 | 20.016
Devonshire Building | 2017-09-26 21:15 | 50986.729 | 39.996
Devonshire Building | 2017-09-26 21:30 | 50986.739 | 39.996
Devonshire Building | 2017-09-26 21:45 | 50986.744 | 20.016
Devonshire Building | 2017-09-26 22:00 | 50986.754 | 39.996
Devonshire Building | 2017-09-26 22:15 | 50986.759 | 20.016
Devonshire Building | 2017-09-26 22:30 | 50986.769 | 39.996
Devonshire Building | 2017-09-26 22:45 | 50986.774 | 20.016
Devonshire Building | 2017-09-26 23:00 | 50986.784 | 39.996
Devonshire Building | 2017-09-26 23:15 | 50986.789 | 20.016
Devonshire Building | 2017-09-26 23:30 | 50986.799 | 39.996
Devonshire Building | 2017-09-26 23:45 | 50986.809 | 39.996
Devonshire Building | 2017-09-27 | 50986.8125 | 20.016
Devonshire Building | 2017-09-27 00:15 | 50986.8225 | 39.996
Devonshire Building | 2017-09-27 00:30 | 50986.8275 | 20.016
Devonshire Building | 2017-09-27 00:45 | 50986.8375 | 39.996
Devonshire Building | 2017-09-27 01:00 | 50986.8425 | 20.016
Devonshire Building | 2017-09-27 01:15 | 50986.8525 | 39.996
Devonshire Building | 2017-09-27 01:30 | 50986.8575 | 20.016
Devonshire Building | 2017-09-27 01:45 | 50986.8725 | 60.012
Devonshire Building | 2017-09-27 02:00 | 50987.0375 | 659.988
Devonshire Building | 2017-09-27 02:15 | 50987.4325 | 1580.004
Devonshire Building | 2017-09-27 02:30 | 50987.4575 | 100.008
Devonshire Building | 2017-09-27 02:45 | 50987.4775 | 79.992
Devonshire Building | 2017-09-27 03:00 | 50987.5025 | 100.008
Devonshire Building | 2017-09-27 03:15 | 50987.5275 | 100.008
Devonshire Building | 2017-09-27 03:30 | 50987.5525 | 100.008
Devonshire Building | 2017-09-27 03:45 | 50987.5725 | 79.992
Devonshire Building | 2017-09-27 04:00 | 50987.5775 | 20.016
Devonshire Building | 2017-09-27 04:15 | 50987.5875 | 39.996
Devonshire Building | 2017-09-27 04:30 | 50987.5925 | 20.016
Devonshire Building | 2017-09-27 04:45 | 50987.5975 | 20.016
Devonshire Building | 2017-09-27 05:00 | 50987.6075 | 39.996
Devonshire Building | 2017-09-27 05:15 | 50987.6125 | 20.016
Devonshire Building | 2017-09-27 05:30 | 50987.6225 | 39.996
Devonshire Building | 2017-09-27 05:45 | 50987.6325 | 39.996
Devonshire Building | 2017-09-27 06:00 | 50987.6475 | 60.012
Devonshire Building | 2017-09-27 06:15 | 50987.6575 | 39.996
Devonshire Building | 2017-09-27 06:30 | 50987.6675 | 39.996
Devonshire Building | 2017-09-27 06:45 | 50987.6775 | 39.996
Devonshire Building | 2017-09-27 07:00 | 50987.6925 | 60.012
Devonshire Building | 2017-09-27 07:15 | 50987.7075 | 60.012
Devonshire Building | 2017-09-27 07:30 | 50987.7225 | 60.012
Devonshire Building | 2017-09-27 07:45 | 50987.7725 | 200.016
Devonshire Building | 2017-09-27 08:00 | 50988.2925 | 2080.008
Devonshire Building | 2017-09-27 08:15 | 50988.3225 | 119.988
Devonshire Building | 2017-09-27 08:30 | 50988.3575 | 140.004
Devonshire Building | 2017-09-27 08:45 | 50988.3925 | 140.004
Devonshire Building | 2017-09-27 09:00 | 50988.4225 | 119.988
Devonshire Building | 2017-09-27 09:15 | 50988.4575 | 140.004
Devonshire Building | 2017-09-27 09:30 | 50988.6975 | 960.012
Devonshire Building | 2017-09-27 09:45 | 50989.1375 | 1760.004
Devonshire Building | 2017-09-27 10:00 | 50989.1775 | 159.984
Devonshire Building | 2017-09-27 10:15 | 50989.2175 | 159.984
Devonshire Building | 2017-09-27 10:30 | 50989.2575 | 159.984
Devonshire Building | 2017-09-27 10:45 | 50989.2975 | 159.984
Devonshire Building | 2017-09-27 11:00 | 50989.8925 | 2379.996
Devonshire Building | 2017-09-27 11:15 | 50989.9575 | 259.992
Devonshire Building | 2017-09-27 11:30 | 50990.0275 | 280.008
Devonshire Building | 2017-09-27 11:45 | 50990.0975 | 280.008
Devonshire Building | 2017-09-27 12:00 | 50990.1675 | 280.008
Devonshire Building | 2017-09-27 12:15 | 50990.2325 | 259.992
Devonshire Building | 2017-09-27 12:30 | 50990.8325 | 2400.012
Devonshire Building | 2017-09-27 12:45 | 50990.8975 | 259.992
Devonshire Building | 2017-09-27 13:00 | 50990.9625 | 259.992
Devonshire Building | 2017-09-27 13:15 | 50991.0225 | 240.012
Devonshire Building | 2017-09-27 13:30 | 50991.0875 | 259.992
Devonshire Building | 2017-09-27 13:45 | 50991.2375 | 600.012
Devonshire Building | 2017-09-27 14:00 | 50991.7275 | 1959.984
Devonshire Building | 2017-09-27 14:15 | 50991.7675 | 159.984
Devonshire Building | 2017-09-27 14:30 | 50991.8125 | 180
Devonshire Building | 2017-09-27 14:45 | 50991.8525 | 159.984
Devonshire Building | 2017-09-27 15:00 | 50991.8925 | 159.984
Devonshire Building | 2017-09-27 15:15 | 50991.9275 | 140.004
Devonshire Building | 2017-09-27 15:30 | 50992.0225 | 380.016
Devonshire Building | 2017-09-27 15:45 | 50992.5275 | 2019.996
Devonshire Building | 2017-09-27 16:00 | 50992.5525 | 100.008
Devonshire Building | 2017-09-27 16:15 | 50992.5775 | 100.008
Devonshire Building | 2017-09-27 16:30 | 50992.6025 | 100.008
Devonshire Building | 2017-09-27 16:45 | 50992.6275 | 100.008
Devonshire Building | 2017-09-27 17:00 | 50992.6525 | 100.008
Devonshire Building | 2017-09-27 17:15 | 50992.6775 | 100.008
Devonshire Building | 2017-09-27 17:30 | 50992.7075 | 119.988
Devonshire Building | 2017-09-27 17:45 | 50992.7325 | 100.008
Devonshire Building | 2017-09-27 18:00 | 50992.7525 | 79.992
Devonshire Building | 2017-09-27 18:15 | 50992.7725 | 79.992
Devonshire Building | 2017-09-27 18:30 | 50992.7925 | 79.992
Devonshire Building | 2017-09-27 18:45 | 50992.8125 | 79.992
Devonshire Building | 2017-09-27 19:00 | 50992.8325 | 79.992
Devonshire Building | 2017-09-27 19:15 | 50992.8475 | 60.012
Devonshire Building | 2017-09-27 19:30 | 50992.8675 | 79.992
Devonshire Building | 2017-09-27 19:45 | 50992.8825 | 60.012
Devonshire Building | 2017-09-27 20:00 | 50992.9025 | 79.992
Devonshire Building | 2017-09-27 20:15 | 50992.9175 | 60.012
Devonshire Building | 2017-09-27 20:30 | 50993.2325 | 1260
Devonshire Building | 2017-09-27 20:45 | 50993.4525 | 879.984
Devonshire Building | 2017-09-27 21:00 | 50993.4625 | 39.996
Devonshire Building | 2017-09-27 21:15 | 50993.4725 | 39.996
Devonshire Building | 2017-09-27 21:30 | 50993.4775 | 20.016
Devonshire Building | 2017-09-27 21:45 | 50993.4875 | 39.996
Devonshire Building | 2017-09-27 22:00 | 50993.4975 | 39.996
Devonshire Building | 2017-09-27 22:15 | 50993.5075 | 39.996
Devonshire Building | 2017-09-27 22:30 | 50993.5125 | 20.016
Devonshire Building | 2017-09-27 22:45 | 50993.5225 | 39.996
Devonshire Building | 2017-09-27 23:00 | 50993.5325 | 39.996
Devonshire Building | 2017-09-27 23:15 | 50993.5425 | 39.996
Devonshire Building | 2017-09-27 23:30 | 50993.5525 | 39.996
Devonshire Building | 2017-09-27 23:45 | 50993.5625 | 39.996
Devonshire Building | 2017-09-28 | 50993.5742 | 39.996
Devonshire Building | 2017-09-28 00:15 | 50993.5842 | 39.996
Devonshire Building | 2017-09-28 00:30 | 50993.5942 | 39.996
Devonshire Building | 2017-09-28 00:45 | 50993.6042 | 39.996
Devonshire Building | 2017-09-28 01:00 | 50993.6142 | 39.996
Devonshire Building | 2017-09-28 01:15 | 50993.6242 | 39.996
Devonshire Building | 2017-09-28 01:30 | 50993.6392 | 60.012
Devonshire Building | 2017-09-28 01:45 | 50993.6642 | 100.008
Devonshire Building | 2017-09-28 02:00 | 50993.6892 | 100.008
Devonshire Building | 2017-09-28 02:15 | 50993.7142 | 100.008
Devonshire Building | 2017-09-28 02:30 | 50993.7392 | 100.008
Devonshire Building | 2017-09-28 02:45 | 50993.7692 | 119.988
Devonshire Building | 2017-09-28 03:00 | 50993.7942 | 100.008
Devonshire Building | 2017-09-28 03:15 | 50993.8192 | 100.008
Devonshire Building | 2017-09-28 03:30 | 50993.8442 | 100.008
Devonshire Building | 2017-09-28 03:45 | 50993.8642 | 79.992
Devonshire Building | 2017-09-28 04:00 | 50993.8792 | 60.012
Devonshire Building | 2017-09-28 04:15 | 50993.8842 | 20.016
Devonshire Building | 2017-09-28 04:30 | 50993.8942 | 39.996
Devonshire Building | 2017-09-28 04:45 | 50993.9042 | 39.996
Devonshire Building | 2017-09-28 05:00 | 50993.9142 | 39.996
Devonshire Building | 2017-09-28 05:15 | 50993.9192 | 20.016
Devonshire Building | 2017-09-28 05:30 | 50993.9292 | 39.996
Devonshire Building | 2017-09-28 05:45 | 50994.3942 | 1860.012
Devonshire Building | 2017-09-28 06:00 | 50994.4492 | 219.996
Devonshire Building | 2017-09-28 06:15 | 50994.4642 | 60.012
Devonshire Building | 2017-09-28 06:30 | 50994.4742 | 39.996
Devonshire Building | 2017-09-28 06:45 | 50994.4842 | 39.996
Devonshire Building | 2017-09-28 07:00 | 50994.5042 | 79.992
Devonshire Building | 2017-09-28 07:15 | 50994.5142 | 39.996
Devonshire Building | 2017-09-28 07:30 | 50994.5292 | 60.012
Devonshire Building | 2017-09-28 07:45 | 50994.5492 | 79.992
Devonshire Building | 2017-09-28 08:00 | 50994.5742 | 100.008
Devonshire Building | 2017-09-28 08:15 | 50994.5942 | 79.992
Devonshire Building | 2017-09-28 08:30 | 50994.6442 | 200.016
Devonshire Building | 2017-09-28 08:45 | 50994.7942 | 600.012
Devonshire Building | 2017-09-28 09:00 | 50995.3592 | 2260.008
Devonshire Building | 2017-09-28 09:15 | 50995.6342 | 1100.016
Devonshire Building | 2017-09-28 09:30 | 50995.7692 | 540
Devonshire Building | 2017-09-28 09:45 | 50995.8743 | 420.012
Devonshire Building | 2017-09-28 10:00 | 50996.2343 | 1440
Devonshire Building | 2017-09-28 10:15 | 50996.5393 | 1220.004
Devonshire Building | 2017-09-28 10:30 | 50996.6042 | 259.992
Devonshire Building | 2017-09-28 10:45 | 50996.6692 | 259.992
Devonshire Building | 2017-09-28 11:00 | 50996.7342 | 259.992
Devonshire Building | 2017-09-28 11:15 | 50996.8042 | 280.008
Devonshire Building | 2017-09-28 11:30 | 50997.4292 | 2499.984
Devonshire Building | 2017-09-28 11:45 | 50997.5142 | 339.984
Devonshire Building | 2017-09-28 12:00 | 50997.5992 | 339.984
Devonshire Building | 2017-09-28 12:15 | 50997.6742 | 299.988
Devonshire Building | 2017-09-28 12:30 | 50997.7442 | 280.008
Devonshire Building | 2017-09-28 12:45 | 50997.8192 | 299.988
Devonshire Building | 2017-09-28 13:00 | 50998.4492 | 2520
Devonshire Building | 2017-09-28 13:15 | 50998.5242 | 299.988
Devonshire Building | 2017-09-28 13:30 | 50998.5992 | 299.988
Devonshire Building | 2017-09-28 13:45 | 50998.6792 | 320.004
Devonshire Building | 2017-09-28 14:00 | 50998.7542 | 299.988
Devonshire Building | 2017-09-28 14:15 | 50998.8292 | 299.988
Devonshire Building | 2017-09-28 14:30 | 50998.8942 | 259.992
Devonshire Building | 2017-09-28 14:45 | 50998.9992 | 420.012
Devonshire Building | 2017-09-28 15:00 | 50999.5392 | 2160
Devonshire Building | 2017-09-28 15:15 | 50999.5742 | 140.004
Devonshire Building | 2017-09-28 15:30 | 50999.6092 | 140.004
Devonshire Building | 2017-09-28 15:45 | 50999.6442 | 140.004
Devonshire Building | 2017-09-28 16:00 | 50999.6842 | 159.984
Devonshire Building | 2017-09-28 16:15 | 50999.7192 | 140.004
Devonshire Building | 2017-09-28 16:30 | 50999.9692 | 1000.008
Devonshire Building | 2017-09-28 16:45 | 51000.3042 | 1339.992
Devonshire Building | 2017-09-28 17:00 | 51000.3242 | 79.992
Devonshire Building | 2017-09-28 17:15 | 51000.3442 | 79.992
Devonshire Building | 2017-09-28 17:30 | 51000.3592 | 60.012
Devonshire Building | 2017-09-28 17:45 | 51000.3792 | 79.992
Devonshire Building | 2017-09-28 18:00 | 51000.3942 | 60.012
Devonshire Building | 2017-09-28 18:15 | 51000.4142 | 79.992
Devonshire Building | 2017-09-28 18:30 | 51000.4292 | 60.012
Devonshire Building | 2017-09-28 18:45 | 51000.4492 | 79.992
Devonshire Building | 2017-09-28 19:00 | 51000.4642 | 60.012
Devonshire Building | 2017-09-28 19:15 | 51000.4842 | 79.992
Devonshire Building | 2017-09-28 19:30 | 51000.4992 | 60.012
Devonshire Building | 2017-09-28 19:45 | 51000.5142 | 60.012
Devonshire Building | 2017-09-28 20:00 | 51000.5342 | 79.992
Devonshire Building | 2017-09-28 20:15 | 51000.5492 | 60.012
Devonshire Building | 2017-09-28 20:30 | 51000.5642 | 60.012
Devonshire Building | 2017-09-28 20:45 | 51000.5942 | 119.988
Devonshire Building | 2017-09-28 21:00 | 51000.6042 | 39.996
Devonshire Building | 2017-09-28 21:15 | 51000.6192 | 60.012
Devonshire Building | 2017-09-28 21:30 | 51000.6292 | 39.996
Devonshire Building | 2017-09-28 21:45 | 51000.6392 | 39.996
Devonshire Building | 2017-09-28 22:00 | 51000.6492 | 39.996
Devonshire Building | 2017-09-28 22:15 | 51000.6592 | 39.996
Devonshire Building | 2017-09-28 22:30 | 51000.6692 | 39.996
Devonshire Building | 2017-09-28 22:45 | 51000.6792 | 39.996
Devonshire Building | 2017-09-28 23:00 | 51000.6942 | 60.012
Devonshire Building | 2017-09-28 23:15 | 51000.7042 | 39.996
Devonshire Building | 2017-09-28 23:30 | 51000.7142 | 39.996
Devonshire Building | 2017-09-28 23:45 | 51000.7242 | 39.996
Devonshire Building | 2017-09-29 | 51000.7344 | 39.996
Devonshire Building | 2017-09-29 00:15 | 51000.7444 | 39.996
Devonshire Building | 2017-09-29 00:30 | 51000.7544 | 39.996
Devonshire Building | 2017-09-29 00:45 | 51000.7644 | 39.996
Devonshire Building | 2017-09-29 01:00 | 51000.7744 | 39.996
Devonshire Building | 2017-09-29 01:15 | 51000.7844 | 39.996
Devonshire Building | 2017-09-29 01:30 | 51000.7944 | 39.996
Devonshire Building | 2017-09-29 01:45 | 51000.8194 | 100.008
Devonshire Building | 2017-09-29 02:00 | 51001.3544 | 2139.984
Devonshire Building | 2017-09-29 02:15 | 51001.3794 | 100.008
Devonshire Building | 2017-09-29 02:30 | 51001.4044 | 100.008
Devonshire Building | 2017-09-29 02:45 | 51001.4294 | 100.008
Devonshire Building | 2017-09-29 03:00 | 51001.4544 | 100.008
Devonshire Building | 2017-09-29 03:15 | 51001.4794 | 100.008
Devonshire Building | 2017-09-29 03:30 | 51001.5044 | 100.008
Devonshire Building | 2017-09-29 03:45 | 51001.5344 | 119.988
Devonshire Building | 2017-09-29 04:00 | 51001.5494 | 60.012
Devonshire Building | 2017-09-29 04:15 | 51001.5594 | 39.996
Devonshire Building | 2017-09-29 04:30 | 51001.5694 | 39.996
Devonshire Building | 2017-09-29 04:45 | 51001.5794 | 39.996
Devonshire Building | 2017-09-29 05:00 | 51001.5944 | 60.012
Devonshire Building | 2017-09-29 05:15 | 51001.6044 | 39.996
Devonshire Building | 2017-09-29 05:30 | 51001.6144 | 39.996
Devonshire Building | 2017-09-29 05:45 | 51001.6294 | 60.012
Devonshire Building | 2017-09-29 06:00 | 51001.6394 | 39.996
Devonshire Building | 2017-09-29 06:15 | 51001.6544 | 60.012
Devonshire Building | 2017-09-29 06:30 | 51001.6644 | 39.996
Devonshire Building | 2017-09-29 06:45 | 51001.6794 | 60.012
Devonshire Building | 2017-09-29 07:00 | 51001.6894 | 39.996
Devonshire Building | 2017-09-29 07:15 | 51001.6994 | 39.996
Devonshire Building | 2017-09-29 07:30 | 51001.7194 | 79.992
Devonshire Building | 2017-09-29 07:45 | 51001.7444 | 100.008
Devonshire Building | 2017-09-29 08:00 | 51002.2994 | 2220.012
Devonshire Building | 2017-09-29 08:15 | 51002.3094 | 39.996
Devonshire Building | 2017-09-29 08:30 | 51002.3294 | 79.992
Devonshire Building | 2017-09-29 08:45 | 51002.3494 | 79.992
Devonshire Building | 2017-09-29 09:00 | 51002.3644 | 60.012
Devonshire Building | 2017-09-29 09:15 | 51002.3844 | 79.992
Devonshire Building | 2017-09-29 09:30 | 51002.4394 | 219.996
Devonshire Building | 2017-09-29 09:45 | 51002.9644 | 2099.988
Devonshire Building | 2017-09-29 10:00 | 51002.9944 | 119.988
Devonshire Building | 2017-09-29 10:15 | 51003.0244 | 119.988
Devonshire Building | 2017-09-29 10:30 | 51003.0544 | 119.988
Devonshire Building | 2017-09-29 10:45 | 51003.0894 | 140.004
Devonshire Building | 2017-09-29 11:00 | 51003.1244 | 140.004
Devonshire Building | 2017-09-29 11:15 | 51003.5144 | 1559.988
Devonshire Building | 2017-09-29 11:30 | 51003.7244 | 839.988
Devonshire Building | 2017-09-29 11:45 | 51003.7544 | 119.988
Devonshire Building | 2017-09-29 12:00 | 51003.7894 | 140.004
Devonshire Building | 2017-09-29 12:15 | 51003.8194 | 119.988
Devonshire Building | 2017-09-29 12:30 | 51003.8494 | 119.988
Devonshire Building | 2017-09-29 12:45 | 51003.8744 | 100.008
Devonshire Building | 2017-09-29 13:00 | 51003.9044 | 119.988
Devonshire Building | 2017-09-29 13:15 | 51004.2644 | 1440
Devonshire Building | 2017-09-29 13:30 | 51004.4544 | 759.996
Devonshire Building | 2017-09-29 13:45 | 51004.4844 | 119.988
Devonshire Building | 2017-09-29 14:00 | 51004.5094 | 100.008
Devonshire Building | 2017-09-29 14:15 | 51004.5344 | 100.008
Devonshire Building | 2017-09-29 14:30 | 51004.5594 | 100.008
Devonshire Building | 2017-09-29 14:45 | 51004.5844 | 100.008
Devonshire Building | 2017-09-29 15:00 | 51004.6094 | 100.008
Devonshire Building | 2017-09-29 15:15 | 51004.7444 | 540
Devonshire Building | 2017-09-29 15:30 | 51005.1894 | 1779.984
Devonshire Building | 2017-09-29 15:45 | 51005.2044 | 60.012
Devonshire Building | 2017-09-29 16:00 | 51005.2244 | 79.992
Devonshire Building | 2017-09-29 16:15 | 51005.2444 | 79.992
Devonshire Building | 2017-09-29 16:30 | 51005.2644 | 79.992
Devonshire Building | 2017-09-29 16:45 | 51005.2844 | 79.992
Devonshire Building | 2017-09-29 17:00 | 51005.3044 | 79.992
Devonshire Building | 2017-09-29 17:15 | 51005.3244 | 79.992
Devonshire Building | 2017-09-29 17:30 | 51005.3444 | 79.992
Devonshire Building | 2017-09-29 17:45 | 51005.3643 | 79.992
Devonshire Building | 2017-09-29 18:00 | 51005.3794 | 60.012
Devonshire Building | 2017-09-29 18:15 | 51005.3993 | 79.992
Devonshire Building | 2017-09-29 18:30 | 51005.4144 | 60.012
Devonshire Building | 2017-09-29 18:45 | 51005.4344 | 79.992
Devonshire Building | 2017-09-29 19:00 | 51005.4494 | 60.012
Devonshire Building | 2017-09-29 19:15 | 51005.4644 | 60.012
Devonshire Building | 2017-09-29 19:30 | 51005.4894 | 100.008
Devonshire Building | 2017-09-29 19:45 | 51006.0194 | 2120.004
Devonshire Building | 2017-09-29 20:00 | 51006.0444 | 100.008
Devonshire Building | 2017-09-29 20:15 | 51006.0744 | 119.988
Devonshire Building | 2017-09-29 20:30 | 51006.1044 | 119.988
Devonshire Building | 2017-09-29 20:45 | 51006.1394 | 140.004
Devonshire Building | 2017-09-29 21:00 | 51006.1644 | 100.008
Devonshire Building | 2017-09-29 21:15 | 51006.1944 | 119.988
Devonshire Building | 2017-09-29 21:30 | 51006.2194 | 100.008
Devonshire Building | 2017-09-29 21:45 | 51006.2494 | 119.988
Devonshire Building | 2017-09-29 22:00 | 51006.2644 | 60.012
Devonshire Building | 2017-09-29 22:15 | 51006.2744 | 39.996
Devonshire Building | 2017-09-29 22:30 | 51006.2894 | 60.012
Devonshire Building | 2017-09-29 22:45 | 51006.3044 | 60.012
Devonshire Building | 2017-09-29 23:00 | 51006.3194 | 60.012
Devonshire Building | 2017-09-29 23:15 | 51006.3344 | 60.012
Devonshire Building | 2017-09-29 23:30 | 51006.3444 | 39.996
Devonshire Building | 2017-09-29 23:45 | 51006.3594 | 60.012
Devonshire Building | 2017-09-30 | 51006.3672 | 39.996
Devonshire Building | 2017-09-30 00:15 | 51006.3822 | 60.012
Devonshire Building | 2017-09-30 00:30 | 51006.3972 | 60.012
Devonshire Building | 2017-09-30 00:45 | 51006.4072 | 39.996
Devonshire Building | 2017-09-30 01:00 | 51006.4172 | 39.996
Devonshire Building | 2017-09-30 01:15 | 51006.4322 | 60.012
Devonshire Building | 2017-09-30 01:30 | 51006.4422 | 39.996
Devonshire Building | 2017-09-30 01:45 | 51006.4572 | 60.012
Devonshire Building | 2017-09-30 02:00 | 51006.4672 | 39.996
Devonshire Building | 2017-09-30 02:15 | 51006.4772 | 39.996
Devonshire Building | 2017-09-30 02:30 | 51006.4922 | 60.012
Devonshire Building | 2017-09-30 02:45 | 51006.5022 | 39.996
Devonshire Building | 2017-09-30 03:00 | 51006.5122 | 39.996
Devonshire Building | 2017-09-30 03:15 | 51006.5222 | 39.996
Devonshire Building | 2017-09-30 03:30 | 51006.5372 | 60.012
Devonshire Building | 2017-09-30 03:45 | 51006.5472 | 39.996
Devonshire Building | 2017-09-30 04:00 | 51006.5572 | 39.996
Devonshire Building | 2017-09-30 04:15 | 51006.5672 | 39.996
Devonshire Building | 2017-09-30 04:30 | 51006.5772 | 39.996
Devonshire Building | 2017-09-30 04:45 | 51006.5922 | 60.012
Devonshire Building | 2017-09-30 05:00 | 51006.6022 | 39.996
Devonshire Building | 2017-09-30 05:15 | 51006.6122 | 39.996
Devonshire Building | 2017-09-30 05:30 | 51007.1222 | 2040.012
Devonshire Building | 2017-09-30 05:45 | 51007.1322 | 39.996
Devonshire Building | 2017-09-30 06:00 | 51007.1422 | 39.996
Devonshire Building | 2017-09-30 06:15 | 51007.1522 | 39.996
Devonshire Building | 2017-09-30 06:30 | 51007.1622 | 39.996
Devonshire Building | 2017-09-30 06:45 | 51007.1722 | 39.996
Devonshire Building | 2017-09-30 07:00 | 51007.1822 | 39.996
Devonshire Building | 2017-09-30 07:15 | 51007.1872 | 20.016
Devonshire Building | 2017-09-30 07:30 | 51007.1972 | 39.996
Devonshire Building | 2017-09-30 07:45 | 51007.2072 | 39.996
Devonshire Building | 2017-09-30 08:00 | 51007.2172 | 39.996
Devonshire Building | 2017-09-30 08:15 | 51007.2272 | 39.996
Devonshire Building | 2017-09-30 08:30 | 51007.2422 | 60.012
Devonshire Building | 2017-09-30 08:45 | 51007.2522 | 39.996
Devonshire Building | 2017-09-30 09:00 | 51007.2622 | 39.996
Devonshire Building | 2017-09-30 09:15 | 51007.2722 | 39.996
Devonshire Building | 2017-09-30 09:30 | 51007.2872 | 60.012
Devonshire Building | 2017-09-30 09:45 | 51007.2972 | 39.996
Devonshire Building | 2017-09-30 10:00 | 51007.3072 | 39.996
Devonshire Building | 2017-09-30 10:15 | 51007.3172 | 39.996
Devonshire Building | 2017-09-30 10:30 | 51007.3322 | 60.012
Devonshire Building | 2017-09-30 10:45 | 51007.3422 | 39.996
Devonshire Building | 2017-09-30 11:00 | 51007.3522 | 39.996
Devonshire Building | 2017-09-30 11:15 | 51007.3622 | 39.996
Devonshire Building | 2017-09-30 11:30 | 51007.3722 | 39.996
Devonshire Building | 2017-09-30 11:45 | 51007.3822 | 39.996
Devonshire Building | 2017-09-30 12:00 | 51007.3922 | 39.996
Devonshire Building | 2017-09-30 12:15 | 51007.4022 | 39.996
Devonshire Building | 2017-09-30 12:30 | 51007.4122 | 39.996
Devonshire Building | 2017-09-30 12:45 | 51007.4272 | 60.012
Devonshire Building | 2017-09-30 13:00 | 51007.9322 | 2019.996
Devonshire Building | 2017-09-30 13:15 | 51007.9472 | 60.012
Devonshire Building | 2017-09-30 13:30 | 51007.9572 | 39.996
Devonshire Building | 2017-09-30 13:45 | 51007.9672 | 39.996
Devonshire Building | 2017-09-30 14:00 | 51007.9822 | 60.012
Devonshire Building | 2017-09-30 14:15 | 51007.9922 | 39.996
Devonshire Building | 2017-09-30 14:30 | 51008.0022 | 39.996
Devonshire Building | 2017-09-30 14:45 | 51008.0122 | 39.996
Devonshire Building | 2017-09-30 15:00 | 51008.0272 | 60.012
Devonshire Building | 2017-09-30 15:15 | 51008.0372 | 39.996
Devonshire Building | 2017-09-30 15:30 | 51008.0472 | 39.996
Devonshire Building | 2017-09-30 15:45 | 51008.0622 | 60.012
Devonshire Building | 2017-09-30 16:00 | 51008.0772 | 60.012
Devonshire Building | 2017-09-30 16:15 | 51008.0922 | 60.012
Devonshire Building | 2017-09-30 16:30 | 51008.1022 | 39.996
Devonshire Building | 2017-09-30 16:45 | 51008.1172 | 60.012
Devonshire Building | 2017-09-30 17:00 | 51008.1322 | 60.012
Devonshire Building | 2017-09-30 17:15 | 51008.1422 | 39.996
Devonshire Building | 2017-09-30 17:30 | 51008.1572 | 60.012
Devonshire Building | 2017-09-30 17:45 | 51008.1672 | 39.996
Devonshire Building | 2017-09-30 18:00 | 51008.1822 | 60.012
Devonshire Building | 2017-09-30 18:15 | 51008.1972 | 60.012
Devonshire Building | 2017-09-30 18:30 | 51008.2072 | 39.996
Devonshire Building | 2017-09-30 18:45 | 51008.2172 | 39.996
Devonshire Building | 2017-09-30 19:00 | 51008.2322 | 60.012
Devonshire Building | 2017-09-30 19:15 | 51008.2422 | 39.996
Devonshire Building | 2017-09-30 19:30 | 51008.2572 | 60.012
Devonshire Building | 2017-09-30 19:45 | 51008.2822 | 100.008
Devonshire Building | 2017-09-30 20:00 | 51008.3122 | 119.988
Devonshire Building | 2017-09-30 20:15 | 51008.3372 | 100.008
Devonshire Building | 2017-09-30 20:30 | 51008.3672 | 119.988
Devonshire Building | 2017-09-30 20:45 | 51008.4172 | 200.016
Devonshire Building | 2017-09-30 21:00 | 51008.4472 | 119.988
Devonshire Building | 2017-09-30 21:15 | 51008.4722 | 100.008
Devonshire Building | 2017-09-30 21:30 | 51008.5022 | 119.988
Devonshire Building | 2017-09-30 21:45 | 51008.5322 | 119.988
Devonshire Building | 2017-09-30 22:00 | 51008.5472 | 60.012
Devonshire Building | 2017-09-30 22:15 | 51008.5572 | 39.996
Devonshire Building | 2017-09-30 22:30 | 51009.0772 | 2080.008
Devonshire Building | 2017-09-30 22:45 | 51009.0872 | 39.996
Devonshire Building | 2017-09-30 23:00 | 51009.0972 | 39.996
Devonshire Building | 2017-09-30 23:15 | 51009.1122 | 60.012
Devonshire Building | 2017-09-30 23:30 | 51009.1222 | 39.996
Devonshire Building | 2017-09-30 23:45 | 51009.1322 | 39.996
Devonshire Building | 2017-10-01 | 51009.1484 | 60.012
Devonshire Building | 2017-10-01 00:15 | 51009.1584 | 39.996
Devonshire Building | 2017-10-01 00:30 | 51009.1734 | 60.012
Devonshire Building | 2017-10-01 00:45 | 51009.1884 | 60.012
Devonshire Building | 2017-10-01 01:00 | 51009.2034 | 60.012
Devonshire Building | 2017-10-01 01:15 | 51009.2185 | 60.012
Devonshire Building | 2017-10-01 01:30 | 51009.2335 | 60.012
Devonshire Building | 2017-10-01 01:45 | 51009.2485 | 60.012
Devonshire Building | 2017-10-01 02:00 | 51009.2635 | 60.012
Devonshire Building | 2017-10-01 02:15 | 51009.2785 | 60.012
Devonshire Building | 2017-10-01 02:30 | 51009.2935 | 60.012
Devonshire Building | 2017-10-01 02:45 | 51009.3085 | 60.012
Devonshire Building | 2017-10-01 03:00 | 51009.3235 | 60.012
Devonshire Building | 2017-10-01 03:15 | 51009.3385 | 60.012
Devonshire Building | 2017-10-01 03:30 | 51009.3535 | 60.012
Devonshire Building | 2017-10-01 03:45 | 51009.3635 | 39.996
Devonshire Building | 2017-10-01 04:00 | 51009.3785 | 60.012
Devonshire Building | 2017-10-01 04:15 | 51009.3935 | 60.012
Devonshire Building | 2017-10-01 04:30 | 51009.4085 | 60.012
Devonshire Building | 2017-10-01 04:45 | 51009.4185 | 39.996
Devonshire Building | 2017-10-01 05:00 | 51009.4335 | 60.012
Devonshire Building | 2017-10-01 05:15 | 51009.4435 | 39.996
Devonshire Building | 2017-10-01 05:30 | 51009.4585 | 60.012
Devonshire Building | 2017-10-01 05:45 | 51009.4685 | 39.996
Devonshire Building | 2017-10-01 06:00 | 51009.4835 | 60.012
Devonshire Building | 2017-10-01 06:15 | 51009.4935 | 39.996
Devonshire Building | 2017-10-01 06:30 | 51009.5085 | 60.012
Devonshire Building | 2017-10-01 06:45 | 51009.5185 | 39.996
Devonshire Building | 2017-10-01 07:00 | 51009.5335 | 60.012
Devonshire Building | 2017-10-01 07:15 | 51009.5435 | 39.996
Devonshire Building | 2017-10-01 07:30 | 51009.5535 | 39.996
Devonshire Building | 2017-10-01 07:45 | 51009.9035 | 1400.004
Devonshire Building | 2017-10-01 08:00 | 51010.0785 | 699.984
Devonshire Building | 2017-10-01 08:15 | 51010.0885 | 39.996
Devonshire Building | 2017-10-01 08:30 | 51010.0985 | 39.996
Devonshire Building | 2017-10-01 08:45 | 51010.1135 | 60.012
Devonshire Building | 2017-10-01 09:00 | 51010.1235 | 39.996
Devonshire Building | 2017-10-01 09:15 | 51010.1335 | 39.996
Devonshire Building | 2017-10-01 09:30 | 51010.1435 | 39.996
Devonshire Building | 2017-10-01 09:45 | 51010.1535 | 39.996
Devonshire Building | 2017-10-01 10:00 | 51010.1635 | 39.996
Devonshire Building | 2017-10-01 10:15 | 51010.1735 | 39.996
Devonshire Building | 2017-10-01 10:30 | 51010.1835 | 39.996
Devonshire Building | 2017-10-01 10:45 | 51010.1985 | 60.012
Devonshire Building | 2017-10-01 11:00 | 51010.2085 | 39.996
Devonshire Building | 2017-10-01 11:15 | 51010.2235 | 60.012
Devonshire Building | 2017-10-01 11:30 | 51010.2335 | 39.996
Devonshire Building | 2017-10-01 11:45 | 51010.2485 | 60.012
Devonshire Building | 2017-10-01 12:00 | 51010.2585 | 39.996
Devonshire Building | 2017-10-01 12:15 | 51010.2735 | 60.012
Devonshire Building | 2017-10-01 12:30 | 51010.2835 | 39.996
Devonshire Building | 2017-10-01 12:45 | 51010.2985 | 60.012
Devonshire Building | 2017-10-01 13:00 | 51010.3085 | 39.996
Devonshire Building | 2017-10-01 13:15 | 51010.3185 | 39.996
Devonshire Building | 2017-10-01 13:30 | 51010.3335 | 60.012
Devonshire Building | 2017-10-01 13:45 | 51010.3435 | 39.996
Devonshire Building | 2017-10-01 14:00 | 51010.3535 | 39.996
Devonshire Building | 2017-10-01 14:15 | 51010.3635 | 39.996
Devonshire Building | 2017-10-01 14:30 | 51010.3785 | 60.012
Devonshire Building | 2017-10-01 14:45 | 51010.3885 | 39.996
Devonshire Building | 2017-10-01 15:00 | 51010.3985 | 39.996
Devonshire Building | 2017-10-01 15:15 | 51010.4135 | 60.012
Devonshire Building | 2017-10-01 15:30 | 51010.4235 | 39.996
Devonshire Building | 2017-10-01 15:45 | 51010.4335 | 39.996
Devonshire Building | 2017-10-01 16:00 | 51010.4485 | 60.012
Devonshire Building | 2017-10-01 16:15 | 51010.4585 | 39.996
Devonshire Building | 2017-10-01 16:30 | 51010.4735 | 60.012
Devonshire Building | 2017-10-01 16:45 | 51010.4835 | 39.996
Devonshire Building | 2017-10-01 17:00 | 51010.9885 | 2019.996
Devonshire Building | 2017-10-01 17:15 | 51010.9985 | 39.996
Devonshire Building | 2017-10-01 17:30 | 51011.0135 | 60.012
Devonshire Building | 2017-10-01 17:45 | 51011.0235 | 39.996
Devonshire Building | 2017-10-01 18:00 | 51011.0335 | 39.996
Devonshire Building | 2017-10-01 18:15 | 51011.0435 | 39.996
Devonshire Building | 2017-10-01 18:30 | 51011.0535 | 39.996
Devonshire Building | 2017-10-01 18:45 | 51011.0635 | 39.996
Devonshire Building | 2017-10-01 19:00 | 51011.0735 | 39.996
Devonshire Building | 2017-10-01 19:15 | 51011.0835 | 39.996
Devonshire Building | 2017-10-01 19:30 | 51011.0985 | 60.012
Devonshire Building | 2017-10-01 19:45 | 51011.1285 | 119.988
Devonshire Building | 2017-10-01 20:00 | 51011.1585 | 119.988
Devonshire Building | 2017-10-01 20:15 | 51011.1835 | 100.008
Devonshire Building | 2017-10-01 20:30 | 51011.2135 | 119.988
Devonshire Building | 2017-10-01 20:45 | 51011.2585 | 180
Devonshire Building | 2017-10-01 21:00 | 51011.2885 | 119.988
Devonshire Building | 2017-10-01 21:15 | 51011.3185 | 119.988
Devonshire Building | 2017-10-01 21:30 | 51011.3485 | 119.988
Devonshire Building | 2017-10-01 21:45 | 51011.3735 | 100.008
Devonshire Building | 2017-10-01 22:00 | 51011.3935 | 79.992
Devonshire Building | 2017-10-01 22:15 | 51011.4085 | 60.012
Devonshire Building | 2017-10-01 22:30 | 51011.4185 | 39.996
Devonshire Building | 2017-10-01 22:45 | 51011.4285 | 39.996
Devonshire Building | 2017-10-01 23:00 | 51011.4435 | 60.012
Devonshire Building | 2017-10-01 23:15 | 51011.4535 | 39.996
Devonshire Building | 2017-10-01 23:30 | 51011.4685 | 60.012
Devonshire Building | 2017-10-01 23:45 | 51011.4785 | 39.996
Devonshire Building | 2017-10-02 | 51011.4883 | 39.996
Devonshire Building | 2017-10-02 00:15 | 51011.5033 | 60.012
Devonshire Building | 2017-10-02 00:30 | 51011.5133 | 39.996
Devonshire Building | 2017-10-02 00:45 | 51011.5233 | 39.996
Devonshire Building | 2017-10-02 01:00 | 51011.5383 | 60.012
Devonshire Building | 2017-10-02 01:15 | 51011.5483 | 39.996
Devonshire Building | 2017-10-02 01:30 | 51011.5583 | 39.996
Devonshire Building | 2017-10-02 01:45 | 51011.5683 | 39.996
Devonshire Building | 2017-10-02 02:00 | 51011.5783 | 39.996
Devonshire Building | 2017-10-02 02:15 | 51012.0933 | 2059.992
Devonshire Building | 2017-10-02 02:30 | 51012.1033 | 39.996
Devonshire Building | 2017-10-02 02:45 | 51012.1133 | 39.996
Devonshire Building | 2017-10-02 03:00 | 51012.1233 | 39.996
Devonshire Building | 2017-10-02 03:15 | 51012.1333 | 39.996
Devonshire Building | 2017-10-02 03:30 | 51012.1433 | 39.996
Devonshire Building | 2017-10-02 03:45 | 51012.1533 | 39.996
Devonshire Building | 2017-10-02 04:00 | 51012.1633 | 39.996
Devonshire Building | 2017-10-02 04:15 | 51012.1783 | 60.012
Devonshire Building | 2017-10-02 04:30 | 51012.1883 | 39.996
Devonshire Building | 2017-10-02 04:45 | 51012.1983 | 39.996
Devonshire Building | 2017-10-02 05:00 | 51012.2133 | 60.012
Devonshire Building | 2017-10-02 05:15 | 51012.2283 | 60.012
Devonshire Building | 2017-10-02 05:30 | 51012.2383 | 39.996
Devonshire Building | 2017-10-02 05:45 | 51012.2533 | 60.012
Devonshire Building | 2017-10-02 06:00 | 51012.2683 | 60.012
Devonshire Building | 2017-10-02 06:15 | 51012.2833 | 60.012
Devonshire Building | 2017-10-02 06:30 | 51012.2933 | 39.996
Devonshire Building | 2017-10-02 06:45 | 51012.3083 | 60.012
Devonshire Building | 2017-10-02 07:00 | 51012.3433 | 140.004
Devonshire Building | 2017-10-02 07:15 | 51012.3633 | 79.992
Devonshire Building | 2017-10-02 07:30 | 51012.3783 | 60.012
Devonshire Building | 2017-10-02 07:45 | 51012.4333 | 219.996
Devonshire Building | 2017-10-02 08:00 | 51012.9733 | 2160
Devonshire Building | 2017-10-02 08:15 | 51012.9983 | 100.008
Devonshire Building | 2017-10-02 08:30 | 51013.0183 | 79.992
Devonshire Building | 2017-10-02 08:45 | 51013.0433 | 100.008
Devonshire Building | 2017-10-02 09:00 | 51013.0633 | 79.992
Devonshire Building | 2017-10-02 09:15 | 51013.2433 | 720
Devonshire Building | 2017-10-02 09:30 | 51013.7733 | 2120.004
Devonshire Building | 2017-10-02 09:45 | 51013.8883 | 460.008
Devonshire Building | 2017-10-02 10:00 | 51013.9933 | 420.012
Devonshire Building | 2017-10-02 10:15 | 51014.2833 | 1159.992
Devonshire Building | 2017-10-02 10:30 | 51014.7133 | 1720.008
Devonshire Building | 2017-10-02 10:45 | 51014.7933 | 320.004
Devonshire Building | 2017-10-02 11:00 | 51014.8583 | 259.992
Devonshire Building | 2017-10-02 11:15 | 51014.9183 | 240.012
Devonshire Building | 2017-10-02 11:30 | 51015.2083 | 1159.992
Devonshire Building | 2017-10-02 11:45 | 51015.5683 | 1440
Devonshire Building | 2017-10-02 12:00 | 51015.6183 | 200.016
Devonshire Building | 2017-10-02 12:15 | 51015.6683 | 200.016
Devonshire Building | 2017-10-02 12:30 | 51015.7183 | 200.016
Devonshire Building | 2017-10-02 12:45 | 51015.7733 | 219.996
Devonshire Building | 2017-10-02 13:00 | 51015.8283 | 219.996
Devonshire Building | 2017-10-02 13:15 | 51016.4333 | 2419.992
Devonshire Building | 2017-10-02 13:30 | 51016.5183 | 339.984
Devonshire Building | 2017-10-02 13:45 | 51016.5933 | 299.988
Devonshire Building | 2017-10-02 14:00 | 51016.6683 | 299.988
Devonshire Building | 2017-10-02 14:15 | 51016.7583 | 360
Devonshire Building | 2017-10-02 14:30 | 51016.8483 | 360
Devonshire Building | 2017-10-02 14:45 | 51016.9433 | 380.016
Devonshire Building | 2017-10-02 15:00 | 51017.5883 | 2580.012
Devonshire Building | 2017-10-02 15:15 | 51017.6833 | 380.016
Devonshire Building | 2017-10-02 15:30 | 51017.7683 | 339.984
Devonshire Building | 2017-10-02 15:45 | 51017.8483 | 320.004
Devonshire Building | 2017-10-02 16:00 | 51017.9133 | 259.992
Devonshire Building | 2017-10-02 16:15 | 51017.9683 | 219.996
Devonshire Building | 2017-10-02 16:30 | 51018.5483 | 2319.984
Devonshire Building | 2017-10-02 16:45 | 51018.5883 | 159.984
Devonshire Building | 2017-10-02 17:00 | 51018.6383 | 200.016
Devonshire Building | 2017-10-02 17:15 | 51018.6783 | 159.984
Devonshire Building | 2017-10-02 17:30 | 51018.7183 | 159.984
Devonshire Building | 2017-10-02 17:45 | 51018.7583 | 159.984
Devonshire Building | 2017-10-02 18:00 | 51018.7933 | 140.004
Devonshire Building | 2017-10-02 18:15 | 51018.8233 | 119.988
Devonshire Building | 2017-10-02 18:30 | 51018.8483 | 100.008
Devonshire Building | 2017-10-02 18:45 | 51018.8733 | 100.008
Devonshire Building | 2017-10-02 19:00 | 51018.8983 | 100.008
Devonshire Building | 2017-10-02 19:15 | 51018.9183 | 79.992
Devonshire Building | 2017-10-02 19:30 | 51018.9383 | 79.992
Devonshire Building | 2017-10-02 19:45 | 51018.9583 | 79.992
Devonshire Building | 2017-10-02 20:00 | 51018.9783 | 79.992
Devonshire Building | 2017-10-02 20:15 | 51018.9983 | 79.992
Devonshire Building | 2017-10-02 20:30 | 51019.0133 | 60.012
Devonshire Building | 2017-10-02 20:45 | 51019.0483 | 140.004
Devonshire Building | 2017-10-02 21:00 | 51019.0583 | 39.996
Devonshire Building | 2017-10-02 21:15 | 51019.0633 | 20.016
Devonshire Building | 2017-10-02 21:30 | 51019.0733 | 39.996
Devonshire Building | 2017-10-02 21:45 | 51019.0783 | 20.016
Devonshire Building | 2017-10-02 22:00 | 51019.0883 | 39.996
Devonshire Building | 2017-10-02 22:15 | 51019.0933 | 20.016
Devonshire Building | 2017-10-02 22:30 | 51019.1033 | 39.996
Devonshire Building | 2017-10-02 22:45 | 51019.1133 | 39.996
Devonshire Building | 2017-10-02 23:00 | 51019.1183 | 20.016
Devonshire Building | 2017-10-02 23:15 | 51019.1283 | 39.996
Devonshire Building | 2017-10-02 23:30 | 51019.1333 | 20.016
Devonshire Building | 2017-10-02 23:45 | 51019.1433 | 39.996
Devonshire Building | 2017-10-03 | 51019.1484 | 20.016
Devonshire Building | 2017-10-03 00:15 | 51019.1584 | 39.996
Devonshire Building | 2017-10-03 00:30 | 51019.1684 | 39.996
Devonshire Building | 2017-10-03 00:45 | 51019.1734 | 20.016
Devonshire Building | 2017-10-03 01:00 | 51019.1834 | 39.996
Devonshire Building | 2017-10-03 01:15 | 51019.6984 | 2059.992
Devonshire Building | 2017-10-03 01:30 | 51019.7034 | 20.016
Devonshire Building | 2017-10-03 01:45 | 51019.7134 | 39.996
Devonshire Building | 2017-10-03 02:00 | 51019.7184 | 20.016
Devonshire Building | 2017-10-03 02:15 | 51019.7284 | 39.996
Devonshire Building | 2017-10-03 02:30 | 51019.7334 | 20.016
Devonshire Building | 2017-10-03 02:45 | 51019.7434 | 39.996
Devonshire Building | 2017-10-03 03:00 | 51019.7485 | 20.016
Devonshire Building | 2017-10-03 03:15 | 51019.7585 | 39.996
Devonshire Building | 2017-10-03 03:30 | 51019.7635 | 20.016
Devonshire Building | 2017-10-03 03:45 | 51019.7735 | 39.996
Devonshire Building | 2017-10-03 04:00 | 51019.7785 | 20.016
Devonshire Building | 2017-10-03 04:15 | 51019.7835 | 20.016
Devonshire Building | 2017-10-03 04:30 | 51019.7935 | 39.996
Devonshire Building | 2017-10-03 04:45 | 51019.7985 | 20.016
Devonshire Building | 2017-10-03 05:00 | 51019.8085 | 39.996
Devonshire Building | 2017-10-03 05:15 | 51019.8185 | 39.996
Devonshire Building | 2017-10-03 05:30 | 51019.8235 | 20.016
Devonshire Building | 2017-10-03 05:45 | 51019.8335 | 39.996
Devonshire Building | 2017-10-03 06:00 | 51019.8435 | 39.996
Devonshire Building | 2017-10-03 06:15 | 51019.8485 | 20.016
Devonshire Building | 2017-10-03 06:30 | 51019.8585 | 39.996
Devonshire Building | 2017-10-03 06:45 | 51019.8735 | 60.012
Devonshire Building | 2017-10-03 07:00 | 51019.8885 | 60.012
Devonshire Building | 2017-10-03 07:15 | 51019.8985 | 39.996
Devonshire Building | 2017-10-03 07:30 | 51019.9085 | 39.996
Devonshire Building | 2017-10-03 07:45 | 51020.0135 | 420.012
Devonshire Building | 2017-10-03 08:00 | 51020.4885 | 1900.008
Devonshire Building | 2017-10-03 08:15 | 51020.5135 | 100.008
Devonshire Building | 2017-10-03 08:30 | 51020.5385 | 100.008
Devonshire Building | 2017-10-03 08:45 | 51020.5635 | 100.008
Devonshire Building | 2017-10-03 09:00 | 51020.5885 | 100.008
Devonshire Building | 2017-10-03 09:15 | 51020.6285 | 159.984
Devonshire Building | 2017-10-03 09:30 | 51021.1535 | 2099.988
Devonshire Building | 2017-10-03 09:45 | 51021.3135 | 640.008
Devonshire Building | 2017-10-03 10:00 | 51021.4035 | 360
Devonshire Building | 2017-10-03 10:15 | 51021.4785 | 299.988
Devonshire Building | 2017-10-03 10:30 | 51021.5485 | 280.008
Devonshire Building | 2017-10-03 10:45 | 51021.6285 | 320.004
Devonshire Building | 2017-10-03 11:00 | 51021.9885 | 1440
Devonshire Building | 2017-10-03 11:15 | 51022.3485 | 1440
Devonshire Building | 2017-10-03 11:30 | 51022.4235 | 299.988
Devonshire Building | 2017-10-03 11:45 | 51022.5085 | 339.984
Devonshire Building | 2017-10-03 12:00 | 51022.5835 | 299.988
Devonshire Building | 2017-10-03 12:15 | 51022.6535 | 280.008
Devonshire Building | 2017-10-03 12:30 | 51022.7185 | 259.992
Devonshire Building | 2017-10-03 12:45 | 51023.3135 | 2379.996
Devonshire Building | 2017-10-03 13:00 | 51023.3485 | 140.004
Devonshire Building | 2017-10-03 13:15 | 51023.3885 | 159.984
Devonshire Building | 2017-10-03 13:30 | 51023.4285 | 159.984
Devonshire Building | 2017-10-03 13:45 | 51023.4735 | 180
Devonshire Building | 2017-10-03 14:00 | 51023.5085 | 140.004
Devonshire Building | 2017-10-03 14:15 | 51023.5485 | 159.984
Devonshire Building | 2017-10-03 14:30 | 51024.1285 | 2319.984
Devonshire Building | 2017-10-03 14:45 | 51024.1585 | 119.988
Devonshire Building | 2017-10-03 15:00 | 51024.1835 | 100.008
Devonshire Building | 2017-10-03 15:15 | 51024.2135 | 119.988
Devonshire Building | 2017-10-03 15:30 | 51024.2485 | 140.004
Devonshire Building | 2017-10-03 15:45 | 51024.2985 | 200.016
Devonshire Building | 2017-10-03 16:00 | 51024.3585 | 240.012
Devonshire Building | 2017-10-03 16:15 | 51024.9685 | 2440.008
Devonshire Building | 2017-10-03 16:30 | 51025.0485 | 320.004
Devonshire Building | 2017-10-03 16:45 | 51025.1185 | 280.008
Devonshire Building | 2017-10-03 17:00 | 51025.1835 | 259.992
Devonshire Building | 2017-10-03 17:15 | 51025.2385 | 219.996
Devonshire Building | 2017-10-03 17:30 | 51025.2835 | 180
Devonshire Building | 2017-10-03 17:45 | 51025.3285 | 180
Devonshire Building | 2017-10-03 18:00 | 51025.3585 | 119.988
Devonshire Building | 2017-10-03 18:15 | 51025.3885 | 119.988
Devonshire Building | 2017-10-03 18:30 | 51025.4185 | 119.988
Devonshire Building | 2017-10-03 18:45 | 51025.4435 | 100.008
Devonshire Building | 2017-10-03 19:00 | 51025.4635 | 79.992
Devonshire Building | 2017-10-03 19:15 | 51025.4885 | 100.008
Devonshire Building | 2017-10-03 19:30 | 51025.5085 | 79.992
Devonshire Building | 2017-10-03 19:45 | 51025.5284 | 79.992
Devonshire Building | 2017-10-03 20:00 | 51025.5435 | 60.012
Devonshire Building | 2017-10-03 20:15 | 51025.5635 | 79.992
Devonshire Building | 2017-10-03 20:30 | 51025.5834 | 79.992
Devonshire Building | 2017-10-03 20:45 | 51025.6185 | 140.004
Devonshire Building | 2017-10-03 21:00 | 51025.6284 | 39.996
Devonshire Building | 2017-10-03 21:15 | 51025.6335 | 20.016
Devonshire Building | 2017-10-03 21:30 | 51025.6435 | 39.996
Devonshire Building | 2017-10-03 21:45 | 51025.6535 | 39.996
Devonshire Building | 2017-10-03 22:00 | 51025.6635 | 39.996
Devonshire Building | 2017-10-03 22:15 | 51025.6685 | 20.016
Devonshire Building | 2017-10-03 22:30 | 51025.6785 | 39.996
Devonshire Building | 2017-10-03 22:45 | 51025.6885 | 39.996
Devonshire Building | 2017-10-03 23:00 | 51025.6985 | 39.996
Devonshire Building | 2017-10-03 23:15 | 51026.2134 | 2059.992
Devonshire Building | 2017-10-03 23:30 | 51026.2234 | 39.996
Devonshire Building | 2017-10-03 23:45 | 51026.2285 | 20.016
Devonshire Building | 2017-10-04 | 51026.2383 | 39.996
Devonshire Building | 2017-10-04 00:15 | 51026.2483 | 39.996
Devonshire Building | 2017-10-04 00:30 | 51026.2533 | 20.016
Devonshire Building | 2017-10-04 00:45 | 51026.2633 | 39.996
Devonshire Building | 2017-10-04 01:00 | 51026.2683 | 20.016
Devonshire Building | 2017-10-04 01:15 | 51026.2783 | 39.996
Devonshire Building | 2017-10-04 01:30 | 51026.2883 | 39.996
Devonshire Building | 2017-10-04 01:45 | 51026.2933 | 20.016
Devonshire Building | 2017-10-04 02:00 | 51026.3033 | 39.996
Devonshire Building | 2017-10-04 02:15 | 51026.3083 | 20.016
Devonshire Building | 2017-10-04 02:30 | 51026.3183 | 39.996
Devonshire Building | 2017-10-04 02:45 | 51026.3233 | 20.016
Devonshire Building | 2017-10-04 03:00 | 51026.3333 | 39.996
Devonshire Building | 2017-10-04 03:15 | 51026.3433 | 39.996
Devonshire Building | 2017-10-04 03:30 | 51026.3483 | 20.016
Devonshire Building | 2017-10-04 03:45 | 51026.3583 | 39.996
Devonshire Building | 2017-10-04 04:00 | 51026.3683 | 39.996
Devonshire Building | 2017-10-04 04:15 | 51026.3733 | 20.016
Devonshire Building | 2017-10-04 04:30 | 51026.3833 | 39.996
Devonshire Building | 2017-10-04 04:45 | 51026.3933 | 39.996
Devonshire Building | 2017-10-04 05:00 | 51026.3983 | 20.016
Devonshire Building | 2017-10-04 05:15 | 51026.4083 | 39.996
Devonshire Building | 2017-10-04 05:30 | 51026.4183 | 39.996
Devonshire Building | 2017-10-04 05:45 | 51026.4283 | 39.996
Devonshire Building | 2017-10-04 06:00 | 51026.4383 | 39.996
Devonshire Building | 2017-10-04 06:15 | 51026.4483 | 39.996
Devonshire Building | 2017-10-04 06:30 | 51026.4533 | 20.016
Devonshire Building | 2017-10-04 06:45 | 51026.4633 | 39.996
Devonshire Building | 2017-10-04 07:00 | 51026.9833 | 2080.008
Devonshire Building | 2017-10-04 07:15 | 51027.0183 | 140.004
Devonshire Building | 2017-10-04 07:30 | 51027.0533 | 140.004
Devonshire Building | 2017-10-04 07:45 | 51027.0933 | 159.984
Devonshire Building | 2017-10-04 08:00 | 51027.1583 | 259.992
Devonshire Building | 2017-10-04 08:15 | 51027.2233 | 259.992
Devonshire Building | 2017-10-04 08:30 | 51027.2833 | 240.012
Devonshire Building | 2017-10-04 08:45 | 51027.3433 | 240.012
Devonshire Building | 2017-10-04 09:00 | 51027.6033 | 1040.004
Devonshire Building | 2017-10-04 09:15 | 51028.0283 | 1699.992
Devonshire Building | 2017-10-04 09:30 | 51028.0983 | 280.008
Devonshire Building | 2017-10-04 09:45 | 51028.1683 | 280.008
Devonshire Building | 2017-10-04 10:00 | 51028.2383 | 280.008
Devonshire Building | 2017-10-04 10:15 | 51028.8333 | 2379.996
Devonshire Building | 2017-10-04 10:30 | 51028.8883 | 219.996
Devonshire Building | 2017-10-04 10:45 | 51028.9333 | 180
Devonshire Building | 2017-10-04 11:00 | 51028.9783 | 180
Devonshire Building | 2017-10-04 11:15 | 51029.0233 | 180
Devonshire Building | 2017-10-04 11:30 | 51029.3783 | 1419.984
Devonshire Building | 2017-10-04 11:45 | 51029.6683 | 1159.992
Devonshire Building | 2017-10-04 12:00 | 51029.7083 | 159.984
Devonshire Building | 2017-10-04 12:15 | 51029.7483 | 159.984
Devonshire Building | 2017-10-04 12:30 | 51029.8083 | 240.012
Devonshire Building | 2017-10-04 12:45 | 51030.2133 | 1620
Devonshire Building | 2017-10-04 13:00 | 51030.5033 | 1159.992
Devonshire Building | 2017-10-04 13:15 | 51030.5733 | 280.008
Devonshire Building | 2017-10-04 13:30 | 51030.6383 | 259.992
Devonshire Building | 2017-10-04 13:45 | 51030.7033 | 259.992
Devonshire Building | 2017-10-04 14:00 | 51030.7583 | 219.996
Devonshire Building | 2017-10-04 14:15 | 51030.8183 | 240.012
Devonshire Building | 2017-10-04 14:30 | 51031.3983 | 2319.984
Devonshire Building | 2017-10-04 14:45 | 51031.4333 | 140.004
Devonshire Building | 2017-10-04 15:00 | 51031.4783 | 180
Devonshire Building | 2017-10-04 15:15 | 51031.5183 | 159.984
Devonshire Building | 2017-10-04 15:30 | 51031.5583 | 159.984
Devonshire Building | 2017-10-04 15:45 | 51031.5983 | 159.984
Devonshire Building | 2017-10-04 16:00 | 51031.6333 | 140.004
Devonshire Building | 2017-10-04 16:15 | 51032.1933 | 2239.992
Devonshire Building | 2017-10-04 16:30 | 51032.2133 | 79.992
Devonshire Building | 2017-10-04 16:45 | 51032.2383 | 100.008
Devonshire Building | 2017-10-04 17:00 | 51032.2633 | 100.008
Devonshire Building | 2017-10-04 17:15 | 51032.2833 | 79.992
Devonshire Building | 2017-10-04 17:30 | 51032.3033 | 79.992
Devonshire Building | 2017-10-04 17:45 | 51032.3283 | 100.008
Devonshire Building | 2017-10-04 18:00 | 51032.3483 | 79.992
Devonshire Building | 2017-10-04 18:15 | 51032.3683 | 79.992
Devonshire Building | 2017-10-04 18:30 | 51032.3883 | 79.992
Devonshire Building | 2017-10-04 18:45 | 51032.4083 | 79.992
Devonshire Building | 2017-10-04 19:00 | 51032.4283 | 79.992
Devonshire Building | 2017-10-04 19:15 | 51032.4433 | 60.012
Devonshire Building | 2017-10-04 19:30 | 51032.4633 | 79.992
Devonshire Building | 2017-10-04 19:45 | 51032.4833 | 79.992
Devonshire Building | 2017-10-04 20:00 | 51032.4983 | 60.012
Devonshire Building | 2017-10-04 20:15 | 51032.5183 | 79.992
Devonshire Building | 2017-10-04 20:30 | 51032.5333 | 60.012
Devonshire Building | 2017-10-04 20:45 | 51032.5733 | 159.984
Devonshire Building | 2017-10-04 21:00 | 51032.5833 | 39.996
Devonshire Building | 2017-10-04 21:15 | 51032.5983 | 60.012
Devonshire Building | 2017-10-04 21:30 | 51032.6133 | 60.012
Devonshire Building | 2017-10-04 21:45 | 51032.6233 | 39.996
Devonshire Building | 2017-10-04 22:00 | 51032.6383 | 60.012
Devonshire Building | 2017-10-04 22:15 | 51032.6483 | 39.996
Devonshire Building | 2017-10-04 22:30 | 51032.6633 | 60.012
Devonshire Building | 2017-10-04 22:45 | 51033.1733 | 2040.012
Devonshire Building | 2017-10-04 23:00 | 51033.1833 | 39.996
Devonshire Building | 2017-10-04 23:15 | 51033.1933 | 39.996
Devonshire Building | 2017-10-04 23:30 | 51033.2033 | 39.996
Devonshire Building | 2017-10-04 23:45 | 51033.2133 | 39.996
Devonshire Building | 2017-10-05 | 51033.2305 | 60.012
Devonshire Building | 2017-10-05 00:15 | 51033.2405 | 39.996
Devonshire Building | 2017-10-05 00:30 | 51033.2505 | 39.996
Devonshire Building | 2017-10-05 00:45 | 51033.2605 | 39.996
Devonshire Building | 2017-10-05 01:00 | 51033.2705 | 39.996
Devonshire Building | 2017-10-05 01:15 | 51033.2855 | 60.012
Devonshire Building | 2017-10-05 01:30 | 51033.2955 | 39.996
Devonshire Building | 2017-10-05 01:45 | 51033.3105 | 60.012
Devonshire Building | 2017-10-05 02:00 | 51033.3205 | 39.996
Devonshire Building | 2017-10-05 02:15 | 51033.3355 | 60.012
Devonshire Building | 2017-10-05 02:30 | 51033.3455 | 39.996
Devonshire Building | 2017-10-05 02:45 | 51033.3605 | 60.012
Devonshire Building | 2017-10-05 03:00 | 51033.3705 | 39.996
Devonshire Building | 2017-10-05 03:15 | 51033.3855 | 60.012
Devonshire Building | 2017-10-05 03:30 | 51033.3955 | 39.996
Devonshire Building | 2017-10-05 03:45 | 51033.4055 | 39.996
Devonshire Building | 2017-10-05 04:00 | 51033.4205 | 60.012
Devonshire Building | 2017-10-05 04:15 | 51033.4305 | 39.996
Devonshire Building | 2017-10-05 04:30 | 51033.4405 | 39.996
Devonshire Building | 2017-10-05 04:45 | 51033.4505 | 39.996
Devonshire Building | 2017-10-05 05:00 | 51033.4605 | 39.996
Devonshire Building | 2017-10-05 05:15 | 51033.4755 | 60.012
Devonshire Building | 2017-10-05 05:30 | 51033.4855 | 39.996
Devonshire Building | 2017-10-05 05:45 | 51033.5005 | 60.012
Devonshire Building | 2017-10-05 06:00 | 51033.5105 | 39.996
Devonshire Building | 2017-10-05 06:15 | 51033.5205 | 39.996
Devonshire Building | 2017-10-05 06:30 | 51033.5305 | 39.996
Devonshire Building | 2017-10-05 06:45 | 51033.5455 | 60.012
Devonshire Building | 2017-10-05 07:00 | 51033.5605 | 60.012
Devonshire Building | 2017-10-05 07:15 | 51034.0805 | 2080.008
Devonshire Building | 2017-10-05 07:30 | 51034.0955 | 60.012
Devonshire Building | 2017-10-05 07:45 | 51034.1205 | 100.008
Devonshire Building | 2017-10-05 08:00 | 51034.1505 | 119.988
Devonshire Building | 2017-10-05 08:15 | 51034.2005 | 200.016
Devonshire Building | 2017-10-05 08:30 | 51034.2455 | 180
Devonshire Building | 2017-10-05 08:45 | 51034.3055 | 240.012
Devonshire Building | 2017-10-05 09:00 | 51034.3655 | 240.012
Devonshire Building | 2017-10-05 09:15 | 51034.7005 | 1339.992
Devonshire Building | 2017-10-05 09:30 | 51035.0355 | 1339.992
Devonshire Building | 2017-10-05 09:45 | 51035.1205 | 339.984
Devonshire Building | 2017-10-05 10:00 | 51035.2005 | 320.004
Devonshire Building | 2017-10-05 10:15 | 51035.2905 | 360
Devonshire Building | 2017-10-05 10:30 | 51035.3655 | 299.988
Devonshire Building | 2017-10-05 10:45 | 51035.9405 | 2300.004
Devonshire Building | 2017-10-05 11:00 | 51035.9955 | 219.996
Devonshire Building | 2017-10-05 11:15 | 51036.0655 | 280.008
Devonshire Building | 2017-10-05 11:30 | 51036.1205 | 219.996
Devonshire Building | 2017-10-05 11:45 | 51036.1755 | 219.996
Devonshire Building | 2017-10-05 12:00 | 51036.7905 | 2459.988
Devonshire Building | 2017-10-05 12:15 | 51036.8455 | 219.996
Devonshire Building | 2017-10-05 12:30 | 51036.8955 | 200.016
Devonshire Building | 2017-10-05 12:45 | 51036.9405 | 180
Devonshire Building | 2017-10-05 13:00 | 51036.9955 | 219.996
Devonshire Building | 2017-10-05 13:15 | 51037.0505 | 219.996
Devonshire Building | 2017-10-05 13:30 | 51037.6605 | 2440.008
Devonshire Building | 2017-10-05 13:45 | 51037.7355 | 299.988
Devonshire Building | 2017-10-05 14:00 | 51037.8005 | 259.992
Devonshire Building | 2017-10-05 14:15 | 51037.8655 | 259.992
Devonshire Building | 2017-10-05 14:30 | 51037.9205 | 219.996
Devonshire Building | 2017-10-05 14:45 | 51037.9705 | 200.016
Devonshire Building | 2017-10-05 15:00 | 51038.0255 | 219.996
Devonshire Building | 2017-10-05 15:15 | 51038.3805 | 1419.984
Devonshire Building | 2017-10-05 15:30 | 51038.6605 | 1119.996
Devonshire Building | 2017-10-05 15:45 | 51038.6905 | 119.988
Devonshire Building | 2017-10-05 16:00 | 51038.7355 | 180
Devonshire Building | 2017-10-05 16:15 | 51038.7855 | 200.016
Devonshire Building | 2017-10-05 16:30 | 51038.8355 | 200.016
Devonshire Building | 2017-10-05 16:45 | 51038.8805 | 180
Devonshire Building | 2017-10-05 17:00 | 51038.9255 | 180
Devonshire Building | 2017-10-05 17:15 | 51038.9705 | 180
Devonshire Building | 2017-10-05 17:30 | 51039.0105 | 159.984
Devonshire Building | 2017-10-05 17:45 | 51039.0505 | 159.984
Devonshire Building | 2017-10-05 18:00 | 51039.1855 | 540
Devonshire Building | 2017-10-05 18:15 | 51039.6305 | 1779.984
Devonshire Building | 2017-10-05 18:30 | 51039.6605 | 119.988
Devonshire Building | 2017-10-05 18:45 | 51039.6905 | 119.988
Devonshire Building | 2017-10-05 19:00 | 51039.7255 | 140.004
Devonshire Building | 2017-10-05 19:15 | 51039.7605 | 140.004
Devonshire Building | 2017-10-05 19:30 | 51039.7905 | 119.988
Devonshire Building | 2017-10-05 19:45 | 51039.8155 | 100.008
Devonshire Building | 2017-10-05 20:00 | 51039.8505 | 140.004
Devonshire Building | 2017-10-05 20:15 | 51039.8755 | 100.008
Devonshire Building | 2017-10-05 20:30 | 51039.8955 | 79.992
Devonshire Building | 2017-10-05 20:45 | 51039.9255 | 119.988
Devonshire Building | 2017-10-05 21:00 | 51039.9405 | 60.012
Devonshire Building | 2017-10-05 21:15 | 51039.9605 | 79.992
Devonshire Building | 2017-10-05 21:30 | 51039.9755 | 60.012
Devonshire Building | 2017-10-05 21:45 | 51039.9905 | 60.012
Devonshire Building | 2017-10-05 22:00 | 51040.0055 | 60.012
Devonshire Building | 2017-10-05 22:15 | 51040.0255 | 79.992
Devonshire Building | 2017-10-05 22:30 | 51040.0405 | 60.012
Devonshire Building | 2017-10-05 22:45 | 51040.0555 | 60.012
Devonshire Building | 2017-10-05 23:00 | 51040.0705 | 60.012
Devonshire Building | 2017-10-05 23:15 | 51040.0855 | 60.012
Devonshire Building | 2017-10-05 23:30 | 51040.1005 | 60.012
Devonshire Building | 2017-10-05 23:45 | 51040.1155 | 60.012
Devonshire Building | 2017-10-06 | 51040.1289 | 60.012
Devonshire Building | 2017-10-06 00:15 | 51040.1439 | 60.012
Devonshire Building | 2017-10-06 00:30 | 51040.1589 | 60.012
Devonshire Building | 2017-10-06 00:45 | 51040.1739 | 60.012
Devonshire Building | 2017-10-06 01:00 | 51040.1889 | 60.012
Devonshire Building | 2017-10-06 01:15 | 51040.2039 | 60.012
Devonshire Building | 2017-10-06 01:30 | 51040.2189 | 60.012
Devonshire Building | 2017-10-06 01:45 | 51040.2339 | 60.012
Devonshire Building | 2017-10-06 02:00 | 51040.2489 | 60.012
Devonshire Building | 2017-10-06 02:15 | 51040.2639 | 60.012
Devonshire Building | 2017-10-06 02:30 | 51040.2739 | 39.996
Devonshire Building | 2017-10-06 02:45 | 51040.3889 | 460.008
Devonshire Building | 2017-10-06 03:00 | 51040.7989 | 1640.016
Devonshire Building | 2017-10-06 03:15 | 51040.8039 | 20.016
Devonshire Building | 2017-10-06 03:30 | 51040.8139 | 39.996
Devonshire Building | 2017-10-06 03:45 | 51040.8189 | 20.016
Devonshire Building | 2017-10-06 04:00 | 51040.8289 | 39.996
Devonshire Building | 2017-10-06 04:15 | 51040.834 | 20.016
Devonshire Building | 2017-10-06 04:30 | 51040.844 | 39.996
Devonshire Building | 2017-10-06 04:45 | 51040.849 | 20.016
Devonshire Building | 2017-10-06 05:00 | 51040.859 | 39.996
Devonshire Building | 2017-10-06 05:15 | 51040.869 | 39.996
Devonshire Building | 2017-10-06 05:30 | 51040.874 | 20.016
Devonshire Building | 2017-10-06 05:45 | 51040.884 | 39.996
Devonshire Building | 2017-10-06 06:00 | 51040.894 | 39.996
Devonshire Building | 2017-10-06 06:15 | 51040.904 | 39.996
Devonshire Building | 2017-10-06 06:30 | 51040.914 | 39.996
Devonshire Building | 2017-10-06 06:45 | 51040.919 | 20.016
Devonshire Building | 2017-10-06 07:00 | 51040.929 | 39.996
Devonshire Building | 2017-10-06 07:15 | 51040.939 | 39.996
Devonshire Building | 2017-10-06 07:30 | 51040.949 | 39.996
Devonshire Building | 2017-10-06 07:45 | 51040.974 | 100.008
Devonshire Building | 2017-10-06 08:00 | 51041.004 | 119.988
Devonshire Building | 2017-10-06 08:15 | 51041.544 | 2160
Devonshire Building | 2017-10-06 08:30 | 51041.5739 | 119.988
Devonshire Building | 2017-10-06 08:45 | 51041.609 | 140.004
Devonshire Building | 2017-10-06 09:00 | 51041.644 | 140.004
Devonshire Building | 2017-10-06 09:15 | 51041.6839 | 159.984
Devonshire Building | 2017-10-06 09:30 | 51041.9089 | 900
Devonshire Building | 2017-10-06 09:45 | 51042.3389 | 1720.008
Devonshire Building | 2017-10-06 10:00 | 51042.399 | 240.012
Devonshire Building | 2017-10-06 10:15 | 51042.469 | 280.008
Devonshire Building | 2017-10-06 10:30 | 51042.559 | 360
Devonshire Building | 2017-10-06 10:45 | 51042.644 | 339.984
Devonshire Building | 2017-10-06 11:00 | 51043.1589 | 2059.992
Devonshire Building | 2017-10-06 11:15 | 51043.389 | 920.016
Devonshire Building | 2017-10-06 11:30 | 51043.489 | 399.996
Devonshire Building | 2017-10-06 11:45 | 51043.589 | 399.996
Devonshire Building | 2017-10-06 12:00 | 51043.684 | 380.016
Devonshire Building | 2017-10-06 12:15 | 51043.784 | 399.996
Devonshire Building | 2017-10-06 12:30 | 51044.439 | 2620.008
Devonshire Building | 2017-10-06 12:45 | 51044.534 | 380.016
Devonshire Building | 2017-10-06 13:00 | 51044.614 | 320.004
Devonshire Building | 2017-10-06 13:15 | 51044.694 | 320.004
Devonshire Building | 2017-10-06 13:30 | 51044.759 | 259.992
Devonshire Building | 2017-10-06 13:45 | 51044.814 | 219.996
Devonshire Building | 2017-10-06 14:00 | 51044.864 | 200.016
Devonshire Building | 2017-10-06 14:15 | 51045.444 | 2319.984
Devonshire Building | 2017-10-06 14:30 | 51045.474 | 119.988
Devonshire Building | 2017-10-06 14:45 | 51045.504 | 119.988
Devonshire Building | 2017-10-06 15:00 | 51045.529 | 100.008
Devonshire Building | 2017-10-06 15:15 | 51045.559 | 119.988
Devonshire Building | 2017-10-06 15:30 | 51045.584 | 100.008
Devonshire Building | 2017-10-06 15:45 | 51045.609 | 100.008
Devonshire Building | 2017-10-06 16:00 | 51046.164 | 2220.012
Devonshire Building | 2017-10-06 16:15 | 51046.184 | 79.992
Devonshire Building | 2017-10-06 16:30 | 51046.204 | 79.992
Devonshire Building | 2017-10-06 16:45 | 51046.229 | 100.008
Devonshire Building | 2017-10-06 17:00 | 51046.254 | 100.008
Devonshire Building | 2017-10-06 17:15 | 51046.279 | 100.008
Devonshire Building | 2017-10-06 17:30 | 51046.304 | 100.008
Devonshire Building | 2017-10-06 17:45 | 51046.329 | 100.008
Devonshire Building | 2017-10-06 18:00 | 51046.354 | 100.008
Devonshire Building | 2017-10-06 18:15 | 51046.379 | 100.008
Devonshire Building | 2017-10-06 18:30 | 51046.404 | 100.008
Devonshire Building | 2017-10-06 18:45 | 51046.424 | 79.992
Devonshire Building | 2017-10-06 19:00 | 51046.449 | 100.008
Devonshire Building | 2017-10-06 19:15 | 51046.469 | 79.992
Devonshire Building | 2017-10-06 19:30 | 51046.489 | 79.992
Devonshire Building | 2017-10-06 19:45 | 51046.514 | 100.008
Devonshire Building | 2017-10-06 20:00 | 51046.534 | 79.992
Devonshire Building | 2017-10-06 20:15 | 51046.554 | 79.992
Devonshire Building | 2017-10-06 20:30 | 51046.574 | 79.992
Devonshire Building | 2017-10-06 20:45 | 51046.619 | 180
Devonshire Building | 2017-10-06 21:00 | 51046.639 | 79.992
Devonshire Building | 2017-10-06 21:15 | 51046.654 | 60.012
Devonshire Building | 2017-10-06 21:30 | 51046.674 | 79.992
Devonshire Building | 2017-10-06 21:45 | 51046.694 | 79.992
Devonshire Building | 2017-10-06 22:00 | 51046.714 | 79.992
Devonshire Building | 2017-10-06 22:15 | 51046.734 | 79.992
Devonshire Building | 2017-10-06 22:30 | 51046.754 | 79.992
Devonshire Building | 2017-10-06 22:45 | 51046.769 | 60.012
Devonshire Building | 2017-10-06 23:00 | 51046.789 | 79.992
Devonshire Building | 2017-10-06 23:15 | 51046.804 | 60.012
Devonshire Building | 2017-10-06 23:30 | 51046.824 | 79.992
Devonshire Building | 2017-10-06 23:45 | 51046.839 | 60.012
Devonshire Building | 2017-10-07 | 51046.8594 | 79.992
Devonshire Building | 2017-10-07 00:15 | 51047.3944 | 2139.984
Devonshire Building | 2017-10-07 00:30 | 51047.4094 | 60.012
Devonshire Building | 2017-10-07 00:45 | 51047.4194 | 39.996
Devonshire Building | 2017-10-07 01:00 | 51047.4344 | 60.012
Devonshire Building | 2017-10-07 01:15 | 51047.4494 | 60.012
Devonshire Building | 2017-10-07 01:30 | 51047.4594 | 39.996
Devonshire Building | 2017-10-07 01:45 | 51047.4744 | 60.012
Devonshire Building | 2017-10-07 02:00 | 51047.4894 | 60.012
Devonshire Building | 2017-10-07 02:15 | 51047.5044 | 60.012
Devonshire Building | 2017-10-07 02:30 | 51047.5194 | 60.012
Devonshire Building | 2017-10-07 02:45 | 51047.5344 | 60.012
Devonshire Building | 2017-10-07 03:00 | 51047.5544 | 79.992
Devonshire Building | 2017-10-07 03:15 | 51047.5694 | 60.012
Devonshire Building | 2017-10-07 03:30 | 51047.5844 | 60.012
Devonshire Building | 2017-10-07 03:45 | 51047.5994 | 60.012
Devonshire Building | 2017-10-07 04:00 | 51047.6144 | 60.012
Devonshire Building | 2017-10-07 04:15 | 51047.6294 | 60.012
Devonshire Building | 2017-10-07 04:30 | 51047.6444 | 60.012
Devonshire Building | 2017-10-07 04:45 | 51047.6594 | 60.012
Devonshire Building | 2017-10-07 05:00 | 51047.6694 | 39.996
Devonshire Building | 2017-10-07 05:15 | 51047.6844 | 60.012
Devonshire Building | 2017-10-07 05:30 | 51047.6994 | 60.012
Devonshire Building | 2017-10-07 05:45 | 51047.7144 | 60.012
Devonshire Building | 2017-10-07 06:00 | 51047.7244 | 39.996
Devonshire Building | 2017-10-07 06:15 | 51047.7394 | 60.012
Devonshire Building | 2017-10-07 06:30 | 51047.7544 | 60.012
Devonshire Building | 2017-10-07 06:45 | 51047.7644 | 39.996
Devonshire Building | 2017-10-07 07:00 | 51047.7794 | 60.012
Devonshire Building | 2017-10-07 07:15 | 51047.7894 | 39.996
Devonshire Building | 2017-10-07 07:30 | 51047.7994 | 39.996
Devonshire Building | 2017-10-07 07:45 | 51047.8194 | 79.992
Devonshire Building | 2017-10-07 08:00 | 51047.8494 | 119.988
Devonshire Building | 2017-10-07 08:15 | 51047.8794 | 119.988
Devonshire Building | 2017-10-07 08:30 | 51047.9044 | 100.008
Devonshire Building | 2017-10-07 08:45 | 51047.9344 | 119.988
Devonshire Building | 2017-10-07 09:00 | 51047.9594 | 100.008
Devonshire Building | 2017-10-07 09:15 | 51047.9894 | 119.988
Devonshire Building | 2017-10-07 09:30 | 51048.0144 | 100.008
Devonshire Building | 2017-10-07 09:45 | 51048.0394 | 100.008
Devonshire Building | 2017-10-07 10:00 | 51048.5094 | 1879.992
Devonshire Building | 2017-10-07 10:15 | 51048.5994 | 360
Devonshire Building | 2017-10-07 10:30 | 51048.6094 | 39.996
Devonshire Building | 2017-10-07 10:45 | 51048.6144 | 20.016
Devonshire Building | 2017-10-07 11:00 | 51048.6244 | 39.996
Devonshire Building | 2017-10-07 11:15 | 51048.6344 | 39.996
Devonshire Building | 2017-10-07 11:30 | 51048.6444 | 39.996
Devonshire Building | 2017-10-07 11:45 | 51048.6544 | 39.996
Devonshire Building | 2017-10-07 12:00 | 51048.6594 | 20.016
Devonshire Building | 2017-10-07 12:15 | 51048.6694 | 39.996
Devonshire Building | 2017-10-07 12:30 | 51048.6794 | 39.996
Devonshire Building | 2017-10-07 12:45 | 51048.6894 | 39.996
Devonshire Building | 2017-10-07 13:00 | 51048.6994 | 39.996
Devonshire Building | 2017-10-07 13:15 | 51048.7094 | 39.996
Devonshire Building | 2017-10-07 13:30 | 51048.7194 | 39.996
Devonshire Building | 2017-10-07 13:45 | 51048.7294 | 39.996
Devonshire Building | 2017-10-07 14:00 | 51048.7394 | 39.996
Devonshire Building | 2017-10-07 14:15 | 51048.7544 | 60.012
Devonshire Building | 2017-10-07 14:30 | 51048.7644 | 39.996
Devonshire Building | 2017-10-07 14:45 | 51048.7744 | 39.996
Devonshire Building | 2017-10-07 15:00 | 51048.7844 | 39.996
Devonshire Building | 2017-10-07 15:15 | 51048.7994 | 60.012
Devonshire Building | 2017-10-07 15:30 | 51048.8094 | 39.996
Devonshire Building | 2017-10-07 15:45 | 51048.8194 | 39.996
Devonshire Building | 2017-10-07 16:00 | 51048.8294 | 39.996
Devonshire Building | 2017-10-07 16:15 | 51048.8394 | 39.996
Devonshire Building | 2017-10-07 16:30 | 51048.8494 | 39.996
Devonshire Building | 2017-10-07 16:45 | 51048.8594 | 39.996
Devonshire Building | 2017-10-07 17:00 | 51048.8694 | 39.996
Devonshire Building | 2017-10-07 17:15 | 51048.8794 | 39.996
Devonshire Building | 2017-10-07 17:30 | 51049.3994 | 2080.008
Devonshire Building | 2017-10-07 17:45 | 51049.4094 | 39.996
Devonshire Building | 2017-10-07 18:00 | 51049.4244 | 60.012
Devonshire Building | 2017-10-07 18:15 | 51049.4344 | 39.996
Devonshire Building | 2017-10-07 18:30 | 51049.4444 | 39.996
Devonshire Building | 2017-10-07 18:45 | 51049.4544 | 39.996
Devonshire Building | 2017-10-07 19:00 | 51049.4644 | 39.996
Devonshire Building | 2017-10-07 19:15 | 51049.4744 | 39.996
Devonshire Building | 2017-10-07 19:30 | 51049.4844 | 39.996
Devonshire Building | 2017-10-07 19:45 | 51049.4944 | 39.996
Devonshire Building | 2017-10-07 20:00 | 51049.5094 | 60.012
Devonshire Building | 2017-10-07 20:15 | 51049.5194 | 39.996
Devonshire Building | 2017-10-07 20:30 | 51049.5344 | 60.012
Devonshire Building | 2017-10-07 20:45 | 51049.5544 | 79.992
Devonshire Building | 2017-10-07 21:00 | 51049.5644 | 39.996
Devonshire Building | 2017-10-07 21:15 | 51049.5794 | 60.012
Devonshire Building | 2017-10-07 21:30 | 51049.5894 | 39.996
Devonshire Building | 2017-10-07 21:45 | 51049.6044 | 60.012
Devonshire Building | 2017-10-07 22:00 | 51049.6144 | 39.996
Devonshire Building | 2017-10-07 22:15 | 51049.6294 | 60.012
Devonshire Building | 2017-10-07 22:30 | 51049.6394 | 39.996
Devonshire Building | 2017-10-07 22:45 | 51049.6494 | 39.996
Devonshire Building | 2017-10-07 23:00 | 51049.6644 | 60.012
Devonshire Building | 2017-10-07 23:15 | 51049.6744 | 39.996
Devonshire Building | 2017-10-07 23:30 | 51049.6844 | 39.996
Devonshire Building | 2017-10-07 23:45 | 51049.6994 | 60.012
Devonshire Building | 2017-10-08 | 51049.7109 | 39.996
Devonshire Building | 2017-10-08 00:15 | 51049.7209 | 39.996
Devonshire Building | 2017-10-08 00:30 | 51049.7309 | 39.996
Devonshire Building | 2017-10-08 00:45 | 51049.7459 | 60.012
Devonshire Building | 2017-10-08 01:00 | 51049.7559 | 39.996
Devonshire Building | 2017-10-08 01:15 | 51049.7659 | 39.996
Devonshire Building | 2017-10-08 01:30 | 51049.7759 | 39.996
Devonshire Building | 2017-10-08 01:45 | 51049.7859 | 39.996
Devonshire Building | 2017-10-08 02:00 | 51049.7959 | 39.996
Devonshire Building | 2017-10-08 02:15 | 51049.8109 | 60.012
Devonshire Building | 2017-10-08 02:30 | 51049.8209 | 39.996
Devonshire Building | 2017-10-08 02:45 | 51049.8309 | 39.996
Devonshire Building | 2017-10-08 03:00 | 51049.8409 | 39.996
Devonshire Building | 2017-10-08 03:15 | 51050.3459 | 2019.996
Devonshire Building | 2017-10-08 03:30 | 51050.3659 | 79.992
Devonshire Building | 2017-10-08 03:45 | 51050.3809 | 60.012
Devonshire Building | 2017-10-08 04:00 | 51050.3959 | 60.012
Devonshire Building | 2017-10-08 04:15 | 51050.4059 | 39.996
Devonshire Building | 2017-10-08 04:30 | 51050.4209 | 60.012
Devonshire Building | 2017-10-08 04:45 | 51050.4359 | 60.012
Devonshire Building | 2017-10-08 05:00 | 51050.4509 | 60.012
Devonshire Building | 2017-10-08 05:15 | 51050.4659 | 60.012
Devonshire Building | 2017-10-08 05:30 | 51050.4859 | 79.992
Devonshire Building | 2017-10-08 05:45 | 51050.5059 | 79.992
Devonshire Building | 2017-10-08 06:00 | 51050.5209 | 60.012
Devonshire Building | 2017-10-08 06:15 | 51050.5409 | 79.992
Devonshire Building | 2017-10-08 06:30 | 51050.556 | 60.012
Devonshire Building | 2017-10-08 06:45 | 51050.5759 | 79.992
Devonshire Building | 2017-10-08 07:00 | 51050.591 | 60.012
Devonshire Building | 2017-10-08 07:15 | 51050.606 | 60.012
Devonshire Building | 2017-10-08 07:30 | 51050.626 | 79.992
Devonshire Building | 2017-10-08 07:45 | 51050.641 | 60.012
Devonshire Building | 2017-10-08 08:00 | 51050.676 | 140.004
Devonshire Building | 2017-10-08 08:15 | 51050.706 | 119.988
Devonshire Building | 2017-10-08 08:30 | 51050.736 | 119.988
Devonshire Building | 2017-10-08 08:45 | 51050.7659 | 119.988
Devonshire Building | 2017-10-08 09:00 | 51050.7959 | 119.988
Devonshire Building | 2017-10-08 09:15 | 51050.8259 | 119.988
Devonshire Building | 2017-10-08 09:30 | 51050.8559 | 119.988
Devonshire Building | 2017-10-08 09:45 | 51050.8859 | 119.988
Devonshire Building | 2017-10-08 10:00 | 51050.9109 | 100.008
Devonshire Building | 2017-10-08 10:15 | 51050.9359 | 100.008
Devonshire Building | 2017-10-08 10:30 | 51050.9459 | 39.996
Devonshire Building | 2017-10-08 10:45 | 51050.9609 | 60.012
Devonshire Building | 2017-10-08 11:00 | 51050.9709 | 39.996
Devonshire Building | 2017-10-08 11:15 | 51050.9859 | 60.012
Devonshire Building | 2017-10-08 11:30 | 51050.9959 | 39.996
Devonshire Building | 2017-10-08 11:45 | 51051.0109 | 60.012
Devonshire Building | 2017-10-08 12:00 | 51051.0209 | 39.996
Devonshire Building | 2017-10-08 12:15 | 51051.0359 | 60.012
Devonshire Building | 2017-10-08 12:30 | 51051.0459 | 39.996
Devonshire Building | 2017-10-08 12:45 | 51051.321 | 1100.016
Devonshire Building | 2017-10-08 13:00 | 51051.571 | 1000.008
Devonshire Building | 2017-10-08 13:15 | 51051.581 | 39.996
Devonshire Building | 2017-10-08 13:30 | 51051.596 | 60.012
Devonshire Building | 2017-10-08 13:45 | 51051.606 | 39.996
Devonshire Building | 2017-10-08 14:00 | 51051.616 | 39.996
Devonshire Building | 2017-10-08 14:15 | 51051.631 | 60.012
Devonshire Building | 2017-10-08 14:30 | 51051.641 | 39.996
Devonshire Building | 2017-10-08 14:45 | 51051.656 | 60.012
Devonshire Building | 2017-10-08 15:00 | 51051.666 | 39.996
Devonshire Building | 2017-10-08 15:15 | 51051.691 | 100.008
Devonshire Building | 2017-10-08 15:30 | 51051.701 | 39.996
Devonshire Building | 2017-10-08 15:45 | 51051.716 | 60.012
Devonshire Building | 2017-10-08 16:00 | 51051.731 | 60.012
Devonshire Building | 2017-10-08 16:15 | 51051.746 | 60.012
Devonshire Building | 2017-10-08 16:30 | 51051.761 | 60.012
Devonshire Building | 2017-10-08 16:45 | 51051.776 | 60.012
Devonshire Building | 2017-10-08 17:00 | 51051.791 | 60.012
Devonshire Building | 2017-10-08 17:15 | 51051.801 | 39.996
Devonshire Building | 2017-10-08 17:30 | 51051.816 | 60.012
Devonshire Building | 2017-10-08 17:45 | 51051.826 | 39.996
Devonshire Building | 2017-10-08 18:00 | 51051.841 | 60.012
Devonshire Building | 2017-10-08 18:15 | 51051.856 | 60.012
Devonshire Building | 2017-10-08 18:30 | 51051.866 | 39.996
Devonshire Building | 2017-10-08 18:45 | 51051.881 | 60.012
Devonshire Building | 2017-10-08 19:00 | 51051.891 | 39.996
Devonshire Building | 2017-10-08 19:15 | 51051.906 | 60.012
Devonshire Building | 2017-10-08 19:30 | 51051.916 | 39.996
Devonshire Building | 2017-10-08 19:45 | 51051.931 | 60.012
Devonshire Building | 2017-10-08 20:00 | 51051.941 | 39.996
Devonshire Building | 2017-10-08 20:15 | 51051.951 | 39.996
Devonshire Building | 2017-10-08 20:30 | 51051.966 | 60.012
Devonshire Building | 2017-10-08 20:45 | 51052.001 | 140.004
Devonshire Building | 2017-10-08 21:00 | 51052.011 | 39.996
Devonshire Building | 2017-10-08 21:15 | 51052.021 | 39.996
Devonshire Building | 2017-10-08 21:30 | 51052.031 | 39.996
Devonshire Building | 2017-10-08 21:45 | 51052.046 | 60.012
Devonshire Building | 2017-10-08 22:00 | 51052.056 | 39.996
Devonshire Building | 2017-10-08 22:15 | 51052.066 | 39.996
Devonshire Building | 2017-10-08 22:30 | 51052.311 | 979.992
Devonshire Building | 2017-10-08 22:45 | 51052.596 | 1140.012
Devonshire Building | 2017-10-08 23:00 | 51052.611 | 60.012
Devonshire Building | 2017-10-08 23:15 | 51052.621 | 39.996
Devonshire Building | 2017-10-08 23:30 | 51052.631 | 39.996
Devonshire Building | 2017-10-08 23:45 | 51052.641 | 39.996
Devonshire Building | 2017-10-09 | 51052.6484 | 39.996
Devonshire Building | 2017-10-09 00:15 | 51052.6584 | 39.996
Devonshire Building | 2017-10-09 00:30 | 51052.6684 | 39.996
Devonshire Building | 2017-10-09 00:45 | 51052.6784 | 39.996
Devonshire Building | 2017-10-09 01:00 | 51052.6934 | 60.012
Devonshire Building | 2017-10-09 01:15 | 51052.7034 | 39.996
Devonshire Building | 2017-10-09 01:30 | 51052.7184 | 60.012
Devonshire Building | 2017-10-09 01:45 | 51052.7284 | 39.996
Devonshire Building | 2017-10-09 02:00 | 51052.7434 | 60.012
Devonshire Building | 2017-10-09 02:15 | 51052.7534 | 39.996
Devonshire Building | 2017-10-09 02:30 | 51052.7684 | 60.012
Devonshire Building | 2017-10-09 02:45 | 51052.7834 | 60.012
Devonshire Building | 2017-10-09 03:00 | 51052.7934 | 39.996
Devonshire Building | 2017-10-09 03:15 | 51052.8085 | 60.012
Devonshire Building | 2017-10-09 03:30 | 51052.8184 | 39.996
Devonshire Building | 2017-10-09 03:45 | 51052.8284 | 39.996
Devonshire Building | 2017-10-09 04:00 | 51052.8435 | 60.012
Devonshire Building | 2017-10-09 04:15 | 51052.8535 | 39.996
Devonshire Building | 2017-10-09 04:30 | 51052.8634 | 39.996
Devonshire Building | 2017-10-09 04:45 | 51052.8785 | 60.012
Devonshire Building | 2017-10-09 05:00 | 51052.8885 | 39.996
Devonshire Building | 2017-10-09 05:15 | 51052.9035 | 60.012
Devonshire Building | 2017-10-09 05:30 | 51052.9135 | 39.996
Devonshire Building | 2017-10-09 05:45 | 51052.9285 | 60.012
Devonshire Building | 2017-10-09 06:00 | 51052.9385 | 39.996
Devonshire Building | 2017-10-09 06:15 | 51052.9485 | 39.996
Devonshire Building | 2017-10-09 06:30 | 51052.9635 | 60.012
Devonshire Building | 2017-10-09 06:45 | 51053.1885 | 900
Devonshire Building | 2017-10-09 07:00 | 51053.5485 | 1440
Devonshire Building | 2017-10-09 07:15 | 51053.5935 | 180
Devonshire Building | 2017-10-09 07:30 | 51053.6535 | 240.012
Devonshire Building | 2017-10-09 07:45 | 51053.7235 | 280.008
Devonshire Building | 2017-10-09 08:00 | 51053.8185 | 380.016
Devonshire Building | 2017-10-09 08:15 | 51053.9035 | 339.984
Devonshire Building | 2017-10-09 08:30 | 51053.9785 | 299.988
Devonshire Building | 2017-10-09 08:45 | 51054.0535 | 299.988
Devonshire Building | 2017-10-09 09:00 | 51054.6685 | 2459.988
Devonshire Building | 2017-10-09 09:15 | 51054.7335 | 259.992
Devonshire Building | 2017-10-09 09:30 | 51054.8184 | 339.984
Devonshire Building | 2017-10-09 09:45 | 51054.8984 | 320.004
Devonshire Building | 2017-10-09 10:00 | 51054.9935 | 380.016
Devonshire Building | 2017-10-09 10:15 | 51055.6084 | 2459.988
Devonshire Building | 2017-10-09 10:30 | 51055.6834 | 299.988
Devonshire Building | 2017-10-09 10:45 | 51055.7534 | 280.008
Devonshire Building | 2017-10-09 11:00 | 51055.8235 | 280.008
Devonshire Building | 2017-10-09 11:15 | 51055.8784 | 219.996
Devonshire Building | 2017-10-09 11:30 | 51056.4435 | 2260.008
Devonshire Building | 2017-10-09 11:45 | 51056.4885 | 180
Devonshire Building | 2017-10-09 12:00 | 51056.5435 | 219.996
Devonshire Building | 2017-10-09 12:15 | 51056.5984 | 219.996
Devonshire Building | 2017-10-09 12:30 | 51056.6435 | 180
Devonshire Building | 2017-10-09 12:45 | 51056.6935 | 200.016
Devonshire Building | 2017-10-09 13:00 | 51057.2885 | 2379.996
Devonshire Building | 2017-10-09 13:15 | 51057.3335 | 180
Devonshire Building | 2017-10-09 13:30 | 51057.3835 | 200.016
Devonshire Building | 2017-10-09 13:45 | 51057.4335 | 200.016
Devonshire Building | 2017-10-09 14:00 | 51057.4835 | 200.016
Devonshire Building | 2017-10-09 14:15 | 51057.6135 | 519.984
Devonshire Building | 2017-10-09 14:30 | 51057.7885 | 699.984
Devonshire Building | 2017-10-09 14:45 | 51058.2485 | 1839.996
Devonshire Building | 2017-10-09 15:00 | 51058.3135 | 259.992
Devonshire Building | 2017-10-09 15:15 | 51058.3835 | 280.008
Devonshire Building | 2017-10-09 15:30 | 51058.4585 | 299.988
Devonshire Building | 2017-10-09 15:45 | 51058.5385 | 320.004
Devonshire Building | 2017-10-09 16:00 | 51059.1185 | 2319.984
Devonshire Building | 2017-10-09 16:15 | 51059.2034 | 339.984
Devonshire Building | 2017-10-09 16:30 | 51059.2884 | 339.984
Devonshire Building | 2017-10-09 16:45 | 51059.3684 | 320.004
Devonshire Building | 2017-10-09 17:00 | 51059.4334 | 259.992
Devonshire Building | 2017-10-09 17:15 | 51059.4934 | 240.012
Devonshire Building | 2017-10-09 17:30 | 51059.5534 | 240.012
Devonshire Building | 2017-10-09 17:45 | 51059.6084 | 219.996
Devonshire Building | 2017-10-09 18:00 | 51059.6585 | 200.016
Devonshire Building | 2017-10-09 18:15 | 51059.6984 | 159.984
Devonshire Building | 2017-10-09 18:30 | 51059.7384 | 159.984
Devonshire Building | 2017-10-09 18:45 | 51059.7734 | 140.004
Devonshire Building | 2017-10-09 19:00 | 51059.8034 | 119.988
Devonshire Building | 2017-10-09 19:15 | 51059.8284 | 100.008
Devonshire Building | 2017-10-09 19:30 | 51059.8534 | 100.008
Devonshire Building | 2017-10-09 19:45 | 51060.3934 | 2160
Devonshire Building | 2017-10-09 20:00 | 51060.4084 | 60.012
Devonshire Building | 2017-10-09 20:15 | 51060.4184 | 39.996
Devonshire Building | 2017-10-09 20:30 | 51060.4334 | 60.012
Devonshire Building | 2017-10-09 20:45 | 51060.4534 | 79.992
Devonshire Building | 2017-10-09 21:00 | 51060.4685 | 60.012
Devonshire Building | 2017-10-09 21:15 | 51060.4835 | 60.012
Devonshire Building | 2017-10-09 21:30 | 51060.4985 | 60.012
Devonshire Building | 2017-10-09 21:45 | 51060.5135 | 60.012
Devonshire Building | 2017-10-09 22:00 | 51060.5285 | 60.012
Devonshire Building | 2017-10-09 22:15 | 51060.5435 | 60.012
Devonshire Building | 2017-10-09 22:30 | 51060.5585 | 60.012
Devonshire Building | 2017-10-09 22:45 | 51060.5735 | 60.012
Devonshire Building | 2017-10-09 23:00 | 51060.5885 | 60.012
Devonshire Building | 2017-10-09 23:15 | 51060.5985 | 39.996
Devonshire Building | 2017-10-09 23:30 | 51060.6135 | 60.012
Devonshire Building | 2017-10-09 23:45 | 51060.6285 | 60.012
Devonshire Building | 2017-10-10 | 51060.6406 | 39.996
Devonshire Building | 2017-10-10 00:15 | 51060.6556 | 60.012
Devonshire Building | 2017-10-10 00:30 | 51060.6706 | 60.012
Devonshire Building | 2017-10-10 00:45 | 51060.6806 | 39.996
Devonshire Building | 2017-10-10 01:00 | 51060.6956 | 60.012
Devonshire Building | 2017-10-10 01:15 | 51060.7056 | 39.996
Devonshire Building | 2017-10-10 01:30 | 51060.7206 | 60.012
Devonshire Building | 2017-10-10 01:45 | 51060.7306 | 39.996
Devonshire Building | 2017-10-10 02:00 | 51060.7406 | 39.996
Devonshire Building | 2017-10-10 02:15 | 51060.7556 | 60.012
Devonshire Building | 2017-10-10 02:30 | 51060.7656 | 39.996
Devonshire Building | 2017-10-10 02:45 | 51060.7756 | 39.996
Devonshire Building | 2017-10-10 03:00 | 51060.7856 | 39.996
Devonshire Building | 2017-10-10 03:15 | 51060.8006 | 60.012
Devonshire Building | 2017-10-10 03:30 | 51060.8106 | 39.996
Devonshire Building | 2017-10-10 03:45 | 51060.8206 | 39.996
Devonshire Building | 2017-10-10 04:00 | 51060.8306 | 39.996
Devonshire Building | 2017-10-10 04:15 | 51060.8406 | 39.996
Devonshire Building | 2017-10-10 04:30 | 51060.8506 | 39.996
Devonshire Building | 2017-10-10 04:45 | 51060.8606 | 39.996
Devonshire Building | 2017-10-10 05:00 | 51061.1106 | 1000.008
Devonshire Building | 2017-10-10 05:15 | 51061.3906 | 1119.996
Devonshire Building | 2017-10-10 05:30 | 51061.4006 | 39.996
Devonshire Building | 2017-10-10 05:45 | 51061.4106 | 39.996
Devonshire Building | 2017-10-10 06:00 | 51061.4256 | 60.012
Devonshire Building | 2017-10-10 06:15 | 51061.4356 | 39.996
Devonshire Building | 2017-10-10 06:30 | 51061.4456 | 39.996
Devonshire Building | 2017-10-10 06:45 | 51061.4606 | 60.012
Devonshire Building | 2017-10-10 07:00 | 51061.4706 | 39.996
Devonshire Building | 2017-10-10 07:15 | 51061.4856 | 60.012
Devonshire Building | 2017-10-10 07:30 | 51061.5056 | 79.992
Devonshire Building | 2017-10-10 07:45 | 51061.5406 | 140.004
Devonshire Building | 2017-10-10 08:00 | 51061.5956 | 219.996
Devonshire Building | 2017-10-10 08:15 | 51061.6356 | 159.984
Devonshire Building | 2017-10-10 08:30 | 51061.7956 | 640.008
Devonshire Building | 2017-10-10 08:45 | 51062.2856 | 1959.984
Devonshire Building | 2017-10-10 09:00 | 51062.3406 | 219.996
Devonshire Building | 2017-10-10 09:15 | 51062.4106 | 280.008
Devonshire Building | 2017-10-10 09:30 | 51062.4806 | 280.008
Devonshire Building | 2017-10-10 09:45 | 51062.5656 | 339.984
Devonshire Building | 2017-10-10 10:00 | 51062.6906 | 500.004
Devonshire Building | 2017-10-10 10:15 | 51063.3356 | 2580.012
Devonshire Building | 2017-10-10 10:30 | 51063.4506 | 460.008
Devonshire Building | 2017-10-10 10:45 | 51063.5456 | 380.016
Devonshire Building | 2017-10-10 11:00 | 51063.6306 | 339.984
Devonshire Building | 2017-10-10 11:15 | 51063.7056 | 299.988
Devonshire Building | 2017-10-10 11:30 | 51063.7756 | 280.008
Devonshire Building | 2017-10-10 11:45 | 51064.3506 | 2300.004
Devonshire Building | 2017-10-10 12:00 | 51064.3956 | 180
Devonshire Building | 2017-10-10 12:15 | 51064.4406 | 180
Devonshire Building | 2017-10-10 12:30 | 51064.4856 | 180
Devonshire Building | 2017-10-10 12:45 | 51064.5256 | 159.984
Devonshire Building | 2017-10-10 13:00 | 51064.5756 | 200.016
Devonshire Building | 2017-10-10 13:15 | 51064.6206 | 180
Devonshire Building | 2017-10-10 13:30 | 51064.6556 | 140.004
Devonshire Building | 2017-10-10 13:45 | 51064.6956 | 159.984
Devonshire Building | 2017-10-10 14:00 | 51065.2706 | 2300.004
Devonshire Building | 2017-10-10 14:15 | 51065.3006 | 119.988
Devonshire Building | 2017-10-10 14:30 | 51065.3256 | 100.008
Devonshire Building | 2017-10-10 14:45 | 51065.3556 | 119.988
Devonshire Building | 2017-10-10 15:00 | 51065.3806 | 100.008
Devonshire Building | 2017-10-10 15:15 | 51065.4206 | 159.984
Devonshire Building | 2017-10-10 15:30 | 51065.8056 | 1540.008
Devonshire Building | 2017-10-10 15:45 | 51066.1006 | 1180.008
Devonshire Building | 2017-10-10 16:00 | 51066.2006 | 399.996
Devonshire Building | 2017-10-10 16:15 | 51066.2956 | 380.016
Devonshire Building | 2017-10-10 16:30 | 51066.3756 | 320.004
Devonshire Building | 2017-10-10 16:45 | 51066.4506 | 299.988
Devonshire Building | 2017-10-10 17:00 | 51066.5156 | 259.992
Devonshire Building | 2017-10-10 17:15 | 51066.5656 | 200.016
Devonshire Building | 2017-10-10 17:30 | 51066.6106 | 180
Devonshire Building | 2017-10-10 17:45 | 51066.6506 | 159.984
Devonshire Building | 2017-10-10 18:00 | 51066.6856 | 140.004
Devonshire Building | 2017-10-10 18:15 | 51067.1806 | 1980
Devonshire Building | 2017-10-10 18:30 | 51067.2256 | 180
Devonshire Building | 2017-10-10 18:45 | 51067.2406 | 60.012
Devonshire Building | 2017-10-10 19:00 | 51067.2556 | 60.012
Devonshire Building | 2017-10-10 19:15 | 51067.2706 | 60.012
Devonshire Building | 2017-10-10 19:30 | 51067.2956 | 100.008
Devonshire Building | 2017-10-10 19:45 | 51067.3106 | 60.012
Devonshire Building | 2017-10-10 20:00 | 51067.3256 | 60.012
Devonshire Building | 2017-10-10 20:15 | 51067.3407 | 60.012
Devonshire Building | 2017-10-10 20:30 | 51067.3607 | 79.992
Devonshire Building | 2017-10-10 20:45 | 51067.3857 | 100.008
Devonshire Building | 2017-10-10 21:00 | 51067.3957 | 39.996
Devonshire Building | 2017-10-10 21:15 | 51067.4107 | 60.012
Devonshire Building | 2017-10-10 21:30 | 51067.4257 | 60.012
Devonshire Building | 2017-10-10 21:45 | 51067.4407 | 60.012
Devonshire Building | 2017-10-10 22:00 | 51067.4557 | 60.012
Devonshire Building | 2017-10-10 22:15 | 51067.4657 | 39.996
Devonshire Building | 2017-10-10 22:30 | 51067.4807 | 60.012
Devonshire Building | 2017-10-10 22:45 | 51067.4957 | 60.012
Devonshire Building | 2017-10-10 23:00 | 51067.5107 | 60.012
Devonshire Building | 2017-10-10 23:15 | 51067.5207 | 39.996
Devonshire Building | 2017-10-10 23:30 | 51067.5357 | 60.012
Devonshire Building | 2017-10-10 23:45 | 51067.5457 | 39.996
Devonshire Building | 2017-10-11 | 51067.5586 | 60.012
Devonshire Building | 2017-10-11 00:15 | 51067.5686 | 39.996
Devonshire Building | 2017-10-11 00:30 | 51067.5836 | 60.012
Devonshire Building | 2017-10-11 00:45 | 51067.5936 | 39.996
Devonshire Building | 2017-10-11 01:00 | 51067.6086 | 60.012
Devonshire Building | 2017-10-11 01:15 | 51067.6186 | 39.996
Devonshire Building | 2017-10-11 01:30 | 51067.6286 | 39.996
Devonshire Building | 2017-10-11 01:45 | 51067.6436 | 60.012
Devonshire Building | 2017-10-11 02:00 | 51067.6536 | 39.996
Devonshire Building | 2017-10-11 02:15 | 51067.6636 | 39.996
Devonshire Building | 2017-10-11 02:30 | 51067.6736 | 39.996
Devonshire Building | 2017-10-11 02:45 | 51067.6886 | 60.012
Devonshire Building | 2017-10-11 03:00 | 51067.6986 | 39.996
Devonshire Building | 2017-10-11 03:15 | 51067.7086 | 39.996
Devonshire Building | 2017-10-11 03:30 | 51067.7186 | 39.996
Devonshire Building | 2017-10-11 03:45 | 51068.2286 | 2040.012
Devonshire Building | 2017-10-11 04:00 | 51068.2386 | 39.996
Devonshire Building | 2017-10-11 04:15 | 51068.2486 | 39.996
Devonshire Building | 2017-10-11 04:30 | 51068.2586 | 39.996
Devonshire Building | 2017-10-11 04:45 | 51068.2686 | 39.996
Devonshire Building | 2017-10-11 05:00 | 51068.2836 | 60.012
Devonshire Building | 2017-10-11 05:15 | 51068.2936 | 39.996
Devonshire Building | 2017-10-11 05:30 | 51068.3036 | 39.996
Devonshire Building | 2017-10-11 05:45 | 51068.3136 | 39.996
Devonshire Building | 2017-10-11 06:00 | 51068.3236 | 39.996
Devonshire Building | 2017-10-11 06:15 | 51068.3386 | 60.012
Devonshire Building | 2017-10-11 06:30 | 51068.3486 | 39.996
Devonshire Building | 2017-10-11 06:45 | 51068.3636 | 60.012
Devonshire Building | 2017-10-11 07:00 | 51068.3786 | 60.012
Devonshire Building | 2017-10-11 07:15 | 51068.3936 | 60.012
Devonshire Building | 2017-10-11 07:30 | 51068.4086 | 60.012
Devonshire Building | 2017-10-11 07:45 | 51068.5936 | 740.016
Devonshire Building | 2017-10-11 08:00 | 51069.0086 | 1659.996
Devonshire Building | 2017-10-11 08:15 | 51069.0436 | 140.004
Devonshire Building | 2017-10-11 08:30 | 51069.0836 | 159.984
Devonshire Building | 2017-10-11 08:45 | 51069.1286 | 180
Devonshire Building | 2017-10-11 09:00 | 51069.1736 | 180
Devonshire Building | 2017-10-11 09:15 | 51069.2236 | 200.016
Devonshire Building | 2017-10-11 09:30 | 51069.2736 | 200.016
Devonshire Building | 2017-10-11 09:45 | 51069.8686 | 2379.996
Devonshire Building | 2017-10-11 10:00 | 51069.9236 | 219.996
Devonshire Building | 2017-10-11 10:15 | 51069.9786 | 219.996
Devonshire Building | 2017-10-11 10:30 | 51070.0286 | 200.016
Devonshire Building | 2017-10-11 10:45 | 51070.0936 | 259.992
Devonshire Building | 2017-10-11 11:00 | 51070.1936 | 399.996
Devonshire Building | 2017-10-11 11:15 | 51070.3086 | 460.008
Devonshire Building | 2017-10-11 11:30 | 51070.9286 | 2480.004
Devonshire Building | 2017-10-11 11:45 | 51071.0286 | 399.996
Devonshire Building | 2017-10-11 12:00 | 51071.1086 | 320.004
Devonshire Building | 2017-10-11 12:15 | 51071.1936 | 339.984
Devonshire Building | 2017-10-11 12:30 | 51071.2636 | 280.008
Devonshire Building | 2017-10-11 12:45 | 51071.5636 | 1199.988
Devonshire Building | 2017-10-11 13:00 | 51071.9386 | 1500.012
Devonshire Building | 2017-10-11 13:15 | 51072.0086 | 280.008
Devonshire Building | 2017-10-11 13:30 | 51072.0686 | 240.012
Devonshire Building | 2017-10-11 13:45 | 51072.1286 | 240.012
Devonshire Building | 2017-10-11 14:00 | 51072.1836 | 219.996
Devonshire Building | 2017-10-11 14:15 | 51072.5286 | 1379.988
Devonshire Building | 2017-10-11 14:30 | 51072.8186 | 1159.992
Devonshire Building | 2017-10-11 14:45 | 51072.8636 | 180
Devonshire Building | 2017-10-11 15:00 | 51072.9086 | 180
Devonshire Building | 2017-10-11 15:15 | 51072.9536 | 180
Devonshire Building | 2017-10-11 15:30 | 51073.0036 | 200.016
Devonshire Building | 2017-10-11 15:45 | 51073.0436 | 159.984
Devonshire Building | 2017-10-11 16:00 | 51073.6586 | 2459.988
Devonshire Building | 2017-10-11 16:15 | 51073.7036 | 180
Devonshire Building | 2017-10-11 16:30 | 51073.7586 | 219.996
Devonshire Building | 2017-10-11 16:45 | 51073.8086 | 200.016
Devonshire Building | 2017-10-11 17:00 | 51073.8536 | 180
Devonshire Building | 2017-10-11 17:15 | 51073.9036 | 200.016
Devonshire Building | 2017-10-11 17:30 | 51073.9486 | 180
Devonshire Building | 2017-10-11 17:45 | 51073.9936 | 180
Devonshire Building | 2017-10-11 18:00 | 51074.0336 | 159.984
Devonshire Building | 2017-10-11 18:15 | 51074.0736 | 159.984
Devonshire Building | 2017-10-11 18:30 | 51074.1136 | 159.984
Devonshire Building | 2017-10-11 18:45 | 51074.1486 | 140.004
Devonshire Building | 2017-10-11 19:00 | 51074.1836 | 140.004
Devonshire Building | 2017-10-11 19:15 | 51074.2136 | 119.988
Devonshire Building | 2017-10-11 19:30 | 51074.2436 | 119.988
Devonshire Building | 2017-10-11 19:45 | 51074.3136 | 280.008
Devonshire Building | 2017-10-11 20:00 | 51074.7836 | 1879.992
Devonshire Building | 2017-10-11 20:15 | 51074.7936 | 39.996
Devonshire Building | 2017-10-11 20:30 | 51074.8086 | 60.012
Devonshire Building | 2017-10-11 20:45 | 51074.8336 | 100.008
Devonshire Building | 2017-10-11 21:00 | 51074.8436 | 39.996
Devonshire Building | 2017-10-11 21:15 | 51074.8586 | 60.012
Devonshire Building | 2017-10-11 21:30 | 51074.8736 | 60.012
Devonshire Building | 2017-10-11 21:45 | 51074.8886 | 60.012
Devonshire Building | 2017-10-11 22:00 | 51074.9036 | 60.012
Devonshire Building | 2017-10-11 22:15 | 51074.9186 | 60.012
Devonshire Building | 2017-10-11 22:30 | 51074.9336 | 60.012
Devonshire Building | 2017-10-11 22:45 | 51074.9486 | 60.012
Devonshire Building | 2017-10-11 23:00 | 51074.9636 | 60.012
Devonshire Building | 2017-10-11 23:15 | 51074.9786 | 60.012
Devonshire Building | 2017-10-11 23:30 | 51074.9936 | 60.012
Devonshire Building | 2017-10-11 23:45 | 51075.0036 | 39.996
Devonshire Building | 2017-10-12 | 51075.0195 | 60.012
Devonshire Building | 2017-10-12 00:15 | 51075.0345 | 60.012
Devonshire Building | 2017-10-12 00:30 | 51075.0495 | 60.012
Devonshire Building | 2017-10-12 00:45 | 51075.0595 | 39.996
Devonshire Building | 2017-10-12 01:00 | 51075.0745 | 60.012
Devonshire Building | 2017-10-12 01:15 | 51075.0845 | 39.996
Devonshire Building | 2017-10-12 01:30 | 51075.0995 | 60.012
Devonshire Building | 2017-10-12 01:45 | 51075.1145 | 60.012
Devonshire Building | 2017-10-12 02:00 | 51075.1245 | 39.996
Devonshire Building | 2017-10-12 02:15 | 51075.1395 | 60.012
Devonshire Building | 2017-10-12 02:30 | 51075.1495 | 39.996
Devonshire Building | 2017-10-12 02:45 | 51075.1595 | 39.996
Devonshire Building | 2017-10-12 03:00 | 51075.1745 | 60.012
Devonshire Building | 2017-10-12 03:15 | 51075.1845 | 39.996
Devonshire Building | 2017-10-12 03:30 | 51075.1945 | 39.996
Devonshire Building | 2017-10-12 03:45 | 51075.2095 | 60.012
Devonshire Building | 2017-10-12 04:00 | 51075.2195 | 39.996
Devonshire Building | 2017-10-12 04:15 | 51075.2295 | 39.996
Devonshire Building | 2017-10-12 04:30 | 51075.2395 | 39.996
Devonshire Building | 2017-10-12 04:45 | 51075.2495 | 39.996
Devonshire Building | 2017-10-12 05:00 | 51075.2645 | 60.012
Devonshire Building | 2017-10-12 05:15 | 51075.2745 | 39.996
Devonshire Building | 2017-10-12 05:30 | 51075.2845 | 39.996
Devonshire Building | 2017-10-12 05:45 | 51075.8045 | 2080.008
Devonshire Building | 2017-10-12 06:00 | 51075.8145 | 39.996
Devonshire Building | 2017-10-12 06:15 | 51075.8295 | 60.012
Devonshire Building | 2017-10-12 06:30 | 51075.8395 | 39.996
Devonshire Building | 2017-10-12 06:45 | 51075.8595 | 79.992
Devonshire Building | 2017-10-12 07:00 | 51075.8695 | 39.996
Devonshire Building | 2017-10-12 07:15 | 51075.8895 | 79.992
Devonshire Building | 2017-10-12 07:30 | 51075.9045 | 60.012
Devonshire Building | 2017-10-12 07:45 | 51075.9195 | 60.012
Devonshire Building | 2017-10-12 08:00 | 51075.9595 | 159.984
Devonshire Building | 2017-10-12 08:15 | 51076.5545 | 2379.996
Devonshire Building | 2017-10-12 08:30 | 51076.6145 | 240.012
Devonshire Building | 2017-10-12 08:45 | 51076.6745 | 240.012
Devonshire Building | 2017-10-12 09:00 | 51076.7395 | 259.992
Devonshire Building | 2017-10-12 09:15 | 51076.7996 | 240.012
Devonshire Building | 2017-10-12 09:30 | 51076.8596 | 240.012
Devonshire Building | 2017-10-12 09:45 | 51076.9146 | 219.996
Devonshire Building | 2017-10-12 10:00 | 51077.5096 | 2379.996
Devonshire Building | 2017-10-12 10:15 | 51077.5845 | 299.988
Devonshire Building | 2017-10-12 10:30 | 51077.6295 | 180
Devonshire Building | 2017-10-12 10:45 | 51077.6645 | 140.004
Devonshire Building | 2017-10-12 11:00 | 51077.7045 | 159.984
Devonshire Building | 2017-10-12 11:15 | 51078.2845 | 2319.984
Devonshire Building | 2017-10-12 11:30 | 51078.3245 | 159.984
Devonshire Building | 2017-10-12 11:45 | 51078.3595 | 140.004
Devonshire Building | 2017-10-12 12:00 | 51078.3995 | 159.984
Devonshire Building | 2017-10-12 12:15 | 51078.4345 | 140.004
Devonshire Building | 2017-10-12 12:30 | 51078.4795 | 180
Devonshire Building | 2017-10-12 12:45 | 51079.0845 | 2419.992
Devonshire Building | 2017-10-12 13:00 | 51079.1395 | 219.996
Devonshire Building | 2017-10-12 13:15 | 51079.1895 | 200.016
Devonshire Building | 2017-10-12 13:30 | 51079.2345 | 180
Devonshire Building | 2017-10-12 13:45 | 51079.2845 | 200.016
Devonshire Building | 2017-10-12 14:00 | 51079.3295 | 180
Devonshire Building | 2017-10-12 14:15 | 51079.3745 | 180
Devonshire Building | 2017-10-12 14:30 | 51079.5295 | 619.992
Devonshire Building | 2017-10-12 14:45 | 51079.9845 | 1820.016
Devonshire Building | 2017-10-12 15:00 | 51080.0245 | 159.984
Devonshire Building | 2017-10-12 15:15 | 51080.0795 | 219.996
Devonshire Building | 2017-10-12 15:30 | 51080.1645 | 339.984
Devonshire Building | 2017-10-12 15:45 | 51080.2545 | 360
Devonshire Building | 2017-10-12 16:00 | 51080.3345 | 320.004
Devonshire Building | 2017-10-12 16:15 | 51080.9345 | 2400.012
Devonshire Building | 2017-10-12 16:30 | 51080.9895 | 219.996
Devonshire Building | 2017-10-12 16:45 | 51081.0495 | 240.012
Devonshire Building | 2017-10-12 17:00 | 51081.1145 | 259.992
Devonshire Building | 2017-10-12 17:15 | 51081.1645 | 200.016
Devonshire Building | 2017-10-12 17:30 | 51081.2095 | 180
Devonshire Building | 2017-10-12 17:45 | 51081.2445 | 140.004
Devonshire Building | 2017-10-12 18:00 | 51081.2795 | 140.004
Devonshire Building | 2017-10-12 18:15 | 51081.3095 | 119.988
Devonshire Building | 2017-10-12 18:30 | 51081.3345 | 100.008
Devonshire Building | 2017-10-12 18:45 | 51081.3595 | 100.008
Devonshire Building | 2017-10-12 19:00 | 51081.3845 | 100.008
Devonshire Building | 2017-10-12 19:15 | 51081.4045 | 79.992
Devonshire Building | 2017-10-12 19:30 | 51081.4345 | 119.988
Devonshire Building | 2017-10-12 19:45 | 51081.4495 | 60.012
Devonshire Building | 2017-10-12 20:00 | 51081.4695 | 79.992
Devonshire Building | 2017-10-12 20:15 | 51081.4845 | 60.012
Devonshire Building | 2017-10-12 20:30 | 51081.5045 | 79.992
Devonshire Building | 2017-10-12 20:45 | 51081.5395 | 140.004
Devonshire Building | 2017-10-12 21:00 | 51081.5495 | 39.996
Devonshire Building | 2017-10-12 21:15 | 51081.5595 | 39.996
Devonshire Building | 2017-10-12 21:30 | 51081.5695 | 39.996
Devonshire Building | 2017-10-12 21:45 | 51081.5795 | 39.996
Devonshire Building | 2017-10-12 22:00 | 51081.5895 | 39.996
Devonshire Building | 2017-10-12 22:15 | 51081.5945 | 20.016
Devonshire Building | 2017-10-12 22:30 | 51081.6045 | 39.996
Devonshire Building | 2017-10-12 22:45 | 51082.1195 | 2059.992
Devonshire Building | 2017-10-12 23:00 | 51082.1295 | 39.996
Devonshire Building | 2017-10-12 23:15 | 51082.1395 | 39.996
Devonshire Building | 2017-10-12 23:30 | 51082.1445 | 20.016
Devonshire Building | 2017-10-12 23:45 | 51082.1545 | 39.996
Devonshire Building | 2017-10-13 | 51082.1641 | 39.996
Devonshire Building | 2017-10-13 00:15 | 51082.1741 | 39.996
Devonshire Building | 2017-10-13 00:30 | 51082.1841 | 39.996
Devonshire Building | 2017-10-13 00:45 | 51082.1891 | 20.016
Devonshire Building | 2017-10-13 01:00 | 51082.1991 | 39.996
Devonshire Building | 2017-10-13 01:15 | 51082.2091 | 39.996
Devonshire Building | 2017-10-13 01:30 | 51082.2141 | 20.016
Devonshire Building | 2017-10-13 01:45 | 51082.2241 | 39.996
Devonshire Building | 2017-10-13 02:00 | 51082.2341 | 39.996
Devonshire Building | 2017-10-13 02:15 | 51082.2441 | 39.996
Devonshire Building | 2017-10-13 02:30 | 51082.2541 | 39.996
Devonshire Building | 2017-10-13 02:45 | 51082.2641 | 39.996
Devonshire Building | 2017-10-13 03:00 | 51082.2691 | 20.016
Devonshire Building | 2017-10-13 03:15 | 51082.2791 | 39.996
Devonshire Building | 2017-10-13 03:30 | 51082.2891 | 39.996
Devonshire Building | 2017-10-13 03:45 | 51082.2991 | 39.996
Devonshire Building | 2017-10-13 04:00 | 51082.3091 | 39.996
Devonshire Building | 2017-10-13 04:15 | 51082.3191 | 39.996
Devonshire Building | 2017-10-13 04:30 | 51082.3291 | 39.996
Devonshire Building | 2017-10-13 04:45 | 51082.3341 | 20.016
Devonshire Building | 2017-10-13 05:00 | 51082.3441 | 39.996
Devonshire Building | 2017-10-13 05:15 | 51082.3541 | 39.996
Devonshire Building | 2017-10-13 05:30 | 51082.3591 | 20.016
Devonshire Building | 2017-10-13 05:45 | 51082.3691 | 39.996
Devonshire Building | 2017-10-13 06:00 | 51082.3791 | 39.996
Devonshire Building | 2017-10-13 06:15 | 51082.3891 | 39.996
Devonshire Building | 2017-10-13 06:30 | 51082.3991 | 39.996
Devonshire Building | 2017-10-13 06:45 | 51082.4041 | 20.016
Devonshire Building | 2017-10-13 07:00 | 51082.4191 | 60.012
Devonshire Building | 2017-10-13 07:15 | 51082.9491 | 2120.004
Devonshire Building | 2017-10-13 07:30 | 51082.9641 | 60.012
Devonshire Building | 2017-10-13 07:45 | 51082.9891 | 100.008
Devonshire Building | 2017-10-13 08:00 | 51083.0291 | 159.984
Devonshire Building | 2017-10-13 08:15 | 51083.0691 | 159.984
Devonshire Building | 2017-10-13 08:30 | 51083.1041 | 140.004
Devonshire Building | 2017-10-13 08:45 | 51083.1441 | 159.984
Devonshire Building | 2017-10-13 09:00 | 51083.1841 | 159.984
Devonshire Building | 2017-10-13 09:15 | 51083.7791 | 2379.996
Devonshire Building | 2017-10-13 09:30 | 51083.8341 | 219.996
Devonshire Building | 2017-10-13 09:45 | 51083.9041 | 280.008
Devonshire Building | 2017-10-13 10:00 | 51083.9791 | 299.988
Devonshire Building | 2017-10-13 10:15 | 51084.0541 | 299.988
Devonshire Building | 2017-10-13 10:30 | 51084.6541 | 2400.012
Devonshire Building | 2017-10-13 10:45 | 51084.7141 | 240.012
Devonshire Building | 2017-10-13 11:00 | 51084.7841 | 280.008
Devonshire Building | 2017-10-13 11:15 | 51084.8541 | 280.008
Devonshire Building | 2017-10-13 11:30 | 51084.9191 | 259.992
Devonshire Building | 2017-10-13 11:45 | 51084.9841 | 259.992
Devonshire Building | 2017-10-13 12:00 | 51085.5441 | 2239.992
Devonshire Building | 2017-10-13 12:15 | 51085.6641 | 479.988
Devonshire Building | 2017-10-13 12:30 | 51085.7241 | 240.012
Devonshire Building | 2017-10-13 12:45 | 51085.7941 | 280.008
Devonshire Building | 2017-10-13 13:00 | 51085.8791 | 339.984
Devonshire Building | 2017-10-13 13:15 | 51085.9691 | 360
Devonshire Building | 2017-10-13 13:30 | 51086.054 | 339.984
Devonshire Building | 2017-10-13 13:45 | 51086.139 | 339.984
Devonshire Building | 2017-10-13 14:00 | 51086.769 | 2520
Devonshire Building | 2017-10-13 14:15 | 51086.849 | 320.004
Devonshire Building | 2017-10-13 14:30 | 51086.929 | 320.004
Devonshire Building | 2017-10-13 14:45 | 51087.004 | 299.988
Devonshire Building | 2017-10-13 15:00 | 51087.079 | 299.988
Devonshire Building | 2017-10-13 15:15 | 51087.139 | 240.012
Devonshire Building | 2017-10-13 15:30 | 51087.189 | 200.016
Devonshire Building | 2017-10-13 15:45 | 51087.229 | 159.984
Devonshire Building | 2017-10-13 16:00 | 51087.779 | 2199.996
Devonshire Building | 2017-10-13 16:15 | 51087.809 | 119.988
Devonshire Building | 2017-10-13 16:30 | 51087.834 | 100.008
Devonshire Building | 2017-10-13 16:45 | 51087.864 | 119.988
Devonshire Building | 2017-10-13 17:00 | 51087.889 | 100.008
Devonshire Building | 2017-10-13 17:15 | 51087.919 | 119.988
Devonshire Building | 2017-10-13 17:30 | 51087.944 | 100.008
Devonshire Building | 2017-10-13 17:45 | 51087.969 | 100.008
Devonshire Building | 2017-10-13 18:00 | 51087.989 | 79.992
Devonshire Building | 2017-10-13 18:15 | 51088.014 | 100.008
Devonshire Building | 2017-10-13 18:30 | 51088.039 | 100.008
Devonshire Building | 2017-10-13 18:45 | 51088.059 | 79.992
Devonshire Building | 2017-10-13 19:00 | 51088.084 | 100.008
Devonshire Building | 2017-10-13 19:15 | 51088.104 | 79.992
Devonshire Building | 2017-10-13 19:30 | 51088.129 | 100.008
Devonshire Building | 2017-10-13 19:45 | 51088.149 | 79.992
Devonshire Building | 2017-10-13 20:00 | 51088.164 | 60.012
Devonshire Building | 2017-10-13 20:15 | 51088.184 | 79.992
Devonshire Building | 2017-10-13 20:30 | 51088.199 | 60.012
Devonshire Building | 2017-10-13 20:45 | 51088.239 | 159.984
Devonshire Building | 2017-10-13 21:00 | 51088.249 | 39.996
Devonshire Building | 2017-10-13 21:15 | 51088.259 | 39.996
Devonshire Building | 2017-10-13 21:30 | 51088.274 | 60.012
Devonshire Building | 2017-10-13 21:45 | 51088.284 | 39.996
Devonshire Building | 2017-10-13 22:00 | 51088.294 | 39.996
Devonshire Building | 2017-10-13 22:15 | 51088.304 | 39.996
Devonshire Building | 2017-10-13 22:30 | 51088.789 | 1940.004
Devonshire Building | 2017-10-13 22:45 | 51088.834 | 180
Devonshire Building | 2017-10-13 23:00 | 51088.844 | 39.996
Devonshire Building | 2017-10-13 23:15 | 51088.854 | 39.996
Devonshire Building | 2017-10-13 23:30 | 51088.859 | 20.016
Devonshire Building | 2017-10-13 23:45 | 51088.869 | 39.996
Devonshire Building | 2017-10-14 | 51088.8789 | 39.996
Devonshire Building | 2017-10-14 00:15 | 51088.8889 | 39.996
Devonshire Building | 2017-10-14 00:30 | 51088.8989 | 39.996
Devonshire Building | 2017-10-14 00:45 | 51088.9089 | 39.996
Devonshire Building | 2017-10-14 01:00 | 51088.9139 | 20.016
Devonshire Building | 2017-10-14 01:15 | 51088.9239 | 39.996
Devonshire Building | 2017-10-14 01:30 | 51088.9339 | 39.996
Devonshire Building | 2017-10-14 01:45 | 51088.9439 | 39.996
Devonshire Building | 2017-10-14 02:00 | 51088.9589 | 60.012
Devonshire Building | 2017-10-14 02:15 | 51088.9689 | 39.996
Devonshire Building | 2017-10-14 02:30 | 51088.9789 | 39.996
Devonshire Building | 2017-10-14 02:45 | 51088.9889 | 39.996
Devonshire Building | 2017-10-14 03:00 | 51088.9989 | 39.996
Devonshire Building | 2017-10-14 03:15 | 51089.0089 | 39.996
Devonshire Building | 2017-10-14 03:30 | 51089.0189 | 39.996
Devonshire Building | 2017-10-14 03:45 | 51089.0289 | 39.996
Devonshire Building | 2017-10-14 04:00 | 51089.0389 | 39.996
Devonshire Building | 2017-10-14 04:15 | 51089.0489 | 39.996
Devonshire Building | 2017-10-14 04:30 | 51089.0589 | 39.996
Devonshire Building | 2017-10-14 04:45 | 51089.0689 | 39.996
Devonshire Building | 2017-10-14 05:00 | 51089.0789 | 39.996
Devonshire Building | 2017-10-14 05:15 | 51089.0889 | 39.996
Devonshire Building | 2017-10-14 05:30 | 51089.0989 | 39.996
Devonshire Building | 2017-10-14 05:45 | 51089.1089 | 39.996
Devonshire Building | 2017-10-14 06:00 | 51089.1189 | 39.996
Devonshire Building | 2017-10-14 06:15 | 51089.1239 | 20.016
Devonshire Building | 2017-10-14 06:30 | 51089.1339 | 39.996
Devonshire Building | 2017-10-14 06:45 | 51089.1439 | 39.996
Devonshire Building | 2017-10-14 07:00 | 51089.1539 | 39.996
Devonshire Building | 2017-10-14 07:15 | 51089.1589 | 20.016
Devonshire Building | 2017-10-14 07:30 | 51089.1689 | 39.996
Devonshire Building | 2017-10-14 07:45 | 51089.1789 | 39.996
Devonshire Building | 2017-10-14 08:00 | 51089.1839 | 20.016
Devonshire Building | 2017-10-14 08:15 | 51089.5239 | 1360.008
Devonshire Building | 2017-10-14 08:30 | 51089.7089 | 740.016
Devonshire Building | 2017-10-14 08:45 | 51089.7189 | 39.996
Devonshire Building | 2017-10-14 09:00 | 51089.7289 | 39.996
Devonshire Building | 2017-10-14 09:15 | 51089.7439 | 60.012
Devonshire Building | 2017-10-14 09:30 | 51089.7539 | 39.996
Devonshire Building | 2017-10-14 09:45 | 51089.7589 | 20.016
Devonshire Building | 2017-10-14 10:00 | 51089.7689 | 39.996
Devonshire Building | 2017-10-14 10:15 | 51089.7789 | 39.996
Devonshire Building | 2017-10-14 10:30 | 51089.7889 | 39.996
Devonshire Building | 2017-10-14 10:45 | 51089.7989 | 39.996
Devonshire Building | 2017-10-14 11:00 | 51089.8139 | 60.012
Devonshire Building | 2017-10-14 11:15 | 51089.8239 | 39.996
Devonshire Building | 2017-10-14 11:30 | 51089.8389 | 60.012
Devonshire Building | 2017-10-14 11:45 | 51089.8489 | 39.996
Devonshire Building | 2017-10-14 12:00 | 51089.8639 | 60.012
Devonshire Building | 2017-10-14 12:15 | 51089.8739 | 39.996
Devonshire Building | 2017-10-14 12:30 | 51089.8889 | 60.012
Devonshire Building | 2017-10-14 12:45 | 51089.8989 | 39.996
Devonshire Building | 2017-10-14 13:00 | 51089.9139 | 60.012
Devonshire Building | 2017-10-14 13:15 | 51089.9239 | 39.996
Devonshire Building | 2017-10-14 13:30 | 51089.9439 | 79.992
Devonshire Building | 2017-10-14 13:45 | 51089.9689 | 100.008
Devonshire Building | 2017-10-14 14:00 | 51089.9939 | 100.008
Devonshire Building | 2017-10-14 14:15 | 51090.0239 | 119.988
Devonshire Building | 2017-10-14 14:30 | 51090.0489 | 100.008
Devonshire Building | 2017-10-14 14:45 | 51090.0789 | 119.988
Devonshire Building | 2017-10-14 15:00 | 51090.1039 | 100.008
Devonshire Building | 2017-10-14 15:15 | 51090.1339 | 119.988
Devonshire Building | 2017-10-14 15:30 | 51090.1589 | 100.008
Devonshire Building | 2017-10-14 15:45 | 51090.1889 | 119.988
Devonshire Building | 2017-10-14 16:00 | 51090.6989 | 2040.012
Devonshire Building | 2017-10-14 16:15 | 51090.7139 | 60.012
Devonshire Building | 2017-10-14 16:30 | 51090.7289 | 60.012
Devonshire Building | 2017-10-14 16:45 | 51090.7439 | 60.012
Devonshire Building | 2017-10-14 17:00 | 51090.7589 | 60.012
Devonshire Building | 2017-10-14 17:15 | 51090.7689 | 39.996
Devonshire Building | 2017-10-14 17:30 | 51090.7839 | 60.012
Devonshire Building | 2017-10-14 17:45 | 51090.8039 | 79.992
Devonshire Building | 2017-10-14 18:00 | 51090.8189 | 60.012
Devonshire Building | 2017-10-14 18:15 | 51090.8389 | 79.992
Devonshire Building | 2017-10-14 18:30 | 51090.8589 | 79.992
Devonshire Building | 2017-10-14 18:45 | 51090.8739 | 60.012
Devonshire Building | 2017-10-14 19:00 | 51090.8939 | 79.992
Devonshire Building | 2017-10-14 19:15 | 51090.9089 | 60.012
Devonshire Building | 2017-10-14 19:30 | 51090.9289 | 79.992
Devonshire Building | 2017-10-14 19:45 | 51090.9439 | 60.012
Devonshire Building | 2017-10-14 20:00 | 51090.9589 | 60.012
Devonshire Building | 2017-10-14 20:15 | 51090.9739 | 60.012
Devonshire Building | 2017-10-14 20:30 | 51090.9939 | 79.992
Devonshire Building | 2017-10-14 20:45 | 51091.0239 | 119.988
Devonshire Building | 2017-10-14 21:00 | 51091.0389 | 60.012
Devonshire Building | 2017-10-14 21:15 | 51091.0539 | 60.012
Devonshire Building | 2017-10-14 21:30 | 51091.0689 | 60.012
Devonshire Building | 2017-10-14 21:45 | 51091.0789 | 39.996
Devonshire Building | 2017-10-14 22:00 | 51091.0939 | 60.012
Devonshire Building | 2017-10-14 22:15 | 51091.1089 | 60.012
Devonshire Building | 2017-10-14 22:30 | 51091.1189 | 39.996
Devonshire Building | 2017-10-14 22:45 | 51091.134 | 60.012
Devonshire Building | 2017-10-14 23:00 | 51091.1439 | 39.996
Devonshire Building | 2017-10-14 23:15 | 51091.159 | 60.012
Devonshire Building | 2017-10-14 23:30 | 51091.169 | 39.996
Devonshire Building | 2017-10-14 23:45 | 51091.184 | 60.012
Devonshire Building | 2017-10-15 | 51091.1953 | 39.996
Devonshire Building | 2017-10-15 00:15 | 51091.2103 | 60.012
Devonshire Building | 2017-10-15 00:30 | 51091.2203 | 39.996
Devonshire Building | 2017-10-15 00:45 | 51091.2353 | 60.012
Devonshire Building | 2017-10-15 01:00 | 51091.2453 | 39.996
Devonshire Building | 2017-10-15 01:15 | 51091.2603 | 60.012
Devonshire Building | 2017-10-15 01:30 | 51091.2703 | 39.996
Devonshire Building | 2017-10-15 01:45 | 51091.2803 | 39.996
Devonshire Building | 2017-10-15 02:00 | 51091.2953 | 60.012
Devonshire Building | 2017-10-15 02:15 | 51091.8103 | 2059.992
Devonshire Building | 2017-10-15 02:30 | 51091.8203 | 39.996
Devonshire Building | 2017-10-15 02:45 | 51091.8303 | 39.996
Devonshire Building | 2017-10-15 03:00 | 51091.8403 | 39.996
Devonshire Building | 2017-10-15 03:15 | 51091.8503 | 39.996
Devonshire Building | 2017-10-15 03:30 | 51091.8653 | 60.012
Devonshire Building | 2017-10-15 03:45 | 51091.8753 | 39.996
Devonshire Building | 2017-10-15 04:00 | 51091.8853 | 39.996
Devonshire Building | 2017-10-15 04:15 | 51091.8953 | 39.996
Devonshire Building | 2017-10-15 04:30 | 51091.9103 | 60.012
Devonshire Building | 2017-10-15 04:45 | 51091.9253 | 60.012
Devonshire Building | 2017-10-15 05:00 | 51091.9353 | 39.996
Devonshire Building | 2017-10-15 05:15 | 51091.9503 | 60.012
Devonshire Building | 2017-10-15 05:30 | 51091.9653 | 60.012
Devonshire Building | 2017-10-15 05:45 | 51091.9803 | 60.012
Devonshire Building | 2017-10-15 06:00 | 51091.9953 | 60.012
Devonshire Building | 2017-10-15 06:15 | 51092.0103 | 60.012
Devonshire Building | 2017-10-15 06:30 | 51092.0203 | 39.996
Devonshire Building | 2017-10-15 06:45 | 51092.0353 | 60.012
Devonshire Building | 2017-10-15 07:00 | 51092.0503 | 60.012
Devonshire Building | 2017-10-15 07:15 | 51092.0603 | 39.996
Devonshire Building | 2017-10-15 07:30 | 51092.0753 | 60.012
Devonshire Building | 2017-10-15 07:45 | 51092.0903 | 60.012
Devonshire Building | 2017-10-15 08:00 | 51092.1003 | 39.996
Devonshire Building | 2017-10-15 08:15 | 51092.1153 | 60.012
Devonshire Building | 2017-10-15 08:30 | 51092.1253 | 39.996
Devonshire Building | 2017-10-15 08:45 | 51092.1353 | 39.996
Devonshire Building | 2017-10-15 09:00 | 51092.1503 | 60.012
Devonshire Building | 2017-10-15 09:15 | 51092.1603 | 39.996
Devonshire Building | 2017-10-15 09:30 | 51092.1753 | 60.012
Devonshire Building | 2017-10-15 09:45 | 51092.1853 | 39.996
Devonshire Building | 2017-10-15 10:00 | 51092.1953 | 39.996
Devonshire Building | 2017-10-15 10:15 | 51092.2103 | 60.012
Devonshire Building | 2017-10-15 10:30 | 51092.2203 | 39.996
Devonshire Building | 2017-10-15 10:45 | 51092.2303 | 39.996
Devonshire Building | 2017-10-15 11:00 | 51092.2403 | 39.996
Devonshire Building | 2017-10-15 11:15 | 51092.2553 | 60.012
Devonshire Building | 2017-10-15 11:30 | 51092.5253 | 1080
Devonshire Building | 2017-10-15 11:45 | 51092.7703 | 979.992
Devonshire Building | 2017-10-15 12:00 | 51092.7803 | 39.996
Devonshire Building | 2017-10-15 12:15 | 51092.7903 | 39.996
Devonshire Building | 2017-10-15 12:30 | 51092.8003 | 39.996
Devonshire Building | 2017-10-15 12:45 | 51092.8103 | 39.996
Devonshire Building | 2017-10-15 13:00 | 51092.8203 | 39.996
Devonshire Building | 2017-10-15 13:15 | 51092.8353 | 60.012
Devonshire Building | 2017-10-15 13:30 | 51092.8453 | 39.996
Devonshire Building | 2017-10-15 13:45 | 51092.8703 | 100.008
Devonshire Building | 2017-10-15 14:00 | 51092.8953 | 100.008
Devonshire Building | 2017-10-15 14:15 | 51092.9203 | 100.008
Devonshire Building | 2017-10-15 14:30 | 51092.9503 | 119.988
Devonshire Building | 2017-10-15 14:45 | 51092.9753 | 100.008
Devonshire Building | 2017-10-15 15:00 | 51093.0053 | 119.988
Devonshire Building | 2017-10-15 15:15 | 51093.0353 | 119.988
Devonshire Building | 2017-10-15 15:30 | 51093.0603 | 100.008
Devonshire Building | 2017-10-15 15:45 | 51093.0903 | 119.988
Devonshire Building | 2017-10-15 16:00 | 51093.1053 | 60.012
Devonshire Building | 2017-10-15 16:15 | 51093.1203 | 60.012
Devonshire Building | 2017-10-15 16:30 | 51093.1303 | 39.996
Devonshire Building | 2017-10-15 16:45 | 51093.1403 | 39.996
Devonshire Building | 2017-10-15 17:00 | 51093.1553 | 60.012
Devonshire Building | 2017-10-15 17:15 | 51093.1653 | 39.996
Devonshire Building | 2017-10-15 17:30 | 51093.1753 | 39.996
Devonshire Building | 2017-10-15 17:45 | 51093.1853 | 39.996
Devonshire Building | 2017-10-15 18:00 | 51093.1953 | 39.996
Devonshire Building | 2017-10-15 18:15 | 51093.2103 | 60.012
Devonshire Building | 2017-10-15 18:30 | 51093.2203 | 39.996
Devonshire Building | 2017-10-15 18:45 | 51093.2303 | 39.996
Devonshire Building | 2017-10-15 19:00 | 51093.2403 | 39.996
Devonshire Building | 2017-10-15 19:15 | 51093.2503 | 39.996
Devonshire Building | 2017-10-15 19:30 | 51093.2603 | 39.996
Devonshire Building | 2017-10-15 19:45 | 51093.2703 | 39.996
Devonshire Building | 2017-10-15 20:00 | 51093.2803 | 39.996
Devonshire Building | 2017-10-15 20:15 | 51093.2903 | 39.996
Devonshire Building | 2017-10-15 20:30 | 51093.7953 | 2019.996
Devonshire Building | 2017-10-15 20:45 | 51093.8153 | 79.992
Devonshire Building | 2017-10-15 21:00 | 51093.8303 | 60.012
Devonshire Building | 2017-10-15 21:15 | 51093.8403 | 39.996
Devonshire Building | 2017-10-15 21:30 | 51093.8503 | 39.996
Devonshire Building | 2017-10-15 21:45 | 51093.8603 | 39.996
Devonshire Building | 2017-10-15 22:00 | 51093.8703 | 39.996
Devonshire Building | 2017-10-15 22:15 | 51093.8803 | 39.996
Devonshire Building | 2017-10-15 22:30 | 51093.8953 | 60.012
Devonshire Building | 2017-10-15 22:45 | 51093.9053 | 39.996
Devonshire Building | 2017-10-15 23:00 | 51093.9203 | 60.012
Devonshire Building | 2017-10-15 23:15 | 51093.9303 | 39.996
Devonshire Building | 2017-10-15 23:30 | 51093.9453 | 60.012
Devonshire Building | 2017-10-15 23:45 | 51093.9603 | 60.012
Devonshire Building | 2017-10-16 | 51093.9727 | 60.012
Devonshire Building | 2017-10-16 00:15 | 51093.9877 | 60.012
Devonshire Building | 2017-10-16 00:30 | 51093.9977 | 39.996
Devonshire Building | 2017-10-16 00:45 | 51094.0127 | 60.012
Devonshire Building | 2017-10-16 01:00 | 51094.0277 | 60.012
Devonshire Building | 2017-10-16 01:15 | 51094.0377 | 39.996
Devonshire Building | 2017-10-16 01:30 | 51094.0527 | 60.012
Devonshire Building | 2017-10-16 01:45 | 51094.0627 | 39.996
Devonshire Building | 2017-10-16 02:00 | 51094.0777 | 60.012
Devonshire Building | 2017-10-16 02:15 | 51094.0877 | 39.996
Devonshire Building | 2017-10-16 02:30 | 51094.1027 | 60.012
Devonshire Building | 2017-10-16 02:45 | 51094.1127 | 39.996
Devonshire Building | 2017-10-16 03:00 | 51094.1277 | 60.012
Devonshire Building | 2017-10-16 03:15 | 51094.1377 | 39.996
Devonshire Building | 2017-10-16 03:30 | 51094.1527 | 60.012
Devonshire Building | 2017-10-16 03:45 | 51094.1627 | 39.996
Devonshire Building | 2017-10-16 04:00 | 51094.1727 | 39.996
Devonshire Building | 2017-10-16 04:15 | 51094.1877 | 60.012
Devonshire Building | 2017-10-16 04:30 | 51094.1977 | 39.996
Devonshire Building | 2017-10-16 04:45 | 51094.2077 | 39.996
Devonshire Building | 2017-10-16 05:00 | 51094.2177 | 39.996
Devonshire Building | 2017-10-16 05:15 | 51094.2277 | 39.996
Devonshire Building | 2017-10-16 05:30 | 51094.2377 | 39.996
Devonshire Building | 2017-10-16 05:45 | 51094.2527 | 60.012
Devonshire Building | 2017-10-16 06:00 | 51094.2627 | 39.996
Devonshire Building | 2017-10-16 06:15 | 51094.7677 | 2019.996
Devonshire Building | 2017-10-16 06:30 | 51094.7777 | 39.996
Devonshire Building | 2017-10-16 06:45 | 51094.7877 | 39.996
Devonshire Building | 2017-10-16 07:00 | 51094.8077 | 79.992
Devonshire Building | 2017-10-16 07:15 | 51094.8177 | 39.996
Devonshire Building | 2017-10-16 07:30 | 51094.8327 | 60.012
Devonshire Building | 2017-10-16 07:45 | 51094.8577 | 100.008
Devonshire Building | 2017-10-16 08:00 | 51094.8827 | 100.008
Devonshire Building | 2017-10-16 08:15 | 51094.9077 | 100.008
Devonshire Building | 2017-10-16 08:30 | 51095.4827 | 2300.004
Devonshire Building | 2017-10-16 08:45 | 51095.5377 | 219.996
Devonshire Building | 2017-10-16 09:00 | 51095.5977 | 240.012
Devonshire Building | 2017-10-16 09:15 | 51095.6827 | 339.984
Devonshire Building | 2017-10-16 09:30 | 51095.7927 | 439.992
Devonshire Building | 2017-10-16 09:45 | 51095.8777 | 339.984
Devonshire Building | 2017-10-16 10:00 | 51096.0827 | 820.008
Devonshire Building | 2017-10-16 10:15 | 51096.1477 | 259.992
Devonshire Building | 2017-10-16 10:30 | 51096.7577 | 2440.008
Devonshire Building | 2017-10-16 10:45 | 51096.8177 | 240.012
Devonshire Building | 2017-10-16 11:00 | 51096.8777 | 240.012
Devonshire Building | 2017-10-16 11:15 | 51096.9377 | 240.012
Devonshire Building | 2017-10-16 11:30 | 51096.9927 | 219.996
Devonshire Building | 2017-10-16 11:45 | 51097.0527 | 240.012
Devonshire Building | 2017-10-16 12:00 | 51097.6377 | 2340
Devonshire Building | 2017-10-16 12:15 | 51097.6977 | 240.012
Devonshire Building | 2017-10-16 12:30 | 51097.7577 | 240.012
Devonshire Building | 2017-10-16 12:45 | 51097.8227 | 259.992
Devonshire Building | 2017-10-16 13:00 | 51097.8827 | 240.012
Devonshire Building | 2017-10-16 13:15 | 51097.9527 | 280.008
Devonshire Building | 2017-10-16 13:30 | 51098.2327 | 1119.996
Devonshire Building | 2017-10-16 13:45 | 51098.7527 | 2080.008
Devonshire Building | 2017-10-16 14:00 | 51098.8827 | 519.984
Devonshire Building | 2017-10-16 14:15 | 51098.9827 | 399.996
Devonshire Building | 2017-10-16 14:30 | 51099.0727 | 360
Devonshire Building | 2017-10-16 14:45 | 51099.1477 | 299.988
Devonshire Building | 2017-10-16 15:00 | 51099.2127 | 259.992
Devonshire Building | 2017-10-16 15:15 | 51099.7977 | 2340
Devonshire Building | 2017-10-16 15:30 | 51099.8377 | 159.984
Devonshire Building | 2017-10-16 15:45 | 51099.8827 | 180
Devonshire Building | 2017-10-16 16:00 | 51099.9177 | 140.004
Devonshire Building | 2017-10-16 16:15 | 51099.9577 | 159.984
Devonshire Building | 2017-10-16 16:30 | 51099.9977 | 159.984
Devonshire Building | 2017-10-16 16:45 | 51100.0327 | 140.004
Devonshire Building | 2017-10-16 17:00 | 51100.0677 | 140.004
Devonshire Building | 2017-10-16 17:15 | 51100.2377 | 680.004
Devonshire Building | 2017-10-16 17:30 | 51100.6177 | 1519.992
Devonshire Building | 2017-10-16 17:45 | 51100.6377 | 79.992
Devonshire Building | 2017-10-16 18:00 | 51100.6527 | 60.012
Devonshire Building | 2017-10-16 18:15 | 51100.6677 | 60.012
Devonshire Building | 2017-10-16 18:30 | 51100.6827 | 60.012
Devonshire Building | 2017-10-16 18:45 | 51100.7027 | 79.992
Devonshire Building | 2017-10-16 19:00 | 51100.7177 | 60.012
Devonshire Building | 2017-10-16 19:15 | 51100.7327 | 60.012
Devonshire Building | 2017-10-16 19:30 | 51100.7477 | 60.012
Devonshire Building | 2017-10-16 19:45 | 51100.7677 | 79.992
Devonshire Building | 2017-10-16 20:00 | 51100.7827 | 60.012
Devonshire Building | 2017-10-16 20:15 | 51100.7977 | 60.012
Devonshire Building | 2017-10-16 20:30 | 51100.8127 | 60.012
Devonshire Building | 2017-10-16 20:45 | 51100.8377 | 100.008
Devonshire Building | 2017-10-16 21:00 | 51100.8527 | 60.012
Devonshire Building | 2017-10-16 21:15 | 51100.8677 | 60.012
Devonshire Building | 2017-10-16 21:30 | 51100.8777 | 39.996
Devonshire Building | 2017-10-16 21:45 | 51100.8927 | 60.012
Devonshire Building | 2017-10-16 22:00 | 51100.9077 | 60.012
Devonshire Building | 2017-10-16 22:15 | 51100.9277 | 79.992
Devonshire Building | 2017-10-16 22:30 | 51100.9377 | 39.996
Devonshire Building | 2017-10-16 22:45 | 51100.9527 | 60.012
Devonshire Building | 2017-10-16 23:00 | 51100.9677 | 60.012
Devonshire Building | 2017-10-16 23:15 | 51100.9777 | 39.996
Devonshire Building | 2017-10-16 23:30 | 51100.9927 | 60.012
Devonshire Building | 2017-10-16 23:45 | 51101.0027 | 39.996
Devonshire Building | 2017-10-17 | 51101.0195 | 60.012
Devonshire Building | 2017-10-17 00:15 | 51101.0295 | 39.996
Devonshire Building | 2017-10-17 00:30 | 51101.0445 | 60.012
Devonshire Building | 2017-10-17 00:45 | 51101.0545 | 39.996
Devonshire Building | 2017-10-17 01:00 | 51101.0645 | 39.996
Devonshire Building | 2017-10-17 01:15 | 51101.0795 | 60.012
Devonshire Building | 2017-10-17 01:30 | 51101.0895 | 39.996
Devonshire Building | 2017-10-17 01:45 | 51101.1145 | 100.008
Devonshire Building | 2017-10-17 02:00 | 51101.1445 | 119.988
Devonshire Building | 2017-10-17 02:15 | 51101.1695 | 100.008
Devonshire Building | 2017-10-17 02:30 | 51101.1995 | 119.988
Devonshire Building | 2017-10-17 02:45 | 51101.7195 | 2080.008
Devonshire Building | 2017-10-17 03:00 | 51101.7495 | 119.988
Devonshire Building | 2017-10-17 03:15 | 51101.7745 | 100.008
Devonshire Building | 2017-10-17 03:30 | 51101.8045 | 119.988
Devonshire Building | 2017-10-17 03:45 | 51101.8295 | 100.008
Devonshire Building | 2017-10-17 04:00 | 51101.8495 | 79.992
Devonshire Building | 2017-10-17 04:15 | 51101.8595 | 39.996
Devonshire Building | 2017-10-17 04:30 | 51101.8745 | 60.012
Devonshire Building | 2017-10-17 04:45 | 51101.8895 | 60.012
Devonshire Building | 2017-10-17 05:00 | 51101.9045 | 60.012
Devonshire Building | 2017-10-17 05:15 | 51101.9195 | 60.012
Devonshire Building | 2017-10-17 05:30 | 51101.9345 | 60.012
Devonshire Building | 2017-10-17 05:45 | 51101.9545 | 79.992
Devonshire Building | 2017-10-17 06:00 | 51101.9695 | 60.012
Devonshire Building | 2017-10-17 06:15 | 51101.9845 | 60.012
Devonshire Building | 2017-10-17 06:30 | 51102.0045 | 79.992
Devonshire Building | 2017-10-17 06:45 | 51102.0195 | 60.012
Devonshire Building | 2017-10-17 07:00 | 51102.0445 | 100.008
Devonshire Building | 2017-10-17 07:15 | 51102.0596 | 60.012
Devonshire Building | 2017-10-17 07:30 | 51102.0746 | 60.012
Devonshire Building | 2017-10-17 07:45 | 51102.0946 | 79.992
Devonshire Building | 2017-10-17 08:00 | 51102.6696 | 2300.004
Devonshire Building | 2017-10-17 08:15 | 51102.6946 | 100.008
Devonshire Building | 2017-10-17 08:30 | 51102.7196 | 100.008
Devonshire Building | 2017-10-17 08:45 | 51102.7396 | 79.992
Devonshire Building | 2017-10-17 09:00 | 51102.7646 | 100.008
Devonshire Building | 2017-10-17 09:15 | 51102.8196 | 219.996
Devonshire Building | 2017-10-17 09:30 | 51102.9146 | 380.016
Devonshire Building | 2017-10-17 09:45 | 51103.5596 | 2580.012
Devonshire Building | 2017-10-17 10:00 | 51103.6646 | 420.012
Devonshire Building | 2017-10-17 10:15 | 51103.7746 | 439.992
Devonshire Building | 2017-10-17 10:30 | 51103.8696 | 380.016
Devonshire Building | 2017-10-17 10:45 | 51103.9496 | 320.004
Devonshire Building | 2017-10-17 11:00 | 51104.1046 | 619.992
Devonshire Building | 2017-10-17 11:15 | 51104.5946 | 1959.984
Devonshire Building | 2017-10-17 11:30 | 51104.6396 | 180
Devonshire Building | 2017-10-17 11:45 | 51104.6946 | 219.996
Devonshire Building | 2017-10-17 12:00 | 51104.7446 | 200.016
Devonshire Building | 2017-10-17 12:15 | 51104.7946 | 200.016
Devonshire Building | 2017-10-17 12:30 | 51104.8446 | 200.016
Devonshire Building | 2017-10-17 12:45 | 51105.4346 | 2360.016
Devonshire Building | 2017-10-17 13:00 | 51105.4646 | 119.988
Devonshire Building | 2017-10-17 13:15 | 51105.4946 | 119.988
Devonshire Building | 2017-10-17 13:30 | 51105.5346 | 159.984
Devonshire Building | 2017-10-17 13:45 | 51105.5796 | 180
Devonshire Building | 2017-10-17 14:00 | 51105.6296 | 200.016
Devonshire Building | 2017-10-17 14:15 | 51105.6796 | 200.016
Devonshire Building | 2017-10-17 14:30 | 51106.2446 | 2260.008
Devonshire Building | 2017-10-17 14:45 | 51106.2946 | 200.016
Devonshire Building | 2017-10-17 15:00 | 51106.3496 | 219.996
Devonshire Building | 2017-10-17 15:15 | 51106.3996 | 200.016
Devonshire Building | 2017-10-17 15:30 | 51106.4346 | 140.004
Devonshire Building | 2017-10-17 15:45 | 51106.4696 | 140.004
Devonshire Building | 2017-10-17 16:00 | 51106.5096 | 159.984
Devonshire Building | 2017-10-17 16:15 | 51106.5396 | 119.988
Devonshire Building | 2017-10-17 16:30 | 51107.0946 | 2220.012
Devonshire Building | 2017-10-17 16:45 | 51107.1196 | 100.008
Devonshire Building | 2017-10-17 17:00 | 51107.1446 | 100.008
Devonshire Building | 2017-10-17 17:15 | 51107.1746 | 119.988
Devonshire Building | 2017-10-17 17:30 | 51107.1996 | 100.008
Devonshire Building | 2017-10-17 17:45 | 51107.2296 | 119.988
Devonshire Building | 2017-10-17 18:00 | 51107.2546 | 100.008
Devonshire Building | 2017-10-17 18:15 | 51107.2796 | 100.008
Devonshire Building | 2017-10-17 18:30 | 51107.3096 | 119.988
Devonshire Building | 2017-10-17 18:45 | 51107.3346 | 100.008
Devonshire Building | 2017-10-17 19:00 | 51107.3596 | 100.008
Devonshire Building | 2017-10-17 19:15 | 51107.3846 | 100.008
Devonshire Building | 2017-10-17 19:30 | 51107.4096 | 100.008
Devonshire Building | 2017-10-17 19:45 | 51107.4346 | 100.008
Devonshire Building | 2017-10-17 20:00 | 51107.4596 | 100.008
Devonshire Building | 2017-10-17 20:15 | 51107.4796 | 79.992
Devonshire Building | 2017-10-17 20:30 | 51107.4996 | 79.992
Devonshire Building | 2017-10-17 20:45 | 51107.5446 | 180
Devonshire Building | 2017-10-17 21:00 | 51107.5596 | 60.012
Devonshire Building | 2017-10-17 21:15 | 51107.5696 | 39.996
Devonshire Building | 2017-10-17 21:30 | 51107.5846 | 60.012
Devonshire Building | 2017-10-17 21:45 | 51107.6096 | 100.008
Devonshire Building | 2017-10-17 22:00 | 51107.6246 | 60.012
Devonshire Building | 2017-10-17 22:15 | 51107.6396 | 60.012
Devonshire Building | 2017-10-17 22:30 | 51107.6546 | 60.012
Devonshire Building | 2017-10-17 22:45 | 51107.6696 | 60.012
Devonshire Building | 2017-10-17 23:00 | 51107.6846 | 60.012
Devonshire Building | 2017-10-17 23:15 | 51107.6996 | 60.012
Devonshire Building | 2017-10-17 23:30 | 51107.7146 | 60.012
Devonshire Building | 2017-10-17 23:45 | 51108.1096 | 1580.004
Devonshire Building | 2017-10-18 | 51108.25 | 560.016
Devonshire Building | 2017-10-18 00:15 | 51108.265 | 60.012
Devonshire Building | 2017-10-18 00:30 | 51108.275 | 39.996
Devonshire Building | 2017-10-18 00:45 | 51108.29 | 60.012
Devonshire Building | 2017-10-18 01:00 | 51108.3 | 39.996
Devonshire Building | 2017-10-18 01:15 | 51108.315 | 60.012
Devonshire Building | 2017-10-18 01:30 | 51108.325 | 39.996
Devonshire Building | 2017-10-18 01:45 | 51108.34 | 60.012
Devonshire Building | 2017-10-18 02:00 | 51108.355 | 60.012
Devonshire Building | 2017-10-18 02:15 | 51108.37 | 60.012
Devonshire Building | 2017-10-18 02:30 | 51108.385 | 60.012
Devonshire Building | 2017-10-18 02:45 | 51108.4 | 60.012
Devonshire Building | 2017-10-18 03:00 | 51108.41 | 39.996
Devonshire Building | 2017-10-18 03:15 | 51108.425 | 60.012
Devonshire Building | 2017-10-18 03:30 | 51108.44 | 60.012
Devonshire Building | 2017-10-18 03:45 | 51108.455 | 60.012
Devonshire Building | 2017-10-18 04:00 | 51108.47 | 60.012
Devonshire Building | 2017-10-18 04:15 | 51108.485 | 60.012
Devonshire Building | 2017-10-18 04:30 | 51108.495 | 39.996
Devonshire Building | 2017-10-18 04:45 | 51108.51 | 60.012
Devonshire Building | 2017-10-18 05:00 | 51108.525 | 60.012
Devonshire Building | 2017-10-18 05:15 | 51108.535 | 39.996
Devonshire Building | 2017-10-18 05:30 | 51108.55 | 60.012
Devonshire Building | 2017-10-18 05:45 | 51108.565 | 60.012
Devonshire Building | 2017-10-18 06:00 | 51108.58 | 60.012
Devonshire Building | 2017-10-18 06:15 | 51108.59 | 39.996
Devonshire Building | 2017-10-18 06:30 | 51108.605 | 60.012
Devonshire Building | 2017-10-18 06:45 | 51108.615 | 39.996
Devonshire Building | 2017-10-18 07:00 | 51108.6301 | 60.012
Devonshire Building | 2017-10-18 07:15 | 51109.165 | 2139.984
Devonshire Building | 2017-10-18 07:30 | 51109.185 | 79.992
Devonshire Building | 2017-10-18 07:45 | 51109.195 | 39.996
Devonshire Building | 2017-10-18 08:00 | 51109.225 | 119.988
Devonshire Building | 2017-10-18 08:15 | 51109.245 | 79.992
Devonshire Building | 2017-10-18 08:30 | 51109.265 | 79.992
Devonshire Building | 2017-10-18 08:45 | 51109.295 | 119.988
Devonshire Building | 2017-10-18 09:00 | 51109.325 | 119.988
Devonshire Building | 2017-10-18 09:15 | 51109.95 | 2499.984
Devonshire Building | 2017-10-18 09:30 | 51110.06 | 439.992
Devonshire Building | 2017-10-18 09:45 | 51110.165 | 420.012
Devonshire Building | 2017-10-18 10:00 | 51110.275 | 439.992
Devonshire Building | 2017-10-18 10:15 | 51110.38 | 420.012
Devonshire Building | 2017-10-18 10:30 | 51110.475 | 380.016
Devonshire Building | 2017-10-18 10:45 | 51111.145 | 2679.984
Devonshire Building | 2017-10-18 11:00 | 51111.22 | 299.988
Devonshire Building | 2017-10-18 11:15 | 51111.29 | 280.008
Devonshire Building | 2017-10-18 11:30 | 51111.345 | 219.996
Devonshire Building | 2017-10-18 11:45 | 51111.395 | 200.016
Devonshire Building | 2017-10-18 12:00 | 51111.445 | 200.016
Devonshire Building | 2017-10-18 12:15 | 51112.005 | 2239.992
Devonshire Building | 2017-10-18 12:30 | 51112.035 | 119.988
Devonshire Building | 2017-10-18 12:45 | 51112.065 | 119.988
Devonshire Building | 2017-10-18 13:00 | 51112.09 | 100.008
Devonshire Building | 2017-10-18 13:15 | 51112.12 | 119.988
Devonshire Building | 2017-10-18 13:30 | 51112.15 | 119.988
Devonshire Building | 2017-10-18 13:45 | 51112.66 | 2040.012
Devonshire Building | 2017-10-18 14:00 | 51112.775 | 460.008
Devonshire Building | 2017-10-18 14:15 | 51112.815 | 159.984
Devonshire Building | 2017-10-18 14:30 | 51112.87 | 219.996
Devonshire Building | 2017-10-18 14:45 | 51112.92 | 200.016
Devonshire Building | 2017-10-18 15:00 | 51112.965 | 180
Devonshire Building | 2017-10-18 15:15 | 51113.015 | 200.016
Devonshire Building | 2017-10-18 15:30 | 51113.535 | 2080.008
Devonshire Building | 2017-10-18 15:45 | 51113.625 | 360
Devonshire Building | 2017-10-18 16:00 | 51113.665 | 159.984
Devonshire Building | 2017-10-18 16:15 | 51113.69 | 100.008
Devonshire Building | 2017-10-18 16:30 | 51113.715 | 100.008
Devonshire Building | 2017-10-18 16:45 | 51113.74 | 100.008
Devonshire Building | 2017-10-18 17:00 | 51113.765 | 100.008
Devonshire Building | 2017-10-18 17:15 | 51113.79 | 100.008
Devonshire Building | 2017-10-18 17:30 | 51113.82 | 119.988
Devonshire Building | 2017-10-18 17:45 | 51113.845 | 100.008
Devonshire Building | 2017-10-18 18:00 | 51113.865 | 79.992
Devonshire Building | 2017-10-18 18:15 | 51113.89 | 100.008
Devonshire Building | 2017-10-18 18:30 | 51113.915 | 100.008
Devonshire Building | 2017-10-18 18:45 | 51114.45 | 2139.984
Devonshire Building | 2017-10-18 19:00 | 51114.47 | 79.992
Devonshire Building | 2017-10-18 19:15 | 51114.495 | 100.008
Devonshire Building | 2017-10-18 19:30 | 51114.515 | 79.992
Devonshire Building | 2017-10-18 19:45 | 51114.535 | 79.992
Devonshire Building | 2017-10-18 20:00 | 51114.555 | 79.992
Devonshire Building | 2017-10-18 20:15 | 51114.58 | 100.008
Devonshire Building | 2017-10-18 20:30 | 51114.605 | 100.008
Devonshire Building | 2017-10-18 20:45 | 51114.63 | 100.008
Devonshire Building | 2017-10-18 21:00 | 51114.65 | 79.992
Devonshire Building | 2017-10-18 21:15 | 51114.675 | 100.008
Devonshire Building | 2017-10-18 21:30 | 51114.695 | 79.992
Devonshire Building | 2017-10-18 21:45 | 51114.72 | 100.008
Devonshire Building | 2017-10-18 22:00 | 51114.74 | 79.992
Devonshire Building | 2017-10-18 22:15 | 51114.76 | 79.992
Devonshire Building | 2017-10-18 22:30 | 51114.78 | 79.992
Devonshire Building | 2017-10-18 22:45 | 51114.8 | 79.992
Devonshire Building | 2017-10-18 23:00 | 51114.82 | 79.992
Devonshire Building | 2017-10-18 23:15 | 51114.835 | 60.012
Devonshire Building | 2017-10-18 23:30 | 51114.855 | 79.992
Devonshire Building | 2017-10-18 23:45 | 51114.875 | 79.992
Devonshire Building | 2017-10-19 | 51114.8906 | 60.012
Devonshire Building | 2017-10-19 00:15 | 51114.9106 | 79.992
Devonshire Building | 2017-10-19 00:30 | 51114.9256 | 60.012
Devonshire Building | 2017-10-19 00:45 | 51114.9456 | 79.992
Devonshire Building | 2017-10-19 01:00 | 51114.9656 | 79.992
Devonshire Building | 2017-10-19 01:15 | 51114.9806 | 60.012
Devonshire Building | 2017-10-19 01:30 | 51115.0006 | 79.992
Devonshire Building | 2017-10-19 01:45 | 51115.0156 | 60.012
Devonshire Building | 2017-10-19 02:00 | 51115.0306 | 60.012
Devonshire Building | 2017-10-19 02:15 | 51115.0506 | 79.992
Devonshire Building | 2017-10-19 02:30 | 51115.0656 | 60.012
Devonshire Building | 2017-10-19 02:45 | 51115.0806 | 60.012
Devonshire Building | 2017-10-19 03:00 | 51115.1006 | 79.992
Devonshire Building | 2017-10-19 03:15 | 51115.1156 | 60.012
Devonshire Building | 2017-10-19 03:30 | 51115.1306 | 60.012
Devonshire Building | 2017-10-19 03:45 | 51115.1456 | 60.012
Devonshire Building | 2017-10-19 04:00 | 51115.4206 | 1100.016
Devonshire Building | 2017-10-19 04:15 | 51115.6856 | 1059.984
Devonshire Building | 2017-10-19 04:30 | 51115.6906 | 20.016
Devonshire Building | 2017-10-19 04:45 | 51115.7006 | 39.996
Devonshire Building | 2017-10-19 05:00 | 51115.7106 | 39.996
Devonshire Building | 2017-10-19 05:15 | 51115.7257 | 60.012
Devonshire Building | 2017-10-19 05:30 | 51115.7356 | 39.996
Devonshire Building | 2017-10-19 05:45 | 51115.7456 | 39.996
Devonshire Building | 2017-10-19 06:00 | 51115.7556 | 39.996
Devonshire Building | 2017-10-19 06:15 | 51115.7656 | 39.996
Devonshire Building | 2017-10-19 06:30 | 51115.7756 | 39.996
Devonshire Building | 2017-10-19 06:45 | 51115.7856 | 39.996
Devonshire Building | 2017-10-19 07:00 | 51115.8056 | 79.992
Devonshire Building | 2017-10-19 07:15 | 51115.8206 | 60.012
Devonshire Building | 2017-10-19 07:30 | 51115.8306 | 39.996
Devonshire Building | 2017-10-19 07:45 | 51115.8506 | 79.992
Devonshire Building | 2017-10-19 08:00 | 51115.8756 | 100.008
Devonshire Building | 2017-10-19 08:15 | 51116.4006 | 2099.988
Devonshire Building | 2017-10-19 08:30 | 51116.4256 | 100.008
Devonshire Building | 2017-10-19 08:45 | 51116.4506 | 100.008
Devonshire Building | 2017-10-19 09:00 | 51116.4756 | 100.008
Devonshire Building | 2017-10-19 09:15 | 51116.5257 | 200.016
Devonshire Building | 2017-10-19 09:30 | 51116.5807 | 219.996
Devonshire Building | 2017-10-19 09:45 | 51117.1907 | 2440.008
Devonshire Building | 2017-10-19 10:00 | 51117.2707 | 320.004
Devonshire Building | 2017-10-19 10:15 | 51117.3556 | 339.984
Devonshire Building | 2017-10-19 10:30 | 51117.4406 | 339.984
Devonshire Building | 2017-10-19 10:45 | 51117.5206 | 320.004
Devonshire Building | 2017-10-19 11:00 | 51117.6056 | 339.984
Devonshire Building | 2017-10-19 11:15 | 51118.2356 | 2520
Devonshire Building | 2017-10-19 11:30 | 51118.2956 | 240.012
Devonshire Building | 2017-10-19 11:45 | 51118.3606 | 259.992
Devonshire Building | 2017-10-19 12:00 | 51118.4256 | 259.992
Devonshire Building | 2017-10-19 12:15 | 51118.4856 | 240.012
Devonshire Building | 2017-10-19 12:30 | 51118.6256 | 560.016
Devonshire Building | 2017-10-19 12:45 | 51119.1306 | 2019.996
Devonshire Building | 2017-10-19 13:00 | 51119.1906 | 240.012
Devonshire Building | 2017-10-19 13:15 | 51119.2507 | 240.012
Devonshire Building | 2017-10-19 13:30 | 51119.3107 | 240.012
Devonshire Building | 2017-10-19 13:45 | 51119.3707 | 240.012
Devonshire Building | 2017-10-19 14:00 | 51119.5657 | 780.012
Devonshire Building | 2017-10-19 14:15 | 51120.0307 | 1860.012
Devonshire Building | 2017-10-19 14:30 | 51120.1007 | 280.008
Devonshire Building | 2017-10-19 14:45 | 51120.1657 | 259.992
Devonshire Building | 2017-10-19 15:00 | 51120.2257 | 240.012
Devonshire Building | 2017-10-19 15:15 | 51120.2757 | 200.016
Devonshire Building | 2017-10-19 15:30 | 51120.3257 | 200.016
Devonshire Building | 2017-10-19 15:45 | 51120.3657 | 159.984
Devonshire Building | 2017-10-19 16:00 | 51120.9357 | 2279.988
Devonshire Building | 2017-10-19 16:15 | 51120.9607 | 100.008
Devonshire Building | 2017-10-19 16:30 | 51120.9857 | 100.008
Devonshire Building | 2017-10-19 16:45 | 51121.0107 | 100.008
Devonshire Building | 2017-10-19 17:00 | 51121.0357 | 100.008
Devonshire Building | 2017-10-19 17:15 | 51121.0657 | 119.988
Devonshire Building | 2017-10-19 17:30 | 51121.0907 | 100.008
Devonshire Building | 2017-10-19 17:45 | 51121.1157 | 100.008
Devonshire Building | 2017-10-19 18:00 | 51121.1407 | 100.008
Devonshire Building | 2017-10-19 18:15 | 51121.1657 | 100.008
Devonshire Building | 2017-10-19 18:30 | 51121.1907 | 100.008
Devonshire Building | 2017-10-19 18:45 | 51121.2107 | 79.992
Devonshire Building | 2017-10-19 19:00 | 51121.2407 | 119.988
Devonshire Building | 2017-10-19 19:15 | 51121.2607 | 79.992
Devonshire Building | 2017-10-19 19:30 | 51121.2807 | 79.992
Devonshire Building | 2017-10-19 19:45 | 51121.3007 | 79.992
Devonshire Building | 2017-10-19 20:00 | 51121.3207 | 79.992
Devonshire Building | 2017-10-19 20:15 | 51121.3407 | 79.992
Devonshire Building | 2017-10-19 20:30 | 51121.3607 | 79.992
Devonshire Building | 2017-10-19 20:45 | 51121.3957 | 140.004
Devonshire Building | 2017-10-19 21:00 | 51121.4057 | 39.996
Devonshire Building | 2017-10-19 21:15 | 51121.4207 | 60.012
Devonshire Building | 2017-10-19 21:30 | 51121.4307 | 39.996
Devonshire Building | 2017-10-19 21:45 | 51121.4407 | 39.996
Devonshire Building | 2017-10-19 22:00 | 51121.9607 | 2080.008
Devonshire Building | 2017-10-19 22:15 | 51121.9707 | 39.996
Devonshire Building | 2017-10-19 22:30 | 51121.9807 | 39.996
Devonshire Building | 2017-10-19 22:45 | 51121.9857 | 20.016
Devonshire Building | 2017-10-19 23:00 | 51121.9957 | 39.996
Devonshire Building | 2017-10-19 23:15 | 51122.0057 | 39.996
Devonshire Building | 2017-10-19 23:30 | 51122.0157 | 39.996
Devonshire Building | 2017-10-19 23:45 | 51122.0257 | 39.996
Devonshire Building | 2017-10-20 | 51122.0352 | 39.996
Devonshire Building | 2017-10-20 00:15 | 51122.0452 | 39.996
Devonshire Building | 2017-10-20 00:30 | 51122.0552 | 39.996
Devonshire Building | 2017-10-20 00:45 | 51122.0652 | 39.996
Devonshire Building | 2017-10-20 01:00 | 51122.0802 | 60.012
Devonshire Building | 2017-10-20 01:15 | 51122.0902 | 39.996
Devonshire Building | 2017-10-20 01:30 | 51122.1002 | 39.996
Devonshire Building | 2017-10-20 01:45 | 51122.1152 | 60.012
Devonshire Building | 2017-10-20 02:00 | 51122.1252 | 39.996
Devonshire Building | 2017-10-20 02:15 | 51122.1352 | 39.996
Devonshire Building | 2017-10-20 02:30 | 51122.1452 | 39.996
Devonshire Building | 2017-10-20 02:45 | 51122.1552 | 39.996
Devonshire Building | 2017-10-20 03:00 | 51122.1652 | 39.996
Devonshire Building | 2017-10-20 03:15 | 51122.1802 | 60.012
Devonshire Building | 2017-10-20 03:30 | 51122.1902 | 39.996
Devonshire Building | 2017-10-20 03:45 | 51122.2002 | 39.996
Devonshire Building | 2017-10-20 04:00 | 51122.2102 | 39.996
Devonshire Building | 2017-10-20 04:15 | 51122.2202 | 39.996
Devonshire Building | 2017-10-20 04:30 | 51122.2302 | 39.996
Devonshire Building | 2017-10-20 04:45 | 51122.2352 | 20.016
Devonshire Building | 2017-10-20 05:00 | 51122.2452 | 39.996
Devonshire Building | 2017-10-20 05:15 | 51122.2602 | 60.012
Devonshire Building | 2017-10-20 05:30 | 51122.2702 | 39.996
Devonshire Building | 2017-10-20 05:45 | 51122.2802 | 39.996
Devonshire Building | 2017-10-20 06:00 | 51122.2902 | 39.996
Devonshire Building | 2017-10-20 06:15 | 51122.3002 | 39.996
Devonshire Building | 2017-10-20 06:30 | 51122.3102 | 39.996
Devonshire Building | 2017-10-20 06:45 | 51122.8352 | 2099.988
Devonshire Building | 2017-10-20 07:00 | 51122.8502 | 60.012
Devonshire Building | 2017-10-20 07:15 | 51122.8602 | 39.996
Devonshire Building | 2017-10-20 07:30 | 51122.8852 | 100.008
Devonshire Building | 2017-10-20 07:45 | 51122.9202 | 140.004
Devonshire Building | 2017-10-20 08:00 | 51122.9552 | 140.004
Devonshire Building | 2017-10-20 08:15 | 51122.9902 | 140.004
Devonshire Building | 2017-10-20 08:30 | 51123.0302 | 159.984
Devonshire Building | 2017-10-20 08:45 | 51123.0752 | 180
Devonshire Building | 2017-10-20 09:00 | 51123.1202 | 180
Devonshire Building | 2017-10-20 09:15 | 51123.1602 | 159.984
Devonshire Building | 2017-10-20 09:30 | 51123.7452 | 2340
Devonshire Building | 2017-10-20 09:45 | 51123.8602 | 460.008
Devonshire Building | 2017-10-20 10:00 | 51123.9901 | 519.984
Devonshire Building | 2017-10-20 10:15 | 51124.1101 | 479.988
Devonshire Building | 2017-10-20 10:30 | 51124.2151 | 420.012
Devonshire Building | 2017-10-20 10:45 | 51124.3001 | 339.984
Devonshire Building | 2017-10-20 11:00 | 51124.7801 | 1919.988
Devonshire Building | 2017-10-20 11:15 | 51124.9151 | 540
Devonshire Building | 2017-10-20 11:30 | 51124.9601 | 180
Devonshire Building | 2017-10-20 11:45 | 51125.0051 | 180
Devonshire Building | 2017-10-20 12:00 | 51125.0601 | 219.996
Devonshire Building | 2017-10-20 12:15 | 51125.1051 | 180
Devonshire Building | 2017-10-20 12:30 | 51125.1451 | 159.984
Devonshire Building | 2017-10-20 12:45 | 51125.7201 | 2300.004
Devonshire Building | 2017-10-20 13:00 | 51125.7401 | 79.992
Devonshire Building | 2017-10-20 13:15 | 51125.7601 | 79.992
Devonshire Building | 2017-10-20 13:30 | 51125.7901 | 119.988
Devonshire Building | 2017-10-20 13:45 | 51125.8101 | 79.992
Devonshire Building | 2017-10-20 14:00 | 51125.8251 | 60.012
Devonshire Building | 2017-10-20 14:15 | 51125.8501 | 100.008
Devonshire Building | 2017-10-20 14:30 | 51125.8751 | 100.008
Devonshire Building | 2017-10-20 14:45 | 51125.8951 | 79.992
Devonshire Building | 2017-10-20 15:00 | 51126.4451 | 2199.996
Devonshire Building | 2017-10-20 15:15 | 51126.4751 | 119.988
Devonshire Building | 2017-10-20 15:30 | 51126.5051 | 119.988
Devonshire Building | 2017-10-20 15:45 | 51126.5351 | 119.988
Devonshire Building | 2017-10-20 16:00 | 51126.5751 | 159.984
Devonshire Building | 2017-10-20 16:15 | 51126.6101 | 140.004
Devonshire Building | 2017-10-20 16:30 | 51126.6401 | 119.988
Devonshire Building | 2017-10-20 16:45 | 51126.6701 | 119.988
Devonshire Building | 2017-10-20 17:00 | 51126.7001 | 119.988
Devonshire Building | 2017-10-20 17:15 | 51126.7301 | 119.988
Devonshire Building | 2017-10-20 17:30 | 51126.7601 | 119.988
Devonshire Building | 2017-10-20 17:45 | 51127.2801 | 2080.008
Devonshire Building | 2017-10-20 18:00 | 51127.3051 | 100.008
Devonshire Building | 2017-10-20 18:15 | 51127.3301 | 100.008
Devonshire Building | 2017-10-20 18:30 | 51127.3601 | 119.988
Devonshire Building | 2017-10-20 18:45 | 51127.3851 | 100.008
Devonshire Building | 2017-10-20 19:00 | 51127.4151 | 119.988
Devonshire Building | 2017-10-20 19:15 | 51127.4401 | 100.008
Devonshire Building | 2017-10-20 19:30 | 51127.4651 | 100.008
Devonshire Building | 2017-10-20 19:45 | 51127.4901 | 100.008
Devonshire Building | 2017-10-20 20:00 | 51127.5151 | 100.008
Devonshire Building | 2017-10-20 20:15 | 51127.5351 | 79.992
Devonshire Building | 2017-10-20 20:30 | 51127.5601 | 100.008
Devonshire Building | 2017-10-20 20:45 | 51127.5951 | 140.004
Devonshire Building | 2017-10-20 21:00 | 51127.6101 | 60.012
Devonshire Building | 2017-10-20 21:15 | 51127.6251 | 60.012
Devonshire Building | 2017-10-20 21:30 | 51127.6401 | 60.012
Devonshire Building | 2017-10-20 21:45 | 51127.6551 | 60.012
Devonshire Building | 2017-10-20 22:00 | 51127.6701 | 60.012
Devonshire Building | 2017-10-20 22:15 | 51127.6851 | 60.012
Devonshire Building | 2017-10-20 22:30 | 51127.7001 | 60.012
Devonshire Building | 2017-10-20 22:45 | 51127.7151 | 60.012
Devonshire Building | 2017-10-20 23:00 | 51127.7301 | 60.012
Devonshire Building | 2017-10-20 23:15 | 51127.7451 | 60.012
Devonshire Building | 2017-10-20 23:30 | 51127.7602 | 60.012
Devonshire Building | 2017-10-20 23:45 | 51127.7752 | 60.012
Devonshire Building | 2017-10-21 | 51127.7891 | 60.012
Devonshire Building | 2017-10-21 00:15 | 51127.8041 | 60.012
Devonshire Building | 2017-10-21 00:30 | 51127.8191 | 60.012
Devonshire Building | 2017-10-21 00:45 | 51127.8341 | 60.012
Devonshire Building | 2017-10-21 01:00 | 51127.8441 | 39.996
Devonshire Building | 2017-10-21 01:15 | 51127.8591 | 60.012
Devonshire Building | 2017-10-21 01:30 | 51127.8741 | 60.012
Devonshire Building | 2017-10-21 01:45 | 51127.8891 | 60.012
Devonshire Building | 2017-10-21 02:00 | 51127.9041 | 60.012
Devonshire Building | 2017-10-21 02:15 | 51127.9191 | 60.012
Devonshire Building | 2017-10-21 02:30 | 51128.0391 | 479.988
Devonshire Building | 2017-10-21 02:45 | 51128.4541 | 1659.996
Devonshire Building | 2017-10-21 03:00 | 51128.4691 | 60.012
Devonshire Building | 2017-10-21 03:15 | 51128.4791 | 39.996
Devonshire Building | 2017-10-21 03:30 | 51128.4941 | 60.012
Devonshire Building | 2017-10-21 03:45 | 51128.5041 | 39.996
Devonshire Building | 2017-10-21 04:00 | 51128.5191 | 60.012
Devonshire Building | 2017-10-21 04:15 | 51128.5291 | 39.996
Devonshire Building | 2017-10-21 04:30 | 51128.5441 | 60.012
Devonshire Building | 2017-10-21 04:45 | 51128.5591 | 60.012
Devonshire Building | 2017-10-21 05:00 | 51128.5741 | 60.012
Devonshire Building | 2017-10-21 05:15 | 51128.5891 | 60.012
Devonshire Building | 2017-10-21 05:30 | 51128.6041 | 60.012
Devonshire Building | 2017-10-21 05:45 | 51128.6191 | 60.012
Devonshire Building | 2017-10-21 06:00 | 51128.6341 | 60.012
Devonshire Building | 2017-10-21 06:15 | 51128.6491 | 60.012
Devonshire Building | 2017-10-21 06:30 | 51128.6641 | 60.012
Devonshire Building | 2017-10-21 06:45 | 51128.6791 | 60.012
Devonshire Building | 2017-10-21 07:00 | 51128.6941 | 60.012
Devonshire Building | 2017-10-21 07:15 | 51128.7091 | 60.012
Devonshire Building | 2017-10-21 07:30 | 51128.7191 | 39.996
Devonshire Building | 2017-10-21 07:45 | 51128.7341 | 60.012
Devonshire Building | 2017-10-21 08:00 | 51128.7641 | 119.988
Devonshire Building | 2017-10-21 08:15 | 51128.7941 | 119.988
Devonshire Building | 2017-10-21 08:30 | 51128.8191 | 100.008
Devonshire Building | 2017-10-21 08:45 | 51128.8491 | 119.988
Devonshire Building | 2017-10-21 09:00 | 51128.8791 | 119.988
Devonshire Building | 2017-10-21 09:15 | 51128.9091 | 119.988
Devonshire Building | 2017-10-21 09:30 | 51128.9341 | 100.008
Devonshire Building | 2017-10-21 09:45 | 51128.9641 | 119.988
Devonshire Building | 2017-10-21 10:00 | 51128.9891 | 100.008
Devonshire Building | 2017-10-21 10:15 | 51129.0091 | 79.992
Devonshire Building | 2017-10-21 10:30 | 51129.0191 | 39.996
Devonshire Building | 2017-10-21 10:45 | 51129.0341 | 60.012
Devonshire Building | 2017-10-21 11:00 | 51129.0441 | 39.996
Devonshire Building | 2017-10-21 11:15 | 51129.0541 | 39.996
Devonshire Building | 2017-10-21 11:30 | 51129.0691 | 60.012
Devonshire Building | 2017-10-21 11:45 | 51129.0791 | 39.996
Devonshire Building | 2017-10-21 12:00 | 51129.5891 | 2040.012
Devonshire Building | 2017-10-21 12:15 | 51129.6091 | 79.992
Devonshire Building | 2017-10-21 12:30 | 51129.6291 | 79.992
Devonshire Building | 2017-10-21 12:45 | 51129.6441 | 60.012
Devonshire Building | 2017-10-21 13:00 | 51129.6541 | 39.996
Devonshire Building | 2017-10-21 13:15 | 51129.6641 | 39.996
Devonshire Building | 2017-10-21 13:30 | 51129.6741 | 39.996
Devonshire Building | 2017-10-21 13:45 | 51129.6891 | 60.012
Devonshire Building | 2017-10-21 14:00 | 51129.7041 | 60.012
Devonshire Building | 2017-10-21 14:15 | 51129.7191 | 60.012
Devonshire Building | 2017-10-21 14:30 | 51129.7341 | 60.012
Devonshire Building | 2017-10-21 14:45 | 51129.7491 | 60.012
Devonshire Building | 2017-10-21 15:00 | 51129.7641 | 60.012
Devonshire Building | 2017-10-21 15:15 | 51129.7791 | 60.012
Devonshire Building | 2017-10-21 15:30 | 51129.7941 | 60.012
Devonshire Building | 2017-10-21 15:45 | 51129.8141 | 79.992
Devonshire Building | 2017-10-21 16:00 | 51129.8291 | 60.012
Devonshire Building | 2017-10-21 16:15 | 51129.8441 | 60.012
Devonshire Building | 2017-10-21 16:30 | 51129.8591 | 60.012
Devonshire Building | 2017-10-21 16:45 | 51129.8741 | 60.012
Devonshire Building | 2017-10-21 17:00 | 51129.8891 | 60.012
Devonshire Building | 2017-10-21 17:15 | 51129.8991 | 39.996
Devonshire Building | 2017-10-21 17:30 | 51129.9141 | 60.012
Devonshire Building | 2017-10-21 17:45 | 51129.9292 | 60.012
Devonshire Building | 2017-10-21 18:00 | 51129.9442 | 60.012
Devonshire Building | 2017-10-21 18:15 | 51129.9542 | 39.996
Devonshire Building | 2017-10-21 18:30 | 51129.9692 | 60.012
Devonshire Building | 2017-10-21 18:45 | 51129.9842 | 60.012
Devonshire Building | 2017-10-21 19:00 | 51129.9942 | 39.996
Devonshire Building | 2017-10-21 19:15 | 51130.0092 | 60.012
Devonshire Building | 2017-10-21 19:30 | 51130.0192 | 39.996
Devonshire Building | 2017-10-21 19:45 | 51130.1692 | 600.012
Devonshire Building | 2017-10-21 20:00 | 51130.5492 | 1519.992
Devonshire Building | 2017-10-21 20:15 | 51130.5642 | 60.012
Devonshire Building | 2017-10-21 20:30 | 51130.5792 | 60.012
Devonshire Building | 2017-10-21 20:45 | 51130.5992 | 79.992
Devonshire Building | 2017-10-21 21:00 | 51130.6142 | 60.012
Devonshire Building | 2017-10-21 21:15 | 51130.6292 | 60.012
Devonshire Building | 2017-10-21 21:30 | 51130.6442 | 60.012
Devonshire Building | 2017-10-21 21:45 | 51130.6592 | 60.012
Devonshire Building | 2017-10-21 22:00 | 51130.6742 | 60.012
Devonshire Building | 2017-10-21 22:15 | 51130.6942 | 79.992
Devonshire Building | 2017-10-21 22:30 | 51130.7092 | 60.012
Devonshire Building | 2017-10-21 22:45 | 51130.7292 | 79.992
Devonshire Building | 2017-10-21 23:00 | 51130.7442 | 60.012
Devonshire Building | 2017-10-21 23:15 | 51130.7642 | 79.992
Devonshire Building | 2017-10-21 23:30 | 51130.7792 | 60.012
Devonshire Building | 2017-10-21 23:45 | 51130.7992 | 79.992
Devonshire Building | 2017-10-22 | 51130.8164 | 60.012
Devonshire Building | 2017-10-22 00:15 | 51130.8314 | 60.012
Devonshire Building | 2017-10-22 00:30 | 51130.8464 | 60.012
Devonshire Building | 2017-10-22 00:45 | 51130.8664 | 79.992
Devonshire Building | 2017-10-22 01:00 | 51130.8814 | 60.012
Devonshire Building | 2017-10-22 01:15 | 51130.8964 | 60.012
Devonshire Building | 2017-10-22 01:30 | 51130.9114 | 60.012
Devonshire Building | 2017-10-22 01:45 | 51130.9264 | 60.012
Devonshire Building | 2017-10-22 02:00 | 51130.9414 | 60.012
Devonshire Building | 2017-10-22 02:15 | 51130.9564 | 60.012
Devonshire Building | 2017-10-22 02:30 | 51130.9664 | 39.996
Devonshire Building | 2017-10-22 02:45 | 51130.9814 | 60.012
Devonshire Building | 2017-10-22 03:00 | 51130.9964 | 60.012
Devonshire Building | 2017-10-22 03:15 | 51131.0114 | 60.012
Devonshire Building | 2017-10-22 03:30 | 51131.0264 | 60.012
Devonshire Building | 2017-10-22 03:45 | 51131.0414 | 60.012
Devonshire Building | 2017-10-22 04:00 | 51131.0514 | 39.996
Devonshire Building | 2017-10-22 04:15 | 51131.0664 | 60.012
Devonshire Building | 2017-10-22 04:30 | 51131.0815 | 60.012
Devonshire Building | 2017-10-22 04:45 | 51131.0965 | 60.012
Devonshire Building | 2017-10-22 05:00 | 51131.1065 | 39.996
Devonshire Building | 2017-10-22 05:15 | 51131.1215 | 60.012
Devonshire Building | 2017-10-22 05:30 | 51131.1365 | 60.012
Devonshire Building | 2017-10-22 05:45 | 51131.6565 | 2080.008
Devonshire Building | 2017-10-22 06:00 | 51131.6665 | 39.996
Devonshire Building | 2017-10-22 06:15 | 51131.6765 | 39.996
Devonshire Building | 2017-10-22 06:30 | 51131.6915 | 60.012
Devonshire Building | 2017-10-22 06:45 | 51131.7015 | 39.996
Devonshire Building | 2017-10-22 07:00 | 51131.7115 | 39.996
Devonshire Building | 2017-10-22 07:15 | 51131.7265 | 60.012
Devonshire Building | 2017-10-22 07:30 | 51131.7365 | 39.996
Devonshire Building | 2017-10-22 07:45 | 51131.7565 | 79.992
Devonshire Building | 2017-10-22 08:00 | 51131.7865 | 119.988
Devonshire Building | 2017-10-22 08:15 | 51131.8165 | 119.988
Devonshire Building | 2017-10-22 08:30 | 51131.8465 | 119.988
Devonshire Building | 2017-10-22 08:45 | 51131.8764 | 119.988
Devonshire Building | 2017-10-22 09:00 | 51131.9064 | 119.988
Devonshire Building | 2017-10-22 09:15 | 51131.9364 | 119.988
Devonshire Building | 2017-10-22 09:30 | 51131.9664 | 119.988
Devonshire Building | 2017-10-22 09:45 | 51131.9964 | 119.988
Devonshire Building | 2017-10-22 10:00 | 51132.0264 | 119.988
Devonshire Building | 2017-10-22 10:15 | 51132.0564 | 119.988
Devonshire Building | 2017-10-22 10:30 | 51132.0714 | 60.012
Devonshire Building | 2017-10-22 10:45 | 51132.0814 | 39.996
Devonshire Building | 2017-10-22 11:00 | 51132.0964 | 60.012
Devonshire Building | 2017-10-22 11:15 | 51132.1114 | 60.012
Devonshire Building | 2017-10-22 11:30 | 51132.1264 | 60.012
Devonshire Building | 2017-10-22 11:45 | 51132.1364 | 39.996
Devonshire Building | 2017-10-22 12:00 | 51132.1514 | 60.012
Devonshire Building | 2017-10-22 12:15 | 51132.1664 | 60.012
Devonshire Building | 2017-10-22 12:30 | 51132.1764 | 39.996
Devonshire Building | 2017-10-22 12:45 | 51132.1914 | 60.012
Devonshire Building | 2017-10-22 13:00 | 51132.2065 | 60.012
Devonshire Building | 2017-10-22 13:15 | 51132.2164 | 39.996
Devonshire Building | 2017-10-22 13:30 | 51132.2315 | 60.012
Devonshire Building | 2017-10-22 13:45 | 51132.2465 | 60.012
Devonshire Building | 2017-10-22 14:00 | 51132.2565 | 39.996
Devonshire Building | 2017-10-22 14:15 | 51132.2715 | 60.012
Devonshire Building | 2017-10-22 14:30 | 51132.2815 | 39.996
Devonshire Building | 2017-10-22 14:45 | 51132.6465 | 1460.016
Devonshire Building | 2017-10-22 15:00 | 51132.8065 | 640.008
Devonshire Building | 2017-10-22 15:15 | 51132.8165 | 39.996
Devonshire Building | 2017-10-22 15:30 | 51132.8265 | 39.996
Devonshire Building | 2017-10-22 15:45 | 51132.8365 | 39.996
Devonshire Building | 2017-10-22 16:00 | 51132.8515 | 60.012
Devonshire Building | 2017-10-22 16:15 | 51132.8615 | 39.996
Devonshire Building | 2017-10-22 16:30 | 51132.8715 | 39.996
Devonshire Building | 2017-10-22 16:45 | 51132.8815 | 39.996
Devonshire Building | 2017-10-22 17:00 | 51132.8965 | 60.012
Devonshire Building | 2017-10-22 17:15 | 51132.9065 | 39.996
Devonshire Building | 2017-10-22 17:30 | 51132.9215 | 60.012
Devonshire Building | 2017-10-22 17:45 | 51132.9365 | 60.012
Devonshire Building | 2017-10-22 18:00 | 51132.9515 | 60.012
Devonshire Building | 2017-10-22 18:15 | 51132.9615 | 39.996
Devonshire Building | 2017-10-22 18:30 | 51132.9765 | 60.012
Devonshire Building | 2017-10-22 18:45 | 51132.9865 | 39.996
Devonshire Building | 2017-10-22 19:00 | 51133.0015 | 60.012
Devonshire Building | 2017-10-22 19:15 | 51133.0115 | 39.996
Devonshire Building | 2017-10-22 19:30 | 51133.0265 | 60.012
Devonshire Building | 2017-10-22 19:45 | 51133.0365 | 39.996
Devonshire Building | 2017-10-22 20:00 | 51133.0465 | 39.996
Devonshire Building | 2017-10-22 20:15 | 51133.0615 | 60.012
Devonshire Building | 2017-10-22 20:30 | 51133.0715 | 39.996
Devonshire Building | 2017-10-22 20:45 | 51133.1065 | 140.004
Devonshire Building | 2017-10-22 21:00 | 51133.1165 | 39.996
Devonshire Building | 2017-10-22 21:15 | 51133.1315 | 60.012
Devonshire Building | 2017-10-22 21:30 | 51133.1415 | 39.996
Devonshire Building | 2017-10-22 21:45 | 51133.1515 | 39.996
Devonshire Building | 2017-10-22 22:00 | 51133.1665 | 60.012
Devonshire Building | 2017-10-22 22:15 | 51133.1765 | 39.996
Devonshire Building | 2017-10-22 22:30 | 51133.1865 | 39.996
Devonshire Building | 2017-10-22 22:45 | 51133.1965 | 39.996
Devonshire Building | 2017-10-22 23:00 | 51133.2115 | 60.012
Devonshire Building | 2017-10-22 23:15 | 51133.2215 | 39.996
Devonshire Building | 2017-10-22 23:30 | 51133.2315 | 39.996
Devonshire Building | 2017-10-22 23:45 | 51133.2415 | 39.996
Devonshire Building | 2017-10-23 | 51133.75 | 2040.012
Devonshire Building | 2017-10-23 00:15 | 51133.76 | 39.996
Devonshire Building | 2017-10-23 00:30 | 51133.77 | 39.996
Devonshire Building | 2017-10-23 00:45 | 51133.78 | 39.996
Devonshire Building | 2017-10-23 01:00 | 51133.79 | 39.996
Devonshire Building | 2017-10-23 01:15 | 51133.8 | 39.996
Devonshire Building | 2017-10-23 01:30 | 51133.81 | 39.996
Devonshire Building | 2017-10-23 01:45 | 51133.82 | 39.996
Devonshire Building | 2017-10-23 02:00 | 51133.83 | 39.996
Devonshire Building | 2017-10-23 02:15 | 51133.84 | 39.996
Devonshire Building | 2017-10-23 02:30 | 51133.85 | 39.996
Devonshire Building | 2017-10-23 02:45 | 51133.865 | 60.012
Devonshire Building | 2017-10-23 03:00 | 51133.875 | 39.996
Devonshire Building | 2017-10-23 03:15 | 51133.89 | 60.012
Devonshire Building | 2017-10-23 03:30 | 51133.9 | 39.996
Devonshire Building | 2017-10-23 03:45 | 51133.915 | 60.012
Devonshire Building | 2017-10-23 04:00 | 51133.925 | 39.996
Devonshire Building | 2017-10-23 04:15 | 51133.94 | 60.012
Devonshire Building | 2017-10-23 04:30 | 51133.95 | 39.996
Devonshire Building | 2017-10-23 04:45 | 51133.96 | 39.996
Devonshire Building | 2017-10-23 05:00 | 51133.975 | 60.012
Devonshire Building | 2017-10-23 05:15 | 51133.985 | 39.996
Devonshire Building | 2017-10-23 05:30 | 51134 | 60.012
Devonshire Building | 2017-10-23 05:45 | 51134.01 | 39.996
Devonshire Building | 2017-10-23 06:00 | 51134.025 | 60.012
Devonshire Building | 2017-10-23 06:15 | 51134.035 | 39.996
Devonshire Building | 2017-10-23 06:30 | 51134.05 | 60.012
Devonshire Building | 2017-10-23 06:45 | 51134.065 | 60.012
Devonshire Building | 2017-10-23 07:00 | 51134.49 | 1699.992
Devonshire Building | 2017-10-23 07:15 | 51134.625 | 540
Devonshire Building | 2017-10-23 07:30 | 51134.64 | 60.012
Devonshire Building | 2017-10-23 07:45 | 51134.66 | 79.992
Devonshire Building | 2017-10-23 08:00 | 51134.71 | 200.016
Devonshire Building | 2017-10-23 08:15 | 51134.74 | 119.988
Devonshire Building | 2017-10-23 08:30 | 51134.78 | 159.984
Devonshire Building | 2017-10-23 08:45 | 51134.83 | 200.016
Devonshire Building | 2017-10-23 09:00 | 51134.885 | 219.996
Devonshire Building | 2017-10-23 09:15 | 51135.39 | 2019.996
Devonshire Building | 2017-10-23 09:30 | 51135.56 | 680.004
Devonshire Building | 2017-10-23 09:45 | 51135.655 | 380.016
Devonshire Building | 2017-10-23 10:00 | 51135.78 | 500.004
Devonshire Building | 2017-10-23 10:15 | 51135.91 | 519.984
Devonshire Building | 2017-10-23 10:30 | 51136.51 | 2400.012
Devonshire Building | 2017-10-23 10:45 | 51136.58 | 280.008
Devonshire Building | 2017-10-23 11:00 | 51136.645 | 259.992
Devonshire Building | 2017-10-23 11:15 | 51136.7 | 219.996
Devonshire Building | 2017-10-23 11:30 | 51136.76 | 240.012
Devonshire Building | 2017-10-23 11:45 | 51136.82 | 240.012
Devonshire Building | 2017-10-23 12:00 | 51137.4 | 2319.984
Devonshire Building | 2017-10-23 12:15 | 51137.465 | 259.992
Devonshire Building | 2017-10-23 12:30 | 51137.525 | 240.012
Devonshire Building | 2017-10-23 12:45 | 51137.585 | 240.012
Devonshire Building | 2017-10-23 13:00 | 51137.645 | 240.012
Devonshire Building | 2017-10-23 13:15 | 51137.7 | 219.996
Devonshire Building | 2017-10-23 13:30 | 51138.28 | 2319.984
Devonshire Building | 2017-10-23 13:45 | 51138.34 | 240.012
Devonshire Building | 2017-10-23 14:00 | 51138.4 | 240.012
Devonshire Building | 2017-10-23 14:15 | 51138.46 | 240.012
Devonshire Building | 2017-10-23 14:30 | 51138.525 | 259.992
Devonshire Building | 2017-10-23 14:45 | 51138.615 | 360
Devonshire Building | 2017-10-23 15:00 | 51139.1 | 1940.004
Devonshire Building | 2017-10-23 15:15 | 51139.32 | 879.984
Devonshire Building | 2017-10-23 15:30 | 51139.415 | 380.016
Devonshire Building | 2017-10-23 15:45 | 51139.495 | 320.004
Devonshire Building | 2017-10-23 16:00 | 51139.56 | 259.992
Devonshire Building | 2017-10-23 16:15 | 51139.62 | 240.012
Devonshire Building | 2017-10-23 16:30 | 51139.675 | 219.996
Devonshire Building | 2017-10-23 16:45 | 51139.725 | 200.016
Devonshire Building | 2017-10-23 17:00 | 51139.765 | 159.984
Devonshire Building | 2017-10-23 17:15 | 51140.31 | 2180.016
Devonshire Building | 2017-10-23 17:30 | 51140.335 | 100.008
Devonshire Building | 2017-10-23 17:45 | 51140.355 | 79.992
Devonshire Building | 2017-10-23 18:00 | 51140.385 | 119.988
Devonshire Building | 2017-10-23 18:15 | 51140.41 | 100.008
Devonshire Building | 2017-10-23 18:30 | 51140.435 | 100.008
Devonshire Building | 2017-10-23 18:45 | 51140.455 | 79.992
Devonshire Building | 2017-10-23 19:00 | 51140.48 | 100.008
Devonshire Building | 2017-10-23 19:15 | 51140.505 | 100.008
Devonshire Building | 2017-10-23 19:30 | 51140.525 | 79.992
Devonshire Building | 2017-10-23 19:45 | 51140.545 | 79.992
Devonshire Building | 2017-10-23 20:00 | 51140.565 | 79.992
Devonshire Building | 2017-10-23 20:15 | 51140.585 | 79.992
Devonshire Building | 2017-10-23 20:30 | 51140.6 | 60.012
Devonshire Building | 2017-10-23 20:45 | 51140.63 | 119.988
Devonshire Building | 2017-10-23 21:00 | 51140.645 | 60.012
Devonshire Building | 2017-10-23 21:15 | 51140.655 | 39.996
Devonshire Building | 2017-10-23 21:30 | 51140.67 | 60.012
Devonshire Building | 2017-10-23 21:45 | 51140.68 | 39.996
Devonshire Building | 2017-10-23 22:00 | 51140.69 | 39.996
Devonshire Building | 2017-10-23 22:15 | 51140.705 | 60.012
Devonshire Building | 2017-10-23 22:30 | 51140.715 | 39.996
Devonshire Building | 2017-10-23 22:45 | 51140.725 | 39.996
Devonshire Building | 2017-10-23 23:00 | 51140.74 | 60.012
Devonshire Building | 2017-10-23 23:15 | 51140.75 | 39.996
Devonshire Building | 2017-10-23 23:30 | 51140.76 | 39.996
Devonshire Building | 2017-10-23 23:45 | 51140.775 | 60.012
Devonshire Building | 2017-10-24 | 51140.7852 | 39.996
Devonshire Building | 2017-10-24 00:15 | 51140.7952 | 39.996
Devonshire Building | 2017-10-24 00:30 | 51140.8052 | 39.996
Devonshire Building | 2017-10-24 00:45 | 51140.8152 | 39.996
Devonshire Building | 2017-10-24 01:00 | 51140.8252 | 39.996
Devonshire Building | 2017-10-24 01:15 | 51140.8402 | 60.012
Devonshire Building | 2017-10-24 01:30 | 51140.8502 | 39.996
Devonshire Building | 2017-10-24 01:45 | 51140.8602 | 39.996
Devonshire Building | 2017-10-24 02:00 | 51140.8702 | 39.996
Devonshire Building | 2017-10-24 02:15 | 51140.8802 | 39.996
Devonshire Building | 2017-10-24 02:30 | 51140.8902 | 39.996
Devonshire Building | 2017-10-24 02:45 | 51141.0002 | 439.992
Devonshire Building | 2017-10-24 03:00 | 51141.4102 | 1640.016
Devonshire Building | 2017-10-24 03:15 | 51141.4152 | 20.016
Devonshire Building | 2017-10-24 03:30 | 51141.4252 | 39.996
Devonshire Building | 2017-10-24 03:45 | 51141.4352 | 39.996
Devonshire Building | 2017-10-24 04:00 | 51141.4452 | 39.996
Devonshire Building | 2017-10-24 04:15 | 51141.4502 | 20.016
Devonshire Building | 2017-10-24 04:30 | 51141.4602 | 39.996
Devonshire Building | 2017-10-24 04:45 | 51141.4702 | 39.996
Devonshire Building | 2017-10-24 05:00 | 51141.4752 | 20.016
Devonshire Building | 2017-10-24 05:15 | 51141.4852 | 39.996
Devonshire Building | 2017-10-24 05:30 | 51141.4952 | 39.996
Devonshire Building | 2017-10-24 05:45 | 51141.5102 | 60.012
Devonshire Building | 2017-10-24 06:00 | 51141.5202 | 39.996
Devonshire Building | 2017-10-24 06:15 | 51141.5302 | 39.996
Devonshire Building | 2017-10-24 06:30 | 51141.5452 | 60.012
Devonshire Building | 2017-10-24 06:45 | 51141.5552 | 39.996
Devonshire Building | 2017-10-24 07:00 | 51141.5652 | 39.996
Devonshire Building | 2017-10-24 07:15 | 51141.5802 | 60.012
Devonshire Building | 2017-10-24 07:30 | 51141.5952 | 60.012
Devonshire Building | 2017-10-24 07:45 | 51141.6152 | 79.992
Devonshire Building | 2017-10-24 08:00 | 51141.6602 | 180
Devonshire Building | 2017-10-24 08:15 | 51142.2202 | 2239.992
Devonshire Building | 2017-10-24 08:30 | 51142.2652 | 180
Devonshire Building | 2017-10-24 08:45 | 51142.3002 | 140.004
Devonshire Building | 2017-10-24 09:00 | 51142.3402 | 159.984
Devonshire Building | 2017-10-24 09:15 | 51142.4602 | 479.988
Devonshire Building | 2017-10-24 09:30 | 51142.5752 | 460.008
Devonshire Building | 2017-10-24 09:45 | 51143.2002 | 2499.984
Devonshire Building | 2017-10-24 10:00 | 51143.3002 | 399.996
Devonshire Building | 2017-10-24 10:15 | 51143.3902 | 360
Devonshire Building | 2017-10-24 10:30 | 51143.9752 | 2340
Devonshire Building | 2017-10-24 10:45 | 51144.1252 | 600.012
Devonshire Building | 2017-10-24 11:00 | 51144.1902 | 259.992
Devonshire Building | 2017-10-24 11:15 | 51144.2502 | 240.012
Devonshire Building | 2017-10-24 11:30 | 51144.3052 | 219.996
Devonshire Building | 2017-10-24 11:45 | 51144.5152 | 839.988
Devonshire Building | 2017-10-24 12:00 | 51144.9602 | 1779.984
Devonshire Building | 2017-10-24 12:15 | 51145.0152 | 219.996
Devonshire Building | 2017-10-24 12:30 | 51145.0801 | 259.992
Devonshire Building | 2017-10-24 12:45 | 51145.1351 | 219.996
Devonshire Building | 2017-10-24 13:00 | 51145.1952 | 240.012
Devonshire Building | 2017-10-24 13:15 | 51145.2452 | 200.016
Devonshire Building | 2017-10-24 13:30 | 51145.8102 | 2260.008
Devonshire Building | 2017-10-24 13:45 | 51145.8552 | 180
Devonshire Building | 2017-10-24 14:00 | 51145.9052 | 200.016
Devonshire Building | 2017-10-24 14:15 | 51145.9602 | 219.996
Devonshire Building | 2017-10-24 14:30 | 51146.0152 | 219.996
Devonshire Building | 2017-10-24 14:45 | 51146.0652 | 200.016
Devonshire Building | 2017-10-24 15:00 | 51146.6552 | 2360.016
Devonshire Building | 2017-10-24 15:15 | 51146.6952 | 159.984
Devonshire Building | 2017-10-24 15:30 | 51146.7402 | 180
Devonshire Building | 2017-10-24 15:45 | 51146.7952 | 219.996
Devonshire Building | 2017-10-24 16:00 | 51146.8452 | 200.016
Devonshire Building | 2017-10-24 16:15 | 51146.9002 | 219.996
Devonshire Building | 2017-10-24 16:30 | 51146.9502 | 200.016
Devonshire Building | 2017-10-24 16:45 | 51146.9952 | 180
Devonshire Building | 2017-10-24 17:00 | 51147.5552 | 2239.992
Devonshire Building | 2017-10-24 17:15 | 51147.5952 | 159.984
Devonshire Building | 2017-10-24 17:30 | 51147.6352 | 159.984
Devonshire Building | 2017-10-24 17:45 | 51147.6752 | 159.984
Devonshire Building | 2017-10-24 18:00 | 51147.7152 | 159.984
Devonshire Building | 2017-10-24 18:15 | 51147.7502 | 140.004
Devonshire Building | 2017-10-24 18:30 | 51147.7852 | 140.004
Devonshire Building | 2017-10-24 18:45 | 51147.8102 | 100.008
Devonshire Building | 2017-10-24 19:00 | 51147.8402 | 119.988
Devonshire Building | 2017-10-24 19:15 | 51147.8652 | 100.008
Devonshire Building | 2017-10-24 19:30 | 51147.8852 | 79.992
Devonshire Building | 2017-10-24 19:45 | 51147.9051 | 79.992
Devonshire Building | 2017-10-24 20:00 | 51147.9251 | 79.992
Devonshire Building | 2017-10-24 20:15 | 51147.9451 | 79.992
Devonshire Building | 2017-10-24 20:30 | 51147.9701 | 100.008
Devonshire Building | 2017-10-24 20:45 | 51148.0051 | 140.004
Devonshire Building | 2017-10-24 21:00 | 51148.0151 | 39.996
Devonshire Building | 2017-10-24 21:15 | 51148.0251 | 39.996
Devonshire Building | 2017-10-24 21:30 | 51148.0351 | 39.996
Devonshire Building | 2017-10-24 21:45 | 51148.0402 | 20.016
Devonshire Building | 2017-10-24 22:00 | 51148.0501 | 39.996
Devonshire Building | 2017-10-24 22:15 | 51148.0601 | 39.996
Devonshire Building | 2017-10-24 22:30 | 51148.0701 | 39.996
Devonshire Building | 2017-10-24 22:45 | 51148.0801 | 39.996
Devonshire Building | 2017-10-24 23:00 | 51148.0851 | 20.016
Devonshire Building | 2017-10-24 23:15 | 51148.0951 | 39.996
Devonshire Building | 2017-10-24 23:30 | 51148.1051 | 39.996
Devonshire Building | 2017-10-24 23:45 | 51148.1151 | 39.996
Devonshire Building | 2017-10-25 | 51148.1211 | 20.016
Devonshire Building | 2017-10-25 00:15 | 51148.1311 | 39.996
Devonshire Building | 2017-10-25 00:30 | 51148.1411 | 39.996
Devonshire Building | 2017-10-25 00:45 | 51148.1511 | 39.996
Devonshire Building | 2017-10-25 01:00 | 51148.6611 | 2040.012
Devonshire Building | 2017-10-25 01:15 | 51148.6711 | 39.996
Devonshire Building | 2017-10-25 01:30 | 51148.6811 | 39.996
Devonshire Building | 2017-10-25 01:45 | 51148.6911 | 39.996
Devonshire Building | 2017-10-25 02:00 | 51148.6961 | 20.016
Devonshire Building | 2017-10-25 02:15 | 51148.7061 | 39.996
Devonshire Building | 2017-10-25 02:30 | 51148.7161 | 39.996
Devonshire Building | 2017-10-25 02:45 | 51148.7211 | 20.016
Devonshire Building | 2017-10-25 03:00 | 51148.7311 | 39.996
Devonshire Building | 2017-10-25 03:15 | 51148.7411 | 39.996
Devonshire Building | 2017-10-25 03:30 | 51148.7461 | 20.016
Devonshire Building | 2017-10-25 03:45 | 51148.7561 | 39.996
Devonshire Building | 2017-10-25 04:00 | 51148.7661 | 39.996
Devonshire Building | 2017-10-25 04:15 | 51148.7761 | 39.996
Devonshire Building | 2017-10-25 04:30 | 51148.7861 | 39.996
Devonshire Building | 2017-10-25 04:45 | 51148.7961 | 39.996
Devonshire Building | 2017-10-25 05:00 | 51148.8061 | 39.996
Devonshire Building | 2017-10-25 05:15 | 51148.8161 | 39.996
Devonshire Building | 2017-10-25 05:30 | 51148.8261 | 39.996
Devonshire Building | 2017-10-25 05:45 | 51148.8361 | 39.996
Devonshire Building | 2017-10-25 06:00 | 51148.8511 | 60.012
Devonshire Building | 2017-10-25 06:15 | 51148.8611 | 39.996
Devonshire Building | 2017-10-25 06:30 | 51148.8711 | 39.996
Devonshire Building | 2017-10-25 06:45 | 51148.8811 | 39.996
Devonshire Building | 2017-10-25 07:00 | 51148.9011 | 79.992
Devonshire Building | 2017-10-25 07:15 | 51148.9311 | 119.988
Devonshire Building | 2017-10-25 07:30 | 51149.1611 | 920.016
Devonshire Building | 2017-10-25 07:45 | 51149.5411 | 1519.992
Devonshire Building | 2017-10-25 08:00 | 51149.6161 | 299.988
Devonshire Building | 2017-10-25 08:15 | 51149.7061 | 360
Devonshire Building | 2017-10-25 08:30 | 51149.8011 | 380.016
Devonshire Building | 2017-10-25 08:45 | 51149.8861 | 339.984
Devonshire Building | 2017-10-25 09:00 | 51149.9761 | 360
Devonshire Building | 2017-10-25 09:15 | 51150.3561 | 1519.992
Devonshire Building | 2017-10-25 09:30 | 51150.6861 | 1320.012
Devonshire Building | 2017-10-25 09:45 | 51150.7761 | 360
Devonshire Building | 2017-10-25 10:00 | 51150.8561 | 320.004
Devonshire Building | 2017-10-25 10:15 | 51150.9411 | 339.984
Devonshire Building | 2017-10-25 10:30 | 51151.0161 | 299.988
Devonshire Building | 2017-10-25 10:45 | 51151.3511 | 1339.992
Devonshire Building | 2017-10-25 11:00 | 51151.7361 | 1540.008
Devonshire Building | 2017-10-25 11:15 | 51151.8011 | 259.992
Devonshire Building | 2017-10-25 11:30 | 51151.8711 | 280.008
Devonshire Building | 2017-10-25 11:45 | 51151.9311 | 240.012
Devonshire Building | 2017-10-25 12:00 | 51152.0361 | 420.012
Devonshire Building | 2017-10-25 12:15 | 51152.5761 | 2160
Devonshire Building | 2017-10-25 12:30 | 51152.6311 | 219.996
Devonshire Building | 2017-10-25 12:45 | 51152.6861 | 219.996
Devonshire Building | 2017-10-25 13:00 | 51152.7361 | 200.016
Devonshire Building | 2017-10-25 13:15 | 51152.7811 | 180
Devonshire Building | 2017-10-25 13:30 | 51152.8261 | 180
Devonshire Building | 2017-10-25 13:45 | 51152.8711 | 180
Devonshire Building | 2017-10-25 14:00 | 51153.4311 | 2239.992
Devonshire Building | 2017-10-25 14:15 | 51153.4711 | 159.984
Devonshire Building | 2017-10-25 14:30 | 51153.5161 | 180
Devonshire Building | 2017-10-25 14:45 | 51153.5611 | 180
Devonshire Building | 2017-10-25 15:00 | 51153.6061 | 180
Devonshire Building | 2017-10-25 15:15 | 51153.6461 | 159.984
Devonshire Building | 2017-10-25 15:30 | 51153.6861 | 159.984
Devonshire Building | 2017-10-25 15:45 | 51154.2411 | 2220.012
Devonshire Building | 2017-10-25 16:00 | 51154.2661 | 100.008
Devonshire Building | 2017-10-25 16:15 | 51154.2911 | 100.008
Devonshire Building | 2017-10-25 16:30 | 51154.3211 | 119.988
Devonshire Building | 2017-10-25 16:45 | 51154.3511 | 119.988
Devonshire Building | 2017-10-25 17:00 | 51154.3811 | 119.988
Devonshire Building | 2017-10-25 17:15 | 51154.4061 | 100.008
Devonshire Building | 2017-10-25 17:30 | 51154.4311 | 100.008
Devonshire Building | 2017-10-25 17:45 | 51154.4561 | 100.008
Devonshire Building | 2017-10-25 18:00 | 51154.4811 | 100.008
Devonshire Building | 2017-10-25 18:15 | 51154.5011 | 79.992
Devonshire Building | 2017-10-25 18:30 | 51154.5261 | 100.008
Devonshire Building | 2017-10-25 18:45 | 51154.5511 | 100.008
Devonshire Building | 2017-10-25 19:00 | 51154.5711 | 79.992
Devonshire Building | 2017-10-25 19:15 | 51154.5911 | 79.992
Devonshire Building | 2017-10-25 19:30 | 51155.0761 | 1940.004
Devonshire Building | 2017-10-25 19:45 | 51155.1361 | 240.012
Devonshire Building | 2017-10-25 20:00 | 51155.1561 | 79.992
Devonshire Building | 2017-10-25 20:15 | 51155.1711 | 60.012
Devonshire Building | 2017-10-25 20:30 | 51155.1911 | 79.992
Devonshire Building | 2017-10-25 20:45 | 51155.2161 | 100.008
Devonshire Building | 2017-10-25 21:00 | 51155.2411 | 100.008
Devonshire Building | 2017-10-25 21:15 | 51155.2611 | 79.992
Devonshire Building | 2017-10-25 21:30 | 51155.2811 | 79.992
Devonshire Building | 2017-10-25 21:45 | 51155.3011 | 79.992
Devonshire Building | 2017-10-25 22:00 | 51155.3211 | 79.992
Devonshire Building | 2017-10-25 22:15 | 51155.3411 | 79.992
Devonshire Building | 2017-10-25 22:30 | 51155.3611 | 79.992
Devonshire Building | 2017-10-25 22:45 | 51155.3811 | 79.992
Devonshire Building | 2017-10-25 23:00 | 51155.4011 | 79.992
Devonshire Building | 2017-10-25 23:15 | 51155.4211 | 79.992
Devonshire Building | 2017-10-25 23:30 | 51155.4361 | 60.012
Devonshire Building | 2017-10-25 23:45 | 51155.4561 | 79.992
Devonshire Building | 2017-10-26 | 51155.4688 | 60.012
Devonshire Building | 2017-10-26 00:15 | 51155.4887 | 79.992
Devonshire Building | 2017-10-26 00:30 | 51155.5038 | 60.012
Devonshire Building | 2017-10-26 00:45 | 51155.5188 | 60.012
Devonshire Building | 2017-10-26 01:00 | 51155.5338 | 60.012
Devonshire Building | 2017-10-26 01:15 | 51155.5488 | 60.012
Devonshire Building | 2017-10-26 01:30 | 51155.5688 | 79.992
Devonshire Building | 2017-10-26 01:45 | 51155.5838 | 60.012
Devonshire Building | 2017-10-26 02:00 | 51155.5988 | 60.012
Devonshire Building | 2017-10-26 02:15 | 51155.6088 | 39.996
Devonshire Building | 2017-10-26 02:30 | 51155.6238 | 60.012
Devonshire Building | 2017-10-26 02:45 | 51155.6388 | 60.012
Devonshire Building | 2017-10-26 03:00 | 51155.6538 | 60.012
Devonshire Building | 2017-10-26 03:15 | 51155.6688 | 60.012
Devonshire Building | 2017-10-26 03:30 | 51155.6788 | 39.996
Devonshire Building | 2017-10-26 03:45 | 51155.6938 | 60.012
Devonshire Building | 2017-10-26 04:00 | 51155.7088 | 60.012
Devonshire Building | 2017-10-26 04:15 | 51155.7188 | 39.996
Devonshire Building | 2017-10-26 04:30 | 51155.7338 | 60.012
Devonshire Building | 2017-10-26 04:45 | 51155.7488 | 60.012
Devonshire Building | 2017-10-26 05:00 | 51156.1638 | 1659.996
Devonshire Building | 2017-10-26 05:15 | 51156.2788 | 460.008
Devonshire Building | 2017-10-26 05:30 | 51156.2838 | 20.016
Devonshire Building | 2017-10-26 05:45 | 51156.2938 | 39.996
Devonshire Building | 2017-10-26 06:00 | 51156.2988 | 20.016
Devonshire Building | 2017-10-26 06:15 | 51156.3088 | 39.996
Devonshire Building | 2017-10-26 06:30 | 51156.3188 | 39.996
Devonshire Building | 2017-10-26 06:45 | 51156.3288 | 39.996
Devonshire Building | 2017-10-26 07:00 | 51156.3388 | 39.996
Devonshire Building | 2017-10-26 07:15 | 51156.3488 | 39.996
Devonshire Building | 2017-10-26 07:30 | 51156.3638 | 60.012
Devonshire Building | 2017-10-26 07:45 | 51156.3738 | 39.996
Devonshire Building | 2017-10-26 08:00 | 51156.4138 | 159.984
Devonshire Building | 2017-10-26 08:15 | 51156.4388 | 100.008
Devonshire Building | 2017-10-26 08:30 | 51157.0188 | 2319.984
Devonshire Building | 2017-10-26 08:45 | 51157.0638 | 180
Devonshire Building | 2017-10-26 09:00 | 51157.0938 | 119.988
Devonshire Building | 2017-10-26 09:15 | 51157.1338 | 159.984
Devonshire Building | 2017-10-26 09:30 | 51157.1788 | 180
Devonshire Building | 2017-10-26 09:45 | 51157.2338 | 219.996
Devonshire Building | 2017-10-26 10:00 | 51157.8388 | 2419.992
Devonshire Building | 2017-10-26 10:15 | 51157.9588 | 479.988
Devonshire Building | 2017-10-26 10:30 | 51158.0838 | 500.004
Devonshire Building | 2017-10-26 10:45 | 51158.1838 | 399.996
Devonshire Building | 2017-10-26 11:00 | 51158.2638 | 320.004
Devonshire Building | 2017-10-26 11:15 | 51158.3638 | 399.996
Devonshire Building | 2017-10-26 11:30 | 51158.9488 | 2340
Devonshire Building | 2017-10-26 11:45 | 51158.9988 | 200.016
Devonshire Building | 2017-10-26 12:00 | 51159.0538 | 219.996
Devonshire Building | 2017-10-26 12:15 | 51159.1088 | 219.996
Devonshire Building | 2017-10-26 12:30 | 51159.1588 | 200.016
Devonshire Building | 2017-10-26 12:45 | 51159.4238 | 1059.984
Devonshire Building | 2017-10-26 13:00 | 51159.8188 | 1580.004
Devonshire Building | 2017-10-26 13:15 | 51159.8638 | 180
Devonshire Building | 2017-10-26 13:30 | 51159.9238 | 240.012
Devonshire Building | 2017-10-26 13:45 | 51160.0038 | 320.004
Devonshire Building | 2017-10-26 14:00 | 51160.0838 | 320.004
Devonshire Building | 2017-10-26 14:15 | 51160.1688 | 339.984
Devonshire Building | 2017-10-26 14:30 | 51160.2488 | 320.004
Devonshire Building | 2017-10-26 14:45 | 51160.6188 | 1479.996
Devonshire Building | 2017-10-26 15:00 | 51160.9238 | 1220.004
Devonshire Building | 2017-10-26 15:15 | 51160.9988 | 299.988
Devonshire Building | 2017-10-26 15:30 | 51161.0638 | 259.992
Devonshire Building | 2017-10-26 15:45 | 51161.1388 | 299.988
Devonshire Building | 2017-10-26 16:00 | 51161.1988 | 240.012
Devonshire Building | 2017-10-26 16:15 | 51161.2588 | 240.012
Devonshire Building | 2017-10-26 16:30 | 51161.3088 | 200.016
Devonshire Building | 2017-10-26 16:45 | 51161.8438 | 2139.984
Devonshire Building | 2017-10-26 17:00 | 51161.8988 | 219.996
Devonshire Building | 2017-10-26 17:15 | 51161.9238 | 100.008
Devonshire Building | 2017-10-26 17:30 | 51161.9538 | 119.988
Devonshire Building | 2017-10-26 17:45 | 51161.9838 | 119.988
Devonshire Building | 2017-10-26 18:00 | 51162.0088 | 100.008
Devonshire Building | 2017-10-26 18:15 | 51162.0388 | 119.988
Devonshire Building | 2017-10-26 18:30 | 51162.0638 | 100.008
Devonshire Building | 2017-10-26 18:45 | 51162.0838 | 79.992
Devonshire Building | 2017-10-26 19:00 | 51162.1088 | 100.008
Devonshire Building | 2017-10-26 19:15 | 51162.1288 | 79.992
Devonshire Building | 2017-10-26 19:30 | 51162.1488 | 79.992
Devonshire Building | 2017-10-26 19:45 | 51162.1688 | 79.992
Devonshire Building | 2017-10-26 20:00 | 51162.1888 | 79.992
Devonshire Building | 2017-10-26 20:15 | 51162.2038 | 60.012
Devonshire Building | 2017-10-26 20:30 | 51162.2188 | 60.012
Devonshire Building | 2017-10-26 20:45 | 51162.2538 | 140.004
Devonshire Building | 2017-10-26 21:00 | 51162.2638 | 39.996
Devonshire Building | 2017-10-26 21:15 | 51162.2738 | 39.996
Devonshire Building | 2017-10-26 21:30 | 51162.2788 | 20.016
Devonshire Building | 2017-10-26 21:45 | 51162.2888 | 39.996
Devonshire Building | 2017-10-26 22:00 | 51162.2988 | 39.996
Devonshire Building | 2017-10-26 22:15 | 51162.3038 | 20.016
Devonshire Building | 2017-10-26 22:30 | 51162.3138 | 39.996
Devonshire Building | 2017-10-26 22:45 | 51162.3238 | 39.996
Devonshire Building | 2017-10-26 23:00 | 51162.3288 | 20.016
Devonshire Building | 2017-10-26 23:15 | 51162.3388 | 39.996
Devonshire Building | 2017-10-26 23:30 | 51162.3538 | 60.012
Devonshire Building | 2017-10-26 23:45 | 51162.3588 | 20.016
Devonshire Building | 2017-10-27 | 51162.3672 | 39.996
Devonshire Building | 2017-10-27 00:15 | 51162.3722 | 20.016
Devonshire Building | 2017-10-27 00:30 | 51162.3822 | 39.996
Devonshire Building | 2017-10-27 00:45 | 51162.3922 | 39.996
Devonshire Building | 2017-10-27 01:00 | 51162.3972 | 20.016
Devonshire Building | 2017-10-27 01:15 | 51162.6722 | 1100.016
Devonshire Building | 2017-10-27 01:30 | 51162.9222 | 1000.008
Devonshire Building | 2017-10-27 01:45 | 51162.9322 | 39.996
Devonshire Building | 2017-10-27 02:00 | 51162.9422 | 39.996
Devonshire Building | 2017-10-27 02:15 | 51162.9472 | 20.016
Devonshire Building | 2017-10-27 02:30 | 51162.9572 | 39.996
Devonshire Building | 2017-10-27 02:45 | 51162.9622 | 20.016
Devonshire Building | 2017-10-27 03:00 | 51162.9722 | 39.996
Devonshire Building | 2017-10-27 03:15 | 51162.9772 | 20.016
Devonshire Building | 2017-10-27 03:30 | 51162.9872 | 39.996
Devonshire Building | 2017-10-27 03:45 | 51162.9922 | 20.016
Devonshire Building | 2017-10-27 04:00 | 51163.0022 | 39.996
Devonshire Building | 2017-10-27 04:15 | 51163.0072 | 20.016
Devonshire Building | 2017-10-27 04:30 | 51163.0172 | 39.996
Devonshire Building | 2017-10-27 04:45 | 51163.0272 | 39.996
Devonshire Building | 2017-10-27 05:00 | 51163.0422 | 60.012
Devonshire Building | 2017-10-27 05:15 | 51163.0522 | 39.996
Devonshire Building | 2017-10-27 05:30 | 51163.0622 | 39.996
Devonshire Building | 2017-10-27 05:45 | 51163.0772 | 60.012
Devonshire Building | 2017-10-27 06:00 | 51163.0872 | 39.996
Devonshire Building | 2017-10-27 06:15 | 51163.1022 | 60.012
Devonshire Building | 2017-10-27 06:30 | 51163.1122 | 39.996
Devonshire Building | 2017-10-27 06:45 | 51163.1272 | 60.012
Devonshire Building | 2017-10-27 07:00 | 51163.1522 | 100.008
Devonshire Building | 2017-10-27 07:15 | 51163.7122 | 2239.992
Devonshire Building | 2017-10-27 07:30 | 51163.7572 | 180
Devonshire Building | 2017-10-27 07:45 | 51163.8222 | 259.992
Devonshire Building | 2017-10-27 08:00 | 51163.8872 | 259.992
Devonshire Building | 2017-10-27 08:15 | 51163.9522 | 259.992
Devonshire Building | 2017-10-27 08:30 | 51164.0172 | 259.992
Devonshire Building | 2017-10-27 08:45 | 51164.0772 | 240.012
Devonshire Building | 2017-10-27 09:00 | 51164.1372 | 240.012
Devonshire Building | 2017-10-27 09:15 | 51164.2022 | 259.992
Devonshire Building | 2017-10-27 09:30 | 51164.3772 | 699.984
Devonshire Building | 2017-10-27 09:45 | 51164.8372 | 1839.996
Devonshire Building | 2017-10-27 10:00 | 51164.9022 | 259.992
Devonshire Building | 2017-10-27 10:15 | 51164.9722 | 280.008
Devonshire Building | 2017-10-27 10:30 | 51165.0922 | 479.988
Devonshire Building | 2017-10-27 10:45 | 51165.2272 | 540
Devonshire Building | 2017-10-27 11:00 | 51165.3422 | 460.008
Devonshire Building | 2017-10-27 11:15 | 51165.5722 | 920.016
Devonshire Building | 2017-10-27 11:30 | 51166.0772 | 2019.996
Devonshire Building | 2017-10-27 11:45 | 51166.1772 | 399.996
Devonshire Building | 2017-10-27 12:00 | 51166.2672 | 360
Devonshire Building | 2017-10-27 12:15 | 51166.3422 | 299.988
Devonshire Building | 2017-10-27 12:30 | 51166.4072 | 259.992
Devonshire Building | 2017-10-27 12:45 | 51166.4772 | 280.008
Devonshire Building | 2017-10-27 13:00 | 51166.5422 | 259.992
Devonshire Building | 2017-10-27 13:15 | 51166.8772 | 1339.992
Devonshire Building | 2017-10-27 13:30 | 51167.1622 | 1140.012
Devonshire Building | 2017-10-27 13:45 | 51167.2122 | 200.016
Devonshire Building | 2017-10-27 14:00 | 51167.2622 | 200.016
Devonshire Building | 2017-10-27 14:15 | 51167.3122 | 200.016
Devonshire Building | 2017-10-27 14:30 | 51167.3572 | 180
Devonshire Building | 2017-10-27 14:45 | 51167.4072 | 200.016
Devonshire Building | 2017-10-27 15:00 | 51167.4472 | 159.984
Devonshire Building | 2017-10-27 15:15 | 51167.4922 | 180
Devonshire Building | 2017-10-27 15:30 | 51168.0522 | 2239.992
Devonshire Building | 2017-10-27 15:45 | 51168.0872 | 140.004
Devonshire Building | 2017-10-27 16:00 | 51168.1222 | 140.004
Devonshire Building | 2017-10-27 16:15 | 51168.1572 | 140.004
Devonshire Building | 2017-10-27 16:30 | 51168.1972 | 159.984
Devonshire Building | 2017-10-27 16:45 | 51168.2272 | 119.988
Devonshire Building | 2017-10-27 17:00 | 51168.2622 | 140.004
Devonshire Building | 2017-10-27 17:15 | 51168.2922 | 119.988
Devonshire Building | 2017-10-27 17:30 | 51168.3222 | 119.988
Devonshire Building | 2017-10-27 17:45 | 51168.3472 | 100.008
Devonshire Building | 2017-10-27 18:00 | 51168.3772 | 119.988
Devonshire Building | 2017-10-27 18:15 | 51168.4022 | 100.008
Devonshire Building | 2017-10-27 18:30 | 51168.4222 | 79.992
Devonshire Building | 2017-10-27 18:45 | 51168.4472 | 100.008
Devonshire Building | 2017-10-27 19:00 | 51168.4672 | 79.992
Devonshire Building | 2017-10-27 19:15 | 51168.4872 | 79.992
Devonshire Building | 2017-10-27 19:30 | 51168.5072 | 79.992
Devonshire Building | 2017-10-27 19:45 | 51168.5272 | 79.992
Devonshire Building | 2017-10-27 20:00 | 51168.5472 | 79.992
Devonshire Building | 2017-10-27 20:15 | 51168.5972 | 200.016
Devonshire Building | 2017-10-27 20:30 | 51169.0772 | 1919.988
Devonshire Building | 2017-10-27 20:45 | 51169.0972 | 79.992
Devonshire Building | 2017-10-27 21:00 | 51169.1072 | 39.996
Devonshire Building | 2017-10-27 21:15 | 51169.1172 | 39.996
Devonshire Building | 2017-10-27 21:30 | 51169.1272 | 39.996
Devonshire Building | 2017-10-27 21:45 | 51169.1372 | 39.996
Devonshire Building | 2017-10-27 22:00 | 51169.1472 | 39.996
Devonshire Building | 2017-10-27 22:15 | 51169.1572 | 39.996
Devonshire Building | 2017-10-27 22:30 | 51169.1672 | 39.996
Devonshire Building | 2017-10-27 22:45 | 51169.1772 | 39.996
Devonshire Building | 2017-10-27 23:00 | 51169.1872 | 39.996
Devonshire Building | 2017-10-27 23:15 | 51169.1972 | 39.996
Devonshire Building | 2017-10-27 23:30 | 51169.2072 | 39.996
Devonshire Building | 2017-10-27 23:45 | 51169.2172 | 39.996
Devonshire Building | 2017-10-28 | 51169.2305 | 39.996
Devonshire Building | 2017-10-28 00:15 | 51169.2455 | 60.012
Devonshire Building | 2017-10-28 00:30 | 51169.2555 | 39.996
Devonshire Building | 2017-10-28 00:45 | 51169.2655 | 39.996
Devonshire Building | 2017-10-28 01:00 | 51169.2805 | 60.012
Devonshire Building | 2017-10-28 01:15 | 51169.2905 | 39.996
Devonshire Building | 2017-10-28 01:30 | 51169.3005 | 39.996
Devonshire Building | 2017-10-28 01:45 | 51169.3105 | 39.996
Devonshire Building | 2017-10-28 02:00 | 51169.3205 | 39.996
Devonshire Building | 2017-10-28 02:15 | 51169.3305 | 39.996
Devonshire Building | 2017-10-28 02:30 | 51169.3405 | 39.996
Devonshire Building | 2017-10-28 02:45 | 51169.3505 | 39.996
Devonshire Building | 2017-10-28 03:00 | 51169.3605 | 39.996
Devonshire Building | 2017-10-28 03:15 | 51169.3705 | 39.996
Devonshire Building | 2017-10-28 03:30 | 51169.3805 | 39.996
Devonshire Building | 2017-10-28 03:45 | 51169.3905 | 39.996
Devonshire Building | 2017-10-28 04:00 | 51169.4005 | 39.996
Devonshire Building | 2017-10-28 04:15 | 51169.4105 | 39.996
Devonshire Building | 2017-10-28 04:30 | 51169.4205 | 39.996
Devonshire Building | 2017-10-28 04:45 | 51169.4305 | 39.996
Devonshire Building | 2017-10-28 05:00 | 51169.4405 | 39.996
Devonshire Building | 2017-10-28 05:15 | 51169.4505 | 39.996
Devonshire Building | 2017-10-28 05:30 | 51169.4605 | 39.996
Devonshire Building | 2017-10-28 05:45 | 51169.9655 | 2019.996
Devonshire Building | 2017-10-28 06:00 | 51169.9805 | 60.012
Devonshire Building | 2017-10-28 06:15 | 51169.9905 | 39.996
Devonshire Building | 2017-10-28 06:30 | 51170.0055 | 60.012
Devonshire Building | 2017-10-28 06:45 | 51170.0155 | 39.996
Devonshire Building | 2017-10-28 07:00 | 51170.0255 | 39.996
Devonshire Building | 2017-10-28 07:15 | 51170.0405 | 60.012
Devonshire Building | 2017-10-28 07:30 | 51170.0505 | 39.996
Devonshire Building | 2017-10-28 07:45 | 51170.0655 | 60.012
Devonshire Building | 2017-10-28 08:00 | 51170.0955 | 119.988
Devonshire Building | 2017-10-28 08:15 | 51170.1255 | 119.988
Devonshire Building | 2017-10-28 08:30 | 51170.1555 | 119.988
Devonshire Building | 2017-10-28 08:45 | 51170.1855 | 119.988
Devonshire Building | 2017-10-28 09:00 | 51170.2105 | 100.008
Devonshire Building | 2017-10-28 09:15 | 51170.2404 | 119.988
Devonshire Building | 2017-10-28 09:30 | 51170.2704 | 119.988
Devonshire Building | 2017-10-28 09:45 | 51170.3004 | 119.988
Devonshire Building | 2017-10-28 10:00 | 51170.3304 | 119.988
Devonshire Building | 2017-10-28 10:15 | 51170.3604 | 119.988
Devonshire Building | 2017-10-28 10:30 | 51170.3754 | 60.012
Devonshire Building | 2017-10-28 10:45 | 51170.3904 | 60.012
Devonshire Building | 2017-10-28 11:00 | 51170.4004 | 39.996
Devonshire Building | 2017-10-28 11:15 | 51170.4154 | 60.012
Devonshire Building | 2017-10-28 11:30 | 51170.4304 | 60.012
Devonshire Building | 2017-10-28 11:45 | 51170.4404 | 39.996
Devonshire Building | 2017-10-28 12:00 | 51170.4555 | 60.012
Devonshire Building | 2017-10-28 12:15 | 51170.4655 | 39.996
Devonshire Building | 2017-10-28 12:30 | 51170.4805 | 60.012
Devonshire Building | 2017-10-28 12:45 | 51170.4955 | 60.012
Devonshire Building | 2017-10-28 13:00 | 51170.5105 | 60.012
Devonshire Building | 2017-10-28 13:15 | 51170.5205 | 39.996
Devonshire Building | 2017-10-28 13:30 | 51170.5355 | 60.012
Devonshire Building | 2017-10-28 13:45 | 51171.0555 | 2080.008
Devonshire Building | 2017-10-28 14:00 | 51171.0755 | 79.992
Devonshire Building | 2017-10-28 14:15 | 51171.0905 | 60.012
Devonshire Building | 2017-10-28 14:30 | 51171.1105 | 79.992
Devonshire Building | 2017-10-28 14:45 | 51171.1255 | 60.012
Devonshire Building | 2017-10-28 15:00 | 51171.1455 | 79.992
Devonshire Building | 2017-10-28 15:15 | 51171.1655 | 79.992
Devonshire Building | 2017-10-28 15:30 | 51171.1905 | 100.008
Devonshire Building | 2017-10-28 15:45 | 51171.2155 | 100.008
Devonshire Building | 2017-10-28 16:00 | 51171.2355 | 79.992
Devonshire Building | 2017-10-28 16:15 | 51171.2555 | 79.992
Devonshire Building | 2017-10-28 16:30 | 51171.2755 | 79.992
Devonshire Building | 2017-10-28 16:45 | 51171.3005 | 100.008
Devonshire Building | 2017-10-28 17:00 | 51171.3205 | 79.992
Devonshire Building | 2017-10-28 17:15 | 51171.3405 | 79.992
Devonshire Building | 2017-10-28 17:30 | 51171.3605 | 79.992
Devonshire Building | 2017-10-28 17:45 | 51171.3805 | 79.992
Devonshire Building | 2017-10-28 18:00 | 51171.3955 | 60.012
Devonshire Building | 2017-10-28 18:15 | 51171.4155 | 79.992
Devonshire Building | 2017-10-28 18:30 | 51171.4355 | 79.992
Devonshire Building | 2017-10-28 18:45 | 51171.4505 | 60.012
Devonshire Building | 2017-10-28 19:00 | 51171.4705 | 79.992
Devonshire Building | 2017-10-28 19:15 | 51171.4855 | 60.012
Devonshire Building | 2017-10-28 19:30 | 51171.5055 | 79.992
Devonshire Building | 2017-10-28 19:45 | 51171.5205 | 60.012
Devonshire Building | 2017-10-28 20:00 | 51171.5355 | 60.012
Devonshire Building | 2017-10-28 20:15 | 51171.5555 | 79.992
Devonshire Building | 2017-10-28 20:30 | 51171.5705 | 60.012
Devonshire Building | 2017-10-28 20:45 | 51171.6105 | 159.984
Devonshire Building | 2017-10-28 21:00 | 51171.6255 | 60.012
Devonshire Building | 2017-10-28 21:15 | 51171.6355 | 39.996
Devonshire Building | 2017-10-28 21:30 | 51171.6505 | 60.012
Devonshire Building | 2017-10-28 21:45 | 51171.6655 | 60.012
Devonshire Building | 2017-10-28 22:00 | 51171.6805 | 60.012
Devonshire Building | 2017-10-28 22:15 | 51171.6955 | 60.012
Devonshire Building | 2017-10-28 22:30 | 51171.7105 | 60.012
Devonshire Building | 2017-10-28 22:45 | 51171.7255 | 60.012
Devonshire Building | 2017-10-28 23:00 | 51171.7505 | 100.008
Devonshire Building | 2017-10-28 23:15 | 51172.2605 | 2040.012
Devonshire Building | 2017-10-28 23:30 | 51172.2755 | 60.012
Devonshire Building | 2017-10-28 23:45 | 51172.2855 | 39.996
Devonshire Building | 2017-10-29 | 51172.3008 | 60.012
Devonshire Building | 2017-10-29 00:15 | 51172.3158 | 60.012
Devonshire Building | 2017-10-29 00:30 | 51172.3258 | 39.996
Devonshire Building | 2017-10-29 00:45 | 51172.3408 | 60.012
Devonshire Building | 2017-10-29 01:00 | 51172.3558 | 60.012
Devonshire Building | 2017-10-29 01:15 | 51172.3708 | 60.012
Devonshire Building | 2017-10-29 01:30 | 51172.3858 | 60.012
Devonshire Building | 2017-10-29 01:45 | 51172.4008 | 60.012
Devonshire Building | 2017-10-29 02:00 | 51172.4208 | 79.992
Devonshire Building | 2017-10-29 02:15 | 51172.4358 | 60.012
Devonshire Building | 2017-10-29 02:30 | 51172.4508 | 60.012
Devonshire Building | 2017-10-29 02:45 | 51172.4658 | 60.012
Devonshire Building | 2017-10-29 03:00 | 51172.4808 | 60.012
Devonshire Building | 2017-10-29 03:15 | 51172.4958 | 60.012
Devonshire Building | 2017-10-29 03:30 | 51172.5108 | 60.012
Devonshire Building | 2017-10-29 03:45 | 51172.5258 | 60.012
Devonshire Building | 2017-10-29 04:00 | 51172.5408 | 60.012
Devonshire Building | 2017-10-29 04:15 | 51172.5558 | 60.012
Devonshire Building | 2017-10-29 04:30 | 51172.5708 | 60.012
Devonshire Building | 2017-10-29 04:45 | 51172.5858 | 60.012
Devonshire Building | 2017-10-29 05:00 | 51172.6008 | 60.012
Devonshire Building | 2017-10-29 05:15 | 51172.6108 | 39.996
Devonshire Building | 2017-10-29 05:30 | 51172.6258 | 60.012
Devonshire Building | 2017-10-29 05:45 | 51172.6408 | 60.012
Devonshire Building | 2017-10-29 06:00 | 51172.6558 | 60.012
Devonshire Building | 2017-10-29 06:15 | 51172.6658 | 39.996
Devonshire Building | 2017-10-29 06:30 | 51172.6808 | 60.012
Devonshire Building | 2017-10-29 06:45 | 51172.6908 | 39.996
Devonshire Building | 2017-10-29 07:00 | 51172.7058 | 60.012
Devonshire Building | 2017-10-29 07:15 | 51172.7208 | 60.012
Devonshire Building | 2017-10-29 07:30 | 51172.7308 | 39.996
Devonshire Building | 2017-10-29 07:45 | 51172.7508 | 79.992
Devonshire Building | 2017-10-29 08:00 | 51172.7758 | 100.008
Devonshire Building | 2017-10-29 08:15 | 51172.8058 | 119.988
Devonshire Building | 2017-10-29 08:30 | 51172.8358 | 119.988
Devonshire Building | 2017-10-29 08:45 | 51173.3308 | 1980
Devonshire Building | 2017-10-29 09:00 | 51173.4008 | 280.008
Devonshire Building | 2017-10-29 09:15 | 51173.4258 | 100.008
Devonshire Building | 2017-10-29 09:30 | 51173.4508 | 100.008
Devonshire Building | 2017-10-29 09:45 | 51173.4808 | 119.988
Devonshire Building | 2017-10-29 10:00 | 51173.5058 | 100.008
Devonshire Building | 2017-10-29 10:15 | 51173.5308 | 100.008
Devonshire Building | 2017-10-29 10:30 | 51173.5458 | 60.012
Devonshire Building | 2017-10-29 10:45 | 51173.5558 | 39.996
Devonshire Building | 2017-10-29 11:00 | 51173.5709 | 60.012
Devonshire Building | 2017-10-29 11:15 | 51173.5808 | 39.996
Devonshire Building | 2017-10-29 11:30 | 51173.5908 | 39.996
Devonshire Building | 2017-10-29 11:45 | 51173.6059 | 60.012
Devonshire Building | 2017-10-29 12:00 | 51173.6159 | 39.996
Devonshire Building | 2017-10-29 12:15 | 51173.6309 | 60.012
Devonshire Building | 2017-10-29 12:30 | 51173.6459 | 60.012
Devonshire Building | 2017-10-29 12:45 | 51173.6559 | 39.996
Devonshire Building | 2017-10-29 13:00 | 51173.6709 | 60.012
Devonshire Building | 2017-10-29 13:15 | 51173.6809 | 39.996
Devonshire Building | 2017-10-29 13:30 | 51173.6959 | 60.012
Devonshire Building | 2017-10-29 13:45 | 51173.7109 | 60.012
Devonshire Building | 2017-10-29 14:00 | 51173.7209 | 39.996
Devonshire Building | 2017-10-29 14:15 | 51173.7359 | 60.012
Devonshire Building | 2017-10-29 14:30 | 51173.7459 | 39.996
Devonshire Building | 2017-10-29 14:45 | 51173.7609 | 60.012
Devonshire Building | 2017-10-29 15:00 | 51173.7709 | 39.996
Devonshire Building | 2017-10-29 15:15 | 51173.7859 | 60.012
Devonshire Building | 2017-10-29 15:30 | 51173.7959 | 39.996
Devonshire Building | 2017-10-29 15:45 | 51173.8109 | 60.012
Devonshire Building | 2017-10-29 16:00 | 51173.8209 | 39.996
Devonshire Building | 2017-10-29 16:15 | 51173.8359 | 60.012
Devonshire Building | 2017-10-29 16:30 | 51173.8459 | 39.996
Devonshire Building | 2017-10-29 16:45 | 51173.8609 | 60.012
Devonshire Building | 2017-10-29 17:00 | 51174.2659 | 1620
Devonshire Building | 2017-10-29 17:15 | 51174.3959 | 519.984
Devonshire Building | 2017-10-29 17:30 | 51174.4059 | 39.996
Devonshire Building | 2017-10-29 17:45 | 51174.4209 | 60.012
Devonshire Building | 2017-10-29 18:00 | 51174.4309 | 39.996
Devonshire Building | 2017-10-29 18:15 | 51174.4459 | 60.012
Devonshire Building | 2017-10-29 18:30 | 51174.4559 | 39.996
Devonshire Building | 2017-10-29 18:45 | 51174.4709 | 60.012
Devonshire Building | 2017-10-29 19:00 | 51174.4859 | 60.012
Devonshire Building | 2017-10-29 19:15 | 51174.5009 | 60.012
Devonshire Building | 2017-10-29 19:30 | 51174.5109 | 39.996
Devonshire Building | 2017-10-29 19:45 | 51174.5309 | 79.992
Devonshire Building | 2017-10-29 20:00 | 51174.5459 | 60.012
Devonshire Building | 2017-10-29 20:15 | 51174.5609 | 60.012
Devonshire Building | 2017-10-29 20:30 | 51174.5759 | 60.012
Devonshire Building | 2017-10-29 20:45 | 51174.5909 | 60.012
Devonshire Building | 2017-10-29 21:00 | 51174.6059 | 60.012
Devonshire Building | 2017-10-29 21:15 | 51174.6209 | 60.012
Devonshire Building | 2017-10-29 21:30 | 51174.6309 | 39.996
Devonshire Building | 2017-10-29 21:45 | 51174.6659 | 140.004
Devonshire Building | 2017-10-29 22:00 | 51174.6809 | 60.012
Devonshire Building | 2017-10-29 22:15 | 51174.6959 | 60.012
Devonshire Building | 2017-10-29 22:30 | 51174.7109 | 60.012
Devonshire Building | 2017-10-29 22:45 | 51174.7259 | 60.012
Devonshire Building | 2017-10-29 23:00 | 51174.7409 | 60.012
Devonshire Building | 2017-10-29 23:15 | 51174.7559 | 60.012
Devonshire Building | 2017-10-29 23:30 | 51174.7709 | 60.012
Devonshire Building | 2017-10-29 23:45 | 51174.7859 | 60.012
Devonshire Building | 2017-10-30 | 51174.7969 | 39.996
Devonshire Building | 2017-10-30 00:15 | 51174.8119 | 60.012
Devonshire Building | 2017-10-30 00:30 | 51174.8269 | 60.012
Devonshire Building | 2017-10-30 00:45 | 51174.8419 | 60.012
Devonshire Building | 2017-10-30 01:00 | 51174.8519 | 39.996
Devonshire Building | 2017-10-30 01:15 | 51174.8669 | 60.012
Devonshire Building | 2017-10-30 01:30 | 51174.8819 | 60.012
Devonshire Building | 2017-10-30 01:45 | 51174.9019 | 79.992
Devonshire Building | 2017-10-30 02:00 | 51174.9319 | 119.988
Devonshire Building | 2017-10-30 02:15 | 51174.9619 | 119.988
Devonshire Building | 2017-10-30 02:30 | 51175.1969 | 939.996
Devonshire Building | 2017-10-30 02:45 | 51175.5219 | 1299.996
Devonshire Building | 2017-10-30 03:00 | 51175.5519 | 119.988
Devonshire Building | 2017-10-30 03:15 | 51175.5819 | 119.988
Devonshire Building | 2017-10-30 03:30 | 51175.6069 | 100.008
Devonshire Building | 2017-10-30 03:45 | 51175.6369 | 119.988
Devonshire Building | 2017-10-30 04:00 | 51175.6669 | 119.988
Devonshire Building | 2017-10-30 04:15 | 51175.6819 | 60.012
Devonshire Building | 2017-10-30 04:30 | 51175.6969 | 60.012
Devonshire Building | 2017-10-30 04:45 | 51175.7069 | 39.996
Devonshire Building | 2017-10-30 05:00 | 51175.7269 | 79.992
Devonshire Building | 2017-10-30 05:15 | 51175.7419 | 60.012
Devonshire Building | 2017-10-30 05:30 | 51175.7569 | 60.012
Devonshire Building | 2017-10-30 05:45 | 51175.7719 | 60.012
Devonshire Building | 2017-10-30 06:00 | 51175.7869 | 60.012
Devonshire Building | 2017-10-30 06:15 | 51175.8069 | 79.992
Devonshire Building | 2017-10-30 06:30 | 51175.8219 | 60.012
Devonshire Building | 2017-10-30 06:45 | 51175.8369 | 60.012
Devonshire Building | 2017-10-30 07:00 | 51175.8519 | 60.012
Devonshire Building | 2017-10-30 07:15 | 51175.8669 | 60.012
Devonshire Building | 2017-10-30 07:30 | 51175.8869 | 79.992
Devonshire Building | 2017-10-30 07:45 | 51175.9019 | 60.012
Devonshire Building | 2017-10-30 08:00 | 51175.9169 | 60.012
Devonshire Building | 2017-10-30 08:15 | 51175.9369 | 79.992
Devonshire Building | 2017-10-30 08:30 | 51176.4769 | 2160
Devonshire Building | 2017-10-30 08:45 | 51176.4969 | 79.992
Devonshire Building | 2017-10-30 09:00 | 51176.5319 | 140.004
Devonshire Building | 2017-10-30 09:15 | 51176.5569 | 100.008
Devonshire Building | 2017-10-30 09:30 | 51176.5869 | 119.988
Devonshire Building | 2017-10-30 09:45 | 51176.6219 | 140.004
Devonshire Building | 2017-10-30 10:00 | 51176.7069 | 339.984
Devonshire Building | 2017-10-30 10:15 | 51177.2819 | 2300.004
Devonshire Building | 2017-10-30 10:30 | 51177.3619 | 320.004
Devonshire Building | 2017-10-30 10:45 | 51177.5119 | 600.012
Devonshire Building | 2017-10-30 11:00 | 51177.6719 | 640.008
Devonshire Building | 2017-10-30 11:15 | 51178.2119 | 2160
Devonshire Building | 2017-10-30 11:30 | 51178.4469 | 939.996
Devonshire Building | 2017-10-30 11:45 | 51178.5469 | 399.996
Devonshire Building | 2017-10-30 12:00 | 51178.6569 | 439.992
Devonshire Building | 2017-10-30 12:15 | 51178.7669 | 439.992
Devonshire Building | 2017-10-30 12:30 | 51179.4219 | 2620.008
Devonshire Building | 2017-10-30 12:45 | 51179.5619 | 560.016
Devonshire Building | 2017-10-30 13:00 | 51179.7119 | 600.012
Devonshire Building | 2017-10-30 13:15 | 51179.8769 | 659.988
Devonshire Building | 2017-10-30 13:30 | 51179.9919 | 460.008
Devonshire Building | 2017-10-30 13:45 | 51180.1019 | 439.992
Devonshire Building | 2017-10-30 14:00 | 51180.6969 | 2379.996
Devonshire Building | 2017-10-30 14:15 | 51180.7769 | 320.004
Devonshire Building | 2017-10-30 14:30 | 51180.8519 | 299.988
Devonshire Building | 2017-10-30 14:45 | 51180.9169 | 259.992
Devonshire Building | 2017-10-30 15:00 | 51180.9769 | 240.012
Devonshire Building | 2017-10-30 15:15 | 51181.0319 | 219.996
Devonshire Building | 2017-10-30 15:30 | 51181.0869 | 219.996
Devonshire Building | 2017-10-30 15:45 | 51181.6919 | 2419.992
Devonshire Building | 2017-10-30 16:00 | 51181.7969 | 420.012
Devonshire Building | 2017-10-30 16:15 | 51181.9119 | 460.008
Devonshire Building | 2017-10-30 16:30 | 51182.0219 | 439.992
Devonshire Building | 2017-10-30 16:45 | 51182.1519 | 519.984
Devonshire Building | 2017-10-30 17:00 | 51182.5419 | 1559.988
Devonshire Building | 2017-10-30 17:15 | 51182.9169 | 1500.012
Devonshire Building | 2017-10-30 17:30 | 51183.0169 | 399.996
Devonshire Building | 2017-10-30 17:45 | 51183.0919 | 299.988
Devonshire Building | 2017-10-30 18:00 | 51183.1469 | 219.996
Devonshire Building | 2017-10-30 18:15 | 51183.1969 | 200.016
Devonshire Building | 2017-10-30 18:30 | 51183.2369 | 159.984
Devonshire Building | 2017-10-30 18:45 | 51183.2719 | 140.004
Devonshire Building | 2017-10-30 19:00 | 51183.3069 | 140.004
Devonshire Building | 2017-10-30 19:15 | 51183.3319 | 100.008
Devonshire Building | 2017-10-30 19:30 | 51183.3569 | 100.008
Devonshire Building | 2017-10-30 19:45 | 51183.3919 | 140.004
Devonshire Building | 2017-10-30 20:00 | 51183.4319 | 159.984
Devonshire Building | 2017-10-30 20:15 | 51183.4719 | 159.984
Devonshire Building | 2017-10-30 20:30 | 51183.5069 | 140.004
Devonshire Building | 2017-10-30 20:45 | 51183.5419 | 140.004
Devonshire Building | 2017-10-30 21:00 | 51183.5769 | 140.004
Devonshire Building | 2017-10-30 21:15 | 51183.6119 | 140.004
Devonshire Building | 2017-10-30 21:30 | 51183.6469 | 140.004
Devonshire Building | 2017-10-30 21:45 | 51183.7019 | 219.996
Devonshire Building | 2017-10-30 22:00 | 51183.7269 | 100.008
Devonshire Building | 2017-10-30 22:15 | 51183.7419 | 60.012
Devonshire Building | 2017-10-30 22:30 | 51183.7469 | 20.016
Devonshire Building | 2017-10-30 22:45 | 51183.7569 | 39.996
Devonshire Building | 2017-10-30 23:00 | 51183.7669 | 39.996
Devonshire Building | 2017-10-30 23:15 | 51183.7819 | 60.012
Devonshire Building | 2017-10-30 23:30 | 51183.7919 | 39.996
Devonshire Building | 2017-10-30 23:45 | 51183.8019 | 39.996
Devonshire Building | 2017-10-31 | 51183.8086 | 39.996
Devonshire Building | 2017-10-31 00:15 | 51183.8186 | 39.996
Devonshire Building | 2017-10-31 00:30 | 51183.8236 | 20.016
Devonshire Building | 2017-10-31 00:45 | 51184.3486 | 2099.988
Devonshire Building | 2017-10-31 01:00 | 51184.3586 | 39.996
Devonshire Building | 2017-10-31 01:15 | 51184.3686 | 39.996
Devonshire Building | 2017-10-31 01:30 | 51184.3786 | 39.996
Devonshire Building | 2017-10-31 01:45 | 51184.3886 | 39.996
Devonshire Building | 2017-10-31 02:00 | 51184.3936 | 20.016
Devonshire Building | 2017-10-31 02:15 | 51184.4036 | 39.996
Devonshire Building | 2017-10-31 02:30 | 51184.4136 | 39.996
Devonshire Building | 2017-10-31 02:45 | 51184.4236 | 39.996
Devonshire Building | 2017-10-31 03:00 | 51184.4336 | 39.996
Devonshire Building | 2017-10-31 03:15 | 51184.4386 | 20.016
Devonshire Building | 2017-10-31 03:30 | 51184.4486 | 39.996
Devonshire Building | 2017-10-31 03:45 | 51184.4586 | 39.996
Devonshire Building | 2017-10-31 04:00 | 51184.4686 | 39.996
Devonshire Building | 2017-10-31 04:15 | 51184.4736 | 20.016
Devonshire Building | 2017-10-31 04:30 | 51184.4836 | 39.996
Devonshire Building | 2017-10-31 04:45 | 51184.4936 | 39.996
Devonshire Building | 2017-10-31 05:00 | 51184.5036 | 39.996
Devonshire Building | 2017-10-31 05:15 | 51184.5086 | 20.016
Devonshire Building | 2017-10-31 05:30 | 51184.5186 | 39.996
Devonshire Building | 2017-10-31 05:45 | 51184.5286 | 39.996
Devonshire Building | 2017-10-31 06:00 | 51184.5386 | 39.996
Devonshire Building | 2017-10-31 06:15 | 51184.5486 | 39.996
Devonshire Building | 2017-10-31 06:30 | 51184.5586 | 39.996
Devonshire Building | 2017-10-31 06:45 | 51184.5686 | 39.996
Devonshire Building | 2017-10-31 07:00 | 51184.5836 | 60.012
Devonshire Building | 2017-10-31 07:15 | 51184.5936 | 39.996
Devonshire Building | 2017-10-31 07:30 | 51184.6036 | 39.996
Devonshire Building | 2017-10-31 07:45 | 51184.6186 | 60.012
Devonshire Building | 2017-10-31 08:00 | 51184.9186 | 1199.988
Devonshire Building | 2017-10-31 08:15 | 51185.1636 | 979.992
Devonshire Building | 2017-10-31 08:30 | 51185.1886 | 100.008
Devonshire Building | 2017-10-31 08:45 | 51185.2086 | 79.992
Devonshire Building | 2017-10-31 09:00 | 51185.2236 | 60.012
Devonshire Building | 2017-10-31 09:15 | 51185.2486 | 100.008
Devonshire Building | 2017-10-31 09:30 | 51185.2686 | 79.992
Devonshire Building | 2017-10-31 09:45 | 51185.2986 | 119.988
Devonshire Building | 2017-10-31 10:00 | 51185.5086 | 839.988
Devonshire Building | 2017-10-31 10:15 | 51185.9236 | 1659.996
Devonshire Building | 2017-10-31 10:30 | 51185.9786 | 219.996
Devonshire Building | 2017-10-31 10:45 | 51186.0286 | 200.016
Devonshire Building | 2017-10-31 11:00 | 51186.0886 | 240.012
Devonshire Building | 2017-10-31 11:15 | 51186.7286 | 2559.996
Devonshire Building | 2017-10-31 11:30 | 51186.7986 | 280.008
Devonshire Building | 2017-10-31 11:45 | 51186.8736 | 299.988
Devonshire Building | 2017-10-31 12:00 | 51186.9436 | 280.008
Devonshire Building | 2017-10-31 12:15 | 51187.5386 | 2379.996
Devonshire Building | 2017-10-31 12:30 | 51187.5936 | 219.996
Devonshire Building | 2017-10-31 12:45 | 51187.6486 | 219.996
Devonshire Building | 2017-10-31 13:00 | 51187.7086 | 240.012
Devonshire Building | 2017-10-31 13:15 | 51187.7636 | 219.996
Devonshire Building | 2017-10-31 13:30 | 51187.8186 | 219.996
Devonshire Building | 2017-10-31 13:45 | 51188.4336 | 2459.988
Devonshire Building | 2017-10-31 14:00 | 51188.4936 | 240.012
Devonshire Building | 2017-10-31 14:15 | 51188.5486 | 219.996
Devonshire Building | 2017-10-31 14:30 | 51188.6086 | 240.012
Devonshire Building | 2017-10-31 14:45 | 51188.6636 | 219.996
Devonshire Building | 2017-10-31 15:00 | 51188.7236 | 240.012
Devonshire Building | 2017-10-31 15:15 | 51189.3236 | 2400.012
Devonshire Building | 2017-10-31 15:30 | 51189.3786 | 219.996
Devonshire Building | 2017-10-31 15:45 | 51189.4286 | 200.016
Devonshire Building | 2017-10-31 16:00 | 51189.4836 | 219.996
Devonshire Building | 2017-10-31 16:15 | 51189.5336 | 200.016
Devonshire Building | 2017-10-31 16:30 | 51189.5836 | 200.016
Devonshire Building | 2017-10-31 16:45 | 51189.6236 | 159.984
Devonshire Building | 2017-10-31 17:00 | 51190.2386 | 2459.988
Devonshire Building | 2017-10-31 17:15 | 51190.4136 | 699.984
Devonshire Building | 2017-10-31 17:30 | 51190.5736 | 640.008
Devonshire Building | 2017-10-31 17:45 | 51190.7136 | 560.016
Devonshire Building | 2017-10-31 18:00 | 51190.8436 | 519.984
Devonshire Building | 2017-10-31 18:15 | 51190.9436 | 399.996
Devonshire Building | 2017-10-31 18:30 | 51191.0136 | 280.008
Devonshire Building | 2017-10-31 18:45 | 51191.0686 | 219.996
Devonshire Building | 2017-10-31 19:00 | 51191.1086 | 159.984
Devonshire Building | 2017-10-31 19:15 | 51191.1486 | 159.984
Devonshire Building | 2017-10-31 19:30 | 51191.1786 | 119.988
Devonshire Building | 2017-10-31 19:45 | 51191.2086 | 119.988
Devonshire Building | 2017-10-31 20:00 | 51191.2336 | 100.008
Devonshire Building | 2017-10-31 20:15 | 51191.2586 | 100.008
Devonshire Building | 2017-10-31 20:30 | 51191.3886 | 519.984
Devonshire Building | 2017-10-31 20:45 | 51191.7986 | 1640.016
Devonshire Building | 2017-10-31 21:00 | 51191.8086 | 39.996
Devonshire Building | 2017-10-31 21:15 | 51191.8186 | 39.996
Devonshire Building | 2017-10-31 21:30 | 51191.8286 | 39.996
Devonshire Building | 2017-10-31 21:45 | 51191.8486 | 79.992
Devonshire Building | 2017-10-31 22:00 | 51191.8586 | 39.996
Devonshire Building | 2017-10-31 22:15 | 51191.8686 | 39.996
Devonshire Building | 2017-10-31 22:30 | 51191.8836 | 60.012
Devonshire Building | 2017-10-31 22:45 | 51191.8936 | 39.996
Devonshire Building | 2017-10-31 23:00 | 51191.9036 | 39.996
Devonshire Building | 2017-10-31 23:15 | 51191.9136 | 39.996
Devonshire Building | 2017-10-31 23:30 | 51191.9236 | 39.996
Devonshire Building | 2017-10-31 23:45 | 51191.9336 | 39.996
Devonshire Building | 2017-11-01 | 51191.9453 | 39.996
Devonshire Building | 2017-11-01 00:15 | 51191.9553 | 39.996
Devonshire Building | 2017-11-01 00:30 | 51191.9653 | 39.996
Devonshire Building | 2017-11-01 00:45 | 51191.9753 | 39.996
Devonshire Building | 2017-11-01 01:00 | 51191.9853 | 39.996
Devonshire Building | 2017-11-01 01:15 | 51191.9953 | 39.996
Devonshire Building | 2017-11-01 01:30 | 51192.0053 | 39.996
Devonshire Building | 2017-11-01 01:45 | 51192.0153 | 39.996
Devonshire Building | 2017-11-01 02:00 | 51192.0253 | 39.996
Devonshire Building | 2017-11-01 02:15 | 51192.0353 | 39.996
Devonshire Building | 2017-11-01 02:30 | 51192.0453 | 39.996
Devonshire Building | 2017-11-01 02:45 | 51192.0553 | 39.996
Devonshire Building | 2017-11-01 03:00 | 51192.0653 | 39.996
Devonshire Building | 2017-11-01 03:15 | 51192.0753 | 39.996
Devonshire Building | 2017-11-01 03:30 | 51192.0853 | 39.996
Devonshire Building | 2017-11-01 03:45 | 51192.0953 | 39.996
Devonshire Building | 2017-11-01 04:00 | 51192.1003 | 20.016
Devonshire Building | 2017-11-01 04:15 | 51192.1103 | 39.996
Devonshire Building | 2017-11-01 04:30 | 51192.1203 | 39.996
Devonshire Building | 2017-11-01 04:45 | 51192.1303 | 39.996
Devonshire Building | 2017-11-01 05:00 | 51192.1403 | 39.996
Devonshire Building | 2017-11-01 05:15 | 51192.3303 | 759.996
Devonshire Building | 2017-11-01 05:30 | 51192.6653 | 1339.992
Devonshire Building | 2017-11-01 05:45 | 51192.6803 | 60.012
Devonshire Building | 2017-11-01 06:00 | 51192.6903 | 39.996
Devonshire Building | 2017-11-01 06:15 | 51192.7053 | 60.012
Devonshire Building | 2017-11-01 06:30 | 51192.7153 | 39.996
Devonshire Building | 2017-11-01 06:45 | 51192.7303 | 60.012
Devonshire Building | 2017-11-01 07:00 | 51192.7503 | 79.992
Devonshire Building | 2017-11-01 07:15 | 51192.7603 | 39.996
Devonshire Building | 2017-11-01 07:30 | 51192.7753 | 60.012
Devonshire Building | 2017-11-01 07:45 | 51192.7903 | 60.012
Devonshire Building | 2017-11-01 08:00 | 51192.8103 | 79.992
Devonshire Building | 2017-11-01 08:15 | 51192.8353 | 100.008
Devonshire Building | 2017-11-01 08:30 | 51192.8653 | 119.988
Devonshire Building | 2017-11-01 08:45 | 51192.8953 | 119.988
Devonshire Building | 2017-11-01 09:00 | 51192.9353 | 159.984
Devonshire Building | 2017-11-01 09:15 | 51193.2203 | 1140.012
Devonshire Building | 2017-11-01 09:30 | 51193.5553 | 1339.992
Devonshire Building | 2017-11-01 09:45 | 51193.6153 | 240.012
Devonshire Building | 2017-11-01 10:00 | 51193.6803 | 259.992
Devonshire Building | 2017-11-01 10:15 | 51193.7453 | 259.992
Devonshire Building | 2017-11-01 10:30 | 51194.0703 | 1299.996
Devonshire Building | 2017-11-01 10:45 | 51194.4303 | 1440
Devonshire Building | 2017-11-01 11:00 | 51194.4853 | 219.996
Devonshire Building | 2017-11-01 11:15 | 51194.5453 | 240.012
Devonshire Building | 2017-11-01 11:30 | 51194.6053 | 240.012
Devonshire Building | 2017-11-01 11:45 | 51194.6753 | 280.008
Devonshire Building | 2017-11-01 12:00 | 51195.2903 | 2459.988
Devonshire Building | 2017-11-01 12:15 | 51195.3653 | 299.988
Devonshire Building | 2017-11-01 12:30 | 51195.4353 | 280.008
Devonshire Building | 2017-11-01 12:45 | 51195.5003 | 259.992
Devonshire Building | 2017-11-01 13:00 | 51195.5603 | 240.012
Devonshire Building | 2017-11-01 13:15 | 51196.1303 | 2279.988
Devonshire Building | 2017-11-01 13:30 | 51196.2003 | 280.008
Devonshire Building | 2017-11-01 13:45 | 51196.2653 | 259.992
Devonshire Building | 2017-11-01 14:00 | 51196.3303 | 259.992
Devonshire Building | 2017-11-01 14:15 | 51196.3903 | 240.012
Devonshire Building | 2017-11-01 14:30 | 51196.4553 | 259.992
Devonshire Building | 2017-11-01 14:45 | 51197.0553 | 2400.012
Devonshire Building | 2017-11-01 15:00 | 51197.1153 | 240.012
Devonshire Building | 2017-11-01 15:15 | 51197.1753 | 240.012
Devonshire Building | 2017-11-01 15:30 | 51197.2653 | 360
Devonshire Building | 2017-11-01 15:45 | 51197.4053 | 560.016
Devonshire Building | 2017-11-01 16:00 | 51197.5803 | 699.984
Devonshire Building | 2017-11-01 16:15 | 51198.0803 | 2000.016
Devonshire Building | 2017-11-01 16:30 | 51198.3703 | 1159.992
Devonshire Building | 2017-11-01 16:45 | 51198.4503 | 320.004
Devonshire Building | 2017-11-01 17:00 | 51198.5103 | 240.012
Devonshire Building | 2017-11-01 17:15 | 51198.5603 | 200.016
Devonshire Building | 2017-11-01 17:30 | 51198.6053 | 180
Devonshire Building | 2017-11-01 17:45 | 51198.6403 | 140.004
Devonshire Building | 2017-11-01 18:00 | 51198.6703 | 119.988
Devonshire Building | 2017-11-01 18:15 | 51198.7053 | 140.004
Devonshire Building | 2017-11-01 18:30 | 51198.7303 | 100.008
Devonshire Building | 2017-11-01 18:45 | 51198.7553 | 100.008
Devonshire Building | 2017-11-01 19:00 | 51199.2803 | 2099.988
Devonshire Building | 2017-11-01 19:15 | 51199.2903 | 39.996
Devonshire Building | 2017-11-01 19:30 | 51199.3003 | 39.996
Devonshire Building | 2017-11-01 19:45 | 51199.3153 | 60.012
Devonshire Building | 2017-11-01 20:00 | 51199.3253 | 39.996
Devonshire Building | 2017-11-01 20:15 | 51199.3353 | 39.996
Devonshire Building | 2017-11-01 20:30 | 51199.3453 | 39.996
Devonshire Building | 2017-11-01 20:45 | 51199.3553 | 39.996
Devonshire Building | 2017-11-01 21:00 | 51199.3653 | 39.996
Devonshire Building | 2017-11-01 21:15 | 51199.3753 | 39.996
Devonshire Building | 2017-11-01 21:30 | 51199.3903 | 60.012
Devonshire Building | 2017-11-01 21:45 | 51199.4103 | 79.992
Devonshire Building | 2017-11-01 22:00 | 51199.4253 | 60.012
Devonshire Building | 2017-11-01 22:15 | 51199.4353 | 39.996
Devonshire Building | 2017-11-01 22:30 | 51199.4453 | 39.996
Devonshire Building | 2017-11-01 22:45 | 51199.4603 | 60.012
Devonshire Building | 2017-11-01 23:00 | 51199.4703 | 39.996
Devonshire Building | 2017-11-01 23:15 | 51199.4803 | 39.996
Devonshire Building | 2017-11-01 23:30 | 51199.4903 | 39.996
Devonshire Building | 2017-11-01 23:45 | 51199.5053 | 60.012
Devonshire Building | 2017-11-02 | 51199.5156 | 39.996
Devonshire Building | 2017-11-02 00:15 | 51199.5256 | 39.996
Devonshire Building | 2017-11-02 00:30 | 51199.5356 | 39.996
Devonshire Building | 2017-11-02 00:45 | 51199.5456 | 39.996
Devonshire Building | 2017-11-02 01:00 | 51199.5556 | 39.996
Devonshire Building | 2017-11-02 01:15 | 51199.5656 | 39.996
Devonshire Building | 2017-11-02 01:30 | 51199.5756 | 39.996
Devonshire Building | 2017-11-02 01:45 | 51199.5856 | 39.996
Devonshire Building | 2017-11-02 02:00 | 51199.5956 | 39.996
Devonshire Building | 2017-11-02 02:15 | 51199.6056 | 39.996
Devonshire Building | 2017-11-02 02:30 | 51199.6156 | 39.996
Devonshire Building | 2017-11-02 02:45 | 51199.6256 | 39.996
Devonshire Building | 2017-11-02 03:00 | 51199.6356 | 39.996
Devonshire Building | 2017-11-02 03:15 | 51199.6456 | 39.996
Devonshire Building | 2017-11-02 03:30 | 51199.6556 | 39.996
Devonshire Building | 2017-11-02 03:45 | 51199.6656 | 39.996
Devonshire Building | 2017-11-02 04:00 | 51199.6756 | 39.996
Devonshire Building | 2017-11-02 04:15 | 51200.1956 | 2080.008
Devonshire Building | 2017-11-02 04:30 | 51200.2106 | 60.012
Devonshire Building | 2017-11-02 04:45 | 51200.2206 | 39.996
Devonshire Building | 2017-11-02 05:00 | 51200.2356 | 60.012
Devonshire Building | 2017-11-02 05:15 | 51200.2456 | 39.996
Devonshire Building | 2017-11-02 05:30 | 51200.2606 | 60.012
Devonshire Building | 2017-11-02 05:45 | 51200.2706 | 39.996
Devonshire Building | 2017-11-02 06:00 | 51200.2856 | 60.012
Devonshire Building | 2017-11-02 06:15 | 51200.3006 | 60.012
Devonshire Building | 2017-11-02 06:30 | 51200.3156 | 60.012
Devonshire Building | 2017-11-02 06:45 | 51200.3306 | 60.012
Devonshire Building | 2017-11-02 07:00 | 51200.3506 | 79.992
Devonshire Building | 2017-11-02 07:15 | 51200.3756 | 100.008
Devonshire Building | 2017-11-02 07:30 | 51200.3906 | 60.012
Devonshire Building | 2017-11-02 07:45 | 51200.4106 | 79.992
Devonshire Building | 2017-11-02 08:00 | 51200.4256 | 60.012
Devonshire Building | 2017-11-02 08:15 | 51200.4556 | 119.988
Devonshire Building | 2017-11-02 08:30 | 51200.4806 | 100.008
Devonshire Building | 2017-11-02 08:45 | 51200.5006 | 79.992
Devonshire Building | 2017-11-02 09:00 | 51200.8756 | 1500.012
Devonshire Building | 2017-11-02 09:15 | 51201.0706 | 780.012
Devonshire Building | 2017-11-02 09:30 | 51201.1106 | 159.984
Devonshire Building | 2017-11-02 09:45 | 51201.2156 | 420.012
Devonshire Building | 2017-11-02 10:00 | 51201.3506 | 540
Devonshire Building | 2017-11-02 10:15 | 51201.4756 | 500.004
Devonshire Building | 2017-11-02 10:30 | 51202.0856 | 2440.008
Devonshire Building | 2017-11-02 10:45 | 51202.2906 | 820.008
Devonshire Building | 2017-11-02 11:00 | 51202.4356 | 579.996
Devonshire Building | 2017-11-02 11:15 | 51202.5756 | 560.016
Devonshire Building | 2017-11-02 11:30 | 51202.7306 | 619.992
Devonshire Building | 2017-11-02 11:45 | 51202.9056 | 699.984
Devonshire Building | 2017-11-02 12:00 | 51203.6006 | 2779.992
Devonshire Building | 2017-11-02 12:15 | 51203.7756 | 699.984
Devonshire Building | 2017-11-02 12:30 | 51203.9356 | 640.008
Devonshire Building | 2017-11-02 12:45 | 51204.0706 | 540
Devonshire Building | 2017-11-02 13:00 | 51204.1956 | 500.004
Devonshire Building | 2017-11-02 13:15 | 51204.8056 | 2440.008
Devonshire Building | 2017-11-02 13:30 | 51204.8906 | 339.984
Devonshire Building | 2017-11-02 13:45 | 51204.9856 | 380.016
Devonshire Building | 2017-11-02 14:00 | 51205.0856 | 399.996
Devonshire Building | 2017-11-02 14:15 | 51205.1756 | 360
Devonshire Building | 2017-11-02 14:30 | 51205.2656 | 360
Devonshire Building | 2017-11-02 14:45 | 51205.9656 | 2800.008
Devonshire Building | 2017-11-02 15:00 | 51206.0306 | 259.992
Devonshire Building | 2017-11-02 15:15 | 51206.1006 | 280.008
Devonshire Building | 2017-11-02 15:30 | 51206.1656 | 259.992
Devonshire Building | 2017-11-02 15:45 | 51206.2356 | 280.008
Devonshire Building | 2017-11-02 16:00 | 51206.3206 | 339.984
Devonshire Building | 2017-11-02 16:15 | 51207.0706 | 2999.988
Devonshire Building | 2017-11-02 16:30 | 51207.2956 | 900
Devonshire Building | 2017-11-02 16:45 | 51207.4806 | 740.016
Devonshire Building | 2017-11-02 17:00 | 51207.6556 | 699.984
Devonshire Building | 2017-11-02 17:15 | 51207.7806 | 500.004
Devonshire Building | 2017-11-02 17:30 | 51207.8806 | 399.996
Devonshire Building | 2017-11-02 17:45 | 51208.4656 | 2340
Devonshire Building | 2017-11-02 18:00 | 51208.5006 | 140.004
Devonshire Building | 2017-11-02 18:15 | 51208.5306 | 119.988
Devonshire Building | 2017-11-02 18:30 | 51208.5706 | 159.984
Devonshire Building | 2017-11-02 18:45 | 51208.6256 | 219.996
Devonshire Building | 2017-11-02 19:00 | 51208.6606 | 140.004
Devonshire Building | 2017-11-02 19:15 | 51208.6906 | 119.988
Devonshire Building | 2017-11-02 19:30 | 51208.7206 | 119.988
Devonshire Building | 2017-11-02 19:45 | 51208.7506 | 119.988
Devonshire Building | 2017-11-02 20:00 | 51208.7756 | 100.008
Devonshire Building | 2017-11-02 20:15 | 51208.8006 | 100.008
Devonshire Building | 2017-11-02 20:30 | 51208.8256 | 100.008
Devonshire Building | 2017-11-02 20:45 | 51208.8456 | 79.992
Devonshire Building | 2017-11-02 21:00 | 51208.8656 | 79.992
Devonshire Building | 2017-11-02 21:15 | 51208.8906 | 100.008
Devonshire Building | 2017-11-02 21:30 | 51208.9106 | 79.992
Devonshire Building | 2017-11-02 21:45 | 51208.9456 | 140.004
Devonshire Building | 2017-11-02 22:00 | 51208.9556 | 39.996
Devonshire Building | 2017-11-02 22:15 | 51208.9656 | 39.996
Devonshire Building | 2017-11-02 22:30 | 51208.9756 | 39.996
Devonshire Building | 2017-11-02 22:45 | 51208.9856 | 39.996
Devonshire Building | 2017-11-02 23:00 | 51208.9906 | 20.016
Devonshire Building | 2017-11-02 23:15 | 51209.0006 | 39.996
Devonshire Building | 2017-11-02 23:30 | 51209.0106 | 39.996
Devonshire Building | 2017-11-02 23:45 | 51209.0206 | 39.996
Devonshire Building | 2017-11-03 | 51209.0312 | 39.996
Devonshire Building | 2017-11-03 00:15 | 51209.0412 | 39.996
Devonshire Building | 2017-11-03 00:30 | 51209.0512 | 39.996
Devonshire Building | 2017-11-03 00:45 | 51209.0612 | 39.996
Devonshire Building | 2017-11-03 01:00 | 51209.0712 | 39.996
Devonshire Building | 2017-11-03 01:15 | 51209.0762 | 20.016
Devonshire Building | 2017-11-03 01:30 | 51209.0862 | 39.996
Devonshire Building | 2017-11-03 01:45 | 51209.0962 | 39.996
Devonshire Building | 2017-11-03 02:00 | 51209.1062 | 39.996
Devonshire Building | 2017-11-03 02:15 | 51209.3262 | 879.984
Devonshire Building | 2017-11-03 02:30 | 51209.6312 | 1220.004
Devonshire Building | 2017-11-03 02:45 | 51209.6412 | 39.996
Devonshire Building | 2017-11-03 03:00 | 51209.6512 | 39.996
Devonshire Building | 2017-11-03 03:15 | 51209.6612 | 39.996
Devonshire Building | 2017-11-03 03:30 | 51209.6712 | 39.996
Devonshire Building | 2017-11-03 03:45 | 51209.6762 | 20.016
Devonshire Building | 2017-11-03 04:00 | 51209.6862 | 39.996
Devonshire Building | 2017-11-03 04:15 | 51209.6962 | 39.996
Devonshire Building | 2017-11-03 04:30 | 51209.7062 | 39.996
Devonshire Building | 2017-11-03 04:45 | 51209.7162 | 39.996
Devonshire Building | 2017-11-03 05:00 | 51209.7212 | 20.016
Devonshire Building | 2017-11-03 05:15 | 51209.7312 | 39.996
Devonshire Building | 2017-11-03 05:30 | 51209.7412 | 39.996
Devonshire Building | 2017-11-03 05:45 | 51209.7512 | 39.996
Devonshire Building | 2017-11-03 06:00 | 51209.7612 | 39.996
Devonshire Building | 2017-11-03 06:15 | 51209.7712 | 39.996
Devonshire Building | 2017-11-03 06:30 | 51209.7812 | 39.996
Devonshire Building | 2017-11-03 06:45 | 51209.7912 | 39.996
Devonshire Building | 2017-11-03 07:00 | 51209.8112 | 79.992
Devonshire Building | 2017-11-03 07:15 | 51209.8212 | 39.996
Devonshire Building | 2017-11-03 07:30 | 51209.8312 | 39.996
Devonshire Building | 2017-11-03 07:45 | 51209.8462 | 60.012
Devonshire Building | 2017-11-03 08:00 | 51209.8612 | 60.012
Devonshire Building | 2017-11-03 08:15 | 51209.8962 | 140.004
Devonshire Building | 2017-11-03 08:30 | 51210.4412 | 2180.016
Devonshire Building | 2017-11-03 08:45 | 51210.4862 | 180
Devonshire Building | 2017-11-03 09:00 | 51210.5312 | 180
Devonshire Building | 2017-11-03 09:15 | 51210.5862 | 219.996
Devonshire Building | 2017-11-03 09:30 | 51210.6362 | 200.016
Devonshire Building | 2017-11-03 09:45 | 51210.6812 | 180
Devonshire Building | 2017-11-03 10:00 | 51210.7262 | 180
Devonshire Building | 2017-11-03 10:15 | 51210.7812 | 219.996
Devonshire Building | 2017-11-03 10:30 | 51211.3762 | 2379.996
Devonshire Building | 2017-11-03 10:45 | 51211.4862 | 439.992
Devonshire Building | 2017-11-03 11:00 | 51211.6712 | 740.016
Devonshire Building | 2017-11-03 11:15 | 51211.8563 | 740.016
Devonshire Building | 2017-11-03 11:30 | 51212.0163 | 640.008
Devonshire Building | 2017-11-03 11:45 | 51212.6613 | 2580.012
Devonshire Building | 2017-11-03 12:00 | 51212.7613 | 399.996
Devonshire Building | 2017-11-03 12:15 | 51212.8563 | 380.016
Devonshire Building | 2017-11-03 12:30 | 51212.9513 | 380.016
Devonshire Building | 2017-11-03 12:45 | 51213.0363 | 339.984
Devonshire Building | 2017-11-03 13:00 | 51213.6663 | 2520
Devonshire Building | 2017-11-03 13:15 | 51213.7363 | 280.008
Devonshire Building | 2017-11-03 13:30 | 51213.7963 | 240.012
Devonshire Building | 2017-11-03 13:45 | 51213.8463 | 200.016
Devonshire Building | 2017-11-03 14:00 | 51213.8963 | 200.016
Devonshire Building | 2017-11-03 14:15 | 51213.9413 | 180
Devonshire Building | 2017-11-03 14:30 | 51214.0763 | 540
Devonshire Building | 2017-11-03 14:45 | 51214.5513 | 1900.008
Devonshire Building | 2017-11-03 15:00 | 51214.5813 | 119.988
Devonshire Building | 2017-11-03 15:15 | 51214.6063 | 100.008
Devonshire Building | 2017-11-03 15:30 | 51214.6363 | 119.988
Devonshire Building | 2017-11-03 15:45 | 51214.6713 | 140.004
Devonshire Building | 2017-11-03 16:00 | 51214.8163 | 579.996
Devonshire Building | 2017-11-03 16:15 | 51215.3213 | 2019.996
Devonshire Building | 2017-11-03 16:30 | 51215.4063 | 339.984
Devonshire Building | 2017-11-03 16:45 | 51215.4813 | 299.988
Devonshire Building | 2017-11-03 17:00 | 51215.5563 | 299.988
Devonshire Building | 2017-11-03 17:15 | 51215.6263 | 280.008
Devonshire Building | 2017-11-03 17:30 | 51215.6863 | 240.012
Devonshire Building | 2017-11-03 17:45 | 51215.7413 | 219.996
Devonshire Building | 2017-11-03 18:00 | 51215.7913 | 200.016
Devonshire Building | 2017-11-03 18:15 | 51215.8363 | 180
Devonshire Building | 2017-11-03 18:30 | 51215.8763 | 159.984
Devonshire Building | 2017-11-03 18:45 | 51215.9113 | 140.004
Devonshire Building | 2017-11-03 19:00 | 51215.9413 | 119.988
Devonshire Building | 2017-11-03 19:15 | 51215.9713 | 119.988
Devonshire Building | 2017-11-03 19:30 | 51216.0013 | 119.988
Devonshire Building | 2017-11-03 19:45 | 51216.0263 | 100.008
Devonshire Building | 2017-11-03 20:00 | 51216.5413 | 2059.992
Devonshire Building | 2017-11-03 20:15 | 51216.5613 | 79.992
Devonshire Building | 2017-11-03 20:30 | 51216.5763 | 60.012
Devonshire Building | 2017-11-03 20:45 | 51216.5863 | 39.996
Devonshire Building | 2017-11-03 21:00 | 51216.5963 | 39.996
Devonshire Building | 2017-11-03 21:15 | 51216.6113 | 60.012
Devonshire Building | 2017-11-03 21:30 | 51216.6213 | 39.996
Devonshire Building | 2017-11-03 21:45 | 51216.6413 | 79.992
Devonshire Building | 2017-11-03 22:00 | 51216.6563 | 60.012
Devonshire Building | 2017-11-03 22:15 | 51216.6663 | 39.996
Devonshire Building | 2017-11-03 22:30 | 51216.6763 | 39.996
Devonshire Building | 2017-11-03 22:45 | 51216.6913 | 60.012
Devonshire Building | 2017-11-03 23:00 | 51216.7063 | 60.012
Devonshire Building | 2017-11-03 23:15 | 51216.7163 | 39.996
Devonshire Building | 2017-11-03 23:30 | 51216.7313 | 60.012
Devonshire Building | 2017-11-03 23:45 | 51216.7413 | 39.996
Devonshire Building | 2017-11-04 | 51216.7539 | 60.012
Devonshire Building | 2017-11-04 00:15 | 51216.7639 | 39.996
Devonshire Building | 2017-11-04 00:30 | 51216.7739 | 39.996
Devonshire Building | 2017-11-04 00:45 | 51216.7889 | 60.012
Devonshire Building | 2017-11-04 01:00 | 51216.7989 | 39.996
Devonshire Building | 2017-11-04 01:15 | 51216.8089 | 39.996
Devonshire Building | 2017-11-04 01:30 | 51216.8189 | 39.996
Devonshire Building | 2017-11-04 01:45 | 51216.8339 | 60.012
Devonshire Building | 2017-11-04 02:00 | 51216.8439 | 39.996
Devonshire Building | 2017-11-04 02:15 | 51216.8539 | 39.996
Devonshire Building | 2017-11-04 02:30 | 51216.8639 | 39.996
Devonshire Building | 2017-11-04 02:45 | 51216.8739 | 39.996
Devonshire Building | 2017-11-04 03:00 | 51216.8889 | 60.012
Devonshire Building | 2017-11-04 03:15 | 51216.8989 | 39.996
Devonshire Building | 2017-11-04 03:30 | 51216.9089 | 39.996
Devonshire Building | 2017-11-04 03:45 | 51216.9189 | 39.996
Devonshire Building | 2017-11-04 04:00 | 51216.9289 | 39.996
Devonshire Building | 2017-11-04 04:15 | 51216.9389 | 39.996
Devonshire Building | 2017-11-04 04:30 | 51216.9489 | 39.996
Devonshire Building | 2017-11-04 04:45 | 51216.9589 | 39.996
Devonshire Building | 2017-11-04 05:00 | 51216.9689 | 39.996
Devonshire Building | 2017-11-04 05:15 | 51217.1539 | 740.016
Devonshire Building | 2017-11-04 05:30 | 51217.4939 | 1360.008
Devonshire Building | 2017-11-04 05:45 | 51217.5039 | 39.996
Devonshire Building | 2017-11-04 06:00 | 51217.5189 | 60.012
Devonshire Building | 2017-11-04 06:15 | 51217.5289 | 39.996
Devonshire Building | 2017-11-04 06:30 | 51217.5389 | 39.996
Devonshire Building | 2017-11-04 06:45 | 51217.5489 | 39.996
Devonshire Building | 2017-11-04 07:00 | 51217.5589 | 39.996
Devonshire Building | 2017-11-04 07:15 | 51217.5739 | 60.012
Devonshire Building | 2017-11-04 07:30 | 51217.5839 | 39.996
Devonshire Building | 2017-11-04 07:45 | 51217.6089 | 100.008
Devonshire Building | 2017-11-04 08:00 | 51217.6389 | 119.988
Devonshire Building | 2017-11-04 08:15 | 51217.6639 | 100.008
Devonshire Building | 2017-11-04 08:30 | 51217.6939 | 119.988
Devonshire Building | 2017-11-04 08:45 | 51217.7239 | 119.988
Devonshire Building | 2017-11-04 09:00 | 51217.7539 | 119.988
Devonshire Building | 2017-11-04 09:15 | 51217.7839 | 119.988
Devonshire Building | 2017-11-04 09:30 | 51217.8089 | 100.008
Devonshire Building | 2017-11-04 09:45 | 51217.8389 | 119.988
Devonshire Building | 2017-11-04 10:00 | 51217.8689 | 119.988
Devonshire Building | 2017-11-04 10:15 | 51217.8989 | 119.988
Devonshire Building | 2017-11-04 10:30 | 51217.9239 | 100.008
Devonshire Building | 2017-11-04 10:45 | 51217.9439 | 79.992
Devonshire Building | 2017-11-04 11:00 | 51217.9589 | 60.012
Devonshire Building | 2017-11-04 11:15 | 51217.9739 | 60.012
Devonshire Building | 2017-11-04 11:30 | 51217.9839 | 39.996
Devonshire Building | 2017-11-04 11:45 | 51217.9989 | 60.012
Devonshire Building | 2017-11-04 12:00 | 51218.0089 | 39.996
Devonshire Building | 2017-11-04 12:15 | 51218.0239 | 60.012
Devonshire Building | 2017-11-04 12:30 | 51218.0339 | 39.996
Devonshire Building | 2017-11-04 12:45 | 51218.0489 | 60.012
Devonshire Building | 2017-11-04 13:00 | 51218.0589 | 39.996
Devonshire Building | 2017-11-04 13:15 | 51218.0739 | 60.012
Devonshire Building | 2017-11-04 13:30 | 51218.0839 | 39.996
Devonshire Building | 2017-11-04 13:45 | 51218.0989 | 60.012
Devonshire Building | 2017-11-04 14:00 | 51218.6289 | 2120.004
Devonshire Building | 2017-11-04 14:15 | 51218.6439 | 60.012
Devonshire Building | 2017-11-04 14:30 | 51218.6589 | 60.012
Devonshire Building | 2017-11-04 14:45 | 51218.6739 | 60.012
Devonshire Building | 2017-11-04 15:00 | 51218.6889 | 60.012
Devonshire Building | 2017-11-04 15:15 | 51218.7039 | 60.012
Devonshire Building | 2017-11-04 15:30 | 51218.7239 | 79.992
Devonshire Building | 2017-11-04 15:45 | 51218.7389 | 60.012
Devonshire Building | 2017-11-04 16:00 | 51218.7589 | 79.992
Devonshire Building | 2017-11-04 16:15 | 51218.7789 | 79.992
Devonshire Building | 2017-11-04 16:30 | 51218.7989 | 79.992
Devonshire Building | 2017-11-04 16:45 | 51218.8189 | 79.992
Devonshire Building | 2017-11-04 17:00 | 51218.8339 | 60.012
Devonshire Building | 2017-11-04 17:15 | 51218.8539 | 79.992
Devonshire Building | 2017-11-04 17:30 | 51218.8739 | 79.992
Devonshire Building | 2017-11-04 17:45 | 51218.8939 | 79.992
Devonshire Building | 2017-11-04 18:00 | 51218.9089 | 60.012
Devonshire Building | 2017-11-04 18:15 | 51218.9289 | 79.992
Devonshire Building | 2017-11-04 18:30 | 51218.9439 | 60.012
Devonshire Building | 2017-11-04 18:45 | 51218.9639 | 79.992
Devonshire Building | 2017-11-04 19:00 | 51218.9789 | 60.012
Devonshire Building | 2017-11-04 19:15 | 51218.9939 | 60.012
Devonshire Building | 2017-11-04 19:30 | 51219.0139 | 79.992
Devonshire Building | 2017-11-04 19:45 | 51219.0289 | 60.012
Devonshire Building | 2017-11-04 20:00 | 51219.0439 | 60.012
Devonshire Building | 2017-11-04 20:15 | 51219.0589 | 60.012
Devonshire Building | 2017-11-04 20:30 | 51219.0739 | 60.012
Devonshire Building | 2017-11-04 20:45 | 51219.0889 | 60.012
Devonshire Building | 2017-11-04 21:00 | 51219.1039 | 60.012
Devonshire Building | 2017-11-04 21:15 | 51219.1189 | 60.012
Devonshire Building | 2017-11-04 21:30 | 51219.1339 | 60.012
Devonshire Building | 2017-11-04 21:45 | 51219.1689 | 140.004
Devonshire Building | 2017-11-04 22:00 | 51219.1839 | 60.012
Devonshire Building | 2017-11-04 22:15 | 51219.1989 | 60.012
Devonshire Building | 2017-11-04 22:30 | 51219.214 | 60.012
Devonshire Building | 2017-11-04 22:45 | 51219.229 | 60.012
Devonshire Building | 2017-11-04 23:00 | 51219.239 | 39.996
Devonshire Building | 2017-11-04 23:15 | 51219.254 | 60.012
Devonshire Building | 2017-11-04 23:30 | 51219.269 | 60.012
Devonshire Building | 2017-11-04 23:45 | 51219.794 | 2099.988
Devonshire Building | 2017-11-05 | 51219.8086 | 60.012
Devonshire Building | 2017-11-05 00:15 | 51219.8186 | 39.996
Devonshire Building | 2017-11-05 00:30 | 51219.8336 | 60.012
Devonshire Building | 2017-11-05 00:45 | 51219.8486 | 60.012
Devonshire Building | 2017-11-05 01:00 | 51219.8586 | 39.996
Devonshire Building | 2017-11-05 01:15 | 51219.8736 | 60.012
Devonshire Building | 2017-11-05 01:30 | 51219.8886 | 60.012
Devonshire Building | 2017-11-05 01:45 | 51219.8986 | 39.996
Devonshire Building | 2017-11-05 02:00 | 51219.9186 | 79.992
Devonshire Building | 2017-11-05 02:15 | 51219.9336 | 60.012
Devonshire Building | 2017-11-05 02:30 | 51219.9486 | 60.012
Devonshire Building | 2017-11-05 02:45 | 51219.9636 | 60.012
Devonshire Building | 2017-11-05 03:00 | 51219.9836 | 79.992
Devonshire Building | 2017-11-05 03:15 | 51219.9986 | 60.012
Devonshire Building | 2017-11-05 03:30 | 51220.0136 | 60.012
Devonshire Building | 2017-11-05 03:45 | 51220.0286 | 60.012
Devonshire Building | 2017-11-05 04:00 | 51220.0436 | 60.012
Devonshire Building | 2017-11-05 04:15 | 51220.0586 | 60.012
Devonshire Building | 2017-11-05 04:30 | 51220.0736 | 60.012
Devonshire Building | 2017-11-05 04:45 | 51220.0836 | 39.996
Devonshire Building | 2017-11-05 05:00 | 51220.0986 | 60.012
Devonshire Building | 2017-11-05 05:15 | 51220.1136 | 60.012
Devonshire Building | 2017-11-05 05:30 | 51220.1286 | 60.012
Devonshire Building | 2017-11-05 05:45 | 51220.1436 | 60.012
Devonshire Building | 2017-11-05 06:00 | 51220.1536 | 39.996
Devonshire Building | 2017-11-05 06:15 | 51220.1686 | 60.012
Devonshire Building | 2017-11-05 06:30 | 51220.1836 | 60.012
Devonshire Building | 2017-11-05 06:45 | 51220.1936 | 39.996
Devonshire Building | 2017-11-05 07:00 | 51220.2086 | 60.012
Devonshire Building | 2017-11-05 07:15 | 51220.2236 | 60.012
Devonshire Building | 2017-11-05 07:30 | 51220.2336 | 39.996
Devonshire Building | 2017-11-05 07:45 | 51220.2536 | 79.992
Devonshire Building | 2017-11-05 08:00 | 51220.2786 | 100.008
Devonshire Building | 2017-11-05 08:15 | 51220.3086 | 119.988
Devonshire Building | 2017-11-05 08:30 | 51220.3386 | 119.988
Devonshire Building | 2017-11-05 08:45 | 51220.3636 | 100.008
Devonshire Building | 2017-11-05 09:00 | 51220.3936 | 119.988
Devonshire Building | 2017-11-05 09:15 | 51220.4186 | 100.008
Devonshire Building | 2017-11-05 09:30 | 51220.4536 | 140.004
Devonshire Building | 2017-11-05 09:45 | 51220.9736 | 2080.008
Devonshire Building | 2017-11-05 10:00 | 51220.9986 | 100.008
Devonshire Building | 2017-11-05 10:15 | 51221.0286 | 119.988
Devonshire Building | 2017-11-05 10:30 | 51221.0536 | 100.008
Devonshire Building | 2017-11-05 10:45 | 51221.0636 | 39.996
Devonshire Building | 2017-11-05 11:00 | 51221.0736 | 39.996
Devonshire Building | 2017-11-05 11:15 | 51221.0836 | 39.996
Devonshire Building | 2017-11-05 11:30 | 51221.0986 | 60.012
Devonshire Building | 2017-11-05 11:45 | 51221.1086 | 39.996
Devonshire Building | 2017-11-05 12:00 | 51221.1186 | 39.996
Devonshire Building | 2017-11-05 12:15 | 51221.1336 | 60.012
Devonshire Building | 2017-11-05 12:30 | 51221.1486 | 60.012
Devonshire Building | 2017-11-05 12:45 | 51221.1636 | 60.012
Devonshire Building | 2017-11-05 13:00 | 51221.1787 | 60.012
Devonshire Building | 2017-11-05 13:15 | 51221.1937 | 60.012
Devonshire Building | 2017-11-05 13:30 | 51221.2087 | 60.012
Devonshire Building | 2017-11-05 13:45 | 51221.2237 | 60.012
Devonshire Building | 2017-11-05 14:00 | 51221.2437 | 79.992
Devonshire Building | 2017-11-05 14:15 | 51221.2537 | 39.996
Devonshire Building | 2017-11-05 14:30 | 51221.2687 | 60.012
Devonshire Building | 2017-11-05 14:45 | 51221.2837 | 60.012
Devonshire Building | 2017-11-05 15:00 | 51221.2937 | 39.996
Devonshire Building | 2017-11-05 15:15 | 51221.3037 | 39.996
Devonshire Building | 2017-11-05 15:30 | 51221.3187 | 60.012
Devonshire Building | 2017-11-05 15:45 | 51221.3287 | 39.996
Devonshire Building | 2017-11-05 16:00 | 51221.3437 | 60.012
Devonshire Building | 2017-11-05 16:15 | 51221.3537 | 39.996
Devonshire Building | 2017-11-05 16:30 | 51221.3637 | 39.996
Devonshire Building | 2017-11-05 16:45 | 51221.3787 | 60.012
Devonshire Building | 2017-11-05 17:00 | 51221.3887 | 39.996
Devonshire Building | 2017-11-05 17:15 | 51221.3987 | 39.996
Devonshire Building | 2017-11-05 17:30 | 51221.4137 | 60.012
Devonshire Building | 2017-11-05 17:45 | 51221.4237 | 39.996
Devonshire Building | 2017-11-05 18:00 | 51221.4387 | 60.012
Devonshire Building | 2017-11-05 18:15 | 51221.9537 | 2059.992
Devonshire Building | 2017-11-05 18:30 | 51221.9687 | 60.012
Devonshire Building | 2017-11-05 18:45 | 51221.9787 | 39.996
Devonshire Building | 2017-11-05 19:00 | 51221.9887 | 39.996
Devonshire Building | 2017-11-05 19:15 | 51222.0037 | 60.012
Devonshire Building | 2017-11-05 19:30 | 51222.0137 | 39.996
Devonshire Building | 2017-11-05 19:45 | 51222.0287 | 60.012
Devonshire Building | 2017-11-05 20:00 | 51222.0387 | 39.996
Devonshire Building | 2017-11-05 20:15 | 51222.0487 | 39.996
Devonshire Building | 2017-11-05 20:30 | 51222.0637 | 60.012
Devonshire Building | 2017-11-05 20:45 | 51222.0787 | 60.012
Devonshire Building | 2017-11-05 21:00 | 51222.0937 | 60.012
Devonshire Building | 2017-11-05 21:15 | 51222.1087 | 60.012
Devonshire Building | 2017-11-05 21:30 | 51222.1237 | 60.012
Devonshire Building | 2017-11-05 21:45 | 51222.1437 | 79.992
Devonshire Building | 2017-11-05 22:00 | 51222.1587 | 60.012
Devonshire Building | 2017-11-05 22:15 | 51222.1737 | 60.012
Devonshire Building | 2017-11-05 22:30 | 51222.1887 | 60.012
Devonshire Building | 2017-11-05 22:45 | 51222.2037 | 60.012
Devonshire Building | 2017-11-05 23:00 | 51222.2137 | 39.996
Devonshire Building | 2017-11-05 23:15 | 51222.2287 | 60.012
Devonshire Building | 2017-11-05 23:30 | 51222.2437 | 60.012
Devonshire Building | 2017-11-05 23:45 | 51222.2537 | 39.996
Devonshire Building | 2017-11-06 | 51222.2695 | 60.012
Devonshire Building | 2017-11-06 00:15 | 51222.2845 | 60.012
Devonshire Building | 2017-11-06 00:30 | 51222.2995 | 60.012
Devonshire Building | 2017-11-06 00:45 | 51222.3095 | 39.996
Devonshire Building | 2017-11-06 01:00 | 51222.3245 | 60.012
Devonshire Building | 2017-11-06 01:15 | 51222.3395 | 60.012
Devonshire Building | 2017-11-06 01:30 | 51222.3495 | 39.996
Devonshire Building | 2017-11-06 01:45 | 51222.3645 | 60.012
Devonshire Building | 2017-11-06 02:00 | 51222.3745 | 39.996
Devonshire Building | 2017-11-06 02:15 | 51222.3895 | 60.012
Devonshire Building | 2017-11-06 02:30 | 51222.3995 | 39.996
Devonshire Building | 2017-11-06 02:45 | 51222.4095 | 39.996
Devonshire Building | 2017-11-06 03:00 | 51222.4245 | 60.012
Devonshire Building | 2017-11-06 03:15 | 51222.4345 | 39.996
Devonshire Building | 2017-11-06 03:30 | 51222.4495 | 60.012
Devonshire Building | 2017-11-06 03:45 | 51222.4595 | 39.996
Devonshire Building | 2017-11-06 04:00 | 51222.4695 | 39.996
Devonshire Building | 2017-11-06 04:15 | 51222.4845 | 60.012
Devonshire Building | 2017-11-06 04:30 | 51222.4945 | 39.996
Devonshire Building | 2017-11-06 04:45 | 51223.0195 | 2099.988
Devonshire Building | 2017-11-06 05:00 | 51223.0345 | 60.012
Devonshire Building | 2017-11-06 05:15 | 51223.0445 | 39.996
Devonshire Building | 2017-11-06 05:30 | 51223.0545 | 39.996
Devonshire Building | 2017-11-06 05:45 | 51223.0695 | 60.012
Devonshire Building | 2017-11-06 06:00 | 51223.0795 | 39.996
Devonshire Building | 2017-11-06 06:15 | 51223.0946 | 60.012
Devonshire Building | 2017-11-06 06:30 | 51223.1096 | 60.012
Devonshire Building | 2017-11-06 06:45 | 51223.1196 | 39.996
Devonshire Building | 2017-11-06 07:00 | 51223.1346 | 60.012
Devonshire Building | 2017-11-06 07:15 | 51223.1496 | 60.012
Devonshire Building | 2017-11-06 07:30 | 51223.1746 | 100.008
Devonshire Building | 2017-11-06 07:45 | 51223.2046 | 119.988
Devonshire Building | 2017-11-06 08:00 | 51223.2396 | 140.004
Devonshire Building | 2017-11-06 08:15 | 51223.2746 | 140.004
Devonshire Building | 2017-11-06 08:30 | 51223.3196 | 180
Devonshire Building | 2017-11-06 08:45 | 51223.3596 | 159.984
Devonshire Building | 2017-11-06 09:00 | 51223.9646 | 2419.992
Devonshire Building | 2017-11-06 09:15 | 51224.0146 | 200.016
Devonshire Building | 2017-11-06 09:30 | 51224.0696 | 219.996
Devonshire Building | 2017-11-06 09:45 | 51224.1346 | 259.992
Devonshire Building | 2017-11-06 10:00 | 51224.2696 | 540
Devonshire Building | 2017-11-06 10:15 | 51224.3446 | 299.988
Devonshire Building | 2017-11-06 10:30 | 51224.5995 | 1019.988
Devonshire Building | 2017-11-06 10:45 | 51225.0196 | 1680.012
Devonshire Building | 2017-11-06 11:00 | 51225.0746 | 219.996
Devonshire Building | 2017-11-06 11:15 | 51225.1295 | 219.996
Devonshire Building | 2017-11-06 11:30 | 51225.1945 | 259.992
Devonshire Building | 2017-11-06 11:45 | 51225.2695 | 299.988
Devonshire Building | 2017-11-06 12:00 | 51225.8995 | 2520
Devonshire Building | 2017-11-06 12:15 | 51225.9995 | 399.996
Devonshire Building | 2017-11-06 12:30 | 51226.0845 | 339.984
Devonshire Building | 2017-11-06 12:45 | 51226.1695 | 339.984
Devonshire Building | 2017-11-06 13:00 | 51226.2395 | 280.008
Devonshire Building | 2017-11-06 13:15 | 51226.3145 | 299.988
Devonshire Building | 2017-11-06 13:30 | 51226.9095 | 2379.996
Devonshire Building | 2017-11-06 13:45 | 51226.9645 | 219.996
Devonshire Building | 2017-11-06 14:00 | 51227.0295 | 259.992
Devonshire Building | 2017-11-06 14:15 | 51227.0895 | 240.012
Devonshire Building | 2017-11-06 14:30 | 51227.1545 | 259.992
Devonshire Building | 2017-11-06 14:45 | 51227.2095 | 219.996
Devonshire Building | 2017-11-06 15:00 | 51227.2845 | 299.988
Devonshire Building | 2017-11-06 15:15 | 51227.8795 | 2379.996
Devonshire Building | 2017-11-06 15:30 | 51228.1045 | 900
Devonshire Building | 2017-11-06 15:45 | 51228.2195 | 460.008
Devonshire Building | 2017-11-06 16:00 | 51228.3095 | 360
Devonshire Building | 2017-11-06 16:15 | 51228.3945 | 339.984
Devonshire Building | 2017-11-06 16:30 | 51228.4795 | 339.984
Devonshire Building | 2017-11-06 16:45 | 51228.9995 | 2080.008
Devonshire Building | 2017-11-06 17:00 | 51229.1795 | 720
Devonshire Building | 2017-11-06 17:15 | 51229.2445 | 259.992
Devonshire Building | 2017-11-06 17:30 | 51229.3095 | 259.992
Devonshire Building | 2017-11-06 17:45 | 51229.3645 | 219.996
Devonshire Building | 2017-11-06 18:00 | 51229.4095 | 180
Devonshire Building | 2017-11-06 18:15 | 51229.4545 | 180
Devonshire Building | 2017-11-06 18:30 | 51229.4945 | 159.984
Devonshire Building | 2017-11-06 18:45 | 51229.5295 | 140.004
Devonshire Building | 2017-11-06 19:00 | 51229.5645 | 140.004
Devonshire Building | 2017-11-06 19:15 | 51229.5945 | 119.988
Devonshire Building | 2017-11-06 19:30 | 51229.6245 | 119.988
Devonshire Building | 2017-11-06 19:45 | 51229.6495 | 100.008
Devonshire Building | 2017-11-06 20:00 | 51229.6745 | 100.008
Devonshire Building | 2017-11-06 20:15 | 51229.6995 | 100.008
Devonshire Building | 2017-11-06 20:30 | 51229.7195 | 79.992
Devonshire Building | 2017-11-06 20:45 | 51229.7445 | 100.008
Devonshire Building | 2017-11-06 21:00 | 51229.7645 | 79.992
Devonshire Building | 2017-11-06 21:15 | 51229.7895 | 100.008
Devonshire Building | 2017-11-06 21:30 | 51229.8095 | 79.992
Devonshire Building | 2017-11-06 21:45 | 51229.8445 | 140.004
Devonshire Building | 2017-11-06 22:00 | 51229.8545 | 39.996
Devonshire Building | 2017-11-06 22:15 | 51229.8645 | 39.996
Devonshire Building | 2017-11-06 22:30 | 51230.2595 | 1580.004
Devonshire Building | 2017-11-06 22:45 | 51230.3945 | 540
Devonshire Building | 2017-11-06 23:00 | 51230.3995 | 20.016
Devonshire Building | 2017-11-06 23:15 | 51230.4095 | 39.996
Devonshire Building | 2017-11-06 23:30 | 51230.4195 | 39.996
Devonshire Building | 2017-11-06 23:45 | 51230.4245 | 20.016
Devonshire Building | 2017-11-07 | 51230.4336 | 39.996
Devonshire Building | 2017-11-07 00:15 | 51230.4436 | 39.996
Devonshire Building | 2017-11-07 00:30 | 51230.4486 | 20.016
Devonshire Building | 2017-11-07 00:45 | 51230.4586 | 39.996
Devonshire Building | 2017-11-07 01:00 | 51230.4686 | 39.996
Devonshire Building | 2017-11-07 01:15 | 51230.4736 | 20.016
Devonshire Building | 2017-11-07 01:30 | 51230.4836 | 39.996
Devonshire Building | 2017-11-07 01:45 | 51230.4986 | 60.012
Devonshire Building | 2017-11-07 02:00 | 51230.5186 | 79.992
Devonshire Building | 2017-11-07 02:15 | 51230.5436 | 100.008
Devonshire Building | 2017-11-07 02:30 | 51230.5686 | 100.008
Devonshire Building | 2017-11-07 02:45 | 51230.5936 | 100.008
Devonshire Building | 2017-11-07 03:00 | 51230.6136 | 79.992
Devonshire Building | 2017-11-07 03:15 | 51230.6386 | 100.008
Devonshire Building | 2017-11-07 03:30 | 51230.6636 | 100.008
Devonshire Building | 2017-11-07 03:45 | 51230.6886 | 100.008
Devonshire Building | 2017-11-07 04:00 | 51230.7086 | 79.992
Devonshire Building | 2017-11-07 04:15 | 51230.7186 | 39.996
Devonshire Building | 2017-11-07 04:30 | 51230.7286 | 39.996
Devonshire Building | 2017-11-07 04:45 | 51230.7336 | 20.016
Devonshire Building | 2017-11-07 05:00 | 51230.7436 | 39.996
Devonshire Building | 2017-11-07 05:15 | 51230.7536 | 39.996
Devonshire Building | 2017-11-07 05:30 | 51230.7636 | 39.996
Devonshire Building | 2017-11-07 05:45 | 51230.7686 | 20.016
Devonshire Building | 2017-11-07 06:00 | 51230.7786 | 39.996
Devonshire Building | 2017-11-07 06:15 | 51230.7886 | 39.996
Devonshire Building | 2017-11-07 06:30 | 51230.7986 | 39.996
Devonshire Building | 2017-11-07 06:45 | 51230.8086 | 39.996
Devonshire Building | 2017-11-07 07:00 | 51230.8236 | 60.012
Devonshire Building | 2017-11-07 07:15 | 51231.2036 | 1519.992
Devonshire Building | 2017-11-07 07:30 | 51231.3536 | 600.012
Devonshire Building | 2017-11-07 07:45 | 51231.3636 | 39.996
Devonshire Building | 2017-11-07 08:00 | 51231.3786 | 60.012
Devonshire Building | 2017-11-07 08:15 | 51231.3886 | 39.996
Devonshire Building | 2017-11-07 08:30 | 51231.4136 | 100.008
Devonshire Building | 2017-11-07 08:45 | 51231.4286 | 60.012
Devonshire Building | 2017-11-07 09:00 | 51231.4536 | 100.008
Devonshire Building | 2017-11-07 09:15 | 51231.4836 | 119.988
Devonshire Building | 2017-11-07 09:30 | 51231.5186 | 140.004
Devonshire Building | 2017-11-07 09:45 | 51231.9786 | 1839.996
Devonshire Building | 2017-11-07 10:00 | 51232.1536 | 699.984
Devonshire Building | 2017-11-07 10:15 | 51232.1936 | 159.984
Devonshire Building | 2017-11-07 10:30 | 51232.2486 | 219.996
Devonshire Building | 2017-11-07 10:45 | 51232.3286 | 320.004
Devonshire Building | 2017-11-07 11:00 | 51232.8186 | 1959.984
Devonshire Building | 2017-11-07 11:15 | 51233.0836 | 1059.984
Devonshire Building | 2017-11-07 11:30 | 51233.1786 | 380.016
Devonshire Building | 2017-11-07 11:45 | 51233.2636 | 339.984
Devonshire Building | 2017-11-07 12:00 | 51233.3336 | 280.008
Devonshire Building | 2017-11-07 12:15 | 51233.3986 | 259.992
Devonshire Building | 2017-11-07 12:30 | 51233.9986 | 2400.012
Devonshire Building | 2017-11-07 12:45 | 51234.0586 | 240.012
Devonshire Building | 2017-11-07 13:00 | 51234.1086 | 200.016
Devonshire Building | 2017-11-07 13:15 | 51234.1786 | 280.008
Devonshire Building | 2017-11-07 13:30 | 51234.2536 | 299.988
Devonshire Building | 2017-11-07 13:45 | 51234.9036 | 2599.992
Devonshire Building | 2017-11-07 14:00 | 51235.0336 | 519.984
Devonshire Building | 2017-11-07 14:15 | 51235.1436 | 439.992
Devonshire Building | 2017-11-07 14:30 | 51235.2336 | 360
Devonshire Building | 2017-11-07 14:45 | 51235.3136 | 320.004
Devonshire Building | 2017-11-07 15:00 | 51235.3836 | 280.008
Devonshire Building | 2017-11-07 15:15 | 51235.4686 | 339.984
Devonshire Building | 2017-11-07 15:30 | 51236.0886 | 2480.004
Devonshire Building | 2017-11-07 15:45 | 51236.1486 | 240.012
Devonshire Building | 2017-11-07 16:00 | 51236.2136 | 259.992
Devonshire Building | 2017-11-07 16:15 | 51236.2736 | 240.012
Devonshire Building | 2017-11-07 16:30 | 51236.3436 | 280.008
Devonshire Building | 2017-11-07 16:45 | 51236.4036 | 240.012
Devonshire Building | 2017-11-07 17:00 | 51237.0136 | 2440.008
Devonshire Building | 2017-11-07 17:15 | 51237.0586 | 180
Devonshire Building | 2017-11-07 17:30 | 51237.1086 | 200.016
Devonshire Building | 2017-11-07 17:45 | 51237.1586 | 200.016
Devonshire Building | 2017-11-07 18:00 | 51237.2086 | 200.016
Devonshire Building | 2017-11-07 18:15 | 51237.2486 | 159.984
Devonshire Building | 2017-11-07 18:30 | 51237.2786 | 119.988
Devonshire Building | 2017-11-07 18:45 | 51237.3086 | 119.988
Devonshire Building | 2017-11-07 19:00 | 51237.3386 | 119.988
Devonshire Building | 2017-11-07 19:15 | 51237.3686 | 119.988
Devonshire Building | 2017-11-07 19:30 | 51237.3936 | 100.008
Devonshire Building | 2017-11-07 19:45 | 51237.4236 | 119.988
Devonshire Building | 2017-11-07 20:00 | 51237.4486 | 100.008
Devonshire Building | 2017-11-07 20:15 | 51237.4786 | 119.988
Devonshire Building | 2017-11-07 20:30 | 51237.5036 | 100.008
Devonshire Building | 2017-11-07 20:45 | 51237.5236 | 79.992
Devonshire Building | 2017-11-07 21:00 | 51237.5486 | 100.008
Devonshire Building | 2017-11-07 21:15 | 51237.5736 | 100.008
Devonshire Building | 2017-11-07 21:30 | 51237.5936 | 79.992
Devonshire Building | 2017-11-07 21:45 | 51237.6336 | 159.984
Devonshire Building | 2017-11-07 22:00 | 51237.6486 | 60.012
Devonshire Building | 2017-11-07 22:15 | 51237.6586 | 39.996
Devonshire Building | 2017-11-07 22:30 | 51237.6736 | 60.012
Devonshire Building | 2017-11-07 22:45 | 51238.2036 | 2120.004
Devonshire Building | 2017-11-07 23:00 | 51238.2136 | 39.996
Devonshire Building | 2017-11-07 23:15 | 51238.2236 | 39.996
Devonshire Building | 2017-11-07 23:30 | 51238.2336 | 39.996
Devonshire Building | 2017-11-07 23:45 | 51238.2436 | 39.996
Devonshire Building | 2017-11-08 | 51238.2539 | 39.996
Devonshire Building | 2017-11-08 00:15 | 51238.2639 | 39.996
Devonshire Building | 2017-11-08 00:30 | 51238.2739 | 39.996
Devonshire Building | 2017-11-08 00:45 | 51238.2839 | 39.996
Devonshire Building | 2017-11-08 01:00 | 51238.2939 | 39.996
Devonshire Building | 2017-11-08 01:15 | 51238.3039 | 39.996
Devonshire Building | 2017-11-08 01:30 | 51238.3139 | 39.996
Devonshire Building | 2017-11-08 01:45 | 51238.3239 | 39.996
Devonshire Building | 2017-11-08 02:00 | 51238.3389 | 60.012
Devonshire Building | 2017-11-08 02:15 | 51238.3489 | 39.996
Devonshire Building | 2017-11-08 02:30 | 51238.3589 | 39.996
Devonshire Building | 2017-11-08 02:45 | 51238.3689 | 39.996
Devonshire Building | 2017-11-08 03:00 | 51238.3839 | 60.012
Devonshire Building | 2017-11-08 03:15 | 51238.3939 | 39.996
Devonshire Building | 2017-11-08 03:30 | 51238.4039 | 39.996
Devonshire Building | 2017-11-08 03:45 | 51238.4139 | 39.996
Devonshire Building | 2017-11-08 04:00 | 51238.4239 | 39.996
Devonshire Building | 2017-11-08 04:15 | 51238.4339 | 39.996
Devonshire Building | 2017-11-08 04:30 | 51238.4439 | 39.996
Devonshire Building | 2017-11-08 04:45 | 51238.4539 | 39.996
Devonshire Building | 2017-11-08 05:00 | 51238.4639 | 39.996
Devonshire Building | 2017-11-08 05:15 | 51238.4739 | 39.996
Devonshire Building | 2017-11-08 05:30 | 51238.4839 | 39.996
Devonshire Building | 2017-11-08 05:45 | 51238.4939 | 39.996
Devonshire Building | 2017-11-08 06:00 | 51238.5039 | 39.996
Devonshire Building | 2017-11-08 06:15 | 51238.5139 | 39.996
Devonshire Building | 2017-11-08 06:30 | 51238.5239 | 39.996
Devonshire Building | 2017-11-08 06:45 | 51238.5339 | 39.996
Devonshire Building | 2017-11-08 07:00 | 51238.5439 | 39.996
Devonshire Building | 2017-11-08 07:15 | 51238.5589 | 60.012
Devonshire Building | 2017-11-08 07:30 | 51239.0939 | 2139.984
Devonshire Building | 2017-11-08 07:45 | 51239.1089 | 60.012
Devonshire Building | 2017-11-08 08:00 | 51239.1239 | 60.012
Devonshire Building | 2017-11-08 08:15 | 51239.1389 | 60.012
Devonshire Building | 2017-11-08 08:30 | 51239.1639 | 100.008
Devonshire Building | 2017-11-08 08:45 | 51239.1989 | 140.004
Devonshire Building | 2017-11-08 09:00 | 51239.2239 | 100.008
Devonshire Building | 2017-11-08 09:15 | 51239.2639 | 159.984
Devonshire Building | 2017-11-08 09:30 | 51239.2989 | 140.004
Devonshire Building | 2017-11-08 09:45 | 51239.3389 | 159.984
Devonshire Building | 2017-11-08 10:00 | 51239.3789 | 159.984
Devonshire Building | 2017-11-08 10:15 | 51239.9589 | 2319.984
Devonshire Building | 2017-11-08 10:30 | 51240.0089 | 200.016
Devonshire Building | 2017-11-08 10:45 | 51240.0539 | 180
Devonshire Building | 2017-11-08 11:00 | 51240.1189 | 259.992
Devonshire Building | 2017-11-08 11:15 | 51240.1789 | 240.012
Devonshire Building | 2017-11-08 11:30 | 51240.2439 | 259.992
Devonshire Building | 2017-11-08 11:45 | 51241.0789 | 3340.008
Devonshire Building | 2017-11-08 12:00 | 51242.4289 | 5400
Devonshire Building | 2017-11-08 12:15 | 51242.9889 | 2239.992
Devonshire Building | 2017-11-08 12:30 | 51243.0539 | 259.992
Devonshire Building | 2017-11-08 12:45 | 51243.3589 | 1220.004
Devonshire Building | 2017-11-08 13:00 | 51243.9839 | 2499.984
Devonshire Building | 2017-11-08 13:15 | 51244.1539 | 680.004
Devonshire Building | 2017-11-08 13:30 | 51244.3139 | 640.008
Devonshire Building | 2017-11-08 13:45 | 51244.4489 | 540
Devonshire Building | 2017-11-08 14:00 | 51244.5639 | 460.008
Devonshire Building | 2017-11-08 14:15 | 51245.1089 | 2180.016
Devonshire Building | 2017-11-08 14:30 | 51245.2289 | 479.988
Devonshire Building | 2017-11-08 14:45 | 51245.2889 | 240.012
Devonshire Building | 2017-11-08 15:00 | 51245.3539 | 259.992
Devonshire Building | 2017-11-08 15:15 | 51245.4089 | 219.996
Devonshire Building | 2017-11-08 15:30 | 51245.4689 | 240.012
Devonshire Building | 2017-11-08 15:45 | 51245.5089 | 159.984
Devonshire Building | 2017-11-08 16:00 | 51245.5539 | 180
Devonshire Building | 2017-11-08 16:15 | 51246.1389 | 2340
Devonshire Building | 2017-11-08 16:30 | 51246.1739 | 140.004
Devonshire Building | 2017-11-08 16:45 | 51246.2089 | 140.004
Devonshire Building | 2017-11-08 17:00 | 51246.2489 | 159.984
Devonshire Building | 2017-11-08 17:15 | 51246.2939 | 180
Devonshire Building | 2017-11-08 17:30 | 51246.3289 | 140.004
Devonshire Building | 2017-11-08 17:45 | 51246.3689 | 159.984
Devonshire Building | 2017-11-08 18:00 | 51246.4039 | 140.004
Devonshire Building | 2017-11-08 18:15 | 51246.4389 | 140.004
Devonshire Building | 2017-11-08 18:30 | 51246.4739 | 140.004
Devonshire Building | 2017-11-08 18:45 | 51247.0089 | 2139.984
Devonshire Building | 2017-11-08 19:00 | 51247.0289 | 79.992
Devonshire Building | 2017-11-08 19:15 | 51247.0489 | 79.992
Devonshire Building | 2017-11-08 19:30 | 51247.0639 | 60.012
Devonshire Building | 2017-11-08 19:45 | 51247.0839 | 79.992
Devonshire Building | 2017-11-08 20:00 | 51247.0989 | 60.012
Devonshire Building | 2017-11-08 20:15 | 51247.1189 | 79.992
Devonshire Building | 2017-11-08 20:30 | 51247.1389 | 79.992
Devonshire Building | 2017-11-08 20:45 | 51247.1589 | 79.992
Devonshire Building | 2017-11-08 21:00 | 51247.1789 | 79.992
Devonshire Building | 2017-11-08 21:15 | 51247.1989 | 79.992
Devonshire Building | 2017-11-08 21:30 | 51247.2189 | 79.992
Devonshire Building | 2017-11-08 21:45 | 51247.2439 | 100.008
Devonshire Building | 2017-11-08 22:00 | 51247.2639 | 79.992
Devonshire Building | 2017-11-08 22:15 | 51247.2789 | 60.012
Devonshire Building | 2017-11-08 22:30 | 51247.2989 | 79.992
Devonshire Building | 2017-11-08 22:45 | 51247.3139 | 60.012
Devonshire Building | 2017-11-08 23:00 | 51247.3339 | 79.992
Devonshire Building | 2017-11-08 23:15 | 51247.3489 | 60.012
Devonshire Building | 2017-11-08 23:30 | 51247.3639 | 60.012
Devonshire Building | 2017-11-08 23:45 | 51247.3839 | 79.992
Devonshire Building | 2017-11-09 | 51247.3984 | 60.012
Devonshire Building | 2017-11-09 00:15 | 51247.4134 | 60.012
Devonshire Building | 2017-11-09 00:30 | 51247.4284 | 60.012
Devonshire Building | 2017-11-09 00:45 | 51247.4484 | 79.992
Devonshire Building | 2017-11-09 01:00 | 51247.4634 | 60.012
Devonshire Building | 2017-11-09 01:15 | 51247.4785 | 60.012
Devonshire Building | 2017-11-09 01:30 | 51247.4935 | 60.012
Devonshire Building | 2017-11-09 01:45 | 51247.5085 | 60.012
Devonshire Building | 2017-11-09 02:00 | 51247.5235 | 60.012
Devonshire Building | 2017-11-09 02:15 | 51247.5435 | 79.992
Devonshire Building | 2017-11-09 02:30 | 51247.5585 | 60.012
Devonshire Building | 2017-11-09 02:45 | 51247.5735 | 60.012
Devonshire Building | 2017-11-09 03:00 | 51247.5935 | 79.992
Devonshire Building | 2017-11-09 03:15 | 51247.6135 | 79.992
Devonshire Building | 2017-11-09 03:30 | 51247.6335 | 79.992
Devonshire Building | 2017-11-09 03:45 | 51247.6535 | 79.992
Devonshire Building | 2017-11-09 04:00 | 51247.6835 | 119.988
Devonshire Building | 2017-11-09 04:15 | 51247.7085 | 100.008
Devonshire Building | 2017-11-09 04:30 | 51247.9435 | 939.996
Devonshire Building | 2017-11-09 04:45 | 51248.2735 | 1320.012
Devonshire Building | 2017-11-09 05:00 | 51248.3235 | 200.016
Devonshire Building | 2017-11-09 05:15 | 51248.3785 | 219.996
Devonshire Building | 2017-11-09 05:30 | 51248.4385 | 240.012
Devonshire Building | 2017-11-09 05:45 | 51248.4885 | 200.016
Devonshire Building | 2017-11-09 06:00 | 51248.5385 | 200.016
Devonshire Building | 2017-11-09 06:15 | 51248.5885 | 200.016
Devonshire Building | 2017-11-09 06:30 | 51248.6335 | 180
Devonshire Building | 2017-11-09 06:45 | 51248.6735 | 159.984
Devonshire Building | 2017-11-09 07:00 | 51248.7185 | 180
Devonshire Building | 2017-11-09 07:15 | 51248.7785 | 240.012
Devonshire Building | 2017-11-09 07:30 | 51248.8335 | 219.996
Devonshire Building | 2017-11-09 07:45 | 51248.8935 | 240.012
Devonshire Building | 2017-11-09 08:00 | 51248.9485 | 219.996
Devonshire Building | 2017-11-09 08:15 | 51249.0085 | 240.012
Devonshire Building | 2017-11-09 08:30 | 51249.0635 | 219.996
Devonshire Building | 2017-11-09 08:45 | 51249.1285 | 259.992
Devonshire Building | 2017-11-09 09:00 | 51249.6935 | 2260.008
Devonshire Building | 2017-11-09 09:15 | 51249.7485 | 219.996
Devonshire Building | 2017-11-09 09:30 | 51249.8085 | 240.012
Devonshire Building | 2017-11-09 09:45 | 51249.8685 | 240.012
Devonshire Building | 2017-11-09 10:00 | 51249.9435 | 299.988
Devonshire Building | 2017-11-09 10:15 | 51250.0485 | 420.012
Devonshire Building | 2017-11-09 10:30 | 51250.6685 | 2480.004
Devonshire Building | 2017-11-09 10:45 | 51250.7785 | 439.992
Devonshire Building | 2017-11-09 11:00 | 51250.8785 | 399.996
Devonshire Building | 2017-11-09 11:15 | 51250.9785 | 399.996
Devonshire Building | 2017-11-09 11:30 | 51251.0835 | 420.012
Devonshire Building | 2017-11-09 11:45 | 51251.1835 | 399.996
Devonshire Building | 2017-11-09 12:00 | 51251.8035 | 2480.004
Devonshire Building | 2017-11-09 12:15 | 51251.9035 | 399.996
Devonshire Building | 2017-11-09 12:30 | 51252.0035 | 399.996
Devonshire Building | 2017-11-09 12:45 | 51252.1035 | 399.996
Devonshire Building | 2017-11-09 13:00 | 51252.2035 | 399.996
Devonshire Building | 2017-11-09 13:15 | 51252.8085 | 2419.992
Devonshire Building | 2017-11-09 13:30 | 51252.8885 | 320.004
Devonshire Building | 2017-11-09 13:45 | 51252.9885 | 399.996
Devonshire Building | 2017-11-09 14:00 | 51253.0785 | 360
Devonshire Building | 2017-11-09 14:15 | 51253.1685 | 360
Devonshire Building | 2017-11-09 14:30 | 51253.2535 | 339.984
Devonshire Building | 2017-11-09 14:45 | 51253.3885 | 540
Devonshire Building | 2017-11-09 15:00 | 51253.9385 | 2199.996
Devonshire Building | 2017-11-09 15:15 | 51254.0135 | 299.988
Devonshire Building | 2017-11-09 15:30 | 51254.0985 | 339.984
Devonshire Building | 2017-11-09 15:45 | 51254.1985 | 399.996
Devonshire Building | 2017-11-09 16:00 | 51254.3435 | 579.996
Devonshire Building | 2017-11-09 16:15 | 51254.6185 | 1100.016
Devonshire Building | 2017-11-09 16:30 | 51255.3735 | 3020.004
Devonshire Building | 2017-11-09 16:45 | 51255.5585 | 740.016
Devonshire Building | 2017-11-09 17:00 | 51255.7135 | 619.992
Devonshire Building | 2017-11-09 17:15 | 51255.8685 | 619.992
Devonshire Building | 2017-11-09 17:30 | 51256.0085 | 560.016
Devonshire Building | 2017-11-09 17:45 | 51256.1235 | 460.008
Devonshire Building | 2017-11-09 18:00 | 51256.2185 | 380.016
Devonshire Building | 2017-11-09 18:15 | 51256.3085 | 360
Devonshire Building | 2017-11-09 18:30 | 51256.8835 | 2300.004
Devonshire Building | 2017-11-09 18:45 | 51256.9385 | 219.996
Devonshire Building | 2017-11-09 19:00 | 51257.0085 | 280.008
Devonshire Building | 2017-11-09 19:15 | 51257.0835 | 299.988
Devonshire Building | 2017-11-09 19:30 | 51257.1585 | 299.988
Devonshire Building | 2017-11-09 19:45 | 51257.2285 | 280.008
Devonshire Building | 2017-11-09 20:00 | 51257.2985 | 280.008
Devonshire Building | 2017-11-09 20:15 | 51257.3735 | 299.988
Devonshire Building | 2017-11-09 20:30 | 51257.4435 | 280.008
Devonshire Building | 2017-11-09 20:45 | 51257.5185 | 299.988
Devonshire Building | 2017-11-09 21:00 | 51257.5935 | 299.988
Devonshire Building | 2017-11-09 21:15 | 51257.6685 | 299.988
Devonshire Building | 2017-11-09 21:30 | 51257.7485 | 320.004
Devonshire Building | 2017-11-09 21:45 | 51257.8335 | 339.984
Devonshire Building | 2017-11-09 22:00 | 51257.9135 | 320.004
Devonshire Building | 2017-11-09 22:15 | 51257.9835 | 280.008
Devonshire Building | 2017-11-09 22:30 | 51258.0485 | 259.992
Devonshire Building | 2017-11-09 22:45 | 51258.1185 | 280.008
Devonshire Building | 2017-11-09 23:00 | 51258.1835 | 259.992
Devonshire Building | 2017-11-09 23:15 | 51258.2535 | 280.008
Devonshire Building | 2017-11-09 23:30 | 51258.3185 | 259.992
Devonshire Building | 2017-11-09 23:45 | 51258.3835 | 259.992
Devonshire Building | 2017-11-10 | 51258.4492 | 259.992
Devonshire Building | 2017-11-10 00:15 | 51258.5142 | 259.992
Devonshire Building | 2017-11-10 00:30 | 51258.5792 | 259.992
Devonshire Building | 2017-11-10 00:45 | 51258.6442 | 259.992
Devonshire Building | 2017-11-10 01:00 | 51258.7042 | 240.012
Devonshire Building | 2017-11-10 01:15 | 51258.7692 | 259.992
Devonshire Building | 2017-11-10 01:30 | 51258.8292 | 240.012
Devonshire Building | 2017-11-10 01:45 | 51258.8892 | 240.012
Devonshire Building | 2017-11-10 02:00 | 51258.9492 | 240.012
Devonshire Building | 2017-11-10 02:15 | 51259.0092 | 240.012
Devonshire Building | 2017-11-10 02:30 | 51259.0692 | 240.012
Devonshire Building | 2017-11-10 02:45 | 51259.1292 | 240.012
Devonshire Building | 2017-11-10 03:00 | 51259.1842 | 219.996
Devonshire Building | 2017-11-10 03:15 | 51259.2442 | 240.012
Devonshire Building | 2017-11-10 03:30 | 51259.2992 | 219.996
Devonshire Building | 2017-11-10 03:45 | 51259.3542 | 219.996
Devonshire Building | 2017-11-10 04:00 | 51259.5092 | 619.992
Devonshire Building | 2017-11-10 04:15 | 51259.9442 | 1739.988
Devonshire Building | 2017-11-10 04:30 | 51259.9842 | 159.984
Devonshire Building | 2017-11-10 04:45 | 51260.0192 | 140.004
Devonshire Building | 2017-11-10 05:00 | 51260.0592 | 159.984
Devonshire Building | 2017-11-10 05:15 | 51260.0992 | 159.984
Devonshire Building | 2017-11-10 05:30 | 51260.1392 | 159.984
Devonshire Building | 2017-11-10 05:45 | 51260.1792 | 159.984
Devonshire Building | 2017-11-10 06:00 | 51260.2192 | 159.984
Devonshire Building | 2017-11-10 06:15 | 51260.2592 | 159.984
Devonshire Building | 2017-11-10 06:30 | 51260.3042 | 180
Devonshire Building | 2017-11-10 06:45 | 51260.3492 | 180
Devonshire Building | 2017-11-10 07:00 | 51260.3992 | 200.016
Devonshire Building | 2017-11-10 07:15 | 51260.4592 | 240.012
Devonshire Building | 2017-11-10 07:30 | 51260.5342 | 299.988
Devonshire Building | 2017-11-10 07:45 | 51260.6392 | 420.012
Devonshire Building | 2017-11-10 08:00 | 51260.7442 | 420.012
Devonshire Building | 2017-11-10 08:15 | 51260.8392 | 380.016
Devonshire Building | 2017-11-10 08:30 | 51260.9292 | 360
Devonshire Building | 2017-11-10 08:45 | 51261.0192 | 360
Devonshire Building | 2017-11-10 09:00 | 51261.1042 | 339.984
Devonshire Building | 2017-11-10 09:15 | 51261.7092 | 2419.992
Devonshire Building | 2017-11-10 09:30 | 51261.7792 | 280.008
Devonshire Building | 2017-11-10 09:45 | 51261.8492 | 280.008
Devonshire Building | 2017-11-10 10:00 | 51261.9192 | 280.008
Devonshire Building | 2017-11-10 10:15 | 51261.9842 | 259.992
Devonshire Building | 2017-11-10 10:30 | 51262.0542 | 280.008
Devonshire Building | 2017-11-10 10:45 | 51262.6642 | 2440.008
Devonshire Building | 2017-11-10 11:00 | 51262.7842 | 479.988
Devonshire Building | 2017-11-10 11:15 | 51262.8942 | 439.992
Devonshire Building | 2017-11-10 11:30 | 51262.9942 | 399.996
Devonshire Building | 2017-11-10 11:45 | 51263.0942 | 399.996
Devonshire Building | 2017-11-10 12:00 | 51263.1842 | 360
Devonshire Building | 2017-11-10 12:15 | 51263.2742 | 360
Devonshire Building | 2017-11-10 12:30 | 51263.8942 | 2480.004
Devonshire Building | 2017-11-10 12:45 | 51263.9692 | 299.988
Devonshire Building | 2017-11-10 13:00 | 51264.0492 | 320.004
Devonshire Building | 2017-11-10 13:15 | 51264.1242 | 299.988
Devonshire Building | 2017-11-10 13:30 | 51264.1892 | 259.992
Devonshire Building | 2017-11-10 13:45 | 51264.3642 | 699.984
Devonshire Building | 2017-11-10 14:00 | 51264.8692 | 2019.996
Devonshire Building | 2017-11-10 14:15 | 51264.9542 | 339.984
Devonshire Building | 2017-11-10 14:30 | 51265.0492 | 380.016
Devonshire Building | 2017-11-10 14:45 | 51265.1492 | 399.996
Devonshire Building | 2017-11-10 15:00 | 51265.2392 | 360
Devonshire Building | 2017-11-10 15:15 | 51265.3292 | 360
Devonshire Building | 2017-11-10 15:30 | 51265.5492 | 879.984
Devonshire Building | 2017-11-10 15:45 | 51266.0042 | 1820.016
Devonshire Building | 2017-11-10 16:00 | 51266.0692 | 259.992
Devonshire Building | 2017-11-10 16:15 | 51266.1442 | 299.988
Devonshire Building | 2017-11-10 16:30 | 51266.1992 | 219.996
Devonshire Building | 2017-11-10 16:45 | 51266.2492 | 200.016
Devonshire Building | 2017-11-10 17:00 | 51266.6992 | 1800
Devonshire Building | 2017-11-10 17:15 | 51266.8692 | 680.004
Devonshire Building | 2017-11-10 17:30 | 51266.9092 | 159.984
Devonshire Building | 2017-11-10 17:45 | 51266.9542 | 180
Devonshire Building | 2017-11-10 18:00 | 51266.9992 | 180
Devonshire Building | 2017-11-10 18:15 | 51267.0392 | 159.984
Devonshire Building | 2017-11-10 18:30 | 51267.0842 | 180
Devonshire Building | 2017-11-10 18:45 | 51267.1292 | 180
Devonshire Building | 2017-11-10 19:00 | 51267.1692 | 159.984
Devonshire Building | 2017-11-10 19:15 | 51267.2092 | 159.984
Devonshire Building | 2017-11-10 19:30 | 51267.2492 | 159.984
Devonshire Building | 2017-11-10 19:45 | 51267.2892 | 159.984
Devonshire Building | 2017-11-10 20:00 | 51267.3292 | 159.984
Devonshire Building | 2017-11-10 20:15 | 51267.3642 | 140.004
Devonshire Building | 2017-11-10 20:30 | 51267.4042 | 159.984
Devonshire Building | 2017-11-10 20:45 | 51267.4392 | 140.004
Devonshire Building | 2017-11-10 21:00 | 51267.4792 | 159.984
Devonshire Building | 2017-11-10 21:15 | 51267.5142 | 140.004
Devonshire Building | 2017-11-10 21:30 | 51267.5542 | 159.984
Devonshire Building | 2017-11-10 21:45 | 51267.6042 | 200.016
Devonshire Building | 2017-11-10 22:00 | 51267.6342 | 119.988
Devonshire Building | 2017-11-10 22:15 | 51267.6642 | 119.988
Devonshire Building | 2017-11-10 22:30 | 51267.8192 | 619.992
Devonshire Building | 2017-11-10 22:45 | 51268.2092 | 1559.988
Devonshire Building | 2017-11-10 23:00 | 51268.2342 | 100.008
Devonshire Building | 2017-11-10 23:15 | 51268.2542 | 79.992
Devonshire Building | 2017-11-10 23:30 | 51268.2742 | 79.992
Devonshire Building | 2017-11-10 23:45 | 51268.2992 | 100.008
Devonshire Building | 2017-11-11 | 51268.3242 | 100.008
Devonshire Building | 2017-11-11 00:15 | 51268.3492 | 100.008
Devonshire Building | 2017-11-11 00:30 | 51268.3742 | 100.008
Devonshire Building | 2017-11-11 00:45 | 51268.3992 | 100.008
Devonshire Building | 2017-11-11 01:00 | 51268.4192 | 79.992
Devonshire Building | 2017-11-11 01:15 | 51268.4442 | 100.008
Devonshire Building | 2017-11-11 01:30 | 51268.4642 | 79.992
Devonshire Building | 2017-11-11 01:45 | 51268.4892 | 100.008
Devonshire Building | 2017-11-11 02:00 | 51268.5292 | 159.984
Devonshire Building | 2017-11-11 02:15 | 51268.5642 | 140.004
Devonshire Building | 2017-11-11 02:30 | 51268.5992 | 140.004
Devonshire Building | 2017-11-11 02:45 | 51268.6342 | 140.004
Devonshire Building | 2017-11-11 03:00 | 51268.6692 | 140.004
Devonshire Building | 2017-11-11 03:15 | 51268.7042 | 140.004
Devonshire Building | 2017-11-11 03:30 | 51268.7392 | 140.004
Devonshire Building | 2017-11-11 03:45 | 51268.7742 | 140.004
Devonshire Building | 2017-11-11 04:00 | 51268.8092 | 140.004
Devonshire Building | 2017-11-11 04:15 | 51268.8342 | 100.008
Devonshire Building | 2017-11-11 04:30 | 51268.8542 | 79.992
Devonshire Building | 2017-11-11 04:45 | 51268.8742 | 79.992
Devonshire Building | 2017-11-11 05:00 | 51268.8942 | 79.992
Devonshire Building | 2017-11-11 05:15 | 51268.9142 | 79.992
Devonshire Building | 2017-11-11 05:30 | 51268.9292 | 60.012
Devonshire Building | 2017-11-11 05:45 | 51268.9492 | 79.992
Devonshire Building | 2017-11-11 06:00 | 51268.9692 | 79.992
Devonshire Building | 2017-11-11 06:15 | 51268.9892 | 79.992
Devonshire Building | 2017-11-11 06:30 | 51269.0092 | 79.992
Devonshire Building | 2017-11-11 06:45 | 51269.0292 | 79.992
Devonshire Building | 2017-11-11 07:00 | 51269.0442 | 60.012
Devonshire Building | 2017-11-11 07:15 | 51269.0642 | 79.992
Devonshire Building | 2017-11-11 07:30 | 51269.0842 | 79.992
Devonshire Building | 2017-11-11 07:45 | 51269.1042 | 79.992
Devonshire Building | 2017-11-11 08:00 | 51269.1242 | 79.992
Devonshire Building | 2017-11-11 08:15 | 51269.6542 | 2120.004
Devonshire Building | 2017-11-11 08:30 | 51269.6692 | 60.012
Devonshire Building | 2017-11-11 08:45 | 51269.6842 | 60.012
Devonshire Building | 2017-11-11 09:00 | 51269.6992 | 60.012
Devonshire Building | 2017-11-11 09:15 | 51269.7142 | 60.012
Devonshire Building | 2017-11-11 09:30 | 51269.7292 | 60.012
Devonshire Building | 2017-11-11 09:45 | 51269.7442 | 60.012
Devonshire Building | 2017-11-11 10:00 | 51269.7642 | 79.992
Devonshire Building | 2017-11-11 10:15 | 51269.7842 | 79.992
Devonshire Building | 2017-11-11 10:30 | 51269.7992 | 60.012
Devonshire Building | 2017-11-11 10:45 | 51269.8192 | 79.992
Devonshire Building | 2017-11-11 11:00 | 51269.8392 | 79.992
Devonshire Building | 2017-11-11 11:15 | 51269.8542 | 60.012
Devonshire Building | 2017-11-11 11:30 | 51269.8742 | 79.992
Devonshire Building | 2017-11-11 11:45 | 51269.8892 | 60.012
Devonshire Building | 2017-11-11 12:00 | 51269.9092 | 79.992
Devonshire Building | 2017-11-11 12:15 | 51269.9242 | 60.012
Devonshire Building | 2017-11-11 12:30 | 51269.9442 | 79.992
Devonshire Building | 2017-11-11 12:45 | 51269.9592 | 60.012
Devonshire Building | 2017-11-11 13:00 | 51269.9792 | 79.992
Devonshire Building | 2017-11-11 13:15 | 51269.9942 | 60.012
Devonshire Building | 2017-11-11 13:30 | 51270.0092 | 60.012
Devonshire Building | 2017-11-11 13:45 | 51270.0242 | 60.012
Devonshire Building | 2017-11-11 14:00 | 51270.0442 | 79.992
Devonshire Building | 2017-11-11 14:15 | 51270.0642 | 79.992
Devonshire Building | 2017-11-11 14:30 | 51270.0792 | 60.012
Devonshire Building | 2017-11-11 14:45 | 51270.1042 | 100.008
Devonshire Building | 2017-11-11 15:00 | 51270.1342 | 119.988
Devonshire Building | 2017-11-11 15:15 | 51270.1692 | 140.004
Devonshire Building | 2017-11-11 15:30 | 51270.1992 | 119.988
Devonshire Building | 2017-11-11 15:45 | 51270.2292 | 119.988
Devonshire Building | 2017-11-11 16:00 | 51270.2592 | 119.988
Devonshire Building | 2017-11-11 16:15 | 51270.2892 | 119.988
Devonshire Building | 2017-11-11 16:30 | 51270.3192 | 119.988
Devonshire Building | 2017-11-11 16:45 | 51270.8592 | 2160
Devonshire Building | 2017-11-11 17:00 | 51270.8942 | 140.004
Devonshire Building | 2017-11-11 17:15 | 51270.9292 | 140.004
Devonshire Building | 2017-11-11 17:30 | 51270.9642 | 140.004
Devonshire Building | 2017-11-11 17:45 | 51270.9892 | 100.008
Devonshire Building | 2017-11-11 18:00 | 51271.0092 | 79.992
Devonshire Building | 2017-11-11 18:15 | 51271.0342 | 100.008
Devonshire Building | 2017-11-11 18:30 | 51271.0592 | 100.008
Devonshire Building | 2017-11-11 18:45 | 51271.0842 | 100.008
Devonshire Building | 2017-11-11 19:00 | 51271.1042 | 79.992
Devonshire Building | 2017-11-11 19:15 | 51271.1292 | 100.008
Devonshire Building | 2017-11-11 19:30 | 51271.1492 | 79.992
Devonshire Building | 2017-11-11 19:45 | 51271.1742 | 100.008
Devonshire Building | 2017-11-11 20:00 | 51271.1942 | 79.992
Devonshire Building | 2017-11-11 20:15 | 51271.2142 | 79.992
Devonshire Building | 2017-11-11 20:30 | 51271.2392 | 100.008
Devonshire Building | 2017-11-11 20:45 | 51271.2592 | 79.992
Devonshire Building | 2017-11-11 21:00 | 51271.2792 | 79.992
Devonshire Building | 2017-11-11 21:15 | 51271.2992 | 79.992
Devonshire Building | 2017-11-11 21:30 | 51271.3242 | 100.008
Devonshire Building | 2017-11-11 21:45 | 51271.3642 | 159.984
Devonshire Building | 2017-11-11 22:00 | 51271.3842 | 79.992
Devonshire Building | 2017-11-11 22:15 | 51271.4042 | 79.992
Devonshire Building | 2017-11-11 22:30 | 51271.4242 | 79.992
Devonshire Building | 2017-11-11 22:45 | 51271.4442 | 79.992
Devonshire Building | 2017-11-11 23:00 | 51271.4642 | 79.992
Devonshire Building | 2017-11-11 23:15 | 51271.4842 | 79.992
Devonshire Building | 2017-11-11 23:30 | 51271.5042 | 79.992
Devonshire Building | 2017-11-11 23:45 | 51271.5242 | 79.992
Devonshire Building | 2017-11-12 | 51271.5469 | 79.992
Devonshire Building | 2017-11-12 00:15 | 51271.5669 | 79.992
Devonshire Building | 2017-11-12 00:30 | 51271.5819 | 60.012
Devonshire Building | 2017-11-12 00:45 | 51271.6019 | 79.992
Devonshire Building | 2017-11-12 01:00 | 51271.6219 | 79.992
Devonshire Building | 2017-11-12 01:15 | 51271.6419 | 79.992
Devonshire Building | 2017-11-12 01:30 | 51271.6619 | 79.992
Devonshire Building | 2017-11-12 01:45 | 51271.6819 | 79.992
Devonshire Building | 2017-11-12 02:00 | 51272.2019 | 2080.008
Devonshire Building | 2017-11-12 02:15 | 51272.2169 | 60.012
Devonshire Building | 2017-11-12 02:30 | 51272.2369 | 79.992
Devonshire Building | 2017-11-12 02:45 | 51272.2569 | 79.992
Devonshire Building | 2017-11-12 03:00 | 51272.2719 | 60.012
Devonshire Building | 2017-11-12 03:15 | 51272.2919 | 79.992
Devonshire Building | 2017-11-12 03:30 | 51272.3119 | 79.992
Devonshire Building | 2017-11-12 03:45 | 51272.3369 | 100.008
Devonshire Building | 2017-11-12 04:00 | 51272.3619 | 100.008
Devonshire Building | 2017-11-12 04:15 | 51272.3819 | 79.992
Devonshire Building | 2017-11-12 04:30 | 51272.4019 | 79.992
Devonshire Building | 2017-11-12 04:45 | 51272.4219 | 79.992
Devonshire Building | 2017-11-12 05:00 | 51272.4419 | 79.992
Devonshire Building | 2017-11-12 05:15 | 51272.4669 | 100.008
Devonshire Building | 2017-11-12 05:30 | 51272.4869 | 79.992
Devonshire Building | 2017-11-12 05:45 | 51272.5069 | 79.992
Devonshire Building | 2017-11-12 06:00 | 51272.5269 | 79.992
Devonshire Building | 2017-11-12 06:15 | 51272.5469 | 79.992
Devonshire Building | 2017-11-12 06:30 | 51272.5619 | 60.012
Devonshire Building | 2017-11-12 06:45 | 51272.5819 | 79.992
Devonshire Building | 2017-11-12 07:00 | 51272.6019 | 79.992
Devonshire Building | 2017-11-12 07:15 | 51272.6169 | 60.012
Devonshire Building | 2017-11-12 07:30 | 51272.6369 | 79.992
Devonshire Building | 2017-11-12 07:45 | 51272.6569 | 79.992
Devonshire Building | 2017-11-12 08:00 | 51272.6719 | 60.012
Devonshire Building | 2017-11-12 08:15 | 51272.6919 | 79.992
Devonshire Building | 2017-11-12 08:30 | 51272.7069 | 60.012
Devonshire Building | 2017-11-12 08:45 | 51272.7269 | 79.992
Devonshire Building | 2017-11-12 09:00 | 51272.7419 | 60.012
Devonshire Building | 2017-11-12 09:15 | 51272.7569 | 60.012
Devonshire Building | 2017-11-12 09:30 | 51272.7769 | 79.992
Devonshire Building | 2017-11-12 09:45 | 51272.7919 | 60.012
Devonshire Building | 2017-11-12 10:00 | 51272.8119 | 79.992
Devonshire Building | 2017-11-12 10:15 | 51272.8269 | 60.012
Devonshire Building | 2017-11-12 10:30 | 51272.8469 | 79.992
Devonshire Building | 2017-11-12 10:45 | 51272.8669 | 79.992
Devonshire Building | 2017-11-12 11:00 | 51272.8819 | 60.012
Devonshire Building | 2017-11-12 11:15 | 51272.8969 | 60.012
Devonshire Building | 2017-11-12 11:30 | 51273.4219 | 2099.988
Devonshire Building | 2017-11-12 11:45 | 51273.4369 | 60.012
Devonshire Building | 2017-11-12 12:00 | 51273.4569 | 79.992
Devonshire Building | 2017-11-12 12:15 | 51273.4669 | 39.996
Devonshire Building | 2017-11-12 12:30 | 51273.4819 | 60.012
Devonshire Building | 2017-11-12 12:45 | 51273.4969 | 60.012
Devonshire Building | 2017-11-12 13:00 | 51273.5169 | 79.992
Devonshire Building | 2017-11-12 13:15 | 51273.5369 | 79.992
Devonshire Building | 2017-11-12 13:30 | 51273.5519 | 60.012
Devonshire Building | 2017-11-12 13:45 | 51273.5869 | 140.004
Devonshire Building | 2017-11-12 14:00 | 51273.6219 | 140.004
Devonshire Building | 2017-11-12 14:15 | 51273.6569 | 140.004
Devonshire Building | 2017-11-12 14:30 | 51273.6869 | 119.988
Devonshire Building | 2017-11-12 14:45 | 51273.7219 | 140.004
Devonshire Building | 2017-11-12 15:00 | 51273.7569 | 140.004
Devonshire Building | 2017-11-12 15:15 | 51273.7869 | 119.988
Devonshire Building | 2017-11-12 15:30 | 51273.8219 | 140.004
Devonshire Building | 2017-11-12 15:45 | 51273.8569 | 140.004
Devonshire Building | 2017-11-12 16:00 | 51273.8869 | 119.988
Devonshire Building | 2017-11-12 16:15 | 51273.9219 | 140.004
Devonshire Building | 2017-11-12 16:30 | 51273.9519 | 119.988
Devonshire Building | 2017-11-12 16:45 | 51273.9819 | 119.988
Devonshire Building | 2017-11-12 17:00 | 51274.0169 | 140.004
Devonshire Building | 2017-11-12 17:15 | 51274.0319 | 60.012
Devonshire Building | 2017-11-12 17:30 | 51274.0519 | 79.992
Devonshire Building | 2017-11-12 17:45 | 51274.0669 | 60.012
Devonshire Building | 2017-11-12 18:00 | 51274.0819 | 60.012
Devonshire Building | 2017-11-12 18:15 | 51274.1019 | 79.992
Devonshire Building | 2017-11-12 18:30 | 51274.1169 | 60.012
Devonshire Building | 2017-11-12 18:45 | 51274.1319 | 60.012
Devonshire Building | 2017-11-12 19:00 | 51274.1519 | 79.992
Devonshire Building | 2017-11-12 19:15 | 51274.1669 | 60.012
Devonshire Building | 2017-11-12 19:30 | 51274.1869 | 79.992
Devonshire Building | 2017-11-12 19:45 | 51274.2019 | 60.012
Devonshire Building | 2017-11-12 20:00 | 51274.7369 | 2139.984
Devonshire Building | 2017-11-12 20:15 | 51274.7619 | 100.008
Devonshire Building | 2017-11-12 20:30 | 51274.7819 | 79.992
Devonshire Building | 2017-11-12 20:45 | 51274.8019 | 79.992
Devonshire Building | 2017-11-12 21:00 | 51274.8269 | 100.008
Devonshire Building | 2017-11-12 21:15 | 51274.8569 | 119.988
Devonshire Building | 2017-11-12 21:30 | 51274.8819 | 100.008
Devonshire Building | 2017-11-12 21:45 | 51274.9119 | 119.988
Devonshire Building | 2017-11-12 22:00 | 51274.9369 | 100.008
Devonshire Building | 2017-11-12 22:15 | 51274.9619 | 100.008
Devonshire Building | 2017-11-12 22:30 | 51274.9869 | 100.008
Devonshire Building | 2017-11-12 22:45 | 51275.0119 | 100.008
Devonshire Building | 2017-11-12 23:00 | 51275.0319 | 79.992
Devonshire Building | 2017-11-12 23:15 | 51275.0569 | 100.008
Devonshire Building | 2017-11-12 23:30 | 51275.0819 | 100.008
Devonshire Building | 2017-11-12 23:45 | 51275.1019 | 79.992
Devonshire Building | 2017-11-13 | 51275.125 | 100.008
Devonshire Building | 2017-11-13 00:15 | 51275.145 | 79.992
Devonshire Building | 2017-11-13 00:30 | 51275.165 | 79.992
Devonshire Building | 2017-11-13 00:45 | 51275.19 | 100.008
Devonshire Building | 2017-11-13 01:00 | 51275.21 | 79.992
Devonshire Building | 2017-11-13 01:15 | 51275.23 | 79.992
Devonshire Building | 2017-11-13 01:30 | 51275.255 | 100.008
Devonshire Building | 2017-11-13 01:45 | 51275.275 | 79.992
Devonshire Building | 2017-11-13 02:00 | 51275.295 | 79.992
Devonshire Building | 2017-11-13 02:15 | 51275.315 | 79.992
Devonshire Building | 2017-11-13 02:30 | 51275.34 | 100.008
Devonshire Building | 2017-11-13 02:45 | 51275.36 | 79.992
Devonshire Building | 2017-11-13 03:00 | 51275.38 | 79.992
Devonshire Building | 2017-11-13 03:15 | 51275.4 | 79.992
Devonshire Building | 2017-11-13 03:30 | 51275.42 | 79.992
Devonshire Building | 2017-11-13 03:45 | 51275.44 | 79.992
Devonshire Building | 2017-11-13 04:00 | 51275.46 | 79.992
Devonshire Building | 2017-11-13 04:15 | 51275.48 | 79.992
Devonshire Building | 2017-11-13 04:30 | 51275.98 | 2000.016
Devonshire Building | 2017-11-13 04:45 | 51276.025 | 180
Devonshire Building | 2017-11-13 05:00 | 51276.045 | 79.992
Devonshire Building | 2017-11-13 05:15 | 51276.06 | 60.012
Devonshire Building | 2017-11-13 05:30 | 51276.08 | 79.992
Devonshire Building | 2017-11-13 05:45 | 51276.095 | 60.012
Devonshire Building | 2017-11-13 06:00 | 51276.115 | 79.992
Devonshire Building | 2017-11-13 06:15 | 51276.135 | 79.992
Devonshire Building | 2017-11-13 06:30 | 51276.155 | 79.992
Devonshire Building | 2017-11-13 06:45 | 51276.18 | 100.008
Devonshire Building | 2017-11-13 07:00 | 51276.2 | 79.992
Devonshire Building | 2017-11-13 07:15 | 51276.22 | 79.992
Devonshire Building | 2017-11-13 07:30 | 51276.24 | 79.992
Devonshire Building | 2017-11-13 07:45 | 51276.26 | 79.992
Devonshire Building | 2017-11-13 08:00 | 51276.28 | 79.992
Devonshire Building | 2017-11-13 08:15 | 51276.3 | 79.992
Devonshire Building | 2017-11-13 08:30 | 51276.325 | 100.008
Devonshire Building | 2017-11-13 08:45 | 51276.355 | 119.988
Devonshire Building | 2017-11-13 09:00 | 51276.91 | 2220.012
Devonshire Building | 2017-11-13 09:15 | 51277 | 360
Devonshire Building | 2017-11-13 09:30 | 51277.04 | 159.984
Devonshire Building | 2017-11-13 09:45 | 51277.095 | 219.996
Devonshire Building | 2017-11-13 10:00 | 51277.155 | 240.012
Devonshire Building | 2017-11-13 10:15 | 51277.715 | 2239.992
Devonshire Building | 2017-11-13 10:30 | 51277.8 | 339.984
Devonshire Building | 2017-11-13 10:45 | 51277.87 | 280.008
Devonshire Building | 2017-11-13 11:00 | 51277.945 | 299.988
Devonshire Building | 2017-11-13 11:15 | 51278.02 | 299.988
Devonshire Building | 2017-11-13 11:30 | 51278.64 | 2480.004
Devonshire Building | 2017-11-13 11:45 | 51278.705 | 259.992
Devonshire Building | 2017-11-13 12:00 | 51278.775 | 280.008
Devonshire Building | 2017-11-13 12:15 | 51278.845 | 280.008
Devonshire Building | 2017-11-13 12:30 | 51278.91 | 259.992
Devonshire Building | 2017-11-13 12:45 | 51279.425 | 2059.992
Devonshire Building | 2017-11-13 13:00 | 51279.59 | 659.988
Devonshire Building | 2017-11-13 13:15 | 51279.725 | 540
Devonshire Building | 2017-11-13 13:30 | 51279.805 | 320.004
Devonshire Building | 2017-11-13 13:45 | 51279.875 | 280.008
Devonshire Building | 2017-11-13 14:00 | 51280.365 | 1959.984
Devonshire Building | 2017-11-13 14:15 | 51280.56 | 780.012
Devonshire Building | 2017-11-13 14:30 | 51280.62 | 240.012
Devonshire Building | 2017-11-13 14:45 | 51280.675 | 219.996
Devonshire Building | 2017-11-13 15:00 | 51280.73 | 219.996
Devonshire Building | 2017-11-13 15:15 | 51280.78 | 200.016
Devonshire Building | 2017-11-13 15:30 | 51281.38 | 2400.012
Devonshire Building | 2017-11-13 15:45 | 51281.44 | 240.012
Devonshire Building | 2017-11-13 16:00 | 51281.495 | 219.996
Devonshire Building | 2017-11-13 16:15 | 51281.55 | 219.996
Devonshire Building | 2017-11-13 16:30 | 51281.6 | 200.016
Devonshire Building | 2017-11-13 16:45 | 51281.65 | 200.016
Devonshire Building | 2017-11-13 17:00 | 51282.23 | 2319.984
Devonshire Building | 2017-11-13 17:15 | 51282.275 | 180
Devonshire Building | 2017-11-13 17:30 | 51282.32 | 180
Devonshire Building | 2017-11-13 17:45 | 51282.37 | 200.016
Devonshire Building | 2017-11-13 18:00 | 51282.415 | 180
Devonshire Building | 2017-11-13 18:15 | 51282.455 | 159.984
Devonshire Building | 2017-11-13 18:30 | 51282.495 | 159.984
Devonshire Building | 2017-11-13 18:45 | 51282.53 | 140.004
Devonshire Building | 2017-11-13 19:00 | 51282.565 | 140.004
Devonshire Building | 2017-11-13 19:15 | 51282.6 | 140.004
Devonshire Building | 2017-11-13 19:30 | 51282.63 | 119.988
Devonshire Building | 2017-11-13 19:45 | 51282.66 | 119.988
Devonshire Building | 2017-11-13 20:00 | 51282.69 | 119.988
Devonshire Building | 2017-11-13 20:15 | 51282.715 | 100.008
Devonshire Building | 2017-11-13 20:30 | 51282.74 | 100.008
Devonshire Building | 2017-11-13 20:45 | 51282.765 | 100.008
Devonshire Building | 2017-11-13 21:00 | 51282.79 | 100.008
Devonshire Building | 2017-11-13 21:15 | 51282.815 | 100.008
Devonshire Building | 2017-11-13 21:30 | 51282.84 | 100.008
Devonshire Building | 2017-11-13 21:45 | 51283.36 | 2080.008
Devonshire Building | 2017-11-13 22:00 | 51283.37 | 39.996
Devonshire Building | 2017-11-13 22:15 | 51283.385 | 60.012
Devonshire Building | 2017-11-13 22:30 | 51283.395 | 39.996
Devonshire Building | 2017-11-13 22:45 | 51283.41 | 60.012
Devonshire Building | 2017-11-13 23:00 | 51283.42 | 39.996
Devonshire Building | 2017-11-13 23:15 | 51283.435 | 60.012
Devonshire Building | 2017-11-13 23:30 | 51283.445 | 39.996
Devonshire Building | 2017-11-13 23:45 | 51283.46 | 60.012
Devonshire Building | 2017-11-14 | 51283.4688 | 39.996
Devonshire Building | 2017-11-14 00:15 | 51283.4838 | 60.012
Devonshire Building | 2017-11-14 00:30 | 51283.4988 | 60.012
Devonshire Building | 2017-11-14 00:45 | 51283.5138 | 60.012
Devonshire Building | 2017-11-14 01:00 | 51283.5288 | 60.012
Devonshire Building | 2017-11-14 01:15 | 51283.5388 | 39.996
Devonshire Building | 2017-11-14 01:30 | 51283.5538 | 60.012
Devonshire Building | 2017-11-14 01:45 | 51283.5688 | 60.012
Devonshire Building | 2017-11-14 02:00 | 51283.5788 | 39.996
Devonshire Building | 2017-11-14 02:15 | 51283.5938 | 60.012
Devonshire Building | 2017-11-14 02:30 | 51283.6088 | 60.012
Devonshire Building | 2017-11-14 02:45 | 51283.6188 | 39.996
Devonshire Building | 2017-11-14 03:00 | 51283.6288 | 39.996
Devonshire Building | 2017-11-14 03:15 | 51283.6438 | 60.012
Devonshire Building | 2017-11-14 03:30 | 51283.6538 | 39.996
Devonshire Building | 2017-11-14 03:45 | 51283.6688 | 60.012
Devonshire Building | 2017-11-14 04:00 | 51283.6788 | 39.996
Devonshire Building | 2017-11-14 04:15 | 51283.6888 | 39.996
Devonshire Building | 2017-11-14 04:30 | 51283.7038 | 60.012
Devonshire Building | 2017-11-14 04:45 | 51283.7138 | 39.996
Devonshire Building | 2017-11-14 05:00 | 51283.7288 | 60.012
Devonshire Building | 2017-11-14 05:15 | 51283.7388 | 39.996
Devonshire Building | 2017-11-14 05:30 | 51283.7538 | 60.012
Devonshire Building | 2017-11-14 05:45 | 51283.7638 | 39.996
Devonshire Building | 2017-11-14 06:00 | 51283.7788 | 60.012
Devonshire Building | 2017-11-14 06:15 | 51283.7938 | 60.012
Devonshire Building | 2017-11-14 06:30 | 51283.8038 | 39.996
Devonshire Building | 2017-11-14 06:45 | 51283.8188 | 60.012
Devonshire Building | 2017-11-14 07:00 | 51283.8338 | 60.012
Devonshire Building | 2017-11-14 07:15 | 51283.9438 | 439.992
Devonshire Building | 2017-11-14 07:30 | 51284.3788 | 1739.988
Devonshire Building | 2017-11-14 07:45 | 51284.3988 | 79.992
Devonshire Building | 2017-11-14 08:00 | 51284.4288 | 119.988
Devonshire Building | 2017-11-14 08:15 | 51284.4838 | 219.996
Devonshire Building | 2017-11-14 08:30 | 51284.5538 | 280.008
Devonshire Building | 2017-11-14 08:45 | 51284.6238 | 280.008
Devonshire Building | 2017-11-14 09:00 | 51284.6888 | 259.992
Devonshire Building | 2017-11-14 09:15 | 51284.7538 | 259.992
Devonshire Building | 2017-11-14 09:30 | 51284.8238 | 280.008
Devonshire Building | 2017-11-14 09:45 | 51285.4238 | 2400.012
Devonshire Building | 2017-11-14 10:00 | 51285.4738 | 200.016
Devonshire Building | 2017-11-14 10:15 | 51285.5538 | 320.004
Devonshire Building | 2017-11-14 10:30 | 51285.6238 | 280.008
Devonshire Building | 2017-11-14 10:45 | 51286.2338 | 2440.008
Devonshire Building | 2017-11-14 11:00 | 51286.3038 | 280.008
Devonshire Building | 2017-11-14 11:15 | 51286.3788 | 299.988
Devonshire Building | 2017-11-14 11:30 | 51286.4538 | 299.988
Devonshire Building | 2017-11-14 11:45 | 51286.5238 | 280.008
Devonshire Building | 2017-11-14 12:00 | 51287.1988 | 2700
Devonshire Building | 2017-11-14 12:15 | 51287.2738 | 299.988
Devonshire Building | 2017-11-14 12:30 | 51287.3588 | 339.984
Devonshire Building | 2017-11-14 12:45 | 51287.4338 | 299.988
Devonshire Building | 2017-11-14 13:00 | 51287.5038 | 280.008
Devonshire Building | 2017-11-14 13:15 | 51288.0988 | 2379.996
Devonshire Building | 2017-11-14 13:30 | 51288.1488 | 200.016
Devonshire Building | 2017-11-14 13:45 | 51288.1988 | 200.016
Devonshire Building | 2017-11-14 14:00 | 51288.2538 | 219.996
Devonshire Building | 2017-11-14 14:15 | 51288.3038 | 200.016
Devonshire Building | 2017-11-14 14:30 | 51288.3538 | 200.016
Devonshire Building | 2017-11-14 14:45 | 51288.7538 | 1599.984
Devonshire Building | 2017-11-14 15:00 | 51289.0188 | 1059.984
Devonshire Building | 2017-11-14 15:15 | 51289.0538 | 140.004
Devonshire Building | 2017-11-14 15:30 | 51289.0988 | 180
Devonshire Building | 2017-11-14 15:45 | 51289.1438 | 180
Devonshire Building | 2017-11-14 16:00 | 51289.1788 | 140.004
Devonshire Building | 2017-11-14 16:15 | 51289.7538 | 2300.004
Devonshire Building | 2017-11-14 16:30 | 51289.7988 | 180
Devonshire Building | 2017-11-14 16:45 | 51289.8488 | 200.016
Devonshire Building | 2017-11-14 17:00 | 51289.8938 | 180
Devonshire Building | 2017-11-14 17:15 | 51289.9388 | 180
Devonshire Building | 2017-11-14 17:30 | 51289.9788 | 159.984
Devonshire Building | 2017-11-14 17:45 | 51290.5538 | 2300.004
Devonshire Building | 2017-11-14 18:00 | 51290.5988 | 180
Devonshire Building | 2017-11-14 18:15 | 51290.6438 | 180
Devonshire Building | 2017-11-14 18:30 | 51290.6888 | 180
Devonshire Building | 2017-11-14 18:45 | 51290.7288 | 159.984
Devonshire Building | 2017-11-14 19:00 | 51290.7688 | 159.984
Devonshire Building | 2017-11-14 19:15 | 51290.8038 | 140.004
Devonshire Building | 2017-11-14 19:30 | 51290.8388 | 140.004
Devonshire Building | 2017-11-14 19:45 | 51290.8888 | 200.016
Devonshire Building | 2017-11-14 20:00 | 51290.9338 | 180
Devonshire Building | 2017-11-14 20:15 | 51290.9788 | 180
Devonshire Building | 2017-11-14 20:30 | 51291.0238 | 180
Devonshire Building | 2017-11-14 20:45 | 51291.0638 | 159.984
Devonshire Building | 2017-11-14 21:00 | 51291.1088 | 180
Devonshire Building | 2017-11-14 21:15 | 51291.1488 | 159.984
Devonshire Building | 2017-11-14 21:30 | 51291.1888 | 159.984
Devonshire Building | 2017-11-14 21:45 | 51291.2438 | 219.996
Devonshire Building | 2017-11-14 22:00 | 51291.2738 | 119.988
Devonshire Building | 2017-11-14 22:15 | 51291.3038 | 119.988
Devonshire Building | 2017-11-14 22:30 | 51291.3288 | 100.008
Devonshire Building | 2017-11-14 22:45 | 51291.3438 | 60.012
Devonshire Building | 2017-11-14 23:00 | 51291.3588 | 60.012
Devonshire Building | 2017-11-14 23:15 | 51291.3738 | 60.012
Devonshire Building | 2017-11-14 23:30 | 51291.3888 | 60.012
Devonshire Building | 2017-11-14 23:45 | 51291.4038 | 60.012
Devonshire Building | 2017-11-15 | 51291.4219 | 60.012
Devonshire Building | 2017-11-15 00:15 | 51291.4369 | 60.012
Devonshire Building | 2017-11-15 00:30 | 51291.4519 | 60.012
Devonshire Building | 2017-11-15 00:45 | 51291.4669 | 60.012
Devonshire Building | 2017-11-15 01:00 | 51291.4819 | 60.012
Devonshire Building | 2017-11-15 01:15 | 51291.4969 | 60.012
Devonshire Building | 2017-11-15 01:30 | 51291.5069 | 39.996
Devonshire Building | 2017-11-15 01:45 | 51291.5219 | 60.012
Devonshire Building | 2017-11-15 02:00 | 51291.5369 | 60.012
Devonshire Building | 2017-11-15 02:15 | 51292.0569 | 2080.008
Devonshire Building | 2017-11-15 02:30 | 51292.0719 | 60.012
Devonshire Building | 2017-11-15 02:45 | 51292.0869 | 60.012
Devonshire Building | 2017-11-15 03:00 | 51292.1019 | 60.012
Devonshire Building | 2017-11-15 03:15 | 51292.1169 | 60.012
Devonshire Building | 2017-11-15 03:30 | 51292.1269 | 39.996
Devonshire Building | 2017-11-15 03:45 | 51292.1419 | 60.012
Devonshire Building | 2017-11-15 04:00 | 51292.1569 | 60.012
Devonshire Building | 2017-11-15 04:15 | 51292.1719 | 60.012
Devonshire Building | 2017-11-15 04:30 | 51292.1919 | 79.992
Devonshire Building | 2017-11-15 04:45 | 51292.2069 | 60.012
Devonshire Building | 2017-11-15 05:00 | 51292.2219 | 60.012
Devonshire Building | 2017-11-15 05:15 | 51292.2419 | 79.992
Devonshire Building | 2017-11-15 05:30 | 51292.2569 | 60.012
Devonshire Building | 2017-11-15 05:45 | 51292.2719 | 60.012
Devonshire Building | 2017-11-15 06:00 | 51292.2869 | 60.012
Devonshire Building | 2017-11-15 06:15 | 51292.3019 | 60.012
Devonshire Building | 2017-11-15 06:30 | 51292.3169 | 60.012
Devonshire Building | 2017-11-15 06:45 | 51292.3319 | 60.012
Devonshire Building | 2017-11-15 07:00 | 51292.3469 | 60.012
Devonshire Building | 2017-11-15 07:15 | 51292.3619 | 60.012
Devonshire Building | 2017-11-15 07:30 | 51292.377 | 60.012
Devonshire Building | 2017-11-15 07:45 | 51292.392 | 60.012
Devonshire Building | 2017-11-15 08:00 | 51292.407 | 60.012
Devonshire Building | 2017-11-15 08:15 | 51292.437 | 119.988
Devonshire Building | 2017-11-15 08:30 | 51292.472 | 140.004
Devonshire Building | 2017-11-15 08:45 | 51292.512 | 159.984
Devonshire Building | 2017-11-15 09:00 | 51293.107 | 2379.996
Devonshire Building | 2017-11-15 09:15 | 51293.1619 | 219.996
Devonshire Building | 2017-11-15 09:30 | 51293.222 | 240.012
Devonshire Building | 2017-11-15 09:45 | 51293.282 | 240.012
Devonshire Building | 2017-11-15 10:00 | 51293.337 | 219.996
Devonshire Building | 2017-11-15 10:15 | 51293.392 | 219.996
Devonshire Building | 2017-11-15 10:30 | 51293.447 | 219.996
Devonshire Building | 2017-11-15 10:45 | 51294.057 | 2440.008
Devonshire Building | 2017-11-15 11:00 | 51294.107 | 200.016
Devonshire Building | 2017-11-15 11:15 | 51294.157 | 200.016
Devonshire Building | 2017-11-15 11:30 | 51294.207 | 200.016
Devonshire Building | 2017-11-15 11:45 | 51294.262 | 219.996
Devonshire Building | 2017-11-15 12:00 | 51294.877 | 2459.988
Devonshire Building | 2017-11-15 12:15 | 51294.937 | 240.012
Devonshire Building | 2017-11-15 12:30 | 51295.007 | 280.008
Devonshire Building | 2017-11-15 12:45 | 51295.077 | 280.008
Devonshire Building | 2017-11-15 13:00 | 51295.142 | 259.992
Devonshire Building | 2017-11-15 13:15 | 51295.217 | 299.988
Devonshire Building | 2017-11-15 13:30 | 51295.487 | 1080
Devonshire Building | 2017-11-15 13:45 | 51295.877 | 1559.988
Devonshire Building | 2017-11-15 14:00 | 51295.952 | 299.988
Devonshire Building | 2017-11-15 14:15 | 51296.022 | 280.008
Devonshire Building | 2017-11-15 14:30 | 51296.097 | 299.988
Devonshire Building | 2017-11-15 14:45 | 51296.167 | 280.008
Devonshire Building | 2017-11-15 15:00 | 51296.237 | 280.008
Devonshire Building | 2017-11-15 15:15 | 51296.637 | 1599.984
Devonshire Building | 2017-11-15 15:30 | 51296.937 | 1199.988
Devonshire Building | 2017-11-15 15:45 | 51297.007 | 280.008
Devonshire Building | 2017-11-15 16:00 | 51297.082 | 299.988
Devonshire Building | 2017-11-15 16:15 | 51297.152 | 280.008
Devonshire Building | 2017-11-15 16:30 | 51297.212 | 240.012
Devonshire Building | 2017-11-15 16:45 | 51297.272 | 240.012
Devonshire Building | 2017-11-15 17:00 | 51297.322 | 200.016
Devonshire Building | 2017-11-15 17:15 | 51297.887 | 2260.008
Devonshire Building | 2017-11-15 17:30 | 51297.927 | 159.984
Devonshire Building | 2017-11-15 17:45 | 51297.972 | 180
Devonshire Building | 2017-11-15 18:00 | 51298.012 | 159.984
Devonshire Building | 2017-11-15 18:15 | 51298.052 | 159.984
Devonshire Building | 2017-11-15 18:30 | 51298.092 | 159.984
Devonshire Building | 2017-11-15 18:45 | 51298.1319 | 159.984
Devonshire Building | 2017-11-15 19:00 | 51298.1669 | 140.004
Devonshire Building | 2017-11-15 19:15 | 51298.1969 | 119.988
Devonshire Building | 2017-11-15 19:30 | 51298.2269 | 119.988
Devonshire Building | 2017-11-15 19:45 | 51298.2569 | 119.988
Devonshire Building | 2017-11-15 20:00 | 51298.2819 | 100.008
Devonshire Building | 2017-11-15 20:15 | 51298.3069 | 100.008
Devonshire Building | 2017-11-15 20:30 | 51298.3319 | 100.008
Devonshire Building | 2017-11-15 20:45 | 51298.3669 | 140.004
Devonshire Building | 2017-11-15 21:00 | 51298.3869 | 79.992
Devonshire Building | 2017-11-15 21:15 | 51298.4119 | 100.008
Devonshire Building | 2017-11-15 21:30 | 51298.4319 | 79.992
Devonshire Building | 2017-11-15 21:45 | 51298.4719 | 159.984
Devonshire Building | 2017-11-15 22:00 | 51298.4869 | 60.012
Devonshire Building | 2017-11-15 22:15 | 51298.5019 | 60.012
Devonshire Building | 2017-11-15 22:30 | 51298.5169 | 60.012
Devonshire Building | 2017-11-15 22:45 | 51298.532 | 60.012
Devonshire Building | 2017-11-15 23:00 | 51298.547 | 60.012
Devonshire Building | 2017-11-15 23:15 | 51299.067 | 2080.008
Devonshire Building | 2017-11-15 23:30 | 51299.082 | 60.012
Devonshire Building | 2017-11-15 23:45 | 51299.092 | 39.996
Devonshire Building | 2017-11-16 | 51299.1055 | 60.012
Devonshire Building | 2017-11-16 00:15 | 51299.1205 | 60.012
Devonshire Building | 2017-11-16 00:30 | 51299.1355 | 60.012
Devonshire Building | 2017-11-16 00:45 | 51299.1455 | 39.996
Devonshire Building | 2017-11-16 01:00 | 51299.1605 | 60.012
Devonshire Building | 2017-11-16 01:15 | 51299.1755 | 60.012
Devonshire Building | 2017-11-16 01:30 | 51299.1905 | 60.012
Devonshire Building | 2017-11-16 01:45 | 51299.2105 | 79.992
Devonshire Building | 2017-11-16 02:00 | 51299.2255 | 60.012
Devonshire Building | 2017-11-16 02:15 | 51299.2405 | 60.012
Devonshire Building | 2017-11-16 02:30 | 51299.2555 | 60.012
Devonshire Building | 2017-11-16 02:45 | 51299.2705 | 60.012
Devonshire Building | 2017-11-16 03:00 | 51299.2855 | 60.012
Devonshire Building | 2017-11-16 03:15 | 51299.3005 | 60.012
Devonshire Building | 2017-11-16 03:30 | 51299.3155 | 60.012
Devonshire Building | 2017-11-16 03:45 | 51299.3255 | 39.996
Devonshire Building | 2017-11-16 04:00 | 51299.3405 | 60.012
Devonshire Building | 2017-11-16 04:15 | 51299.3555 | 60.012
Devonshire Building | 2017-11-16 04:30 | 51299.3655 | 39.996
Devonshire Building | 2017-11-16 04:45 | 51299.3805 | 60.012
Devonshire Building | 2017-11-16 05:00 | 51299.3955 | 60.012
Devonshire Building | 2017-11-16 05:15 | 51299.4055 | 39.996
Devonshire Building | 2017-11-16 05:30 | 51299.4205 | 60.012
Devonshire Building | 2017-11-16 05:45 | 51299.4305 | 39.996
Devonshire Building | 2017-11-16 06:00 | 51299.4455 | 60.012
Devonshire Building | 2017-11-16 06:15 | 51299.4605 | 60.012
Devonshire Building | 2017-11-16 06:30 | 51299.4755 | 60.012
Devonshire Building | 2017-11-16 06:45 | 51299.4855 | 39.996
Devonshire Building | 2017-11-16 07:00 | 51299.5005 | 60.012
Devonshire Building | 2017-11-16 07:15 | 51299.5155 | 60.012
Devonshire Building | 2017-11-16 07:30 | 51299.5305 | 60.012
Devonshire Building | 2017-11-16 07:45 | 51299.5455 | 60.012
Devonshire Building | 2017-11-16 08:00 | 51299.5755 | 119.988
Devonshire Building | 2017-11-16 08:15 | 51299.6055 | 119.988
Devonshire Building | 2017-11-16 08:30 | 51300.1655 | 2239.992
Devonshire Building | 2017-11-16 08:45 | 51300.2105 | 180
Devonshire Building | 2017-11-16 09:00 | 51300.2655 | 219.996
Devonshire Building | 2017-11-16 09:15 | 51300.3305 | 259.992
Devonshire Building | 2017-11-16 09:30 | 51300.3955 | 259.992
Devonshire Building | 2017-11-16 09:45 | 51300.4555 | 240.012
Devonshire Building | 2017-11-16 10:00 | 51300.5055 | 200.016
Devonshire Building | 2017-11-16 10:15 | 51300.5555 | 200.016
Devonshire Building | 2017-11-16 10:30 | 51300.8755 | 1280.016
Devonshire Building | 2017-11-16 10:45 | 51301.1955 | 1280.016
Devonshire Building | 2017-11-16 11:00 | 51301.2555 | 240.012
Devonshire Building | 2017-11-16 11:15 | 51301.3155 | 240.012
Devonshire Building | 2017-11-16 11:30 | 51301.3805 | 259.992
Devonshire Building | 2017-11-16 11:45 | 51301.6155 | 939.996
Devonshire Building | 2017-11-16 12:00 | 51302.0755 | 1839.996
Devonshire Building | 2017-11-16 12:15 | 51302.1455 | 280.008
Devonshire Building | 2017-11-16 12:30 | 51302.2255 | 320.004
Devonshire Building | 2017-11-16 12:45 | 51302.3755 | 600.012
Devonshire Building | 2017-11-16 13:00 | 51302.5405 | 659.988
Devonshire Building | 2017-11-16 13:15 | 51303.2205 | 2720.016
Devonshire Building | 2017-11-16 13:30 | 51303.3606 | 560.016
Devonshire Building | 2017-11-16 13:45 | 51303.4806 | 479.988
Devonshire Building | 2017-11-16 14:00 | 51303.6105 | 519.984
Devonshire Building | 2017-11-16 14:15 | 51303.7355 | 500.004
Devonshire Building | 2017-11-16 14:30 | 51303.8406 | 420.012
Devonshire Building | 2017-11-16 14:45 | 51303.9206 | 320.004
Devonshire Building | 2017-11-16 15:00 | 51304.5506 | 2520
Devonshire Building | 2017-11-16 15:15 | 51304.5905 | 159.984
Devonshire Building | 2017-11-16 15:30 | 51304.6355 | 180
Devonshire Building | 2017-11-16 15:45 | 51304.6805 | 180
Devonshire Building | 2017-11-16 16:00 | 51304.7205 | 159.984
Devonshire Building | 2017-11-16 16:15 | 51304.7705 | 200.016
Devonshire Building | 2017-11-16 16:30 | 51304.8155 | 180
Devonshire Building | 2017-11-16 16:45 | 51305.0855 | 1080
Devonshire Building | 2017-11-16 17:00 | 51305.4255 | 1360.008
Devonshire Building | 2017-11-16 17:15 | 51305.4705 | 180
Devonshire Building | 2017-11-16 17:30 | 51305.5056 | 140.004
Devonshire Building | 2017-11-16 17:45 | 51305.5455 | 159.984
Devonshire Building | 2017-11-16 18:00 | 51305.5855 | 159.984
Devonshire Building | 2017-11-16 18:15 | 51305.6255 | 159.984
Devonshire Building | 2017-11-16 18:30 | 51305.6605 | 140.004
Devonshire Building | 2017-11-16 18:45 | 51305.6955 | 140.004
Devonshire Building | 2017-11-16 19:00 | 51305.7305 | 140.004
Devonshire Building | 2017-11-16 19:15 | 51305.7605 | 119.988
Devonshire Building | 2017-11-16 19:30 | 51305.7905 | 119.988
Devonshire Building | 2017-11-16 19:45 | 51305.8205 | 119.988
Devonshire Building | 2017-11-16 20:00 | 51305.8505 | 119.988
Devonshire Building | 2017-11-16 20:15 | 51305.8805 | 119.988
Devonshire Building | 2017-11-16 20:30 | 51305.9055 | 100.008
Devonshire Building | 2017-11-16 20:45 | 51305.9355 | 119.988
Devonshire Building | 2017-11-16 21:00 | 51306.4755 | 2160
Devonshire Building | 2017-11-16 21:15 | 51306.4905 | 60.012
Devonshire Building | 2017-11-16 21:30 | 51306.5055 | 60.012
Devonshire Building | 2017-11-16 21:45 | 51306.5255 | 79.992
Devonshire Building | 2017-11-16 22:00 | 51306.5405 | 60.012
Devonshire Building | 2017-11-16 22:15 | 51306.5555 | 60.012
Devonshire Building | 2017-11-16 22:30 | 51306.5755 | 79.992
Devonshire Building | 2017-11-16 22:45 | 51306.5955 | 79.992
Devonshire Building | 2017-11-16 23:00 | 51306.6105 | 60.012
Devonshire Building | 2017-11-16 23:15 | 51306.6305 | 79.992
Devonshire Building | 2017-11-16 23:30 | 51306.6505 | 79.992
Devonshire Building | 2017-11-16 23:45 | 51306.6655 | 60.012
Devonshire Building | 2017-11-17 | 51306.6836 | 79.992
Devonshire Building | 2017-11-17 00:15 | 51306.7036 | 79.992
Devonshire Building | 2017-11-17 00:30 | 51306.7186 | 60.012
Devonshire Building | 2017-11-17 00:45 | 51306.7336 | 60.012
Devonshire Building | 2017-11-17 01:00 | 51306.7536 | 79.992
Devonshire Building | 2017-11-17 01:15 | 51306.7686 | 60.012
Devonshire Building | 2017-11-17 01:30 | 51306.7836 | 60.012
Devonshire Building | 2017-11-17 01:45 | 51306.7986 | 60.012
Devonshire Building | 2017-11-17 02:00 | 51306.8136 | 60.012
Devonshire Building | 2017-11-17 02:15 | 51306.8336 | 79.992
Devonshire Building | 2017-11-17 02:30 | 51306.8486 | 60.012
Devonshire Building | 2017-11-17 02:45 | 51306.8586 | 39.996
Devonshire Building | 2017-11-17 03:00 | 51306.8736 | 60.012
Devonshire Building | 2017-11-17 03:15 | 51306.8886 | 60.012
Devonshire Building | 2017-11-17 03:30 | 51306.9036 | 60.012
Devonshire Building | 2017-11-17 03:45 | 51306.9186 | 60.012
Devonshire Building | 2017-11-17 04:00 | 51306.9336 | 60.012
Devonshire Building | 2017-11-17 04:15 | 51306.9486 | 60.012
Devonshire Building | 2017-11-17 04:30 | 51306.9586 | 39.996
Devonshire Building | 2017-11-17 04:45 | 51306.9736 | 60.012
Devonshire Building | 2017-11-17 05:00 | 51306.9886 | 60.012
Devonshire Building | 2017-11-17 05:15 | 51307.0036 | 60.012
Devonshire Building | 2017-11-17 05:30 | 51307.0186 | 60.012
Devonshire Building | 2017-11-17 05:45 | 51307.0336 | 60.012
Devonshire Building | 2017-11-17 06:00 | 51307.0486 | 60.012
Devonshire Building | 2017-11-17 06:15 | 51307.0636 | 60.012
Devonshire Building | 2017-11-17 06:30 | 51307.0786 | 60.012
Devonshire Building | 2017-11-17 06:45 | 51307.0936 | 60.012
Devonshire Building | 2017-11-17 07:00 | 51307.4137 | 1280.016
Devonshire Building | 2017-11-17 07:15 | 51307.6487 | 939.996
Devonshire Building | 2017-11-17 07:30 | 51307.6637 | 60.012
Devonshire Building | 2017-11-17 07:45 | 51307.6837 | 79.992
Devonshire Building | 2017-11-17 08:00 | 51307.7136 | 119.988
Devonshire Building | 2017-11-17 08:15 | 51307.7637 | 200.016
Devonshire Building | 2017-11-17 08:30 | 51307.8237 | 240.012
Devonshire Building | 2017-11-17 08:45 | 51307.8987 | 299.988
Devonshire Building | 2017-11-17 09:00 | 51307.9937 | 380.016
Devonshire Building | 2017-11-17 09:15 | 51308.1037 | 439.992
Devonshire Building | 2017-11-17 09:30 | 51308.1987 | 380.016
Devonshire Building | 2017-11-17 09:45 | 51308.5387 | 1360.008
Devonshire Building | 2017-11-17 10:00 | 51308.8987 | 1440
Devonshire Building | 2017-11-17 10:15 | 51308.9787 | 320.004
Devonshire Building | 2017-11-17 10:30 | 51309.0537 | 299.988
Devonshire Building | 2017-11-17 10:45 | 51309.1287 | 299.988
Devonshire Building | 2017-11-17 11:00 | 51309.1937 | 259.992
Devonshire Building | 2017-11-17 11:15 | 51309.7286 | 2139.984
Devonshire Building | 2017-11-17 11:30 | 51309.8687 | 560.016
Devonshire Building | 2017-11-17 11:45 | 51309.9187 | 200.016
Devonshire Building | 2017-11-17 12:00 | 51309.9687 | 200.016
Devonshire Building | 2017-11-17 12:15 | 51310.0237 | 219.996
Devonshire Building | 2017-11-17 12:30 | 51310.0687 | 180
Devonshire Building | 2017-11-17 12:45 | 51310.1237 | 219.996
Devonshire Building | 2017-11-17 13:00 | 51310.1837 | 240.012
Devonshire Building | 2017-11-17 13:15 | 51310.2437 | 240.012
Devonshire Building | 2017-11-17 13:30 | 51310.3037 | 240.012
Devonshire Building | 2017-11-17 13:45 | 51310.3687 | 259.992
Devonshire Building | 2017-11-17 14:00 | 51310.5387 | 680.004
Devonshire Building | 2017-11-17 14:15 | 51310.6887 | 600.012
Devonshire Building | 2017-11-17 14:30 | 51310.7887 | 399.996
Devonshire Building | 2017-11-17 14:45 | 51310.8537 | 259.992
Devonshire Building | 2017-11-17 15:00 | 51310.9237 | 280.008
Devonshire Building | 2017-11-17 15:15 | 51310.9737 | 200.016
Devonshire Building | 2017-11-17 15:30 | 51311.0137 | 159.984
Devonshire Building | 2017-11-17 15:45 | 51311.0487 | 140.004
Devonshire Building | 2017-11-17 16:00 | 51311.0837 | 140.004
Devonshire Building | 2017-11-17 16:15 | 51311.1137 | 119.988
Devonshire Building | 2017-11-17 16:30 | 51311.1487 | 140.004
Devonshire Building | 2017-11-17 16:45 | 51311.1837 | 140.004
Devonshire Building | 2017-11-17 17:00 | 51311.2187 | 140.004
Devonshire Building | 2017-11-17 17:15 | 51311.2487 | 119.988
Devonshire Building | 2017-11-17 17:30 | 51311.2787 | 119.988
Devonshire Building | 2017-11-17 17:45 | 51311.3237 | 180
Devonshire Building | 2017-11-17 18:00 | 51311.3937 | 280.008
Devonshire Building | 2017-11-17 18:15 | 51311.4687 | 299.988
Devonshire Building | 2017-11-17 18:30 | 51311.5487 | 320.004
Devonshire Building | 2017-11-17 18:45 | 51311.6237 | 299.988
Devonshire Building | 2017-11-17 19:00 | 51311.6937 | 280.008
Devonshire Building | 2017-11-17 19:15 | 51311.7637 | 280.008
Devonshire Building | 2017-11-17 19:30 | 51311.8187 | 219.996
Devonshire Building | 2017-11-17 19:45 | 51311.8687 | 200.016
Devonshire Building | 2017-11-17 20:00 | 51311.9137 | 180
Devonshire Building | 2017-11-17 20:15 | 51311.9537 | 159.984
Devonshire Building | 2017-11-17 20:30 | 51311.9887 | 140.004
Devonshire Building | 2017-11-17 20:45 | 51312.0187 | 119.988
Devonshire Building | 2017-11-17 21:00 | 51312.0537 | 140.004
Devonshire Building | 2017-11-17 21:15 | 51312.0837 | 119.988
Devonshire Building | 2017-11-17 21:30 | 51312.1087 | 100.008
Devonshire Building | 2017-11-17 21:45 | 51312.1337 | 100.008
Devonshire Building | 2017-11-17 22:00 | 51312.1587 | 100.008
Devonshire Building | 2017-11-17 22:15 | 51312.1787 | 79.992
Devonshire Building | 2017-11-17 22:30 | 51312.2037 | 100.008
Devonshire Building | 2017-11-17 22:45 | 51312.2237 | 79.992
Devonshire Building | 2017-11-17 23:00 | 51312.2437 | 79.992
Devonshire Building | 2017-11-17 23:15 | 51312.2637 | 79.992
Devonshire Building | 2017-11-17 23:30 | 51312.2837 | 79.992
Devonshire Building | 2017-11-17 23:45 | 51312.3037 | 79.992
Devonshire Building | 2017-11-18 | 51312.3242 | 79.992
Devonshire Building | 2017-11-18 00:15 | 51312.3442 | 79.992
Devonshire Building | 2017-11-18 00:30 | 51312.3642 | 79.992
Devonshire Building | 2017-11-18 00:45 | 51312.3842 | 79.992
Devonshire Building | 2017-11-18 01:00 | 51312.3992 | 60.012
Devonshire Building | 2017-11-18 01:15 | 51312.4192 | 79.992
Devonshire Building | 2017-11-18 01:30 | 51312.4342 | 60.012
Devonshire Building | 2017-11-18 01:45 | 51312.4542 | 79.992
Devonshire Building | 2017-11-18 02:00 | 51312.4742 | 79.992
Devonshire Building | 2017-11-18 02:15 | 51312.4892 | 60.012
Devonshire Building | 2017-11-18 02:30 | 51312.5092 | 79.992
Devonshire Building | 2017-11-18 02:45 | 51312.5242 | 60.012
Devonshire Building | 2017-11-18 03:00 | 51312.5442 | 79.992
Devonshire Building | 2017-11-18 03:15 | 51312.5592 | 60.012
Devonshire Building | 2017-11-18 03:30 | 51312.5742 | 60.012
Devonshire Building | 2017-11-18 03:45 | 51312.5942 | 79.992
Devonshire Building | 2017-11-18 04:00 | 51312.6092 | 60.012
Devonshire Building | 2017-11-18 04:15 | 51312.6242 | 60.012
Devonshire Building | 2017-11-18 04:30 | 51312.6392 | 60.012
Devonshire Building | 2017-11-18 04:45 | 51312.6542 | 60.012
Devonshire Building | 2017-11-18 05:00 | 51312.6692 | 60.012
Devonshire Building | 2017-11-18 05:15 | 51312.6842 | 60.012
Devonshire Building | 2017-11-18 05:30 | 51312.6992 | 60.012
Devonshire Building | 2017-11-18 05:45 | 51312.7192 | 79.992
Devonshire Building | 2017-11-18 06:00 | 51312.7342 | 60.012
Devonshire Building | 2017-11-18 06:15 | 51312.7492 | 60.012
Devonshire Building | 2017-11-18 06:30 | 51312.7642 | 60.012
Devonshire Building | 2017-11-18 06:45 | 51312.7793 | 60.012
Devonshire Building | 2017-11-18 07:00 | 51312.7943 | 60.012
Devonshire Building | 2017-11-18 07:15 | 51312.8093 | 60.012
Devonshire Building | 2017-11-18 07:30 | 51312.8193 | 39.996
Devonshire Building | 2017-11-18 07:45 | 51312.8393 | 79.992
Devonshire Building | 2017-11-18 08:00 | 51312.8693 | 119.988
Devonshire Building | 2017-11-18 08:15 | 51312.8992 | 119.988
Devonshire Building | 2017-11-18 08:30 | 51312.9242 | 100.008
Devonshire Building | 2017-11-18 08:45 | 51312.9542 | 119.988
Devonshire Building | 2017-11-18 09:00 | 51312.9842 | 119.988
Devonshire Building | 2017-11-18 09:15 | 51313.0142 | 119.988
Devonshire Building | 2017-11-18 09:30 | 51313.0442 | 119.988
Devonshire Building | 2017-11-18 09:45 | 51313.0742 | 119.988
Devonshire Building | 2017-11-18 10:00 | 51313.0992 | 100.008
Devonshire Building | 2017-11-18 10:15 | 51313.1292 | 119.988
Devonshire Building | 2017-11-18 10:30 | 51313.1592 | 119.988
Devonshire Building | 2017-11-18 10:45 | 51313.1792 | 79.992
Devonshire Building | 2017-11-18 11:00 | 51313.1942 | 60.012
Devonshire Building | 2017-11-18 11:15 | 51313.2092 | 60.012
Devonshire Building | 2017-11-18 11:30 | 51313.2242 | 60.012
Devonshire Building | 2017-11-18 11:45 | 51313.2392 | 60.012
Devonshire Building | 2017-11-18 12:00 | 51313.2492 | 39.996
Devonshire Building | 2017-11-18 12:15 | 51313.2642 | 60.012
Devonshire Building | 2017-11-18 12:30 | 51313.2792 | 60.012
Devonshire Building | 2017-11-18 12:45 | 51313.2942 | 60.012
Devonshire Building | 2017-11-18 13:00 | 51313.3093 | 60.012
Devonshire Building | 2017-11-18 13:15 | 51313.3193 | 39.996
Devonshire Building | 2017-11-18 13:30 | 51313.3343 | 60.012
Devonshire Building | 2017-11-18 13:45 | 51313.3493 | 60.012
Devonshire Building | 2017-11-18 14:00 | 51313.3643 | 60.012
Devonshire Building | 2017-11-18 14:15 | 51313.3793 | 60.012
Devonshire Building | 2017-11-18 14:30 | 51313.3943 | 60.012
Devonshire Building | 2017-11-18 14:45 | 51313.4093 | 60.012
Devonshire Building | 2017-11-18 15:00 | 51313.4193 | 39.996
Devonshire Building | 2017-11-18 15:15 | 51313.4343 | 60.012
Devonshire Building | 2017-11-18 15:30 | 51313.4493 | 60.012
Devonshire Building | 2017-11-18 15:45 | 51313.4643 | 60.012
Devonshire Building | 2017-11-18 16:00 | 51313.4793 | 60.012
Devonshire Building | 2017-11-18 16:15 | 51313.4943 | 60.012
Devonshire Building | 2017-11-18 16:30 | 51313.5093 | 60.012
Devonshire Building | 2017-11-18 16:45 | 51313.5243 | 60.012
Devonshire Building | 2017-11-18 17:00 | 51313.5443 | 79.992
Devonshire Building | 2017-11-18 17:15 | 51313.5593 | 60.012
Devonshire Building | 2017-11-18 17:30 | 51313.5693 | 39.996
Devonshire Building | 2017-11-18 17:45 | 51313.5843 | 60.012
Devonshire Building | 2017-11-18 18:00 | 51313.5993 | 60.012
Devonshire Building | 2017-11-18 18:15 | 51313.6143 | 60.012
Devonshire Building | 2017-11-18 18:30 | 51313.6293 | 60.012
Devonshire Building | 2017-11-18 18:45 | 51313.6443 | 60.012
Devonshire Building | 2017-11-18 19:00 | 51313.6543 | 39.996
Devonshire Building | 2017-11-18 19:15 | 51313.6693 | 60.012
Devonshire Building | 2017-11-18 19:30 | 51313.6843 | 60.012
Devonshire Building | 2017-11-18 19:45 | 51313.6993 | 60.012
Devonshire Building | 2017-11-18 20:00 | 51313.7143 | 60.012
Devonshire Building | 2017-11-18 20:15 | 51313.7243 | 39.996
Devonshire Building | 2017-11-18 20:30 | 51313.7393 | 60.012
Devonshire Building | 2017-11-18 20:45 | 51313.7543 | 60.012
Devonshire Building | 2017-11-18 21:00 | 51313.7693 | 60.012
Devonshire Building | 2017-11-18 21:15 | 51313.7793 | 39.996
Devonshire Building | 2017-11-18 21:30 | 51313.7943 | 60.012
Devonshire Building | 2017-11-18 21:45 | 51313.8093 | 60.012
Devonshire Building | 2017-11-18 22:00 | 51313.8243 | 60.012
Devonshire Building | 2017-11-18 22:15 | 51313.8343 | 39.996
Devonshire Building | 2017-11-18 22:30 | 51313.8493 | 60.012
Devonshire Building | 2017-11-18 22:45 | 51313.8643 | 60.012
Devonshire Building | 2017-11-18 23:00 | 51313.8793 | 60.012
Devonshire Building | 2017-11-18 23:15 | 51313.8893 | 39.996
Devonshire Building | 2017-11-18 23:30 | 51313.9043 | 60.012
Devonshire Building | 2017-11-18 23:45 | 51313.9193 | 60.012
Devonshire Building | 2017-11-19 | 51313.9336 | 60.012
Devonshire Building | 2017-11-19 00:15 | 51313.9436 | 39.996
Devonshire Building | 2017-11-19 00:30 | 51313.9586 | 60.012
Devonshire Building | 2017-11-19 00:45 | 51313.9736 | 60.012
Devonshire Building | 2017-11-19 01:00 | 51313.9886 | 60.012
Devonshire Building | 2017-11-19 01:15 | 51313.9986 | 39.996
Devonshire Building | 2017-11-19 01:30 | 51314.0136 | 60.012
Devonshire Building | 2017-11-19 01:45 | 51314.0286 | 60.012
Devonshire Building | 2017-11-19 02:00 | 51314.0436 | 60.012
Devonshire Building | 2017-11-19 02:15 | 51314.0536 | 39.996
Devonshire Building | 2017-11-19 02:30 | 51314.0686 | 60.012
Devonshire Building | 2017-11-19 02:45 | 51314.0836 | 60.012
Devonshire Building | 2017-11-19 03:00 | 51314.0986 | 60.012
Devonshire Building | 2017-11-19 03:15 | 51314.1136 | 60.012
Devonshire Building | 2017-11-19 03:30 | 51314.1236 | 39.996
Devonshire Building | 2017-11-19 03:45 | 51314.1386 | 60.012
Devonshire Building | 2017-11-19 04:00 | 51314.1536 | 60.012
Devonshire Building | 2017-11-19 04:15 | 51314.1686 | 60.012
Devonshire Building | 2017-11-19 04:30 | 51314.1786 | 39.996
Devonshire Building | 2017-11-19 04:45 | 51314.1936 | 60.012
Devonshire Building | 2017-11-19 05:00 | 51314.2086 | 60.012
Devonshire Building | 2017-11-19 05:15 | 51314.2236 | 60.012
Devonshire Building | 2017-11-19 05:30 | 51314.2386 | 60.012
Devonshire Building | 2017-11-19 05:45 | 51314.2486 | 39.996
Devonshire Building | 2017-11-19 06:00 | 51314.2636 | 60.012
Devonshire Building | 2017-11-19 06:15 | 51314.2786 | 60.012
Devonshire Building | 2017-11-19 06:30 | 51314.2936 | 60.012
Devonshire Building | 2017-11-19 06:45 | 51314.3036 | 39.996
Devonshire Building | 2017-11-19 07:00 | 51314.3186 | 60.012
Devonshire Building | 2017-11-19 07:15 | 51314.3336 | 60.012
Devonshire Building | 2017-11-19 07:30 | 51314.3487 | 60.012
Devonshire Building | 2017-11-19 07:45 | 51314.3686 | 79.992
Devonshire Building | 2017-11-19 08:00 | 51314.3986 | 119.988
Devonshire Building | 2017-11-19 08:15 | 51314.4236 | 100.008
Devonshire Building | 2017-11-19 08:30 | 51314.4536 | 119.988
Devonshire Building | 2017-11-19 08:45 | 51314.4836 | 119.988
Devonshire Building | 2017-11-19 09:00 | 51314.5136 | 119.988
Devonshire Building | 2017-11-19 09:15 | 51314.5436 | 119.988
Devonshire Building | 2017-11-19 09:30 | 51314.5686 | 100.008
Devonshire Building | 2017-11-19 09:45 | 51314.5986 | 119.988
Devonshire Building | 2017-11-19 10:00 | 51314.6286 | 119.988
Devonshire Building | 2017-11-19 10:15 | 51314.6586 | 119.988
Devonshire Building | 2017-11-19 10:30 | 51314.6836 | 100.008
Devonshire Building | 2017-11-19 10:45 | 51314.7136 | 119.988
Devonshire Building | 2017-11-19 11:00 | 51314.7286 | 60.012
Devonshire Building | 2017-11-19 11:15 | 51314.7436 | 60.012
Devonshire Building | 2017-11-19 11:30 | 51314.7586 | 60.012
Devonshire Building | 2017-11-19 11:45 | 51314.7736 | 60.012
Devonshire Building | 2017-11-19 12:00 | 51314.7886 | 60.012
Devonshire Building | 2017-11-19 12:15 | 51314.8036 | 60.012
Devonshire Building | 2017-11-19 12:30 | 51314.8187 | 60.012
Devonshire Building | 2017-11-19 12:45 | 51314.8337 | 60.012
Devonshire Building | 2017-11-19 13:00 | 51314.8487 | 60.012
Devonshire Building | 2017-11-19 13:15 | 51314.8637 | 60.012
Devonshire Building | 2017-11-19 13:30 | 51314.8787 | 60.012
Devonshire Building | 2017-11-19 13:45 | 51314.8937 | 60.012
Devonshire Building | 2017-11-19 14:00 | 51314.9137 | 79.992
Devonshire Building | 2017-11-19 14:15 | 51314.9287 | 60.012
Devonshire Building | 2017-11-19 14:30 | 51314.9437 | 60.012
Devonshire Building | 2017-11-19 14:45 | 51314.9587 | 60.012
Devonshire Building | 2017-11-19 15:00 | 51314.9787 | 79.992
Devonshire Building | 2017-11-19 15:15 | 51314.9937 | 60.012
Devonshire Building | 2017-11-19 15:30 | 51315.0087 | 60.012
Devonshire Building | 2017-11-19 15:45 | 51315.0287 | 79.992
Devonshire Building | 2017-11-19 16:00 | 51315.0437 | 60.012
Devonshire Building | 2017-11-19 16:15 | 51315.0637 | 79.992
Devonshire Building | 2017-11-19 16:30 | 51315.0787 | 60.012
Devonshire Building | 2017-11-19 16:45 | 51315.0937 | 60.012
Devonshire Building | 2017-11-19 17:00 | 51315.1137 | 79.992
Devonshire Building | 2017-11-19 17:15 | 51315.1287 | 60.012
Devonshire Building | 2017-11-19 17:30 | 51315.1437 | 60.012
Devonshire Building | 2017-11-19 17:45 | 51315.1587 | 60.012
Devonshire Building | 2017-11-19 18:00 | 51315.1737 | 60.012
Devonshire Building | 2017-11-19 18:15 | 51315.1887 | 60.012
Devonshire Building | 2017-11-19 18:30 | 51315.2087 | 79.992
Devonshire Building | 2017-11-19 18:45 | 51315.2237 | 60.012
Devonshire Building | 2017-11-19 19:00 | 51315.2387 | 60.012
Devonshire Building | 2017-11-19 19:15 | 51315.2537 | 60.012
Devonshire Building | 2017-11-19 19:30 | 51315.2687 | 60.012
Devonshire Building | 2017-11-19 19:45 | 51315.2837 | 60.012
Devonshire Building | 2017-11-19 20:00 | 51315.2987 | 60.012
Devonshire Building | 2017-11-19 20:15 | 51315.3187 | 79.992
Devonshire Building | 2017-11-19 20:30 | 51315.3337 | 60.012
Devonshire Building | 2017-11-19 20:45 | 51315.3487 | 60.012
Devonshire Building | 2017-11-19 21:00 | 51315.3637 | 60.012
Devonshire Building | 2017-11-19 21:15 | 51315.3837 | 79.992
Devonshire Building | 2017-11-19 21:30 | 51315.3987 | 60.012
Devonshire Building | 2017-11-19 21:45 | 51315.4137 | 60.012
Devonshire Building | 2017-11-19 22:00 | 51315.4287 | 60.012
Devonshire Building | 2017-11-19 22:15 | 51315.4437 | 60.012
Devonshire Building | 2017-11-19 22:30 | 51315.4587 | 60.012
Devonshire Building | 2017-11-19 22:45 | 51315.4787 | 79.992
Devonshire Building | 2017-11-19 23:00 | 51315.4937 | 60.012
Devonshire Building | 2017-11-19 23:15 | 51315.5087 | 60.012
Devonshire Building | 2017-11-19 23:30 | 51315.5237 | 60.012
Devonshire Building | 2017-11-19 23:45 | 51315.5387 | 60.012
Devonshire Building | 2017-11-20 | 51315.5586 | 79.992
Devonshire Building | 2017-11-20 00:15 | 51315.5736 | 60.012
Devonshire Building | 2017-11-20 00:30 | 51315.5886 | 60.012
Devonshire Building | 2017-11-20 00:45 | 51315.6086 | 79.992
Devonshire Building | 2017-11-20 01:00 | 51315.6236 | 60.012
Devonshire Building | 2017-11-20 01:15 | 51315.6386 | 60.012
Devonshire Building | 2017-11-20 01:30 | 51315.6586 | 79.992
Devonshire Building | 2017-11-20 01:45 | 51315.6736 | 60.012
Devonshire Building | 2017-11-20 02:00 | 51315.6886 | 60.012
Devonshire Building | 2017-11-20 02:15 | 51315.7086 | 79.992
Devonshire Building | 2017-11-20 02:30 | 51315.7236 | 60.012
Devonshire Building | 2017-11-20 02:45 | 51315.7386 | 60.012
Devonshire Building | 2017-11-20 03:00 | 51315.7586 | 79.992
Devonshire Building | 2017-11-20 03:15 | 51315.7736 | 60.012
Devonshire Building | 2017-11-20 03:30 | 51315.7886 | 60.012
Devonshire Building | 2017-11-20 03:45 | 51315.8086 | 79.992
Devonshire Building | 2017-11-20 04:00 | 51315.8236 | 60.012
Devonshire Building | 2017-11-20 04:15 | 51315.8436 | 79.992
Devonshire Building | 2017-11-20 04:30 | 51315.8586 | 60.012
Devonshire Building | 2017-11-20 04:45 | 51315.8736 | 60.012
Devonshire Building | 2017-11-20 05:00 | 51315.8936 | 79.992
Devonshire Building | 2017-11-20 05:15 | 51315.9086 | 60.012
Devonshire Building | 2017-11-20 05:30 | 51315.9236 | 60.012
Devonshire Building | 2017-11-20 05:45 | 51315.9436 | 79.992
Devonshire Building | 2017-11-20 06:00 | 51315.9586 | 60.012
Devonshire Building | 2017-11-20 06:15 | 51315.9786 | 79.992
Devonshire Building | 2017-11-20 06:30 | 51315.9936 | 60.012
Devonshire Building | 2017-11-20 06:45 | 51316.0136 | 79.992
Devonshire Building | 2017-11-20 07:00 | 51316.0286 | 60.012
Devonshire Building | 2017-11-20 07:15 | 51316.0486 | 79.992
Devonshire Building | 2017-11-20 07:30 | 51316.0636 | 60.012
Devonshire Building | 2017-11-20 07:45 | 51316.0936 | 119.988
Devonshire Building | 2017-11-20 08:00 | 51316.1436 | 200.016
Devonshire Building | 2017-11-20 08:15 | 51316.2136 | 280.008
Devonshire Building | 2017-11-20 08:30 | 51316.2786 | 259.992
Devonshire Building | 2017-11-20 08:45 | 51316.9536 | 2700
Devonshire Building | 2017-11-20 09:00 | 51318.3286 | 5500.008
Devonshire Building | 2017-11-20 09:15 | 51319.5086 | 4719.996
Devonshire Building | 2017-11-20 09:30 | 51319.7436 | 939.996
Devonshire Building | 2017-11-20 09:45 | 51319.8786 | 540
Devonshire Building | 2017-11-20 10:00 | 51319.9536 | 299.988
Devonshire Building | 2017-11-20 10:15 | 51320.0286 | 299.988
Devonshire Building | 2017-11-20 10:30 | 51320.0986 | 280.008
Devonshire Building | 2017-11-20 10:45 | 51320.1636 | 259.992
Devonshire Building | 2017-11-20 11:00 | 51320.2286 | 259.992
Devonshire Building | 2017-11-20 11:15 | 51320.2936 | 259.992
Devonshire Building | 2017-11-20 11:30 | 51320.3486 | 219.996
Devonshire Building | 2017-11-20 11:45 | 51320.3936 | 180
Devonshire Building | 2017-11-20 12:00 | 51320.4336 | 159.984
Devonshire Building | 2017-11-20 12:15 | 51320.4786 | 180
Devonshire Building | 2017-11-20 12:30 | 51320.5236 | 180
Devonshire Building | 2017-11-20 12:45 | 51320.5686 | 180
Devonshire Building | 2017-11-20 13:00 | 51320.6136 | 180
Devonshire Building | 2017-11-20 13:15 | 51320.6636 | 200.016
Devonshire Building | 2017-11-20 13:30 | 51320.7136 | 200.016
Devonshire Building | 2017-11-20 13:45 | 51320.7586 | 180
Devonshire Building | 2017-11-20 14:00 | 51320.8036 | 180
Devonshire Building | 2017-11-20 14:15 | 51320.8386 | 140.004
Devonshire Building | 2017-11-20 14:30 | 51320.8886 | 200.016
Devonshire Building | 2017-11-20 14:45 | 51320.9236 | 140.004
Devonshire Building | 2017-11-20 15:00 | 51320.9636 | 159.984
Devonshire Building | 2017-11-20 15:15 | 51320.9986 | 140.004
Devonshire Building | 2017-11-20 15:30 | 51321.0286 | 119.988
Devonshire Building | 2017-11-20 15:45 | 51321.0636 | 140.004
Devonshire Building | 2017-11-20 16:00 | 51321.0936 | 119.988
Devonshire Building | 2017-11-20 16:15 | 51321.1236 | 119.988
Devonshire Building | 2017-11-20 16:30 | 51321.1486 | 100.008
Devonshire Building | 2017-11-20 16:45 | 51321.1786 | 119.988
Devonshire Building | 2017-11-20 17:00 | 51321.2036 | 100.008
Devonshire Building | 2017-11-20 17:15 | 51321.2286 | 100.008
Devonshire Building | 2017-11-20 17:30 | 51321.2586 | 119.988
Devonshire Building | 2017-11-20 17:45 | 51321.2836 | 100.008
Devonshire Building | 2017-11-20 18:00 | 51321.3086 | 100.008
Devonshire Building | 2017-11-20 18:15 | 51321.3336 | 100.008
Devonshire Building | 2017-11-20 18:30 | 51321.3536 | 79.992
Devonshire Building | 2017-11-20 18:45 | 51321.3786 | 100.008
Devonshire Building | 2017-11-20 19:00 | 51321.3986 | 79.992
Devonshire Building | 2017-11-20 19:15 | 51321.4186 | 79.992
Devonshire Building | 2017-11-20 19:30 | 51321.4436 | 100.008
Devonshire Building | 2017-11-20 19:45 | 51321.4636 | 79.992
Devonshire Building | 2017-11-20 20:00 | 51321.4836 | 79.992
Devonshire Building | 2017-11-20 20:15 | 51321.5036 | 79.992
Devonshire Building | 2017-11-20 20:30 | 51321.5236 | 79.992
Devonshire Building | 2017-11-20 20:45 | 51321.5436 | 79.992
Devonshire Building | 2017-11-20 21:00 | 51321.5636 | 79.992
Devonshire Building | 2017-11-20 21:15 | 51321.5836 | 79.992
Devonshire Building | 2017-11-20 21:30 | 51321.6136 | 119.988
Devonshire Building | 2017-11-20 21:45 | 51321.6286 | 60.012
Devonshire Building | 2017-11-20 22:00 | 51321.6486 | 79.992
Devonshire Building | 2017-11-20 22:15 | 51321.6686 | 79.992
Devonshire Building | 2017-11-20 22:30 | 51321.6836 | 60.012
Devonshire Building | 2017-11-20 22:45 | 51321.7036 | 79.992
Devonshire Building | 2017-11-20 23:00 | 51321.7186 | 60.012
Devonshire Building | 2017-11-20 23:15 | 51321.7386 | 79.992
Devonshire Building | 2017-11-20 23:30 | 51321.7536 | 60.012
Devonshire Building | 2017-11-20 23:45 | 51321.7736 | 79.992
Devonshire Building | 2017-11-21 | 51321.7891 | 60.012
Devonshire Building | 2017-11-21 00:15 | 51321.8091 | 79.992
Devonshire Building | 2017-11-21 00:30 | 51321.8241 | 60.012
Devonshire Building | 2017-11-21 00:45 | 51321.8441 | 79.992
Devonshire Building | 2017-11-21 01:00 | 51321.8591 | 60.012
Devonshire Building | 2017-11-21 01:15 | 51321.8791 | 79.992
Devonshire Building | 2017-11-21 01:30 | 51321.8941 | 60.012
Devonshire Building | 2017-11-21 01:45 | 51321.9091 | 60.012
Devonshire Building | 2017-11-21 02:00 | 51321.9291 | 79.992
Devonshire Building | 2017-11-21 02:15 | 51321.9441 | 60.012
Devonshire Building | 2017-11-21 02:30 | 51321.9641 | 79.992
Devonshire Building | 2017-11-21 02:45 | 51321.9791 | 60.012
Devonshire Building | 2017-11-21 03:00 | 51321.9941 | 60.012
Devonshire Building | 2017-11-21 03:15 | 51322.0141 | 79.992
Devonshire Building | 2017-11-21 03:30 | 51322.0291 | 60.012
Devonshire Building | 2017-11-21 03:45 | 51322.0441 | 60.012
Devonshire Building | 2017-11-21 04:00 | 51322.0641 | 79.992
Devonshire Building | 2017-11-21 04:15 | 51322.0791 | 60.012
Devonshire Building | 2017-11-21 04:30 | 51322.0941 | 60.012
Devonshire Building | 2017-11-21 04:45 | 51322.1141 | 79.992
Devonshire Building | 2017-11-21 05:00 | 51322.1291 | 60.012
Devonshire Building | 2017-11-21 05:15 | 51322.1441 | 60.012
Devonshire Building | 2017-11-21 05:30 | 51322.1591 | 60.012
Devonshire Building | 2017-11-21 05:45 | 51322.1791 | 79.992
Devonshire Building | 2017-11-21 06:00 | 51322.1941 | 60.012
Devonshire Building | 2017-11-21 06:15 | 51322.2091 | 60.012
Devonshire Building | 2017-11-21 06:30 | 51322.2291 | 79.992
Devonshire Building | 2017-11-21 06:45 | 51322.2441 | 60.012
Devonshire Building | 2017-11-21 07:00 | 51322.2591 | 60.012
Devonshire Building | 2017-11-21 07:15 | 51322.2791 | 79.992
Devonshire Building | 2017-11-21 07:30 | 51322.2991 | 79.992
Devonshire Building | 2017-11-21 07:45 | 51322.3241 | 100.008
Devonshire Building | 2017-11-21 08:00 | 51322.3591 | 140.004
Devonshire Building | 2017-11-21 08:15 | 51322.3891 | 119.988
Devonshire Building | 2017-11-21 08:30 | 51322.4241 | 140.004
Devonshire Building | 2017-11-21 08:45 | 51322.4591 | 140.004
Devonshire Building | 2017-11-21 09:00 | 51322.5041 | 180
Devonshire Building | 2017-11-21 09:15 | 51322.5391 | 140.004
Devonshire Building | 2017-11-21 09:30 | 51322.5741 | 140.004
Devonshire Building | 2017-11-21 09:45 | 51322.6091 | 140.004
Devonshire Building | 2017-11-21 10:00 | 51322.6491 | 159.984
Devonshire Building | 2017-11-21 10:15 | 51322.6941 | 180
Devonshire Building | 2017-11-21 10:30 | 51322.7341 | 159.984
Devonshire Building | 2017-11-21 10:45 | 51322.7791 | 180
Devonshire Building | 2017-11-21 11:00 | 51322.8941 | 460.008
Devonshire Building | 2017-11-21 11:15 | 51323.0341 | 560.016
Devonshire Building | 2017-11-21 11:30 | 51323.1491 | 460.008
Devonshire Building | 2017-11-21 11:45 | 51323.3141 | 659.988
Devonshire Building | 2017-11-21 12:00 | 51323.4341 | 479.988
Devonshire Building | 2017-11-21 12:15 | 51323.6141 | 720
Devonshire Building | 2017-11-21 12:30 | 51323.7941 | 720
Devonshire Building | 2017-11-21 12:45 | 51324.0141 | 879.984
Devonshire Building | 2017-11-21 13:00 | 51324.1941 | 720
Devonshire Building | 2017-11-21 13:15 | 51324.3691 | 699.984
Devonshire Building | 2017-11-21 13:30 | 51324.6241 | 1019.988
Devonshire Building | 2017-11-21 13:45 | 51324.8141 | 759.996
Devonshire Building | 2017-11-21 14:00 | 51324.9891 | 699.984
Devonshire Building | 2017-11-21 14:15 | 51325.1191 | 519.984
Devonshire Building | 2017-11-21 14:30 | 51325.2941 | 699.984
Devonshire Building | 2017-11-21 14:45 | 51325.4891 | 780.012
Devonshire Building | 2017-11-21 15:00 | 51325.6741 | 740.016
Devonshire Building | 2017-11-21 15:15 | 51325.8491 | 699.984
Devonshire Building | 2017-11-21 15:30 | 51326.0741 | 900
Devonshire Building | 2017-11-21 15:45 | 51326.2691 | 780.012
Devonshire Building | 2017-11-21 16:00 | 51326.4491 | 720
Devonshire Building | 2017-11-21 16:15 | 51326.6491 | 799.992
Devonshire Building | 2017-11-21 16:30 | 51326.7941 | 579.996
Devonshire Building | 2017-11-21 16:45 | 51327.0041 | 839.988
Devonshire Building | 2017-11-21 17:00 | 51327.2191 | 860.004
Devonshire Building | 2017-11-21 17:15 | 51327.4991 | 1119.996
Devonshire Building | 2017-11-21 17:30 | 51327.6841 | 740.016
Devonshire Building | 2017-11-21 17:45 | 51327.8391 | 619.992
Devonshire Building | 2017-11-21 18:00 | 51327.9641 | 500.004
Devonshire Building | 2017-11-21 18:15 | 51328.0641 | 399.996
Devonshire Building | 2017-11-21 18:30 | 51328.1541 | 360
Devonshire Building | 2017-11-21 18:45 | 51328.2391 | 339.984
Devonshire Building | 2017-11-21 19:00 | 51328.3191 | 320.004
Devonshire Building | 2017-11-21 19:15 | 51328.3891 | 280.008
Devonshire Building | 2017-11-21 19:30 | 51328.4591 | 280.008
Devonshire Building | 2017-11-21 19:45 | 51328.5191 | 240.012
Devonshire Building | 2017-11-21 20:00 | 51328.5941 | 299.988
Devonshire Building | 2017-11-21 20:15 | 51328.6641 | 280.008
Devonshire Building | 2017-11-21 20:30 | 51328.7291 | 259.992
Devonshire Building | 2017-11-21 20:45 | 51328.7891 | 240.012
Devonshire Building | 2017-11-21 21:00 | 51328.8541 | 259.992
Devonshire Building | 2017-11-21 21:15 | 51328.9141 | 240.012
Devonshire Building | 2017-11-21 21:30 | 51328.9741 | 240.012
Devonshire Building | 2017-11-21 21:45 | 51329.0341 | 240.012
Devonshire Building | 2017-11-21 22:00 | 51329.0941 | 240.012
Devonshire Building | 2017-11-21 22:15 | 51329.1491 | 219.996
Devonshire Building | 2017-11-21 22:30 | 51329.1991 | 200.016
Devonshire Building | 2017-11-21 22:45 | 51329.2391 | 159.984
Devonshire Building | 2017-11-21 23:00 | 51329.2841 | 180
Devonshire Building | 2017-11-21 23:15 | 51329.3291 | 180
Devonshire Building | 2017-11-21 23:30 | 51329.3691 | 159.984
Devonshire Building | 2017-11-21 23:45 | 51329.4091 | 159.984
Devonshire Building | 2017-11-22 | 51329.4531 | 180
Devonshire Building | 2017-11-22 00:15 | 51329.4931 | 159.984
Devonshire Building | 2017-11-22 00:30 | 51329.5381 | 180
Devonshire Building | 2017-11-22 00:45 | 51329.5781 | 159.984
Devonshire Building | 2017-11-22 01:00 | 51329.6181 | 159.984
Devonshire Building | 2017-11-22 01:15 | 51329.6631 | 180
Devonshire Building | 2017-11-22 01:30 | 51329.7031 | 159.984
Devonshire Building | 2017-11-22 01:45 | 51329.7431 | 159.984
Devonshire Building | 2017-11-22 02:00 | 51329.7881 | 180
Devonshire Building | 2017-11-22 02:15 | 51329.8281 | 159.984
Devonshire Building | 2017-11-22 02:30 | 51329.8681 | 159.984
Devonshire Building | 2017-11-22 02:45 | 51329.9131 | 180
Devonshire Building | 2017-11-22 03:00 | 51329.9531 | 159.984
Devonshire Building | 2017-11-22 03:15 | 51329.9931 | 159.984
Devonshire Building | 2017-11-22 03:30 | 51330.0331 | 159.984
Devonshire Building | 2017-11-22 03:45 | 51330.0731 | 159.984
Devonshire Building | 2017-11-22 04:00 | 51330.1131 | 159.984
Devonshire Building | 2017-11-22 04:15 | 51330.1531 | 159.984
Devonshire Building | 2017-11-22 04:30 | 51330.1931 | 159.984
Devonshire Building | 2017-11-22 04:45 | 51330.2331 | 159.984
Devonshire Building | 2017-11-22 05:00 | 51330.2731 | 159.984
Devonshire Building | 2017-11-22 05:15 | 51330.3131 | 159.984
Devonshire Building | 2017-11-22 05:30 | 51330.3631 | 200.016
Devonshire Building | 2017-11-22 05:45 | 51330.4231 | 240.012
Devonshire Building | 2017-11-22 06:00 | 51330.4781 | 219.996
Devonshire Building | 2017-11-22 06:15 | 51330.5181 | 159.984
Devonshire Building | 2017-11-22 06:30 | 51330.5531 | 140.004
Devonshire Building | 2017-11-22 06:45 | 51330.5931 | 159.984
Devonshire Building | 2017-11-22 07:00 | 51330.6331 | 159.984
Devonshire Building | 2017-11-22 07:15 | 51330.6731 | 159.984
Devonshire Building | 2017-11-22 07:30 | 51330.7181 | 180
Devonshire Building | 2017-11-22 07:45 | 51330.8181 | 399.996
Devonshire Building | 2017-11-22 08:00 | 51330.903 | 339.984
Devonshire Building | 2017-11-22 08:15 | 51330.9631 | 240.012
Devonshire Building | 2017-11-22 08:30 | 51331.0581 | 380.016
Devonshire Building | 2017-11-22 08:45 | 51331.1331 | 299.988
Devonshire Building | 2017-11-22 09:00 | 51331.243 | 439.992
Devonshire Building | 2017-11-22 09:15 | 51331.4131 | 680.004
Devonshire Building | 2017-11-22 09:30 | 51331.5281 | 460.008
Devonshire Building | 2017-11-22 09:45 | 51331.6681 | 560.016
Devonshire Building | 2017-11-22 10:00 | 51331.8081 | 560.016
Devonshire Building | 2017-11-22 10:15 | 51331.9631 | 619.992
Devonshire Building | 2017-11-22 10:30 | 51332.1381 | 699.984
Devonshire Building | 2017-11-22 10:45 | 51332.2631 | 500.004
Devonshire Building | 2017-11-22 11:00 | 51332.4431 | 720
Devonshire Building | 2017-11-22 11:15 | 51332.7881 | 1379.988
Devonshire Building | 2017-11-22 11:30 | 51333.0231 | 939.996
Devonshire Building | 2017-11-22 11:45 | 51333.2131 | 759.996
Devonshire Building | 2017-11-22 12:00 | 51333.493 | 1119.996
Devonshire Building | 2017-11-22 12:15 | 51333.7081 | 860.004
Devonshire Building | 2017-11-22 12:30 | 51333.873 | 659.988
Devonshire Building | 2017-11-22 12:45 | 51334.063 | 759.996
Devonshire Building | 2017-11-22 13:00 | 51334.213 | 600.012
Devonshire Building | 2017-11-22 13:15 | 51334.3831 | 680.004
Devonshire Building | 2017-11-22 13:30 | 51334.5281 | 579.996
Devonshire Building | 2017-11-22 13:45 | 51334.6881 | 640.008
Devonshire Building | 2017-11-22 14:00 | 51334.8031 | 460.008
Devonshire Building | 2017-11-22 14:15 | 51335.0281 | 900
Devonshire Building | 2017-11-22 14:30 | 51335.2631 | 939.996
Devonshire Building | 2017-11-22 14:45 | 51335.5231 | 1040.004
Devonshire Building | 2017-11-22 15:00 | 51335.7631 | 960.012
Devonshire Building | 2017-11-22 15:15 | 51336.0331 | 1080
Devonshire Building | 2017-11-22 15:30 | 51336.2381 | 820.008
Devonshire Building | 2017-11-22 15:45 | 51336.4281 | 759.996
Devonshire Building | 2017-11-22 16:00 | 51336.6781 | 1000.008
Devonshire Building | 2017-11-22 16:15 | 51336.8381 | 640.008
Devonshire Building | 2017-11-22 16:30 | 51336.9981 | 640.008
Devonshire Building | 2017-11-22 16:45 | 51337.1781 | 720
Devonshire Building | 2017-11-22 17:00 | 51337.3831 | 820.008
Devonshire Building | 2017-11-22 17:15 | 51337.5831 | 799.992
Devonshire Building | 2017-11-22 17:30 | 51337.7881 | 820.008
Devonshire Building | 2017-11-22 17:45 | 51338.0331 | 979.992
Devonshire Building | 2017-11-22 18:00 | 51338.3031 | 1080
Devonshire Building | 2017-11-22 18:15 | 51338.5581 | 1019.988
Devonshire Building | 2017-11-22 18:30 | 51338.7981 | 960.012
Devonshire Building | 2017-11-22 18:45 | 51339.0281 | 920.016
Devonshire Building | 2017-11-22 19:00 | 51339.2481 | 879.984
Devonshire Building | 2017-11-22 19:15 | 51339.4681 | 879.984
Devonshire Building | 2017-11-22 19:30 | 51339.6881 | 879.984
Devonshire Building | 2017-11-22 19:45 | 51339.8981 | 839.988
Devonshire Building | 2017-11-22 20:00 | 51340.118 | 879.984
Devonshire Building | 2017-11-22 20:15 | 51340.263 | 579.996
Devonshire Building | 2017-11-22 20:30 | 51340.303 | 159.984
Devonshire Building | 2017-11-22 20:45 | 51340.343 | 159.984
Devonshire Building | 2017-11-22 21:00 | 51340.383 | 159.984
Devonshire Building | 2017-11-22 21:15 | 51340.428 | 180
Devonshire Building | 2017-11-22 21:30 | 51340.468 | 159.984
Devonshire Building | 2017-11-22 21:45 | 51340.513 | 180
Devonshire Building | 2017-11-22 22:00 | 51340.548 | 140.004
Devonshire Building | 2017-11-22 22:15 | 51340.588 | 159.984
Devonshire Building | 2017-11-22 22:30 | 51340.628 | 159.984
Devonshire Building | 2017-11-22 22:45 | 51340.663 | 140.004
Devonshire Building | 2017-11-22 23:00 | 51340.703 | 159.984
Devonshire Building | 2017-11-22 23:15 | 51340.738 | 140.004
Devonshire Building | 2017-11-22 23:30 | 51340.778 | 159.984
Devonshire Building | 2017-11-22 23:45 | 51340.813 | 140.004
Devonshire Building | 2017-11-23 | 51340.8516 | 140.004
Devonshire Building | 2017-11-23 00:15 | 51340.8916 | 159.984
Devonshire Building | 2017-11-23 00:30 | 51340.9266 | 140.004
Devonshire Building | 2017-11-23 00:45 | 51340.9616 | 140.004
Devonshire Building | 2017-11-23 01:00 | 51341.0016 | 159.984
Devonshire Building | 2017-11-23 01:15 | 51341.0366 | 140.004
Devonshire Building | 2017-11-23 01:30 | 51341.0716 | 140.004
Devonshire Building | 2017-11-23 01:45 | 51341.1116 | 159.984
Devonshire Building | 2017-11-23 02:00 | 51341.1466 | 140.004
Devonshire Building | 2017-11-23 02:15 | 51341.1816 | 140.004
Devonshire Building | 2017-11-23 02:30 | 51341.2166 | 140.004
Devonshire Building | 2017-11-23 02:45 | 51341.2566 | 159.984
Devonshire Building | 2017-11-23 03:00 | 51341.2916 | 140.004
Devonshire Building | 2017-11-23 03:15 | 51341.3266 | 140.004
Devonshire Building | 2017-11-23 03:30 | 51341.3616 | 140.004
Devonshire Building | 2017-11-23 03:45 | 51341.3966 | 140.004
Devonshire Building | 2017-11-23 04:00 | 51341.4366 | 159.984
Devonshire Building | 2017-11-23 04:15 | 51341.4716 | 140.004
Devonshire Building | 2017-11-23 04:30 | 51341.5166 | 180
Devonshire Building | 2017-11-23 04:45 | 51341.5716 | 219.996
Devonshire Building | 2017-11-23 05:00 | 51341.6166 | 180
Devonshire Building | 2017-11-23 05:15 | 51341.6516 | 140.004
Devonshire Building | 2017-11-23 05:30 | 51341.6866 | 140.004
Devonshire Building | 2017-11-23 05:45 | 51341.7216 | 140.004
Devonshire Building | 2017-11-23 06:00 | 51341.7616 | 159.984
Devonshire Building | 2017-11-23 06:15 | 51341.7966 | 140.004
Devonshire Building | 2017-11-23 06:30 | 51341.8316 | 140.004
Devonshire Building | 2017-11-23 06:45 | 51341.8715 | 159.984
Devonshire Building | 2017-11-23 07:00 | 51341.9065 | 140.004
Devonshire Building | 2017-11-23 07:15 | 51341.9416 | 140.004
Devonshire Building | 2017-11-23 07:30 | 51342.0265 | 339.984
Devonshire Building | 2017-11-23 07:45 | 51342.0965 | 280.008
Devonshire Building | 2017-11-23 08:00 | 51342.1815 | 339.984
Devonshire Building | 2017-11-23 08:15 | 51342.2315 | 200.016
Devonshire Building | 2017-11-23 08:30 | 51342.3165 | 339.984
Devonshire Building | 2017-11-23 08:45 | 51342.3865 | 280.008
Devonshire Building | 2017-11-23 09:00 | 51342.4665 | 320.004
Devonshire Building | 2017-11-23 09:15 | 51342.5915 | 500.004
Devonshire Building | 2017-11-23 09:30 | 51342.6715 | 320.004
Devonshire Building | 2017-11-23 09:45 | 51342.8015 | 519.984
Devonshire Building | 2017-11-23 10:00 | 51342.9315 | 519.984
Devonshire Building | 2017-11-23 10:15 | 51343.0915 | 640.008
Devonshire Building | 2017-11-23 10:30 | 51343.2665 | 699.984
Devonshire Building | 2017-11-23 10:45 | 51343.5115 | 979.992
Devonshire Building | 2017-11-23 11:00 | 51343.7065 | 780.012
Devonshire Building | 2017-11-23 11:15 | 51343.8565 | 600.012
Devonshire Building | 2017-11-23 11:30 | 51344.1265 | 1080
Devonshire Building | 2017-11-23 11:45 | 51344.3715 | 979.992
Devonshire Building | 2017-11-23 12:00 | 51344.5915 | 879.984
Devonshire Building | 2017-11-23 12:15 | 51344.8465 | 1019.988
Devonshire Building | 2017-11-23 12:30 | 51345.0915 | 979.992
Devonshire Building | 2017-11-23 12:45 | 51345.3215 | 920.016
Devonshire Building | 2017-11-23 13:00 | 51345.5915 | 1080
Devonshire Building | 2017-11-23 13:15 | 51345.8565 | 1059.984
Devonshire Building | 2017-11-23 13:30 | 51346.0915 | 939.996
Devonshire Building | 2017-11-23 13:45 | 51346.2915 | 799.992
Devonshire Building | 2017-11-23 14:00 | 51346.4815 | 759.996
Devonshire Building | 2017-11-23 14:15 | 51346.6715 | 759.996
Devonshire Building | 2017-11-23 14:30 | 51346.8315 | 640.008
Devonshire Building | 2017-11-23 14:45 | 51347.0165 | 740.016
Devonshire Building | 2017-11-23 15:00 | 51347.1965 | 720
Devonshire Building | 2017-11-23 15:15 | 51347.4115 | 860.004
Devonshire Building | 2017-11-23 15:30 | 51347.5615 | 600.012
Devonshire Building | 2017-11-23 15:45 | 51347.6915 | 519.984
Devonshire Building | 2017-11-23 16:00 | 51347.8165 | 500.004
Devonshire Building | 2017-11-23 16:15 | 51347.9515 | 540
Devonshire Building | 2017-11-23 16:30 | 51348.1315 | 720
Devonshire Building | 2017-11-23 16:45 | 51348.2915 | 640.008
Devonshire Building | 2017-11-23 17:00 | 51348.4515 | 640.008
Devonshire Building | 2017-11-23 17:15 | 51348.7115 | 1040.004
Devonshire Building | 2017-11-23 17:30 | 51348.9365 | 900
Devonshire Building | 2017-11-23 17:45 | 51349.1465 | 839.988
Devonshire Building | 2017-11-23 18:00 | 51349.3065 | 640.008
Devonshire Building | 2017-11-23 18:15 | 51349.4365 | 519.984
Devonshire Building | 2017-11-23 18:30 | 51349.5215 | 339.984
Devonshire Building | 2017-11-23 18:45 | 51349.5965 | 299.988
Devonshire Building | 2017-11-23 19:00 | 51349.6615 | 259.992
Devonshire Building | 2017-11-23 19:15 | 51349.7215 | 240.012
Devonshire Building | 2017-11-23 19:30 | 51349.7765 | 219.996
Devonshire Building | 2017-11-23 19:45 | 51349.8565 | 320.004
Devonshire Building | 2017-11-23 20:00 | 51349.9165 | 240.012
Devonshire Building | 2017-11-23 20:15 | 51349.9615 | 180
Devonshire Building | 2017-11-23 20:30 | 51350.0165 | 219.996
Devonshire Building | 2017-11-23 20:45 | 51350.0715 | 219.996
Devonshire Building | 2017-11-23 21:00 | 51350.1165 | 180
Devonshire Building | 2017-11-23 21:15 | 51350.1665 | 200.016
Devonshire Building | 2017-11-23 21:30 | 51350.2115 | 180
Devonshire Building | 2017-11-23 21:45 | 51350.2565 | 180
Devonshire Building | 2017-11-23 22:00 | 51350.2965 | 159.984
Devonshire Building | 2017-11-23 22:15 | 51350.3465 | 200.016
Devonshire Building | 2017-11-23 22:30 | 51350.3915 | 180
Devonshire Building | 2017-11-23 22:45 | 51350.4315 | 159.984
Devonshire Building | 2017-11-23 23:00 | 51350.4715 | 159.984
Devonshire Building | 2017-11-23 23:15 | 51350.5165 | 180
Devonshire Building | 2017-11-23 23:30 | 51350.5565 | 159.984
Devonshire Building | 2017-11-23 23:45 | 51350.6015 | 180
Devonshire Building | 2017-11-24 | 51350.6406 | 159.984
Devonshire Building | 2017-11-24 00:15 | 51350.6806 | 159.984
Devonshire Building | 2017-11-24 00:30 | 51350.7256 | 180
Devonshire Building | 2017-11-24 00:45 | 51350.7656 | 159.984
Devonshire Building | 2017-11-24 01:00 | 51350.8056 | 159.984
Devonshire Building | 2017-11-24 01:15 | 51350.8506 | 180
Devonshire Building | 2017-11-24 01:30 | 51350.8906 | 159.984
Devonshire Building | 2017-11-24 01:45 | 51350.9306 | 159.984
Devonshire Building | 2017-11-24 02:00 | 51350.9706 | 159.984
Devonshire Building | 2017-11-24 02:15 | 51351.0156 | 180
Devonshire Building | 2017-11-24 02:30 | 51351.0556 | 159.984
Devonshire Building | 2017-11-24 02:45 | 51351.0956 | 159.984
Devonshire Building | 2017-11-24 03:00 | 51351.1356 | 159.984
Devonshire Building | 2017-11-24 03:15 | 51351.1756 | 159.984
Devonshire Building | 2017-11-24 03:30 | 51351.2206 | 180
Devonshire Building | 2017-11-24 03:45 | 51351.2606 | 159.984
Devonshire Building | 2017-11-24 04:00 | 51351.3006 | 159.984
Devonshire Building | 2017-11-24 04:15 | 51351.3406 | 159.984
Devonshire Building | 2017-11-24 04:30 | 51351.3806 | 159.984
Devonshire Building | 2017-11-24 04:45 | 51351.4206 | 159.984
Devonshire Building | 2017-11-24 05:00 | 51351.4606 | 159.984
Devonshire Building | 2017-11-24 05:15 | 51351.5006 | 159.984
Devonshire Building | 2017-11-24 05:30 | 51351.5556 | 219.996
Devonshire Building | 2017-11-24 05:45 | 51351.6156 | 240.012
Devonshire Building | 2017-11-24 06:00 | 51351.6606 | 180
Devonshire Building | 2017-11-24 06:15 | 51351.7006 | 159.984
Devonshire Building | 2017-11-24 06:30 | 51351.7406 | 159.984
Devonshire Building | 2017-11-24 06:45 | 51351.7806 | 159.984
Devonshire Building | 2017-11-24 07:00 | 51351.8205 | 159.984
Devonshire Building | 2017-11-24 07:15 | 51351.8605 | 159.984
Devonshire Building | 2017-11-24 07:30 | 51351.9105 | 200.016
Devonshire Building | 2017-11-24 07:45 | 51351.9905 | 320.004
Devonshire Building | 2017-11-24 08:00 | 51352.0755 | 339.984
Devonshire Building | 2017-11-24 08:15 | 51352.1255 | 200.016
Devonshire Building | 2017-11-24 08:30 | 51352.1956 | 280.008
Devonshire Building | 2017-11-24 08:45 | 51352.2956 | 399.996
Devonshire Building | 2017-11-24 09:00 | 51352.3955 | 399.996
Devonshire Building | 2017-11-24 09:15 | 51352.5055 | 439.992
Devonshire Building | 2017-11-24 09:30 | 51352.5905 | 339.984
Devonshire Building | 2017-11-24 09:45 | 51352.7355 | 579.996
Devonshire Building | 2017-11-24 10:00 | 51352.8455 | 439.992
Devonshire Building | 2017-11-24 10:15 | 51352.9755 | 519.984
Devonshire Building | 2017-11-24 10:30 | 51353.1055 | 519.984
Devonshire Building | 2017-11-24 10:45 | 51353.3005 | 780.012
Devonshire Building | 2017-11-24 11:00 | 51353.4805 | 720
Devonshire Building | 2017-11-24 11:15 | 51353.6605 | 720
Devonshire Building | 2017-11-24 11:30 | 51353.9105 | 1000.008
Devonshire Building | 2017-11-24 11:45 | 51354.1305 | 879.984
Devonshire Building | 2017-11-24 12:00 | 51354.4055 | 1100.016
Devonshire Building | 2017-11-24 12:15 | 51354.6455 | 960.012
Devonshire Building | 2017-11-24 12:30 | 51354.8305 | 740.016
Devonshire Building | 2017-11-24 12:45 | 51354.9955 | 659.988
Devonshire Building | 2017-11-24 13:00 | 51355.1705 | 699.984
Devonshire Building | 2017-11-24 13:15 | 51355.3255 | 619.992
Devonshire Building | 2017-11-24 13:30 | 51355.4655 | 560.016
Devonshire Building | 2017-11-24 13:45 | 51355.6255 | 640.008
Devonshire Building | 2017-11-24 14:00 | 51355.7505 | 500.004
Devonshire Building | 2017-11-24 14:15 | 51355.8955 | 579.996
Devonshire Building | 2017-11-24 14:30 | 51356.0205 | 500.004
Devonshire Building | 2017-11-24 14:45 | 51356.1055 | 339.984
Devonshire Building | 2017-11-24 15:00 | 51356.1955 | 360
Devonshire Building | 2017-11-24 15:15 | 51356.3255 | 519.984
Devonshire Building | 2017-11-24 15:30 | 51356.4305 | 420.012
Devonshire Building | 2017-11-24 15:45 | 51356.5605 | 519.984
Devonshire Building | 2017-11-24 16:00 | 51356.7155 | 619.992
Devonshire Building | 2017-11-24 16:15 | 51356.8805 | 659.988
Devonshire Building | 2017-11-24 16:30 | 51357.0405 | 640.008
Devonshire Building | 2017-11-24 16:45 | 51357.1755 | 540
Devonshire Building | 2017-11-24 17:00 | 51357.3305 | 619.992
Devonshire Building | 2017-11-24 17:15 | 51357.4455 | 460.008
Devonshire Building | 2017-11-24 17:30 | 51357.5705 | 500.004
Devonshire Building | 2017-11-24 17:45 | 51357.6755 | 420.012
Devonshire Building | 2017-11-24 18:00 | 51357.8005 | 500.004
Devonshire Building | 2017-11-24 18:15 | 51357.9055 | 420.012
Devonshire Building | 2017-11-24 18:30 | 51357.9955 | 360
Devonshire Building | 2017-11-24 18:45 | 51358.0505 | 219.996
Devonshire Building | 2017-11-24 19:00 | 51358.1105 | 240.012
Devonshire Building | 2017-11-24 19:15 | 51358.1605 | 200.016
Devonshire Building | 2017-11-24 19:30 | 51358.2155 | 219.996
Devonshire Building | 2017-11-24 19:45 | 51358.2655 | 200.016
Devonshire Building | 2017-11-24 20:00 | 51358.3105 | 180
Devonshire Building | 2017-11-24 20:15 | 51358.3555 | 180
Devonshire Building | 2017-11-24 20:30 | 51358.4005 | 180
Devonshire Building | 2017-11-24 20:45 | 51358.4455 | 180
Devonshire Building | 2017-11-24 21:00 | 51358.4855 | 159.984
Devonshire Building | 2017-11-24 21:15 | 51358.5305 | 180
Devonshire Building | 2017-11-24 21:30 | 51358.5705 | 159.984
Devonshire Building | 2017-11-24 21:45 | 51358.6105 | 159.984
Devonshire Building | 2017-11-24 22:00 | 51358.6505 | 159.984
Devonshire Building | 2017-11-24 22:15 | 51358.6905 | 159.984
Devonshire Building | 2017-11-24 22:30 | 51358.7305 | 159.984
Devonshire Building | 2017-11-24 22:45 | 51358.7705 | 159.984
Devonshire Building | 2017-11-24 23:00 | 51358.8105 | 159.984
Devonshire Building | 2017-11-24 23:15 | 51358.8505 | 159.984
Devonshire Building | 2017-11-24 23:30 | 51358.8905 | 159.984
Devonshire Building | 2017-11-24 23:45 | 51358.9255 | 140.004
Devonshire Building | 2017-11-25 | 51358.9648 | 159.984
Devonshire Building | 2017-11-25 00:15 | 51359.0048 | 159.984
Devonshire Building | 2017-11-25 00:30 | 51359.0448 | 159.984
Devonshire Building | 2017-11-25 00:45 | 51359.0798 | 140.004
Devonshire Building | 2017-11-25 01:00 | 51359.1198 | 159.984
Devonshire Building | 2017-11-25 01:15 | 51359.1598 | 159.984
Devonshire Building | 2017-11-25 01:30 | 51359.1948 | 140.004
Devonshire Building | 2017-11-25 01:45 | 51359.2348 | 159.984
Devonshire Building | 2017-11-25 02:00 | 51359.2748 | 159.984
Devonshire Building | 2017-11-25 02:15 | 51359.3098 | 140.004
Devonshire Building | 2017-11-25 02:30 | 51359.3498 | 159.984
Devonshire Building | 2017-11-25 02:45 | 51359.3848 | 140.004
Devonshire Building | 2017-11-25 03:00 | 51359.4248 | 159.984
Devonshire Building | 2017-11-25 03:15 | 51359.4648 | 159.984
Devonshire Building | 2017-11-25 03:30 | 51359.4998 | 140.004
Devonshire Building | 2017-11-25 03:45 | 51359.5398 | 159.984
Devonshire Building | 2017-11-25 04:00 | 51359.5748 | 140.004
Devonshire Building | 2017-11-25 04:15 | 51359.6148 | 159.984
Devonshire Building | 2017-11-25 04:30 | 51359.6498 | 140.004
Devonshire Building | 2017-11-25 04:45 | 51359.6898 | 159.984
Devonshire Building | 2017-11-25 05:00 | 51359.7248 | 140.004
Devonshire Building | 2017-11-25 05:15 | 51359.7648 | 159.984
Devonshire Building | 2017-11-25 05:30 | 51359.7998 | 140.004
Devonshire Building | 2017-11-25 05:45 | 51359.8398 | 159.984
Devonshire Building | 2017-11-25 06:00 | 51359.8748 | 140.004
Devonshire Building | 2017-11-25 06:15 | 51359.9098 | 140.004
Devonshire Building | 2017-11-25 06:30 | 51359.9648 | 219.996
Devonshire Building | 2017-11-25 06:45 | 51360.0198 | 219.996
Devonshire Building | 2017-11-25 07:00 | 51360.0548 | 140.004
Devonshire Building | 2017-11-25 07:15 | 51360.0898 | 140.004
Devonshire Building | 2017-11-25 07:30 | 51360.1248 | 140.004
Devonshire Building | 2017-11-25 07:45 | 51360.1598 | 140.004
Devonshire Building | 2017-11-25 08:00 | 51360.1998 | 159.984
Devonshire Building | 2017-11-25 08:15 | 51360.2498 | 200.016
Devonshire Building | 2017-11-25 08:30 | 51360.2998 | 200.016
Devonshire Building | 2017-11-25 08:45 | 51360.3498 | 200.016
Devonshire Building | 2017-11-25 09:00 | 51360.3998 | 200.016
Devonshire Building | 2017-11-25 09:15 | 51360.4498 | 200.016
Devonshire Building | 2017-11-25 09:30 | 51360.4948 | 180
Devonshire Building | 2017-11-25 09:45 | 51360.5448 | 200.016
Devonshire Building | 2017-11-25 10:00 | 51360.5948 | 200.016
Devonshire Building | 2017-11-25 10:15 | 51360.6448 | 200.016
Devonshire Building | 2017-11-25 10:30 | 51360.6948 | 200.016
Devonshire Building | 2017-11-25 10:45 | 51360.7498 | 219.996
Devonshire Building | 2017-11-25 11:00 | 51360.8148 | 259.992
Devonshire Building | 2017-11-25 11:15 | 51360.8948 | 320.004
Devonshire Building | 2017-11-25 11:30 | 51360.9298 | 140.004
Devonshire Building | 2017-11-25 11:45 | 51360.9648 | 140.004
Devonshire Building | 2017-11-25 12:00 | 51361.0048 | 159.984
Devonshire Building | 2017-11-25 12:15 | 51361.0498 | 180
Devonshire Building | 2017-11-25 12:30 | 51361.0898 | 159.984
Devonshire Building | 2017-11-25 12:45 | 51361.1898 | 399.996
Devonshire Building | 2017-11-25 13:00 | 51361.2248 | 140.004
Devonshire Building | 2017-11-25 13:15 | 51361.2598 | 140.004
Devonshire Building | 2017-11-25 13:30 | 51361.3998 | 560.016
Devonshire Building | 2017-11-25 13:45 | 51361.5398 | 560.016
Devonshire Building | 2017-11-25 14:00 | 51361.5898 | 200.016
Devonshire Building | 2017-11-25 14:15 | 51361.6198 | 119.988
Devonshire Building | 2017-11-25 14:30 | 51361.6748 | 219.996
Devonshire Building | 2017-11-25 14:45 | 51361.7098 | 140.004
Devonshire Building | 2017-11-25 15:00 | 51361.7598 | 200.016
Devonshire Building | 2017-11-25 15:15 | 51361.7998 | 159.984
Devonshire Building | 2017-11-25 15:30 | 51361.9398 | 560.016
Devonshire Building | 2017-11-25 15:45 | 51361.9898 | 200.016
Devonshire Building | 2017-11-25 16:00 | 51362.0598 | 280.008
Devonshire Building | 2017-11-25 16:15 | 51362.0948 | 140.004
Devonshire Building | 2017-11-25 16:30 | 51362.1298 | 140.004
Devonshire Building | 2017-11-25 16:45 | 51362.1848 | 219.996
Devonshire Building | 2017-11-25 17:00 | 51362.2198 | 140.004
Devonshire Building | 2017-11-25 17:15 | 51362.2648 | 180
Devonshire Building | 2017-11-25 17:30 | 51362.2998 | 140.004
Devonshire Building | 2017-11-25 17:45 | 51362.3348 | 140.004
Devonshire Building | 2017-11-25 18:00 | 51362.3698 | 140.004
Devonshire Building | 2017-11-25 18:15 | 51362.4048 | 140.004
Devonshire Building | 2017-11-25 18:30 | 51362.4348 | 119.988
Devonshire Building | 2017-11-25 18:45 | 51362.4698 | 140.004
Devonshire Building | 2017-11-25 19:00 | 51362.5048 | 140.004
Devonshire Building | 2017-11-25 19:15 | 51362.5398 | 140.004
Devonshire Building | 2017-11-25 19:30 | 51362.5698 | 119.988
Devonshire Building | 2017-11-25 19:45 | 51362.6048 | 140.004
Devonshire Building | 2017-11-25 20:00 | 51362.6398 | 140.004
Devonshire Building | 2017-11-25 20:15 | 51362.6748 | 140.004
Devonshire Building | 2017-11-25 20:30 | 51362.7098 | 140.004
Devonshire Building | 2017-11-25 20:45 | 51362.7398 | 119.988
Devonshire Building | 2017-11-25 21:00 | 51362.7748 | 140.004
Devonshire Building | 2017-11-25 21:15 | 51362.8098 | 140.004
Devonshire Building | 2017-11-25 21:30 | 51362.8448 | 140.004
Devonshire Building | 2017-11-25 21:45 | 51362.8798 | 140.004
Devonshire Building | 2017-11-25 22:00 | 51362.9098 | 119.988
Devonshire Building | 2017-11-25 22:15 | 51362.9448 | 140.004
Devonshire Building | 2017-11-25 22:30 | 51362.9798 | 140.004
Devonshire Building | 2017-11-25 22:45 | 51363.0148 | 140.004
Devonshire Building | 2017-11-25 23:00 | 51363.0499 | 140.004
Devonshire Building | 2017-11-25 23:15 | 51363.0849 | 140.004
Devonshire Building | 2017-11-25 23:30 | 51363.1199 | 140.004
Devonshire Building | 2017-11-25 23:45 | 51363.1549 | 140.004
Devonshire Building | 2017-11-26 | 51363.1875 | 140.004
Devonshire Building | 2017-11-26 00:15 | 51363.2275 | 159.984
Devonshire Building | 2017-11-26 00:30 | 51363.2625 | 140.004
Devonshire Building | 2017-11-26 00:45 | 51363.2975 | 140.004
Devonshire Building | 2017-11-26 01:00 | 51363.3325 | 140.004
Devonshire Building | 2017-11-26 01:15 | 51363.3725 | 159.984
Devonshire Building | 2017-11-26 01:30 | 51363.4075 | 140.004
Devonshire Building | 2017-11-26 01:45 | 51363.4425 | 140.004
Devonshire Building | 2017-11-26 02:00 | 51363.5025 | 240.012
Devonshire Building | 2017-11-26 02:15 | 51363.5575 | 219.996
Devonshire Building | 2017-11-26 02:30 | 51363.5975 | 159.984
Devonshire Building | 2017-11-26 02:45 | 51363.6375 | 159.984
Devonshire Building | 2017-11-26 03:00 | 51363.6725 | 140.004
Devonshire Building | 2017-11-26 03:15 | 51363.7125 | 159.984
Devonshire Building | 2017-11-26 03:30 | 51363.7475 | 140.004
Devonshire Building | 2017-11-26 03:45 | 51363.7875 | 159.984
Devonshire Building | 2017-11-26 04:00 | 51363.8275 | 159.984
Devonshire Building | 2017-11-26 04:15 | 51363.8625 | 140.004
Devonshire Building | 2017-11-26 04:30 | 51363.9025 | 159.984
Devonshire Building | 2017-11-26 04:45 | 51363.9375 | 140.004
Devonshire Building | 2017-11-26 05:00 | 51363.9775 | 159.984
Devonshire Building | 2017-11-26 05:15 | 51364.0175 | 159.984
Devonshire Building | 2017-11-26 05:30 | 51364.0525 | 140.004
Devonshire Building | 2017-11-26 05:45 | 51364.0925 | 159.984
Devonshire Building | 2017-11-26 06:00 | 51364.1325 | 159.984
Devonshire Building | 2017-11-26 06:15 | 51364.1675 | 140.004
Devonshire Building | 2017-11-26 06:30 | 51364.2075 | 159.984
Devonshire Building | 2017-11-26 06:45 | 51364.2425 | 140.004
Devonshire Building | 2017-11-26 07:00 | 51364.2825 | 159.984
Devonshire Building | 2017-11-26 07:15 | 51364.3175 | 140.004
Devonshire Building | 2017-11-26 07:30 | 51364.3575 | 159.984
Devonshire Building | 2017-11-26 07:45 | 51364.4025 | 180
Devonshire Building | 2017-11-26 08:00 | 51364.4525 | 200.016
Devonshire Building | 2017-11-26 08:15 | 51364.5025 | 200.016
Devonshire Building | 2017-11-26 08:30 | 51364.5575 | 219.996
Devonshire Building | 2017-11-26 08:45 | 51364.6075 | 200.016
Devonshire Building | 2017-11-26 09:00 | 51364.6575 | 200.016
Devonshire Building | 2017-11-26 09:15 | 51364.7075 | 200.016
Devonshire Building | 2017-11-26 09:30 | 51364.7625 | 219.996
Devonshire Building | 2017-11-26 09:45 | 51364.8125 | 200.016
Devonshire Building | 2017-11-26 10:00 | 51364.8625 | 200.016
Devonshire Building | 2017-11-26 10:15 | 51364.9175 | 219.996
Devonshire Building | 2017-11-26 10:30 | 51364.9675 | 200.016
Devonshire Building | 2017-11-26 10:45 | 51365.0175 | 200.016
Devonshire Building | 2017-11-26 11:00 | 51365.0725 | 219.996
Devonshire Building | 2017-11-26 11:15 | 51365.1125 | 159.984
Devonshire Building | 2017-11-26 11:30 | 51365.1825 | 280.008
Devonshire Building | 2017-11-26 11:45 | 51365.2275 | 180
Devonshire Building | 2017-11-26 12:00 | 51365.2625 | 140.004
Devonshire Building | 2017-11-26 12:15 | 51365.3075 | 180
Devonshire Building | 2017-11-26 12:30 | 51365.3475 | 159.984
Devonshire Building | 2017-11-26 12:45 | 51365.3925 | 180
Devonshire Building | 2017-11-26 13:00 | 51365.4325 | 159.984
Devonshire Building | 2017-11-26 13:15 | 51365.4725 | 159.984
Devonshire Building | 2017-11-26 13:30 | 51365.5125 | 159.984
Devonshire Building | 2017-11-26 13:45 | 51365.5675 | 219.996
Devonshire Building | 2017-11-26 14:00 | 51365.6175 | 200.016
Devonshire Building | 2017-11-26 14:15 | 51365.6675 | 200.016
Devonshire Building | 2017-11-26 14:30 | 51365.7375 | 280.008
Devonshire Building | 2017-11-26 14:45 | 51365.8175 | 320.004
Devonshire Building | 2017-11-26 15:00 | 51365.8675 | 200.016
Devonshire Building | 2017-11-26 15:15 | 51365.9125 | 180
Devonshire Building | 2017-11-26 15:30 | 51365.9825 | 280.008
Devonshire Building | 2017-11-26 15:45 | 51366.0325 | 200.016
Devonshire Building | 2017-11-26 16:00 | 51366.0825 | 200.016
Devonshire Building | 2017-11-26 16:15 | 51366.1275 | 180
Devonshire Building | 2017-11-26 16:30 | 51366.1675 | 159.984
Devonshire Building | 2017-11-26 16:45 | 51366.2125 | 180
Devonshire Building | 2017-11-26 17:00 | 51366.2875 | 299.988
Devonshire Building | 2017-11-26 17:15 | 51366.3375 | 200.016
Devonshire Building | 2017-11-26 17:30 | 51366.3825 | 180
Devonshire Building | 2017-11-26 17:45 | 51366.4275 | 180
Devonshire Building | 2017-11-26 18:00 | 51366.4675 | 159.984
Devonshire Building | 2017-11-26 18:15 | 51366.5125 | 180
Devonshire Building | 2017-11-26 18:30 | 51366.5575 | 180
Devonshire Building | 2017-11-26 18:45 | 51366.5975 | 159.984
Devonshire Building | 2017-11-26 19:00 | 51366.6425 | 180
Devonshire Building | 2017-11-26 19:15 | 51366.6925 | 200.016
Devonshire Building | 2017-11-26 19:30 | 51366.7575 | 259.992
Devonshire Building | 2017-11-26 19:45 | 51366.7975 | 159.984
Devonshire Building | 2017-11-26 20:00 | 51366.8425 | 180
Devonshire Building | 2017-11-26 20:15 | 51366.8825 | 159.984
Devonshire Building | 2017-11-26 20:30 | 51366.9275 | 180
Devonshire Building | 2017-11-26 20:45 | 51366.9675 | 159.984
Devonshire Building | 2017-11-26 21:00 | 51367.0125 | 180
Devonshire Building | 2017-11-26 21:15 | 51367.0525 | 159.984
Devonshire Building | 2017-11-26 21:30 | 51367.0975 | 180
Devonshire Building | 2017-11-26 21:45 | 51367.1375 | 159.984
Devonshire Building | 2017-11-26 22:00 | 51367.1775 | 159.984
Devonshire Building | 2017-11-26 22:15 | 51367.2225 | 180
Devonshire Building | 2017-11-26 22:30 | 51367.2625 | 159.984
Devonshire Building | 2017-11-26 22:45 | 51367.3075 | 180
Devonshire Building | 2017-11-26 23:00 | 51367.3475 | 159.984
Devonshire Building | 2017-11-26 23:15 | 51367.3874 | 159.984
Devonshire Building | 2017-11-26 23:30 | 51367.4324 | 180
Devonshire Building | 2017-11-26 23:45 | 51367.4724 | 159.984
Devonshire Building | 2017-11-27 | 51367.5156 | 159.984
Devonshire Building | 2017-11-27 00:15 | 51367.5556 | 159.984
Devonshire Building | 2017-11-27 00:30 | 51367.6006 | 180
Devonshire Building | 2017-11-27 00:45 | 51367.6406 | 159.984
Devonshire Building | 2017-11-27 01:00 | 51367.6806 | 159.984
Devonshire Building | 2017-11-27 01:15 | 51367.7256 | 180
Devonshire Building | 2017-11-27 01:30 | 51367.7656 | 159.984
Devonshire Building | 2017-11-27 01:45 | 51367.8056 | 159.984
Devonshire Building | 2017-11-27 02:00 | 51367.8456 | 159.984
Devonshire Building | 2017-11-27 02:15 | 51367.8906 | 180
Devonshire Building | 2017-11-27 02:30 | 51367.9306 | 159.984
Devonshire Building | 2017-11-27 02:45 | 51367.9706 | 159.984
Devonshire Building | 2017-11-27 03:00 | 51368.0256 | 219.996
Devonshire Building | 2017-11-27 03:15 | 51368.0856 | 240.012
Devonshire Building | 2017-11-27 03:30 | 51368.1406 | 219.996
Devonshire Building | 2017-11-27 03:45 | 51368.1806 | 159.984
Devonshire Building | 2017-11-27 04:00 | 51368.2206 | 159.984
Devonshire Building | 2017-11-27 04:15 | 51368.2606 | 159.984
Devonshire Building | 2017-11-27 04:30 | 51368.3106 | 200.016
Devonshire Building | 2017-11-27 04:45 | 51368.3556 | 180
Devonshire Building | 2017-11-27 05:00 | 51368.3956 | 159.984
Devonshire Building | 2017-11-27 05:15 | 51368.4356 | 159.984
Devonshire Building | 2017-11-27 05:30 | 51368.4756 | 159.984
Devonshire Building | 2017-11-27 05:45 | 51368.5156 | 159.984
Devonshire Building | 2017-11-27 06:00 | 51368.5556 | 159.984
Devonshire Building | 2017-11-27 06:15 | 51368.6006 | 180
Devonshire Building | 2017-11-27 06:30 | 51368.6406 | 159.984
Devonshire Building | 2017-11-27 06:45 | 51368.6806 | 159.984
Devonshire Building | 2017-11-27 07:00 | 51368.7206 | 159.984
Devonshire Building | 2017-11-27 07:15 | 51368.7606 | 159.984
Devonshire Building | 2017-11-27 07:30 | 51368.8256 | 259.992
Devonshire Building | 2017-11-27 07:45 | 51368.9256 | 399.996
Devonshire Building | 2017-11-27 08:00 | 51369.0156 | 360
Devonshire Building | 2017-11-27 08:15 | 51369.1005 | 339.984
Devonshire Building | 2017-11-27 08:30 | 51369.2056 | 420.012
Devonshire Building | 2017-11-27 08:45 | 51369.3556 | 600.012
Devonshire Building | 2017-11-27 09:00 | 51369.4706 | 460.008
Devonshire Building | 2017-11-27 09:15 | 51369.5906 | 479.988
Devonshire Building | 2017-11-27 09:30 | 51369.6906 | 399.996
Devonshire Building | 2017-11-27 09:45 | 51369.8056 | 460.008
Devonshire Building | 2017-11-27 10:00 | 51369.9506 | 579.996
Devonshire Building | 2017-11-27 10:15 | 51370.1056 | 619.992
Devonshire Building | 2017-11-27 10:30 | 51370.2805 | 699.984
Devonshire Building | 2017-11-27 10:45 | 51370.4805 | 799.992
Devonshire Building | 2017-11-27 11:00 | 51370.7605 | 1119.996
Devonshire Building | 2017-11-27 11:15 | 51371.1305 | 1479.996
Devonshire Building | 2017-11-27 11:30 | 51371.3655 | 939.996
Devonshire Building | 2017-11-27 11:45 | 51371.6055 | 960.012
Devonshire Building | 2017-11-27 12:00 | 51371.8555 | 1000.008
Devonshire Building | 2017-11-27 12:15 | 51372.1205 | 1059.984
Devonshire Building | 2017-11-27 12:30 | 51372.2905 | 680.004
Devonshire Building | 2017-11-27 12:45 | 51372.5405 | 1000.008
Devonshire Building | 2017-11-27 13:00 | 51372.7706 | 920.016
Devonshire Building | 2017-11-27 13:15 | 51373.0106 | 960.012
Devonshire Building | 2017-11-27 13:30 | 51373.2205 | 839.988
Devonshire Building | 2017-11-27 13:45 | 51373.4855 | 1059.984
Devonshire Building | 2017-11-27 14:00 | 51373.7505 | 1059.984
Devonshire Building | 2017-11-27 14:15 | 51373.9805 | 920.016
Devonshire Building | 2017-11-27 14:30 | 51374.1755 | 780.012
Devonshire Building | 2017-11-27 14:45 | 51374.4356 | 1040.004
Devonshire Building | 2017-11-27 15:00 | 51374.7005 | 1059.984
Devonshire Building | 2017-11-27 15:15 | 51374.9205 | 879.984
Devonshire Building | 2017-11-27 15:30 | 51375.0955 | 699.984
Devonshire Building | 2017-11-27 15:45 | 51375.3655 | 1080
Devonshire Building | 2017-11-27 16:00 | 51375.5555 | 759.996
Devonshire Building | 2017-11-27 16:15 | 51375.7055 | 600.012
Devonshire Building | 2017-11-27 16:30 | 51375.8955 | 759.996
Devonshire Building | 2017-11-27 16:45 | 51376.0655 | 680.004
Devonshire Building | 2017-11-27 17:00 | 51376.2255 | 640.008
Devonshire Building | 2017-11-27 17:15 | 51376.4055 | 720
Devonshire Building | 2017-11-27 17:30 | 51376.5505 | 579.996
Devonshire Building | 2017-11-27 17:45 | 51376.6505 | 399.996
Devonshire Building | 2017-11-27 18:00 | 51376.7305 | 320.004
Devonshire Building | 2017-11-27 18:15 | 51376.8105 | 320.004
Devonshire Building | 2017-11-27 18:30 | 51376.8755 | 259.992
Devonshire Building | 2017-11-27 18:45 | 51376.9505 | 299.988
Devonshire Building | 2017-11-27 19:00 | 51377.0055 | 219.996
Devonshire Building | 2017-11-27 19:15 | 51377.0555 | 200.016
Devonshire Building | 2017-11-27 19:30 | 51377.1105 | 219.996
Devonshire Building | 2017-11-27 19:45 | 51377.1605 | 200.016
Devonshire Building | 2017-11-27 20:00 | 51377.2055 | 180
Devonshire Building | 2017-11-27 20:15 | 51377.2505 | 180
Devonshire Building | 2017-11-27 20:30 | 51377.2955 | 180
Devonshire Building | 2017-11-27 20:45 | 51377.3405 | 180
Devonshire Building | 2017-11-27 21:00 | 51377.3855 | 180
Devonshire Building | 2017-11-27 21:15 | 51377.4305 | 180
Devonshire Building | 2017-11-27 21:30 | 51377.4805 | 200.016
Devonshire Building | 2017-11-27 21:45 | 51377.5205 | 159.984
Devonshire Building | 2017-11-27 22:00 | 51377.5655 | 180
Devonshire Building | 2017-11-27 22:15 | 51377.6055 | 159.984
Devonshire Building | 2017-11-27 22:30 | 51377.6505 | 180
Devonshire Building | 2017-11-27 22:45 | 51377.6955 | 180
Devonshire Building | 2017-11-27 23:00 | 51377.7405 | 180
Devonshire Building | 2017-11-27 23:15 | 51377.7805 | 159.984
Devonshire Building | 2017-11-27 23:30 | 51377.8205 | 159.984
Devonshire Building | 2017-11-27 23:45 | 51377.8655 | 180
Devonshire Building | 2017-11-28 | 51377.9062 | 159.984
Devonshire Building | 2017-11-28 00:15 | 51377.9462 | 159.984
Devonshire Building | 2017-11-28 00:30 | 51377.9862 | 159.984
Devonshire Building | 2017-11-28 00:45 | 51378.0312 | 180
Devonshire Building | 2017-11-28 01:00 | 51378.0712 | 159.984
Devonshire Building | 2017-11-28 01:15 | 51378.1112 | 159.984
Devonshire Building | 2017-11-28 01:30 | 51378.1512 | 159.984
Devonshire Building | 2017-11-28 01:45 | 51378.1962 | 180
Devonshire Building | 2017-11-28 02:00 | 51378.2362 | 159.984
Devonshire Building | 2017-11-28 02:15 | 51378.2762 | 159.984
Devonshire Building | 2017-11-28 02:30 | 51378.3162 | 159.984
Devonshire Building | 2017-11-28 02:45 | 51378.3562 | 159.984
Devonshire Building | 2017-11-28 03:00 | 51378.4012 | 180
Devonshire Building | 2017-11-28 03:15 | 51378.4412 | 159.984
Devonshire Building | 2017-11-28 03:30 | 51378.4812 | 159.984
Devonshire Building | 2017-11-28 03:45 | 51378.5212 | 159.984
Devonshire Building | 2017-11-28 04:00 | 51378.5612 | 159.984
Devonshire Building | 2017-11-28 04:15 | 51378.6012 | 159.984
Devonshire Building | 2017-11-28 04:30 | 51378.6462 | 180
Devonshire Building | 2017-11-28 04:45 | 51378.6862 | 159.984
Devonshire Building | 2017-11-28 05:00 | 51378.7262 | 159.984
Devonshire Building | 2017-11-28 05:15 | 51378.7662 | 159.984
Devonshire Building | 2017-11-28 05:30 | 51378.8062 | 159.984
Devonshire Building | 2017-11-28 05:45 | 51378.8612 | 219.996
Devonshire Building | 2017-11-28 06:00 | 51378.9212 | 240.012
Devonshire Building | 2017-11-28 06:15 | 51378.9712 | 200.016
Devonshire Building | 2017-11-28 06:30 | 51379.0162 | 180
Devonshire Building | 2017-11-28 06:45 | 51379.0562 | 159.984
Devonshire Building | 2017-11-28 07:00 | 51379.1012 | 180
Devonshire Building | 2017-11-28 07:15 | 51379.1512 | 200.016
Devonshire Building | 2017-11-28 07:30 | 51379.2812 | 519.984
Devonshire Building | 2017-11-28 07:45 | 51379.3812 | 399.996
Devonshire Building | 2017-11-28 08:00 | 51379.5062 | 500.004
Devonshire Building | 2017-11-28 08:15 | 51379.5712 | 259.992
Devonshire Building | 2017-11-28 08:30 | 51379.6362 | 259.992
Devonshire Building | 2017-11-28 08:45 | 51379.7112 | 299.988
Devonshire Building | 2017-11-28 09:00 | 51379.8462 | 540
Devonshire Building | 2017-11-28 09:15 | 51379.9862 | 560.016
Devonshire Building | 2017-11-28 09:30 | 51380.1112 | 500.004
Devonshire Building | 2017-11-28 09:45 | 51380.2912 | 720
Devonshire Building | 2017-11-28 10:00 | 51380.4562 | 659.988
Devonshire Building | 2017-11-28 10:15 | 51380.6112 | 619.992
Devonshire Building | 2017-11-28 10:30 | 51380.7562 | 579.996
Devonshire Building | 2017-11-28 10:45 | 51380.9762 | 879.984
Devonshire Building | 2017-11-28 11:00 | 51381.1662 | 759.996
Devonshire Building | 2017-11-28 11:15 | 51381.3412 | 699.984
Devonshire Building | 2017-11-28 11:30 | 51381.5462 | 820.008
Devonshire Building | 2017-11-28 11:45 | 51381.7212 | 699.984
Devonshire Building | 2017-11-28 12:00 | 51381.9762 | 1019.988
Devonshire Building | 2017-11-28 12:15 | 51382.1712 | 780.012
Devonshire Building | 2017-11-28 12:30 | 51382.3612 | 759.996
Devonshire Building | 2017-11-28 12:45 | 51382.4712 | 439.992
Devonshire Building | 2017-11-28 13:00 | 51382.6262 | 619.992
Devonshire Building | 2017-11-28 13:15 | 51382.8162 | 759.996
Devonshire Building | 2017-11-28 13:30 | 51383.0112 | 780.012
Devonshire Building | 2017-11-28 13:45 | 51383.1562 | 579.996
Devonshire Building | 2017-11-28 14:00 | 51383.3812 | 900
Devonshire Building | 2017-11-28 14:15 | 51383.5162 | 540
Devonshire Building | 2017-11-28 14:30 | 51383.6462 | 519.984
Devonshire Building | 2017-11-28 14:45 | 51383.7912 | 579.996
Devonshire Building | 2017-11-28 15:00 | 51383.9312 | 560.016
Devonshire Building | 2017-11-28 15:15 | 51384.1212 | 759.996
Devonshire Building | 2017-11-28 15:30 | 51384.3062 | 740.016
Devonshire Building | 2017-11-28 15:45 | 51384.5162 | 839.988
Devonshire Building | 2017-11-28 16:00 | 51384.6862 | 680.004
Devonshire Building | 2017-11-28 16:15 | 51384.8212 | 540
Devonshire Building | 2017-11-28 16:30 | 51384.9612 | 560.016
Devonshire Building | 2017-11-28 16:45 | 51385.1312 | 680.004
Devonshire Building | 2017-11-28 17:00 | 51385.2662 | 540
Devonshire Building | 2017-11-28 17:15 | 51385.4162 | 600.012
Devonshire Building | 2017-11-28 17:30 | 51385.5062 | 360
Devonshire Building | 2017-11-28 17:45 | 51385.6062 | 399.996
Devonshire Building | 2017-11-28 18:00 | 51385.7162 | 439.992
Devonshire Building | 2017-11-28 18:15 | 51385.8012 | 339.984
Devonshire Building | 2017-11-28 18:30 | 51385.8762 | 299.988
Devonshire Building | 2017-11-28 18:45 | 51385.9512 | 299.988
Devonshire Building | 2017-11-28 19:00 | 51386.0312 | 320.004
Devonshire Building | 2017-11-28 19:15 | 51386.0912 | 240.012
Devonshire Building | 2017-11-28 19:30 | 51386.1512 | 240.012
Devonshire Building | 2017-11-28 19:45 | 51386.2162 | 259.992
Devonshire Building | 2017-11-28 20:00 | 51386.2712 | 219.996
Devonshire Building | 2017-11-28 20:15 | 51386.3212 | 200.016
Devonshire Building | 2017-11-28 20:30 | 51386.3662 | 180
Devonshire Building | 2017-11-28 20:45 | 51386.4162 | 200.016
Devonshire Building | 2017-11-28 21:00 | 51386.4612 | 180
Devonshire Building | 2017-11-28 21:15 | 51386.5062 | 180
Devonshire Building | 2017-11-28 21:30 | 51386.5512 | 180
Devonshire Building | 2017-11-28 21:45 | 51386.5962 | 180
Devonshire Building | 2017-11-28 22:00 | 51386.6362 | 159.984
Devonshire Building | 2017-11-28 22:15 | 51386.6812 | 180
Devonshire Building | 2017-11-28 22:30 | 51386.7212 | 159.984
Devonshire Building | 2017-11-28 22:45 | 51386.7612 | 159.984
Devonshire Building | 2017-11-28 23:00 | 51386.8062 | 180
Devonshire Building | 2017-11-28 23:15 | 51386.8461 | 159.984
Devonshire Building | 2017-11-28 23:30 | 51386.8861 | 159.984
Devonshire Building | 2017-11-28 23:45 | 51386.9261 | 159.984
Devonshire Building | 2017-11-29 | 51386.9688 | 180
Devonshire Building | 2017-11-29 00:15 | 51387.0087 | 159.984
Devonshire Building | 2017-11-29 00:30 | 51387.0487 | 159.984
Devonshire Building | 2017-11-29 00:45 | 51387.0837 | 140.004
Devonshire Building | 2017-11-29 01:00 | 51387.1237 | 159.984
Devonshire Building | 2017-11-29 01:15 | 51387.1637 | 159.984
Devonshire Building | 2017-11-29 01:30 | 51387.2037 | 159.984
Devonshire Building | 2017-11-29 01:45 | 51387.2437 | 159.984
Devonshire Building | 2017-11-29 02:00 | 51387.2837 | 159.984
Devonshire Building | 2017-11-29 02:15 | 51387.3237 | 159.984
Devonshire Building | 2017-11-29 02:30 | 51387.3587 | 140.004
Devonshire Building | 2017-11-29 02:45 | 51387.3987 | 159.984
Devonshire Building | 2017-11-29 03:00 | 51387.4387 | 159.984
Devonshire Building | 2017-11-29 03:15 | 51387.4787 | 159.984
Devonshire Building | 2017-11-29 03:30 | 51387.5187 | 159.984
Devonshire Building | 2017-11-29 03:45 | 51387.5537 | 140.004
Devonshire Building | 2017-11-29 04:00 | 51387.5937 | 159.984
Devonshire Building | 2017-11-29 04:15 | 51387.6337 | 159.984
Devonshire Building | 2017-11-29 04:30 | 51387.6687 | 140.004
Devonshire Building | 2017-11-29 04:45 | 51387.7087 | 159.984
Devonshire Building | 2017-11-29 05:00 | 51387.7487 | 159.984
Devonshire Building | 2017-11-29 05:15 | 51387.7887 | 159.984
Devonshire Building | 2017-11-29 05:30 | 51387.8437 | 219.996
Devonshire Building | 2017-11-29 05:45 | 51387.8987 | 219.996
Devonshire Building | 2017-11-29 06:00 | 51387.9437 | 180
Devonshire Building | 2017-11-29 06:15 | 51387.9837 | 159.984
Devonshire Building | 2017-11-29 06:30 | 51388.0187 | 140.004
Devonshire Building | 2017-11-29 06:45 | 51388.0587 | 159.984
Devonshire Building | 2017-11-29 07:00 | 51388.0987 | 159.984
Devonshire Building | 2017-11-29 07:15 | 51388.1487 | 200.016
Devonshire Building | 2017-11-29 07:30 | 51388.2187 | 280.008
Devonshire Building | 2017-11-29 07:45 | 51388.3187 | 399.996
Devonshire Building | 2017-11-29 08:00 | 51388.3937 | 299.988
Devonshire Building | 2017-11-29 08:15 | 51388.4587 | 259.992
Devonshire Building | 2017-11-29 08:30 | 51388.5187 | 240.012
Devonshire Building | 2017-11-29 08:45 | 51388.6587 | 560.016
Devonshire Building | 2017-11-29 09:00 | 51388.7887 | 519.984
Devonshire Building | 2017-11-29 09:15 | 51388.9287 | 560.016
Devonshire Building | 2017-11-29 09:30 | 51389.0687 | 560.016
Devonshire Building | 2017-11-29 09:45 | 51389.1787 | 439.992
Devonshire Building | 2017-11-29 10:00 | 51389.3587 | 720
Devonshire Building | 2017-11-29 10:15 | 51389.4837 | 500.004
Devonshire Building | 2017-11-29 10:30 | 51389.6387 | 619.992
Devonshire Building | 2017-11-29 10:45 | 51389.7987 | 640.008
Devonshire Building | 2017-11-29 11:00 | 51389.9837 | 740.016
Devonshire Building | 2017-11-29 11:15 | 51390.1487 | 659.988
Devonshire Building | 2017-11-29 11:30 | 51390.3137 | 659.988
Devonshire Building | 2017-11-29 11:45 | 51390.4787 | 659.988
Devonshire Building | 2017-11-29 12:00 | 51390.6537 | 699.984
Devonshire Building | 2017-11-29 12:15 | 51390.8737 | 879.984
Devonshire Building | 2017-11-29 12:30 | 51391.0837 | 839.988
Devonshire Building | 2017-11-29 12:45 | 51391.3487 | 1059.984
Devonshire Building | 2017-11-29 13:00 | 51391.7587 | 1640.016
Devonshire Building | 2017-11-29 13:15 | 51392.1087 | 1400.004
Devonshire Building | 2017-11-29 13:30 | 51392.3337 | 900
Devonshire Building | 2017-11-29 13:45 | 51392.5437 | 839.988
Devonshire Building | 2017-11-29 14:00 | 51392.7387 | 780.012
Devonshire Building | 2017-11-29 14:15 | 51392.8837 | 579.996
Devonshire Building | 2017-11-29 14:30 | 51393.0387 | 619.992
Devonshire Building | 2017-11-29 14:45 | 51393.2387 | 799.992
Devonshire Building | 2017-11-29 15:00 | 51393.3537 | 460.008
Devonshire Building | 2017-11-29 15:15 | 51393.4687 | 460.008
Devonshire Building | 2017-11-29 15:30 | 51393.5787 | 439.992
Devonshire Building | 2017-11-29 15:45 | 51393.7387 | 640.008
Devonshire Building | 2017-11-29 16:00 | 51393.9037 | 659.988
Devonshire Building | 2017-11-29 16:15 | 51394.0737 | 680.004
Devonshire Building | 2017-11-29 16:30 | 51394.2237 | 600.012
Devonshire Building | 2017-11-29 16:45 | 51394.3787 | 619.992
Devonshire Building | 2017-11-29 17:00 | 51394.5137 | 540
Devonshire Building | 2017-11-29 17:15 | 51394.6487 | 540
Devonshire Building | 2017-11-29 17:30 | 51394.7187 | 280.008
Devonshire Building | 2017-11-29 17:45 | 51394.8287 | 439.992
Devonshire Building | 2017-11-29 18:00 | 51394.9237 | 380.016
Devonshire Building | 2017-11-29 18:15 | 51395.0437 | 479.988
Devonshire Building | 2017-11-29 18:30 | 51395.0987 | 219.996
Devonshire Building | 2017-11-29 18:45 | 51395.1487 | 200.016
Devonshire Building | 2017-11-29 19:00 | 51395.2037 | 219.996
Devonshire Building | 2017-11-29 19:15 | 51395.2537 | 200.016
Devonshire Building | 2017-11-29 19:30 | 51395.3037 | 200.016
Devonshire Building | 2017-11-29 19:45 | 51395.3537 | 200.016
Devonshire Building | 2017-11-29 20:00 | 51395.4037 | 200.016
Devonshire Building | 2017-11-29 20:15 | 51395.4487 | 180
Devonshire Building | 2017-11-29 20:30 | 51395.4887 | 159.984
Devonshire Building | 2017-11-29 20:45 | 51395.5337 | 180
Devonshire Building | 2017-11-29 21:00 | 51395.5737 | 159.984
Devonshire Building | 2017-11-29 21:15 | 51395.6187 | 180
Devonshire Building | 2017-11-29 21:30 | 51395.6587 | 159.984
Devonshire Building | 2017-11-29 21:45 | 51395.6987 | 159.984
Devonshire Building | 2017-11-29 22:00 | 51395.7437 | 180
Devonshire Building | 2017-11-29 22:15 | 51395.7837 | 159.984
Devonshire Building | 2017-11-29 22:30 | 51395.8237 | 159.984
Devonshire Building | 2017-11-29 22:45 | 51395.8637 | 159.984
Devonshire Building | 2017-11-29 23:00 | 51395.9037 | 159.984
Devonshire Building | 2017-11-29 23:15 | 51395.9436 | 159.984
Devonshire Building | 2017-11-29 23:30 | 51395.9836 | 159.984
Devonshire Building | 2017-11-29 23:45 | 51396.0236 | 159.984
Devonshire Building | 2017-11-30 | 51396.0703 | 180
Devonshire Building | 2017-11-30 00:15 | 51396.1103 | 159.984
Devonshire Building | 2017-11-30 00:30 | 51396.1503 | 159.984
Devonshire Building | 2017-11-30 00:45 | 51396.1903 | 159.984
Devonshire Building | 2017-11-30 01:00 | 51396.2303 | 159.984
Devonshire Building | 2017-11-30 01:15 | 51396.2703 | 159.984
Devonshire Building | 2017-11-30 01:30 | 51396.3103 | 159.984
Devonshire Building | 2017-11-30 01:45 | 51396.3503 | 159.984
Devonshire Building | 2017-11-30 02:00 | 51396.3903 | 159.984
Devonshire Building | 2017-11-30 02:15 | 51396.4303 | 159.984
Devonshire Building | 2017-11-30 02:30 | 51396.4703 | 159.984
Devonshire Building | 2017-11-30 02:45 | 51396.5153 | 180
Devonshire Building | 2017-11-30 03:00 | 51396.5553 | 159.984
Devonshire Building | 2017-11-30 03:15 | 51396.5953 | 159.984
Devonshire Building | 2017-11-30 03:30 | 51396.6353 | 159.984
Devonshire Building | 2017-11-30 03:45 | 51396.6753 | 159.984
Devonshire Building | 2017-11-30 04:00 | 51396.7153 | 159.984
Devonshire Building | 2017-11-30 04:15 | 51396.7552 | 159.984
Devonshire Building | 2017-11-30 04:30 | 51396.7952 | 159.984
Devonshire Building | 2017-11-30 04:45 | 51396.8352 | 159.984
Devonshire Building | 2017-11-30 05:00 | 51396.8702 | 140.004
Devonshire Building | 2017-11-30 05:15 | 51396.9102 | 159.984
Devonshire Building | 2017-11-30 05:30 | 51396.9502 | 159.984
Devonshire Building | 2017-11-30 05:45 | 51396.9902 | 159.984
Devonshire Building | 2017-11-30 06:00 | 51397.0302 | 159.984
Devonshire Building | 2017-11-30 06:15 | 51397.0752 | 180
Devonshire Building | 2017-11-30 06:30 | 51397.1352 | 240.012
Devonshire Building | 2017-11-30 06:45 | 51397.1902 | 219.996
Devonshire Building | 2017-11-30 07:00 | 51397.2302 | 159.984
Devonshire Building | 2017-11-30 07:15 | 51397.2702 | 159.984
Devonshire Building | 2017-11-30 07:30 | 51397.3052 | 140.004
Devonshire Building | 2017-11-30 07:45 | 51397.3702 | 259.992
Devonshire Building | 2017-11-30 08:00 | 51397.4402 | 280.008
Devonshire Building | 2017-11-30 08:15 | 51397.5552 | 460.008
Devonshire Building | 2017-11-30 08:30 | 51397.6352 | 320.004
Devonshire Building | 2017-11-30 08:45 | 51397.7352 | 399.996
Devonshire Building | 2017-11-30 09:00 | 51397.8602 | 500.004
Devonshire Building | 2017-11-30 09:15 | 51398.0352 | 699.984
Devonshire Building | 2017-11-30 09:30 | 51398.1202 | 339.984
Devonshire Building | 2017-11-30 09:45 | 51398.2302 | 439.992
Devonshire Building | 2017-11-30 10:00 | 51398.4102 | 720
Devonshire Building | 2017-11-30 10:15 | 51398.5502 | 560.016
Devonshire Building | 2017-11-30 10:30 | 51398.7052 | 619.992
Devonshire Building | 2017-11-30 10:45 | 51398.8452 | 560.016
Devonshire Building | 2017-11-30 11:00 | 51399.0302 | 740.016
Devonshire Building | 2017-11-30 11:15 | 51399.2202 | 759.996
Devonshire Building | 2017-11-30 11:30 | 51399.3952 | 699.984
Devonshire Building | 2017-11-30 11:45 | 51399.5202 | 500.004
Devonshire Building | 2017-11-30 12:00 | 51399.7302 | 839.988
Devonshire Building | 2017-11-30 12:15 | 51399.9202 | 759.996
Devonshire Building | 2017-11-30 12:30 | 51400.0852 | 659.988
Devonshire Building | 2017-11-30 12:45 | 51400.2152 | 519.984
Devonshire Building | 2017-11-30 13:00 | 51400.3752 | 640.008
Devonshire Building | 2017-11-30 13:15 | 51400.5302 | 619.992
Devonshire Building | 2017-11-30 13:30 | 51400.6952 | 659.988
Devonshire Building | 2017-11-30 13:45 | 51400.8202 | 500.004
Devonshire Building | 2017-11-30 14:00 | 51401.0302 | 839.988
Devonshire Building | 2017-11-30 14:15 | 51401.1852 | 619.992
Devonshire Building | 2017-11-30 14:30 | 51401.3202 | 540
Devonshire Building | 2017-11-30 14:45 | 51401.4402 | 479.988
Devonshire Building | 2017-11-30 15:00 | 51401.5752 | 540
Devonshire Building | 2017-11-30 15:15 | 51401.7452 | 680.004
Devonshire Building | 2017-11-30 15:30 | 51401.9202 | 699.984
Devonshire Building | 2017-11-30 15:45 | 51402.1152 | 780.012
Devonshire Building | 2017-11-30 16:00 | 51402.3202 | 820.008
Devonshire Building | 2017-11-30 16:15 | 51402.5202 | 799.992
Devonshire Building | 2017-11-30 16:30 | 51402.6752 | 619.992
Devonshire Building | 2017-11-30 16:45 | 51402.8652 | 759.996
Devonshire Building | 2017-11-30 17:00 | 51403.0352 | 680.004
Devonshire Building | 2017-11-30 17:15 | 51403.1902 | 619.992
Devonshire Building | 2017-11-30 17:30 | 51403.2852 | 380.016
Devonshire Building | 2017-11-30 17:45 | 51403.3852 | 399.996
Devonshire Building | 2017-11-30 18:00 | 51403.4852 | 399.996
Devonshire Building | 2017-11-30 18:15 | 51403.5652 | 320.004
Devonshire Building | 2017-11-30 18:30 | 51403.6402 | 299.988
Devonshire Building | 2017-11-30 18:45 | 51403.7052 | 259.992
Devonshire Building | 2017-11-30 19:00 | 51403.7602 | 219.996
Devonshire Building | 2017-11-30 19:15 | 51403.8202 | 240.012
Devonshire Building | 2017-11-30 19:30 | 51403.8702 | 200.016
Devonshire Building | 2017-11-30 19:45 | 51403.9352 | 259.992
Devonshire Building | 2017-11-30 20:00 | 51404.0202 | 339.984
Devonshire Building | 2017-11-30 20:15 | 51404.0952 | 299.988
Devonshire Building | 2017-11-30 20:30 | 51404.1502 | 219.996
Devonshire Building | 2017-11-30 20:45 | 51404.2102 | 240.012
Devonshire Building | 2017-11-30 21:00 | 51404.2802 | 280.008
Devonshire Building | 2017-11-30 21:15 | 51404.3452 | 259.992
Devonshire Building | 2017-11-30 21:30 | 51404.4052 | 240.012
Devonshire Building | 2017-11-30 21:45 | 51404.4702 | 259.992
Devonshire Building | 2017-11-30 22:00 | 51404.5252 | 219.996
Devonshire Building | 2017-11-30 22:15 | 51404.5802 | 219.996
Devonshire Building | 2017-11-30 22:30 | 51404.6352 | 219.996
Devonshire Building | 2017-11-30 22:45 | 51404.6902 | 219.996
Devonshire Building | 2017-11-30 23:00 | 51404.7302 | 159.984
Devonshire Building | 2017-11-30 23:15 | 51404.7752 | 180
Devonshire Building | 2017-11-30 23:30 | 51404.8152 | 159.984
Devonshire Building | 2017-11-30 23:45 | 51404.8552 | 159.984
Devonshire Building | 2017-12-01 | 51404.8945 | 159.984
Devonshire Building | 2017-12-01 00:15 | 51404.9345 | 159.984
Devonshire Building | 2017-12-01 00:30 | 51404.9745 | 159.984
Devonshire Building | 2017-12-01 00:45 | 51405.0145 | 159.984
Devonshire Building | 2017-12-01 01:00 | 51405.0545 | 159.984
Devonshire Building | 2017-12-01 01:15 | 51405.0995 | 180
Devonshire Building | 2017-12-01 01:30 | 51405.1395 | 159.984
Devonshire Building | 2017-12-01 01:45 | 51405.1795 | 159.984
Devonshire Building | 2017-12-01 02:00 | 51405.2195 | 159.984
Devonshire Building | 2017-12-01 02:15 | 51405.2595 | 159.984
Devonshire Building | 2017-12-01 02:30 | 51405.2995 | 159.984
Devonshire Building | 2017-12-01 02:45 | 51405.3395 | 159.984
Devonshire Building | 2017-12-01 03:00 | 51405.3795 | 159.984
Devonshire Building | 2017-12-01 03:15 | 51405.4195 | 159.984
Devonshire Building | 2017-12-01 03:30 | 51405.4595 | 159.984
Devonshire Building | 2017-12-01 03:45 | 51405.4995 | 159.984
Devonshire Building | 2017-12-01 04:00 | 51405.5395 | 159.984
Devonshire Building | 2017-12-01 04:15 | 51405.5795 | 159.984
Devonshire Building | 2017-12-01 04:30 | 51405.6145 | 140.004
Devonshire Building | 2017-12-01 04:45 | 51405.6545 | 159.984
Devonshire Building | 2017-12-01 05:00 | 51405.6945 | 159.984
Devonshire Building | 2017-12-01 05:15 | 51405.7345 | 159.984
Devonshire Building | 2017-12-01 05:30 | 51405.7945 | 240.012
Devonshire Building | 2017-12-01 05:45 | 51405.8545 | 240.012
Devonshire Building | 2017-12-01 06:00 | 51405.8945 | 159.984
Devonshire Building | 2017-12-01 06:15 | 51405.9345 | 159.984
Devonshire Building | 2017-12-01 06:30 | 51405.9744 | 159.984
Devonshire Building | 2017-12-01 06:45 | 51406.0144 | 159.984
Devonshire Building | 2017-12-01 07:00 | 51406.0544 | 159.984
Devonshire Building | 2017-12-01 07:15 | 51406.0944 | 159.984
Devonshire Building | 2017-12-01 07:30 | 51406.1694 | 299.988
Devonshire Building | 2017-12-01 07:45 | 51406.2294 | 240.012
Devonshire Building | 2017-12-01 08:00 | 51406.2844 | 219.996
Devonshire Building | 2017-12-01 08:15 | 51406.3644 | 320.004
Devonshire Building | 2017-12-01 08:30 | 51406.4094 | 180
Devonshire Building | 2017-12-01 08:45 | 51406.5094 | 399.996
Devonshire Building | 2017-12-01 09:00 | 51406.6194 | 439.992
Devonshire Building | 2017-12-01 09:15 | 51406.7244 | 420.012
Devonshire Building | 2017-12-01 09:30 | 51406.8894 | 659.988
Devonshire Building | 2017-12-01 09:45 | 51406.9644 | 299.988
Devonshire Building | 2017-12-01 10:00 | 51407.0494 | 339.984
Devonshire Building | 2017-12-01 10:15 | 51407.1294 | 320.004
Devonshire Building | 2017-12-01 10:30 | 51407.2394 | 439.992
Devonshire Building | 2017-12-01 10:45 | 51407.3844 | 579.996
Devonshire Building | 2017-12-01 11:00 | 51407.5494 | 659.988
Devonshire Building | 2017-12-01 11:15 | 51407.6744 | 500.004
Devonshire Building | 2017-12-01 11:30 | 51407.8594 | 740.016
Devonshire Building | 2017-12-01 11:45 | 51407.9994 | 560.016
Devonshire Building | 2017-12-01 12:00 | 51408.1394 | 560.016
Devonshire Building | 2017-12-01 12:15 | 51408.2994 | 640.008
Devonshire Building | 2017-12-01 12:30 | 51408.4694 | 680.004
Devonshire Building | 2017-12-01 12:45 | 51408.5694 | 399.996
Devonshire Building | 2017-12-01 13:00 | 51408.6794 | 439.992
Devonshire Building | 2017-12-01 13:15 | 51408.8294 | 600.012
Devonshire Building | 2017-12-01 13:30 | 51408.9594 | 519.984
Devonshire Building | 2017-12-01 13:45 | 51409.0844 | 500.004
Devonshire Building | 2017-12-01 14:00 | 51409.2194 | 540
Devonshire Building | 2017-12-01 14:15 | 51409.3194 | 399.996
Devonshire Building | 2017-12-01 14:30 | 51409.4394 | 479.988
Devonshire Building | 2017-12-01 14:45 | 51409.5794 | 560.016
Devonshire Building | 2017-12-01 15:00 | 51409.7394 | 640.008
Devonshire Building | 2017-12-01 15:15 | 51409.8844 | 579.996
Devonshire Building | 2017-12-01 15:30 | 51410.0044 | 479.988
Devonshire Building | 2017-12-01 15:45 | 51410.1244 | 479.988
Devonshire Building | 2017-12-01 16:00 | 51410.2494 | 500.004
Devonshire Building | 2017-12-01 16:15 | 51410.3894 | 560.016
Devonshire Building | 2017-12-01 16:30 | 51410.5294 | 560.016
Devonshire Building | 2017-12-01 16:45 | 51410.6344 | 420.012
Devonshire Building | 2017-12-01 17:00 | 51410.7544 | 479.988
Devonshire Building | 2017-12-01 17:15 | 51410.8894 | 540
Devonshire Building | 2017-12-01 17:30 | 51411.0194 | 519.984
Devonshire Building | 2017-12-01 17:45 | 51411.0944 | 299.988
Devonshire Building | 2017-12-01 18:00 | 51411.1744 | 320.004
Devonshire Building | 2017-12-01 18:15 | 51411.2744 | 399.996
Devonshire Building | 2017-12-01 18:30 | 51411.3644 | 360
Devonshire Building | 2017-12-01 18:45 | 51411.4494 | 339.984
Devonshire Building | 2017-12-01 19:00 | 51411.5344 | 339.984
Devonshire Building | 2017-12-01 19:15 | 51411.6444 | 439.992
Devonshire Building | 2017-12-01 19:30 | 51411.7494 | 420.012
Devonshire Building | 2017-12-01 19:45 | 51411.8294 | 320.004
Devonshire Building | 2017-12-01 20:00 | 51411.9144 | 339.984
Devonshire Building | 2017-12-01 20:15 | 51411.9894 | 299.988
Devonshire Building | 2017-12-01 20:30 | 51412.0594 | 280.008
Devonshire Building | 2017-12-01 20:45 | 51412.1244 | 259.992
Devonshire Building | 2017-12-01 21:00 | 51412.1844 | 240.012
Devonshire Building | 2017-12-01 21:15 | 51412.2444 | 240.012
Devonshire Building | 2017-12-01 21:30 | 51412.2994 | 219.996
Devonshire Building | 2017-12-01 21:45 | 51412.3544 | 219.996
Devonshire Building | 2017-12-01 22:00 | 51412.4044 | 200.016
Devonshire Building | 2017-12-01 22:15 | 51412.4544 | 200.016
Devonshire Building | 2017-12-01 22:30 | 51412.5044 | 200.016
Devonshire Building | 2017-12-01 22:45 | 51412.5494 | 180
Devonshire Building | 2017-12-01 23:00 | 51412.5994 | 200.016
Devonshire Building | 2017-12-01 23:15 | 51412.6444 | 180
Devonshire Building | 2017-12-01 23:30 | 51412.6894 | 180
Devonshire Building | 2017-12-01 23:45 | 51412.7394 | 200.016
Devonshire Building | 2017-12-02 | 51412.7812 | 159.984
Devonshire Building | 2017-12-02 00:15 | 51412.8262 | 180
Devonshire Building | 2017-12-02 00:30 | 51412.8662 | 159.984
Devonshire Building | 2017-12-02 00:45 | 51412.9112 | 180
Devonshire Building | 2017-12-02 01:00 | 51412.9512 | 159.984
Devonshire Building | 2017-12-02 01:15 | 51412.9962 | 180
Devonshire Building | 2017-12-02 01:30 | 51413.0362 | 159.984
Devonshire Building | 2017-12-02 01:45 | 51413.0762 | 159.984
Devonshire Building | 2017-12-02 02:00 | 51413.1212 | 180
Devonshire Building | 2017-12-02 02:15 | 51413.1612 | 159.984
Devonshire Building | 2017-12-02 02:30 | 51413.2062 | 180
Devonshire Building | 2017-12-02 02:45 | 51413.2462 | 159.984
Devonshire Building | 2017-12-02 03:00 | 51413.2862 | 159.984
Devonshire Building | 2017-12-02 03:15 | 51413.3262 | 159.984
Devonshire Building | 2017-12-02 03:30 | 51413.3712 | 180
Devonshire Building | 2017-12-02 03:45 | 51413.4112 | 159.984
Devonshire Building | 2017-12-02 04:00 | 51413.4512 | 159.984
Devonshire Building | 2017-12-02 04:15 | 51413.4912 | 159.984
Devonshire Building | 2017-12-02 04:30 | 51413.5362 | 180
Devonshire Building | 2017-12-02 04:45 | 51413.5762 | 159.984
Devonshire Building | 2017-12-02 05:00 | 51413.6162 | 159.984
Devonshire Building | 2017-12-02 05:15 | 51413.6562 | 159.984
Devonshire Building | 2017-12-02 05:30 | 51413.7012 | 180
Devonshire Building | 2017-12-02 05:45 | 51413.7412 | 159.984
Devonshire Building | 2017-12-02 06:00 | 51413.7812 | 159.984
Devonshire Building | 2017-12-02 06:15 | 51413.8212 | 159.984
Devonshire Building | 2017-12-02 06:30 | 51413.8612 | 159.984
Devonshire Building | 2017-12-02 06:45 | 51413.9012 | 159.984
Devonshire Building | 2017-12-02 07:00 | 51413.9412 | 159.984
Devonshire Building | 2017-12-02 07:15 | 51413.9812 | 159.984
Devonshire Building | 2017-12-02 07:30 | 51414.0212 | 159.984
Devonshire Building | 2017-12-02 07:45 | 51414.0762 | 219.996
Devonshire Building | 2017-12-02 08:00 | 51414.1362 | 240.012
Devonshire Building | 2017-12-02 08:15 | 51414.1812 | 180
Devonshire Building | 2017-12-02 08:30 | 51414.2162 | 140.004
Devonshire Building | 2017-12-02 08:45 | 51414.2562 | 159.984
Devonshire Building | 2017-12-02 09:00 | 51414.3062 | 200.016
Devonshire Building | 2017-12-02 09:15 | 51414.3712 | 259.992
Devonshire Building | 2017-12-02 09:30 | 51414.4212 | 200.016
Devonshire Building | 2017-12-02 09:45 | 51414.4612 | 159.984
Devonshire Building | 2017-12-02 10:00 | 51414.5112 | 200.016
Devonshire Building | 2017-12-02 10:15 | 51414.5462 | 140.004
Devonshire Building | 2017-12-02 10:30 | 51414.5962 | 200.016
Devonshire Building | 2017-12-02 10:45 | 51414.6362 | 159.984
Devonshire Building | 2017-12-02 11:00 | 51414.7062 | 280.008
Devonshire Building | 2017-12-02 11:15 | 51414.7562 | 200.016
Devonshire Building | 2017-12-02 11:30 | 51414.8262 | 280.008
Devonshire Building | 2017-12-02 11:45 | 51414.8962 | 280.008
Devonshire Building | 2017-12-02 12:00 | 51414.9512 | 219.996
Devonshire Building | 2017-12-02 12:15 | 51415.0012 | 200.016
Devonshire Building | 2017-12-02 12:30 | 51415.0512 | 200.016
Devonshire Building | 2017-12-02 12:45 | 51415.1062 | 219.996
Devonshire Building | 2017-12-02 13:00 | 51415.1962 | 360
Devonshire Building | 2017-12-02 13:15 | 51415.2562 | 240.012
Devonshire Building | 2017-12-02 13:30 | 51415.3062 | 200.016
Devonshire Building | 2017-12-02 13:45 | 51415.3662 | 240.012
Devonshire Building | 2017-12-02 14:00 | 51415.4162 | 200.016
Devonshire Building | 2017-12-02 14:15 | 51415.4712 | 219.996
Devonshire Building | 2017-12-02 14:30 | 51415.5212 | 200.016
Devonshire Building | 2017-12-02 14:45 | 51415.5762 | 219.996
Devonshire Building | 2017-12-02 15:00 | 51415.6262 | 200.016
Devonshire Building | 2017-12-02 15:15 | 51415.6862 | 240.012
Devonshire Building | 2017-12-02 15:30 | 51415.7512 | 259.992
Devonshire Building | 2017-12-02 15:45 | 51415.8062 | 219.996
Devonshire Building | 2017-12-02 16:00 | 51415.8812 | 299.988
Devonshire Building | 2017-12-02 16:15 | 51415.9362 | 219.996
Devonshire Building | 2017-12-02 16:30 | 51415.9912 | 219.996
Devonshire Building | 2017-12-02 16:45 | 51416.0612 | 280.008
Devonshire Building | 2017-12-02 17:00 | 51416.1112 | 200.016
Devonshire Building | 2017-12-02 17:15 | 51416.1512 | 159.984
Devonshire Building | 2017-12-02 17:30 | 51416.1962 | 180
Devonshire Building | 2017-12-02 17:45 | 51416.2362 | 159.984
Devonshire Building | 2017-12-02 18:00 | 51416.2712 | 140.004
Devonshire Building | 2017-12-02 18:15 | 51416.3112 | 159.984
Devonshire Building | 2017-12-02 18:30 | 51416.3462 | 140.004
Devonshire Building | 2017-12-02 18:45 | 51416.3862 | 159.984
Devonshire Building | 2017-12-02 19:00 | 51416.4262 | 159.984
Devonshire Building | 2017-12-02 19:15 | 51416.4662 | 159.984
Devonshire Building | 2017-12-02 19:30 | 51416.5012 | 140.004
Devonshire Building | 2017-12-02 19:45 | 51416.5412 | 159.984
Devonshire Building | 2017-12-02 20:00 | 51416.5862 | 180
Devonshire Building | 2017-12-02 20:15 | 51416.6262 | 159.984
Devonshire Building | 2017-12-02 20:30 | 51416.6612 | 140.004
Devonshire Building | 2017-12-02 20:45 | 51416.6962 | 140.004
Devonshire Building | 2017-12-02 21:00 | 51416.7362 | 159.984
Devonshire Building | 2017-12-02 21:15 | 51416.7712 | 140.004
Devonshire Building | 2017-12-02 21:30 | 51416.8112 | 159.984
Devonshire Building | 2017-12-02 21:45 | 51416.8462 | 140.004
Devonshire Building | 2017-12-02 22:00 | 51416.8812 | 140.004
Devonshire Building | 2017-12-02 22:15 | 51416.9212 | 159.984
Devonshire Building | 2017-12-02 22:30 | 51416.9562 | 140.004
Devonshire Building | 2017-12-02 22:45 | 51416.9962 | 159.984
Devonshire Building | 2017-12-02 23:00 | 51417.0312 | 140.004
Devonshire Building | 2017-12-02 23:15 | 51417.0662 | 140.004
Devonshire Building | 2017-12-02 23:30 | 51417.1062 | 159.984
Devonshire Building | 2017-12-02 23:45 | 51417.1412 | 140.004
Devonshire Building | 2017-12-03 | 51417.1797 | 159.984
Devonshire Building | 2017-12-03 00:15 | 51417.2397 | 240.012
Devonshire Building | 2017-12-03 00:30 | 51417.2947 | 219.996
Devonshire Building | 2017-12-03 00:45 | 51417.3297 | 140.004
Devonshire Building | 2017-12-03 01:00 | 51417.3697 | 159.984
Devonshire Building | 2017-12-03 01:15 | 51417.4097 | 159.984
Devonshire Building | 2017-12-03 01:30 | 51417.4447 | 140.004
Devonshire Building | 2017-12-03 01:45 | 51417.4847 | 159.984
Devonshire Building | 2017-12-03 02:00 | 51417.5247 | 159.984
Devonshire Building | 2017-12-03 02:15 | 51417.5597 | 140.004
Devonshire Building | 2017-12-03 02:30 | 51417.5997 | 159.984
Devonshire Building | 2017-12-03 02:45 | 51417.6397 | 159.984
Devonshire Building | 2017-12-03 03:00 | 51417.6747 | 140.004
Devonshire Building | 2017-12-03 03:15 | 51417.7147 | 159.984
Devonshire Building | 2017-12-03 03:30 | 51417.7547 | 159.984
Devonshire Building | 2017-12-03 03:45 | 51417.7947 | 159.984
Devonshire Building | 2017-12-03 04:00 | 51417.8297 | 140.004
Devonshire Building | 2017-12-03 04:15 | 51417.8697 | 159.984
Devonshire Building | 2017-12-03 04:30 | 51417.9097 | 159.984
Devonshire Building | 2017-12-03 04:45 | 51417.9447 | 140.004
Devonshire Building | 2017-12-03 05:00 | 51417.9846 | 159.984
Devonshire Building | 2017-12-03 05:15 | 51418.0246 | 159.984
Devonshire Building | 2017-12-03 05:30 | 51418.0596 | 140.004
Devonshire Building | 2017-12-03 05:45 | 51418.0996 | 159.984
Devonshire Building | 2017-12-03 06:00 | 51418.1396 | 159.984
Devonshire Building | 2017-12-03 06:15 | 51418.1746 | 140.004
Devonshire Building | 2017-12-03 06:30 | 51418.2146 | 159.984
Devonshire Building | 2017-12-03 06:45 | 51418.2546 | 159.984
Devonshire Building | 2017-12-03 07:00 | 51418.2946 | 159.984
Devonshire Building | 2017-12-03 07:15 | 51418.3296 | 140.004
Devonshire Building | 2017-12-03 07:30 | 51418.3696 | 159.984
Devonshire Building | 2017-12-03 07:45 | 51418.4096 | 159.984
Devonshire Building | 2017-12-03 08:00 | 51418.4496 | 159.984
Devonshire Building | 2017-12-03 08:15 | 51418.5046 | 219.996
Devonshire Building | 2017-12-03 08:30 | 51418.5546 | 200.016
Devonshire Building | 2017-12-03 08:45 | 51418.6096 | 219.996
Devonshire Building | 2017-12-03 09:00 | 51418.6596 | 200.016
Devonshire Building | 2017-12-03 09:15 | 51418.7146 | 219.996
Devonshire Building | 2017-12-03 09:30 | 51418.7746 | 240.012
Devonshire Building | 2017-12-03 09:45 | 51418.8246 | 200.016
Devonshire Building | 2017-12-03 10:00 | 51418.8796 | 219.996
Devonshire Building | 2017-12-03 10:15 | 51418.9296 | 200.016
Devonshire Building | 2017-12-03 10:30 | 51418.9846 | 219.996
Devonshire Building | 2017-12-03 10:45 | 51419.0346 | 200.016
Devonshire Building | 2017-12-03 11:00 | 51419.0796 | 180
Devonshire Building | 2017-12-03 11:15 | 51419.1196 | 159.984
Devonshire Building | 2017-12-03 11:30 | 51419.1546 | 140.004
Devonshire Building | 2017-12-03 11:45 | 51419.1946 | 159.984
Devonshire Building | 2017-12-03 12:00 | 51419.2396 | 180
Devonshire Building | 2017-12-03 12:15 | 51419.2846 | 180
Devonshire Building | 2017-12-03 12:30 | 51419.3296 | 180
Devonshire Building | 2017-12-03 12:45 | 51419.3896 | 240.012
Devonshire Building | 2017-12-03 13:00 | 51419.4546 | 259.992
Devonshire Building | 2017-12-03 13:15 | 51419.4946 | 159.984
Devonshire Building | 2017-12-03 13:30 | 51419.5396 | 180
Devonshire Building | 2017-12-03 13:45 | 51419.5796 | 159.984
Devonshire Building | 2017-12-03 14:00 | 51419.6196 | 159.984
Devonshire Building | 2017-12-03 14:15 | 51419.6646 | 180
Devonshire Building | 2017-12-03 14:30 | 51419.7046 | 159.984
Devonshire Building | 2017-12-03 14:45 | 51419.7446 | 159.984
Devonshire Building | 2017-12-03 15:00 | 51419.7946 | 200.016
Devonshire Building | 2017-12-03 15:15 | 51419.8546 | 240.012
Devonshire Building | 2017-12-03 15:30 | 51419.8946 | 159.984
Devonshire Building | 2017-12-03 15:45 | 51419.9396 | 180
Devonshire Building | 2017-12-03 16:00 | 51419.9796 | 159.984
Devonshire Building | 2017-12-03 16:15 | 51420.0196 | 159.984
Devonshire Building | 2017-12-03 16:30 | 51420.0596 | 159.984
Devonshire Building | 2017-12-03 16:45 | 51420.0946 | 140.004
Devonshire Building | 2017-12-03 17:00 | 51420.1446 | 200.016
Devonshire Building | 2017-12-03 17:15 | 51420.1946 | 200.016
Devonshire Building | 2017-12-03 17:30 | 51420.2346 | 159.984
Devonshire Building | 2017-12-03 17:45 | 51420.2746 | 159.984
Devonshire Building | 2017-12-03 18:00 | 51420.3146 | 159.984
Devonshire Building | 2017-12-03 18:15 | 51420.3546 | 159.984
Devonshire Building | 2017-12-03 18:30 | 51420.4096 | 219.996
Devonshire Building | 2017-12-03 18:45 | 51420.4696 | 240.012
Devonshire Building | 2017-12-03 19:00 | 51420.5146 | 180
Devonshire Building | 2017-12-03 19:15 | 51420.5546 | 159.984
Devonshire Building | 2017-12-03 19:30 | 51420.5946 | 159.984
Devonshire Building | 2017-12-03 19:45 | 51420.6396 | 180
Devonshire Building | 2017-12-03 20:00 | 51420.6946 | 219.996
Devonshire Building | 2017-12-03 20:15 | 51420.7596 | 259.992
Devonshire Building | 2017-12-03 20:30 | 51420.8346 | 299.988
Devonshire Building | 2017-12-03 20:45 | 51420.8946 | 240.012
Devonshire Building | 2017-12-03 21:00 | 51420.9496 | 219.996
Devonshire Building | 2017-12-03 21:15 | 51421.0046 | 219.996
Devonshire Building | 2017-12-03 21:30 | 51421.0596 | 219.996
Devonshire Building | 2017-12-03 21:45 | 51421.1296 | 280.008
Devonshire Building | 2017-12-03 22:00 | 51421.1996 | 280.008
Devonshire Building | 2017-12-03 22:15 | 51421.2596 | 240.012
Devonshire Building | 2017-12-03 22:30 | 51421.3146 | 219.996
Devonshire Building | 2017-12-03 22:45 | 51421.3646 | 200.016
Devonshire Building | 2017-12-03 23:00 | 51421.4046 | 159.984
Devonshire Building | 2017-12-03 23:15 | 51421.4446 | 159.984
Devonshire Building | 2017-12-03 23:30 | 51421.4846 | 159.984
Devonshire Building | 2017-12-03 23:45 | 51421.5446 | 240.012
Devonshire Building | 2017-12-04 | 51421.6055 | 240.012
Devonshire Building | 2017-12-04 00:15 | 51421.6505 | 180
Devonshire Building | 2017-12-04 00:30 | 51421.6905 | 159.984
Devonshire Building | 2017-12-04 00:45 | 51421.7305 | 159.984
Devonshire Building | 2017-12-04 01:00 | 51421.7705 | 159.984
Devonshire Building | 2017-12-04 01:15 | 51421.8105 | 159.984
Devonshire Building | 2017-12-04 01:30 | 51421.8504 | 159.984
Devonshire Building | 2017-12-04 01:45 | 51421.8904 | 159.984
Devonshire Building | 2017-12-04 02:00 | 51421.9304 | 159.984
Devonshire Building | 2017-12-04 02:15 | 51421.9704 | 159.984
Devonshire Building | 2017-12-04 02:30 | 51422.0104 | 159.984
Devonshire Building | 2017-12-04 02:45 | 51422.0504 | 159.984
Devonshire Building | 2017-12-04 03:00 | 51422.0904 | 159.984
Devonshire Building | 2017-12-04 03:15 | 51422.1304 | 159.984
Devonshire Building | 2017-12-04 03:30 | 51422.1704 | 159.984
Devonshire Building | 2017-12-04 03:45 | 51422.2104 | 159.984
Devonshire Building | 2017-12-04 04:00 | 51422.2454 | 140.004
Devonshire Building | 2017-12-04 04:15 | 51422.2854 | 159.984
Devonshire Building | 2017-12-04 04:30 | 51422.3254 | 159.984
Devonshire Building | 2017-12-04 04:45 | 51422.3654 | 159.984
Devonshire Building | 2017-12-04 05:00 | 51422.4054 | 159.984
Devonshire Building | 2017-12-04 05:15 | 51422.4454 | 159.984
Devonshire Building | 2017-12-04 05:30 | 51422.4804 | 140.004
Devonshire Building | 2017-12-04 05:45 | 51422.5204 | 159.984
Devonshire Building | 2017-12-04 06:00 | 51422.5604 | 159.984
Devonshire Building | 2017-12-04 06:15 | 51422.6004 | 159.984
Devonshire Building | 2017-12-04 06:30 | 51422.6404 | 159.984
Devonshire Building | 2017-12-04 06:45 | 51422.6804 | 159.984
Devonshire Building | 2017-12-04 07:00 | 51422.7204 | 159.984
Devonshire Building | 2017-12-04 07:15 | 51422.7554 | 140.004
Devonshire Building | 2017-12-04 07:30 | 51422.8004 | 180
Devonshire Building | 2017-12-04 07:45 | 51422.8854 | 339.984
Devonshire Building | 2017-12-04 08:00 | 51422.9554 | 280.008
Devonshire Building | 2017-12-04 08:15 | 51423.0104 | 219.996
Devonshire Building | 2017-12-04 08:30 | 51423.1054 | 380.016
Devonshire Building | 2017-12-04 08:45 | 51423.1604 | 219.996
Devonshire Building | 2017-12-04 09:00 | 51423.2754 | 460.008
Devonshire Building | 2017-12-04 09:15 | 51423.3904 | 460.008
Devonshire Building | 2017-12-04 09:30 | 51423.5204 | 519.984
Devonshire Building | 2017-12-04 09:45 | 51423.6504 | 519.984
Devonshire Building | 2017-12-04 10:00 | 51423.7754 | 500.004
Devonshire Building | 2017-12-04 10:15 | 51423.9654 | 759.996
Devonshire Building | 2017-12-04 10:30 | 51424.1354 | 680.004
Devonshire Building | 2017-12-04 10:45 | 51424.3654 | 920.016
Devonshire Building | 2017-12-04 11:00 | 51424.5554 | 759.996
Devonshire Building | 2017-12-04 11:15 | 51424.7104 | 619.992
Devonshire Building | 2017-12-04 11:30 | 51424.9304 | 879.984
Devonshire Building | 2017-12-04 11:45 | 51425.0704 | 560.016
Devonshire Building | 2017-12-04 12:00 | 51425.2854 | 860.004
Devonshire Building | 2017-12-04 12:15 | 51425.4704 | 740.016
Devonshire Building | 2017-12-04 12:30 | 51425.6304 | 640.008
Devonshire Building | 2017-12-04 12:45 | 51425.7854 | 619.992
Devonshire Building | 2017-12-04 13:00 | 51426.0154 | 920.016
Devonshire Building | 2017-12-04 13:15 | 51426.1854 | 680.004
Devonshire Building | 2017-12-04 13:30 | 51426.3554 | 680.004
Devonshire Building | 2017-12-04 13:45 | 51426.5104 | 619.992
Devonshire Building | 2017-12-04 14:00 | 51426.7004 | 759.996
Devonshire Building | 2017-12-04 14:15 | 51426.8954 | 780.012
Devonshire Building | 2017-12-04 14:30 | 51427.0754 | 720
Devonshire Building | 2017-12-04 14:45 | 51427.2354 | 640.008
Devonshire Building | 2017-12-04 15:00 | 51427.3854 | 600.012
Devonshire Building | 2017-12-04 15:15 | 51427.5504 | 659.988
Devonshire Building | 2017-12-04 15:30 | 51427.7004 | 600.012
Devonshire Building | 2017-12-04 15:45 | 51427.8754 | 699.984
Devonshire Building | 2017-12-04 16:00 | 51428.0404 | 659.988
Devonshire Building | 2017-12-04 16:15 | 51428.1904 | 600.012
Devonshire Building | 2017-12-04 16:30 | 51428.3654 | 699.984
Devonshire Building | 2017-12-04 16:45 | 51428.5454 | 720
Devonshire Building | 2017-12-04 17:00 | 51428.7304 | 740.016
Devonshire Building | 2017-12-04 17:15 | 51428.9054 | 699.984
Devonshire Building | 2017-12-04 17:30 | 51429.0804 | 699.984
Devonshire Building | 2017-12-04 17:45 | 51429.2204 | 560.016
Devonshire Building | 2017-12-04 18:00 | 51429.3054 | 339.984
Devonshire Building | 2017-12-04 18:15 | 51429.3854 | 320.004
Devonshire Building | 2017-12-04 18:30 | 51429.4554 | 280.008
Devonshire Building | 2017-12-04 18:45 | 51429.5204 | 259.992
Devonshire Building | 2017-12-04 19:00 | 51429.5754 | 219.996
Devonshire Building | 2017-12-04 19:15 | 51429.6404 | 259.992
Devonshire Building | 2017-12-04 19:30 | 51429.6904 | 200.016
Devonshire Building | 2017-12-04 19:45 | 51429.7354 | 180
Devonshire Building | 2017-12-04 20:00 | 51429.7954 | 240.012
Devonshire Building | 2017-12-04 20:15 | 51429.8704 | 299.988
Devonshire Building | 2017-12-04 20:30 | 51429.9304 | 240.012
Devonshire Building | 2017-12-04 20:45 | 51429.9754 | 180
Devonshire Building | 2017-12-04 21:00 | 51430.0154 | 159.984
Devonshire Building | 2017-12-04 21:15 | 51430.0654 | 200.016
Devonshire Building | 2017-12-04 21:30 | 51430.1204 | 219.996
Devonshire Building | 2017-12-04 21:45 | 51430.1604 | 159.984
Devonshire Building | 2017-12-04 22:00 | 51430.2004 | 159.984
Devonshire Building | 2017-12-04 22:15 | 51430.2404 | 159.984
Devonshire Building | 2017-12-04 22:30 | 51430.2804 | 159.984
Devonshire Building | 2017-12-04 22:45 | 51430.3204 | 159.984
Devonshire Building | 2017-12-04 23:00 | 51430.3604 | 159.984
Devonshire Building | 2017-12-04 23:15 | 51430.4004 | 159.984
Devonshire Building | 2017-12-04 23:30 | 51430.4403 | 159.984
Devonshire Building | 2017-12-04 23:45 | 51430.4803 | 159.984
Devonshire Building | 2017-12-05 | 51430.5195 | 159.984
Devonshire Building | 2017-12-05 00:15 | 51430.5595 | 159.984
Devonshire Building | 2017-12-05 00:30 | 51430.5995 | 159.984
Devonshire Building | 2017-12-05 00:45 | 51430.6395 | 159.984
Devonshire Building | 2017-12-05 01:00 | 51430.6795 | 159.984
Devonshire Building | 2017-12-05 01:15 | 51430.7195 | 159.984
Devonshire Building | 2017-12-05 01:30 | 51430.7595 | 159.984
Devonshire Building | 2017-12-05 01:45 | 51430.7995 | 159.984
Devonshire Building | 2017-12-05 02:00 | 51430.8395 | 159.984
Devonshire Building | 2017-12-05 02:15 | 51430.8745 | 140.004
Devonshire Building | 2017-12-05 02:30 | 51430.9145 | 159.984
Devonshire Building | 2017-12-05 02:45 | 51430.9545 | 159.984
Devonshire Building | 2017-12-05 03:00 | 51430.9945 | 159.984
Devonshire Building | 2017-12-05 03:15 | 51431.0345 | 159.984
Devonshire Building | 2017-12-05 03:30 | 51431.0745 | 159.984
Devonshire Building | 2017-12-05 03:45 | 51431.1095 | 140.004
Devonshire Building | 2017-12-05 04:00 | 51431.1495 | 159.984
Devonshire Building | 2017-12-05 04:15 | 51431.1895 | 159.984
Devonshire Building | 2017-12-05 04:30 | 51431.2295 | 159.984
Devonshire Building | 2017-12-05 04:45 | 51431.2695 | 159.984
Devonshire Building | 2017-12-05 05:00 | 51431.3045 | 140.004
Devonshire Building | 2017-12-05 05:15 | 51431.3445 | 159.984
Devonshire Building | 2017-12-05 05:30 | 51431.3845 | 159.984
Devonshire Building | 2017-12-05 05:45 | 51431.4245 | 159.984
Devonshire Building | 2017-12-05 06:00 | 51431.4644 | 159.984
Devonshire Building | 2017-12-05 06:15 | 51431.4995 | 140.004
Devonshire Building | 2017-12-05 06:30 | 51431.5394 | 159.984
Devonshire Building | 2017-12-05 06:45 | 51431.5844 | 180
Devonshire Building | 2017-12-05 07:00 | 51431.6244 | 159.984
Devonshire Building | 2017-12-05 07:15 | 51431.6594 | 140.004
Devonshire Building | 2017-12-05 07:30 | 51431.7444 | 339.984
Devonshire Building | 2017-12-05 07:45 | 51431.8494 | 420.012
Devonshire Building | 2017-12-05 08:00 | 51431.9094 | 240.012
Devonshire Building | 2017-12-05 08:15 | 51432.0144 | 420.012
Devonshire Building | 2017-12-05 08:30 | 51432.1144 | 399.996
Devonshire Building | 2017-12-05 08:45 | 51432.1944 | 320.004
Devonshire Building | 2017-12-05 09:00 | 51432.3294 | 540
Devonshire Building | 2017-12-05 09:15 | 51432.4494 | 479.988
Devonshire Building | 2017-12-05 09:30 | 51432.5644 | 460.008
Devonshire Building | 2017-12-05 09:45 | 51432.6544 | 360
Devonshire Building | 2017-12-05 10:00 | 51432.8845 | 920.016
Devonshire Building | 2017-12-05 10:15 | 51433.0095 | 500.004
Devonshire Building | 2017-12-05 10:30 | 51433.1945 | 740.016
Devonshire Building | 2017-12-05 10:45 | 51433.3545 | 640.008
Devonshire Building | 2017-12-05 11:00 | 51433.5545 | 799.992
Devonshire Building | 2017-12-05 11:15 | 51433.7395 | 740.016
Devonshire Building | 2017-12-05 11:30 | 51434.0545 | 1260
Devonshire Building | 2017-12-05 11:45 | 51434.2345 | 720
Devonshire Building | 2017-12-05 12:00 | 51434.3995 | 659.988
Devonshire Building | 2017-12-05 12:15 | 51434.6145 | 860.004
Devonshire Building | 2017-12-05 12:30 | 51434.8445 | 920.016
Devonshire Building | 2017-12-05 12:45 | 51435.0295 | 740.016
Devonshire Building | 2017-12-05 13:00 | 51435.1995 | 680.004
Devonshire Building | 2017-12-05 13:15 | 51435.3795 | 720
Devonshire Building | 2017-12-05 13:30 | 51435.5945 | 860.004
Devonshire Building | 2017-12-05 13:45 | 51435.8295 | 939.996
Devonshire Building | 2017-12-05 14:00 | 51435.9645 | 540
Devonshire Building | 2017-12-05 14:15 | 51436.1295 | 659.988
Devonshire Building | 2017-12-05 14:30 | 51436.2595 | 519.984
Devonshire Building | 2017-12-05 14:45 | 51436.3845 | 500.004
Devonshire Building | 2017-12-05 15:00 | 51436.5995 | 860.004
Devonshire Building | 2017-12-05 15:15 | 51436.7545 | 619.992
Devonshire Building | 2017-12-05 15:30 | 51436.8945 | 560.016
Devonshire Building | 2017-12-05 15:45 | 51437.0345 | 560.016
Devonshire Building | 2017-12-05 16:00 | 51437.2245 | 759.996
Devonshire Building | 2017-12-05 16:15 | 51437.3695 | 579.996
Devonshire Building | 2017-12-05 16:30 | 51437.5195 | 600.012
Devonshire Building | 2017-12-05 16:45 | 51437.6445 | 500.004
Devonshire Building | 2017-12-05 17:00 | 51437.8045 | 640.008
Devonshire Building | 2017-12-05 17:15 | 51437.9995 | 780.012
Devonshire Building | 2017-12-05 17:30 | 51438.1695 | 680.004
Devonshire Building | 2017-12-05 17:45 | 51438.3245 | 619.992
Devonshire Building | 2017-12-05 18:00 | 51438.4595 | 540
Devonshire Building | 2017-12-05 18:15 | 51438.5645 | 420.012
Devonshire Building | 2017-12-05 18:30 | 51438.6695 | 420.012
Devonshire Building | 2017-12-05 18:45 | 51438.7545 | 339.984
Devonshire Building | 2017-12-05 19:00 | 51438.8545 | 399.996
Devonshire Building | 2017-12-05 19:15 | 51438.9295 | 299.988
Devonshire Building | 2017-12-05 19:30 | 51438.9995 | 280.008
Devonshire Building | 2017-12-05 19:45 | 51439.0545 | 219.996
Devonshire Building | 2017-12-05 20:00 | 51439.1345 | 320.004
Devonshire Building | 2017-12-05 20:15 | 51439.1945 | 240.012
Devonshire Building | 2017-12-05 20:30 | 51439.2395 | 180
Devonshire Building | 2017-12-05 20:45 | 51439.2845 | 180
Devonshire Building | 2017-12-05 21:00 | 51439.3345 | 200.016
Devonshire Building | 2017-12-05 21:15 | 51439.3795 | 180
Devonshire Building | 2017-12-05 21:30 | 51439.4245 | 180
Devonshire Building | 2017-12-05 21:45 | 51439.4645 | 159.984
Devonshire Building | 2017-12-05 22:00 | 51439.5045 | 159.984
Devonshire Building | 2017-12-05 22:15 | 51439.5395 | 140.004
Devonshire Building | 2017-12-05 22:30 | 51439.5795 | 159.984
Devonshire Building | 2017-12-05 22:45 | 51439.6195 | 159.984
Devonshire Building | 2017-12-05 23:00 | 51439.6545 | 140.004
Devonshire Building | 2017-12-05 23:15 | 51439.6945 | 159.984
Devonshire Building | 2017-12-05 23:30 | 51439.7295 | 140.004
Devonshire Building | 2017-12-05 23:45 | 51439.7695 | 159.984
Devonshire Building | 2017-12-06 | 51439.8047 | 140.004
Devonshire Building | 2017-12-06 00:15 | 51439.8447 | 159.984
Devonshire Building | 2017-12-06 00:30 | 51439.8997 | 219.996
Devonshire Building | 2017-12-06 00:45 | 51439.9547 | 219.996
Devonshire Building | 2017-12-06 01:00 | 51439.9947 | 159.984
Devonshire Building | 2017-12-06 01:15 | 51440.0297 | 140.004
Devonshire Building | 2017-12-06 01:30 | 51440.0647 | 140.004
Devonshire Building | 2017-12-06 01:45 | 51440.0997 | 140.004
Devonshire Building | 2017-12-06 02:00 | 51440.1347 | 140.004
Devonshire Building | 2017-12-06 02:15 | 51440.1747 | 159.984
Devonshire Building | 2017-12-06 02:30 | 51440.2097 | 140.004
Devonshire Building | 2017-12-06 02:45 | 51440.2447 | 140.004
Devonshire Building | 2017-12-06 03:00 | 51440.2797 | 140.004
Devonshire Building | 2017-12-06 03:15 | 51440.3147 | 140.004
Devonshire Building | 2017-12-06 03:30 | 51440.3497 | 140.004
Devonshire Building | 2017-12-06 03:45 | 51440.3847 | 140.004
Devonshire Building | 2017-12-06 04:00 | 51440.4197 | 140.004
Devonshire Building | 2017-12-06 04:15 | 51440.4547 | 140.004
Devonshire Building | 2017-12-06 04:30 | 51440.4847 | 119.988
Devonshire Building | 2017-12-06 04:45 | 51440.5197 | 140.004
Devonshire Building | 2017-12-06 05:00 | 51440.5497 | 119.988
Devonshire Building | 2017-12-06 05:15 | 51440.5847 | 140.004
Devonshire Building | 2017-12-06 05:30 | 51440.6197 | 140.004
Devonshire Building | 2017-12-06 05:45 | 51440.6497 | 119.988
Devonshire Building | 2017-12-06 06:00 | 51440.6847 | 140.004
Devonshire Building | 2017-12-06 06:15 | 51440.7197 | 140.004
Devonshire Building | 2017-12-06 06:30 | 51440.7497 | 119.988
Devonshire Building | 2017-12-06 06:45 | 51440.7847 | 140.004
Devonshire Building | 2017-12-06 07:00 | 51440.8197 | 140.004
Devonshire Building | 2017-12-06 07:15 | 51440.8497 | 119.988
Devonshire Building | 2017-12-06 07:30 | 51440.8847 | 140.004
Devonshire Building | 2017-12-06 07:45 | 51440.9597 | 299.988
Devonshire Building | 2017-12-06 08:00 | 51441.0297 | 280.008
Devonshire Building | 2017-12-06 08:15 | 51441.1397 | 439.992
Devonshire Building | 2017-12-06 08:30 | 51441.2197 | 320.004
Devonshire Building | 2017-12-06 08:45 | 51441.3047 | 339.984
Devonshire Building | 2017-12-06 09:00 | 51441.3997 | 380.016
Devonshire Building | 2017-12-06 09:15 | 51441.5047 | 420.012
Devonshire Building | 2017-12-06 09:30 | 51441.6797 | 699.984
Devonshire Building | 2017-12-06 09:45 | 51441.7647 | 339.984
Devonshire Building | 2017-12-06 10:00 | 51441.8597 | 380.016
Devonshire Building | 2017-12-06 10:15 | 51441.9797 | 479.988
Devonshire Building | 2017-12-06 10:30 | 51442.1697 | 759.996
Devonshire Building | 2017-12-06 10:45 | 51442.3947 | 900
Devonshire Building | 2017-12-06 11:00 | 51442.5997 | 820.008
Devonshire Building | 2017-12-06 11:15 | 51442.7847 | 740.016
Devonshire Building | 2017-12-06 11:30 | 51443.0347 | 1000.008
Devonshire Building | 2017-12-06 11:45 | 51443.2747 | 960.012
Devonshire Building | 2017-12-06 12:00 | 51443.4897 | 860.004
Devonshire Building | 2017-12-06 12:15 | 51443.7247 | 939.996
Devonshire Building | 2017-12-06 12:30 | 51443.8997 | 699.984
Devonshire Building | 2017-12-06 12:45 | 51444.0847 | 740.016
Devonshire Building | 2017-12-06 13:00 | 51444.2347 | 600.012
Devonshire Building | 2017-12-06 13:15 | 51444.3897 | 619.992
Devonshire Building | 2017-12-06 13:30 | 51444.5747 | 740.016
Devonshire Building | 2017-12-06 13:45 | 51444.7447 | 680.004
Devonshire Building | 2017-12-06 14:00 | 51444.9147 | 680.004
Devonshire Building | 2017-12-06 14:15 | 51445.1097 | 780.012
Devonshire Building | 2017-12-06 14:30 | 51445.3147 | 820.008
Devonshire Building | 2017-12-06 14:45 | 51445.5347 | 879.984
Devonshire Building | 2017-12-06 15:00 | 51445.6597 | 500.004
Devonshire Building | 2017-12-06 15:15 | 51445.7997 | 560.016
Devonshire Building | 2017-12-06 15:30 | 51445.9347 | 540
Devonshire Building | 2017-12-06 15:45 | 51446.1597 | 900
Devonshire Building | 2017-12-06 16:00 | 51446.3047 | 579.996
Devonshire Building | 2017-12-06 16:15 | 51446.4597 | 619.992
Devonshire Building | 2017-12-06 16:30 | 51446.6197 | 640.008
Devonshire Building | 2017-12-06 16:45 | 51446.7397 | 479.988
Devonshire Building | 2017-12-06 17:00 | 51446.8647 | 500.004
Devonshire Building | 2017-12-06 17:15 | 51447.0097 | 579.996
Devonshire Building | 2017-12-06 17:30 | 51447.1097 | 399.996
Devonshire Building | 2017-12-06 17:45 | 51447.1847 | 299.988
Devonshire Building | 2017-12-06 18:00 | 51447.2597 | 299.988
Devonshire Building | 2017-12-06 18:15 | 51447.3247 | 259.992
Devonshire Building | 2017-12-06 18:30 | 51447.3897 | 259.992
Devonshire Building | 2017-12-06 18:45 | 51447.4497 | 240.012
Devonshire Building | 2017-12-06 19:00 | 51447.4997 | 200.016
Devonshire Building | 2017-12-06 19:15 | 51447.5397 | 159.984
Devonshire Building | 2017-12-06 19:30 | 51447.5897 | 200.016
Devonshire Building | 2017-12-06 19:45 | 51447.6447 | 219.996
Devonshire Building | 2017-12-06 20:00 | 51447.6847 | 159.984
Devonshire Building | 2017-12-06 20:15 | 51447.7347 | 200.016
Devonshire Building | 2017-12-06 20:30 | 51447.7797 | 180
Devonshire Building | 2017-12-06 20:45 | 51447.8247 | 180
Devonshire Building | 2017-12-06 21:00 | 51447.8597 | 140.004
Devonshire Building | 2017-12-06 21:15 | 51447.8997 | 159.984
Devonshire Building | 2017-12-06 21:30 | 51447.9347 | 140.004
Devonshire Building | 2017-12-06 21:45 | 51447.9697 | 140.004
Devonshire Building | 2017-12-06 22:00 | 51448.0097 | 159.984
Devonshire Building | 2017-12-06 22:15 | 51448.0447 | 140.004
Devonshire Building | 2017-12-06 22:30 | 51448.0797 | 140.004
Devonshire Building | 2017-12-06 22:45 | 51448.1147 | 140.004
Devonshire Building | 2017-12-06 23:00 | 51448.1497 | 140.004
Devonshire Building | 2017-12-06 23:15 | 51448.1847 | 140.004
Devonshire Building | 2017-12-06 23:30 | 51448.2247 | 159.984
Devonshire Building | 2017-12-06 23:45 | 51448.2597 | 140.004
Devonshire Building | 2017-12-07 | 51448.293 | 140.004
Devonshire Building | 2017-12-07 00:15 | 51448.328 | 140.004
Devonshire Building | 2017-12-07 00:30 | 51448.363 | 140.004
Devonshire Building | 2017-12-07 00:45 | 51448.393 | 119.988
Devonshire Building | 2017-12-07 01:00 | 51448.428 | 140.004
Devonshire Building | 2017-12-07 01:15 | 51448.463 | 140.004
Devonshire Building | 2017-12-07 01:30 | 51448.498 | 140.004
Devonshire Building | 2017-12-07 01:45 | 51448.533 | 140.004
Devonshire Building | 2017-12-07 02:00 | 51448.568 | 140.004
Devonshire Building | 2017-12-07 02:15 | 51448.598 | 119.988
Devonshire Building | 2017-12-07 02:30 | 51448.633 | 140.004
Devonshire Building | 2017-12-07 02:45 | 51448.673 | 159.984
Devonshire Building | 2017-12-07 03:00 | 51448.728 | 219.996
Devonshire Building | 2017-12-07 03:15 | 51448.773 | 180
Devonshire Building | 2017-12-07 03:30 | 51448.808 | 140.004
Devonshire Building | 2017-12-07 03:45 | 51448.843 | 140.004
Devonshire Building | 2017-12-07 04:00 | 51448.873 | 119.988
Devonshire Building | 2017-12-07 04:15 | 51448.908 | 140.004
Devonshire Building | 2017-12-07 04:30 | 51448.943 | 140.004
Devonshire Building | 2017-12-07 04:45 | 51448.973 | 119.988
Devonshire Building | 2017-12-07 05:00 | 51449.008 | 140.004
Devonshire Building | 2017-12-07 05:15 | 51449.048 | 159.984
Devonshire Building | 2017-12-07 05:30 | 51449.083 | 140.004
Devonshire Building | 2017-12-07 05:45 | 51449.118 | 140.004
Devonshire Building | 2017-12-07 06:00 | 51449.148 | 119.988
Devonshire Building | 2017-12-07 06:15 | 51449.183 | 140.004
Devonshire Building | 2017-12-07 06:30 | 51449.218 | 140.004
Devonshire Building | 2017-12-07 06:45 | 51449.248 | 119.988
Devonshire Building | 2017-12-07 07:00 | 51449.283 | 140.004
Devonshire Building | 2017-12-07 07:15 | 51449.318 | 140.004
Devonshire Building | 2017-12-07 07:30 | 51449.408 | 360
Devonshire Building | 2017-12-07 07:45 | 51449.488 | 320.004
Devonshire Building | 2017-12-07 08:00 | 51449.548 | 240.012
Devonshire Building | 2017-12-07 08:15 | 51449.613 | 259.992
Devonshire Building | 2017-12-07 08:30 | 51449.708 | 380.016
Devonshire Building | 2017-12-07 08:45 | 51449.803 | 380.016
Devonshire Building | 2017-12-07 09:00 | 51449.923 | 479.988
Devonshire Building | 2017-12-07 09:15 | 51450.038 | 460.008
Devonshire Building | 2017-12-07 09:30 | 51450.133 | 380.016
Devonshire Building | 2017-12-07 09:45 | 51450.288 | 619.992
Devonshire Building | 2017-12-07 10:00 | 51450.398 | 439.992
Devonshire Building | 2017-12-07 10:15 | 51450.538 | 560.016
Devonshire Building | 2017-12-07 10:30 | 51450.653 | 460.008
Devonshire Building | 2017-12-07 10:45 | 51450.883 | 920.016
Devonshire Building | 2017-12-07 11:00 | 51451.118 | 939.996
Devonshire Building | 2017-12-07 11:15 | 51451.333 | 860.004
Devonshire Building | 2017-12-07 11:30 | 51451.518 | 740.016
Devonshire Building | 2017-12-07 11:45 | 51451.693 | 699.984
Devonshire Building | 2017-12-07 12:00 | 51451.903 | 839.988
Devonshire Building | 2017-12-07 12:15 | 51452.118 | 860.004
Devonshire Building | 2017-12-07 12:30 | 51452.338 | 879.984
Devonshire Building | 2017-12-07 12:45 | 51452.523 | 740.016
Devonshire Building | 2017-12-07 13:00 | 51452.683 | 640.008
Devonshire Building | 2017-12-07 13:15 | 51452.858 | 699.984
Devonshire Building | 2017-12-07 13:30 | 51453.038 | 720
Devonshire Building | 2017-12-07 13:45 | 51453.198 | 640.008
Devonshire Building | 2017-12-07 14:00 | 51453.468 | 1080
Devonshire Building | 2017-12-07 14:15 | 51453.688 | 879.984
Devonshire Building | 2017-12-07 14:30 | 51453.853 | 659.988
Devonshire Building | 2017-12-07 14:45 | 51453.988 | 540
Devonshire Building | 2017-12-07 15:00 | 51454.203 | 860.004
Devonshire Building | 2017-12-07 15:15 | 51454.403 | 799.992
Devonshire Building | 2017-12-07 15:30 | 51454.543 | 560.016
Devonshire Building | 2017-12-07 15:45 | 51454.728 | 740.016
Devonshire Building | 2017-12-07 16:00 | 51454.863 | 540
Devonshire Building | 2017-12-07 16:15 | 51455.018 | 619.992
Devonshire Building | 2017-12-07 16:30 | 51455.183 | 659.988
Devonshire Building | 2017-12-07 16:45 | 51455.313 | 519.984
Devonshire Building | 2017-12-07 17:00 | 51455.433 | 479.988
Devonshire Building | 2017-12-07 17:15 | 51455.543 | 439.992
Devonshire Building | 2017-12-07 17:30 | 51455.638 | 380.016
Devonshire Building | 2017-12-07 17:45 | 51455.718 | 320.004
Devonshire Building | 2017-12-07 18:00 | 51455.808 | 360
Devonshire Building | 2017-12-07 18:15 | 51455.903 | 380.016
Devonshire Building | 2017-12-07 18:30 | 51455.978 | 299.988
Devonshire Building | 2017-12-07 18:45 | 51456.033 | 219.996
Devonshire Building | 2017-12-07 19:00 | 51456.108 | 299.988
Devonshire Building | 2017-12-07 19:15 | 51456.163 | 219.996
Devonshire Building | 2017-12-07 19:30 | 51456.218 | 219.996
Devonshire Building | 2017-12-07 19:45 | 51456.278 | 240.012
Devonshire Building | 2017-12-07 20:00 | 51456.328 | 200.016
Devonshire Building | 2017-12-07 20:15 | 51456.383 | 219.996
Devonshire Building | 2017-12-07 20:30 | 51456.438 | 219.996
Devonshire Building | 2017-12-07 20:45 | 51456.483 | 180
Devonshire Building | 2017-12-07 21:00 | 51456.528 | 180
Devonshire Building | 2017-12-07 21:15 | 51456.578 | 200.016
Devonshire Building | 2017-12-07 21:30 | 51456.618 | 159.984
Devonshire Building | 2017-12-07 21:45 | 51456.658 | 159.984
Devonshire Building | 2017-12-07 22:00 | 51456.703 | 180
Devonshire Building | 2017-12-07 22:15 | 51456.753 | 200.016
Devonshire Building | 2017-12-07 22:30 | 51456.793 | 159.984
Devonshire Building | 2017-12-07 22:45 | 51456.828 | 140.004
Devonshire Building | 2017-12-07 23:00 | 51456.868 | 159.984
Devonshire Building | 2017-12-07 23:15 | 51456.903 | 140.004
Devonshire Building | 2017-12-07 23:30 | 51456.938 | 140.004
Devonshire Building | 2017-12-07 23:45 | 51456.973 | 140.004
Devonshire Building | 2017-12-08 | 51457.0078 | 140.004
Devonshire Building | 2017-12-08 00:15 | 51457.0478 | 159.984
Devonshire Building | 2017-12-08 00:30 | 51457.0878 | 159.984
Devonshire Building | 2017-12-08 00:45 | 51457.1428 | 219.996
Devonshire Building | 2017-12-08 01:00 | 51457.1928 | 200.016
Devonshire Building | 2017-12-08 01:15 | 51457.2278 | 140.004
Devonshire Building | 2017-12-08 01:30 | 51457.2628 | 140.004
Devonshire Building | 2017-12-08 01:45 | 51457.2928 | 119.988
Devonshire Building | 2017-12-08 02:00 | 51457.3278 | 140.004
Devonshire Building | 2017-12-08 02:15 | 51457.3628 | 140.004
Devonshire Building | 2017-12-08 02:30 | 51457.3978 | 140.004
Devonshire Building | 2017-12-08 02:45 | 51457.4328 | 140.004
Devonshire Building | 2017-12-08 03:00 | 51457.4678 | 140.004
Devonshire Building | 2017-12-08 03:15 | 51457.5028 | 140.004
Devonshire Building | 2017-12-08 03:30 | 51457.5378 | 140.004
Devonshire Building | 2017-12-08 03:45 | 51457.5678 | 119.988
Devonshire Building | 2017-12-08 04:00 | 51457.6028 | 140.004
Devonshire Building | 2017-12-08 04:15 | 51457.6378 | 140.004
Devonshire Building | 2017-12-08 04:30 | 51457.6728 | 140.004
Devonshire Building | 2017-12-08 04:45 | 51457.7028 | 119.988
Devonshire Building | 2017-12-08 05:00 | 51457.7378 | 140.004
Devonshire Building | 2017-12-08 05:15 | 51457.7678 | 119.988
Devonshire Building | 2017-12-08 05:30 | 51457.8028 | 140.004
Devonshire Building | 2017-12-08 05:45 | 51457.8328 | 119.988
Devonshire Building | 2017-12-08 06:00 | 51457.8678 | 140.004
Devonshire Building | 2017-12-08 06:15 | 51457.8978 | 119.988
Devonshire Building | 2017-12-08 06:30 | 51457.9328 | 140.004
Devonshire Building | 2017-12-08 06:45 | 51457.9628 | 119.988
Devonshire Building | 2017-12-08 07:00 | 51457.9978 | 140.004
Devonshire Building | 2017-12-08 07:15 | 51458.0278 | 119.988
Devonshire Building | 2017-12-08 07:30 | 51458.0978 | 280.008
Devonshire Building | 2017-12-08 07:45 | 51458.1478 | 200.016
Devonshire Building | 2017-12-08 08:00 | 51458.2078 | 240.012
Devonshire Building | 2017-12-08 08:15 | 51458.2978 | 360
Devonshire Building | 2017-12-08 08:30 | 51458.3628 | 259.992
Devonshire Building | 2017-12-08 08:45 | 51458.4778 | 460.008
Devonshire Building | 2017-12-08 09:00 | 51458.5928 | 460.008
Devonshire Building | 2017-12-08 09:15 | 51458.6778 | 339.984
Devonshire Building | 2017-12-08 09:30 | 51458.7878 | 439.992
Devonshire Building | 2017-12-08 09:45 | 51458.8978 | 439.992
Devonshire Building | 2017-12-08 10:00 | 51459.0528 | 619.992
Devonshire Building | 2017-12-08 10:15 | 51459.2078 | 619.992
Devonshire Building | 2017-12-08 10:30 | 51459.3328 | 500.004
Devonshire Building | 2017-12-08 10:45 | 51459.4828 | 600.012
Devonshire Building | 2017-12-08 11:00 | 51459.7078 | 900
Devonshire Building | 2017-12-08 11:15 | 51459.8978 | 759.996
Devonshire Building | 2017-12-08 11:30 | 51460.1178 | 879.984
Devonshire Building | 2017-12-08 11:45 | 51460.2728 | 619.992
Devonshire Building | 2017-12-08 12:00 | 51460.4428 | 680.004
Devonshire Building | 2017-12-08 12:15 | 51460.6578 | 860.004
Devonshire Building | 2017-12-08 12:30 | 51460.8928 | 939.996
Devonshire Building | 2017-12-08 12:45 | 51461.0778 | 740.016
Devonshire Building | 2017-12-08 13:00 | 51461.2478 | 680.004
Devonshire Building | 2017-12-08 13:15 | 51461.3478 | 399.996
Devonshire Building | 2017-12-08 13:30 | 51461.4728 | 500.004
Devonshire Building | 2017-12-08 13:45 | 51461.5628 | 360
Devonshire Building | 2017-12-08 14:00 | 51461.6828 | 479.988
Devonshire Building | 2017-12-08 14:15 | 51461.7578 | 299.988
Devonshire Building | 2017-12-08 14:30 | 51461.8928 | 540
Devonshire Building | 2017-12-08 14:45 | 51461.9978 | 420.012
Devonshire Building | 2017-12-08 15:00 | 51462.1578 | 640.008
Devonshire Building | 2017-12-08 15:15 | 51462.2528 | 380.016
Devonshire Building | 2017-12-08 15:30 | 51462.3778 | 500.004
Devonshire Building | 2017-12-08 15:45 | 51462.4728 | 380.016
Devonshire Building | 2017-12-08 16:00 | 51462.6178 | 579.996
Devonshire Building | 2017-12-08 16:15 | 51462.7528 | 540
Devonshire Building | 2017-12-08 16:30 | 51462.8578 | 420.012
Devonshire Building | 2017-12-08 16:45 | 51462.9628 | 420.012
Devonshire Building | 2017-12-08 17:00 | 51463.0778 | 460.008
Devonshire Building | 2017-12-08 17:15 | 51463.1928 | 460.008
Devonshire Building | 2017-12-08 17:30 | 51463.2978 | 420.012
Devonshire Building | 2017-12-08 17:45 | 51463.3578 | 240.012
Devonshire Building | 2017-12-08 18:00 | 51463.4328 | 299.988
Devonshire Building | 2017-12-08 18:15 | 51463.5278 | 380.016
Devonshire Building | 2017-12-08 18:30 | 51463.5978 | 280.008
Devonshire Building | 2017-12-08 18:45 | 51463.6628 | 259.992
Devonshire Building | 2017-12-08 19:00 | 51463.7128 | 200.016
Devonshire Building | 2017-12-08 19:15 | 51463.7578 | 180
Devonshire Building | 2017-12-08 19:30 | 51463.8078 | 200.016
Devonshire Building | 2017-12-08 19:45 | 51463.8628 | 219.996
Devonshire Building | 2017-12-08 20:00 | 51463.9028 | 159.984
Devonshire Building | 2017-12-08 20:15 | 51463.9428 | 159.984
Devonshire Building | 2017-12-08 20:30 | 51463.9828 | 159.984
Devonshire Building | 2017-12-08 20:45 | 51464.0178 | 140.004
Devonshire Building | 2017-12-08 21:00 | 51464.0578 | 159.984
Devonshire Building | 2017-12-08 21:15 | 51464.0928 | 140.004
Devonshire Building | 2017-12-08 21:30 | 51464.1328 | 159.984
Devonshire Building | 2017-12-08 21:45 | 51464.1678 | 140.004
Devonshire Building | 2017-12-08 22:00 | 51464.2028 | 140.004
Devonshire Building | 2017-12-08 22:15 | 51464.2378 | 140.004
Devonshire Building | 2017-12-08 22:30 | 51464.2728 | 140.004
Devonshire Building | 2017-12-08 22:45 | 51464.3078 | 140.004
Devonshire Building | 2017-12-08 23:00 | 51464.3428 | 140.004
Devonshire Building | 2017-12-08 23:15 | 51464.3778 | 140.004
Devonshire Building | 2017-12-08 23:30 | 51464.4178 | 159.984
Devonshire Building | 2017-12-08 23:45 | 51464.4678 | 200.016
Devonshire Building | 2017-12-09 | 51464.5195 | 200.016
Devonshire Building | 2017-12-09 00:15 | 51464.5545 | 140.004
Devonshire Building | 2017-12-09 00:30 | 51464.5895 | 140.004
Devonshire Building | 2017-12-09 00:45 | 51464.6195 | 119.988
Devonshire Building | 2017-12-09 01:00 | 51464.6545 | 140.004
Devonshire Building | 2017-12-09 01:15 | 51464.6895 | 140.004
Devonshire Building | 2017-12-09 01:30 | 51464.7245 | 140.004
Devonshire Building | 2017-12-09 01:45 | 51464.7595 | 140.004
Devonshire Building | 2017-12-09 02:00 | 51464.7945 | 140.004
Devonshire Building | 2017-12-09 02:15 | 51464.8245 | 119.988
Devonshire Building | 2017-12-09 02:30 | 51464.8595 | 140.004
Devonshire Building | 2017-12-09 02:45 | 51464.8945 | 140.004
Devonshire Building | 2017-12-09 03:00 | 51464.9295 | 140.004
Devonshire Building | 2017-12-09 03:15 | 51464.9645 | 140.004
Devonshire Building | 2017-12-09 03:30 | 51464.9995 | 140.004
Devonshire Building | 2017-12-09 03:45 | 51465.0295 | 119.988
Devonshire Building | 2017-12-09 04:00 | 51465.0645 | 140.004
Devonshire Building | 2017-12-09 04:15 | 51465.0995 | 140.004
Devonshire Building | 2017-12-09 04:30 | 51465.1295 | 119.988
Devonshire Building | 2017-12-09 04:45 | 51465.1645 | 140.004
Devonshire Building | 2017-12-09 05:00 | 51465.1995 | 140.004
Devonshire Building | 2017-12-09 05:15 | 51465.2295 | 119.988
Devonshire Building | 2017-12-09 05:30 | 51465.2645 | 140.004
Devonshire Building | 2017-12-09 05:45 | 51465.2995 | 140.004
Devonshire Building | 2017-12-09 06:00 | 51465.3295 | 119.988
Devonshire Building | 2017-12-09 06:15 | 51465.3645 | 140.004
Devonshire Building | 2017-12-09 06:30 | 51465.3945 | 119.988
Devonshire Building | 2017-12-09 06:45 | 51465.4245 | 119.988
Devonshire Building | 2017-12-09 07:00 | 51465.4595 | 140.004
Devonshire Building | 2017-12-09 07:15 | 51465.4895 | 119.988
Devonshire Building | 2017-12-09 07:30 | 51465.5195 | 119.988
Devonshire Building | 2017-12-09 07:45 | 51465.5595 | 159.984
Devonshire Building | 2017-12-09 08:00 | 51465.6045 | 180
Devonshire Building | 2017-12-09 08:15 | 51465.6495 | 180
Devonshire Building | 2017-12-09 08:30 | 51465.6945 | 180
Devonshire Building | 2017-12-09 08:45 | 51465.7395 | 180
Devonshire Building | 2017-12-09 09:00 | 51465.7845 | 180
Devonshire Building | 2017-12-09 09:15 | 51465.8295 | 180
Devonshire Building | 2017-12-09 09:30 | 51465.8745 | 180
Devonshire Building | 2017-12-09 09:45 | 51465.9195 | 180
Devonshire Building | 2017-12-09 10:00 | 51465.9645 | 180
Devonshire Building | 2017-12-09 10:15 | 51466.0095 | 180
Devonshire Building | 2017-12-09 10:30 | 51466.0545 | 180
Devonshire Building | 2017-12-09 10:45 | 51466.1095 | 219.996
Devonshire Building | 2017-12-09 11:00 | 51466.1495 | 159.984
Devonshire Building | 2017-12-09 11:15 | 51466.1995 | 200.016
Devonshire Building | 2017-12-09 11:30 | 51466.2395 | 159.984
Devonshire Building | 2017-12-09 11:45 | 51466.2595 | 79.992
Devonshire Building | 2017-12-09 12:00 | 51466.2695 | 39.996
Devonshire Building | 2017-12-09 12:15 | 51467.2145 | 3780
Devonshire Building | 2017-12-09 12:30 | 51467.2695 | 219.996
Devonshire Building | 2017-12-09 12:45 | 51467.2745 | 20.016
Devonshire Building | 2017-12-09 13:00 | 51467.2845 | 39.996
Devonshire Building | 2017-12-09 13:15 | 51467.2945 | 39.996
Devonshire Building | 2017-12-09 13:30 | 51467.3045 | 39.996
Devonshire Building | 2017-12-09 13:45 | 51467.3095 | 20.016
Devonshire Building | 2017-12-09 14:00 | 51467.3145 | 20.016
Devonshire Building | 2017-12-09 14:15 | 51467.3245 | 39.996
Devonshire Building | 2017-12-09 14:30 | 51467.3345 | 39.996
Devonshire Building | 2017-12-09 14:45 | 51467.3395 | 20.016
Devonshire Building | 2017-12-09 15:00 | 51467.3445 | 20.016
Devonshire Building | 2017-12-09 15:15 | 51467.3545 | 39.996
Devonshire Building | 2017-12-09 15:30 | 51467.3595 | 20.016
Devonshire Building | 2017-12-09 15:45 | 51467.3695 | 39.996
Devonshire Building | 2017-12-09 16:00 | 51467.3745 | 20.016
Devonshire Building | 2017-12-09 16:15 | 51467.3845 | 39.996
Devonshire Building | 2017-12-09 16:30 | 51467.3895 | 20.016
Devonshire Building | 2017-12-09 16:45 | 51467.3995 | 39.996
Devonshire Building | 2017-12-09 17:00 | 51467.4095 | 39.996
Devonshire Building | 2017-12-09 17:15 | 51467.4845 | 299.988
Devonshire Building | 2017-12-09 17:30 | 51467.6795 | 780.012
Devonshire Building | 2017-12-09 17:45 | 51467.6995 | 79.992
Devonshire Building | 2017-12-09 18:00 | 51467.7145 | 60.012
Devonshire Building | 2017-12-09 18:15 | 51467.7345 | 79.992
Devonshire Building | 2017-12-09 18:30 | 51467.7545 | 79.992
Devonshire Building | 2017-12-09 18:45 | 51467.7745 | 79.992
Devonshire Building | 2017-12-09 19:00 | 51467.8045 | 119.988
Devonshire Building | 2017-12-09 19:15 | 51467.8245 | 79.992
Devonshire Building | 2017-12-09 19:30 | 51467.8445 | 79.992
Devonshire Building | 2017-12-09 19:45 | 51467.8695 | 100.008
Devonshire Building | 2017-12-09 20:00 | 51467.8945 | 100.008
Devonshire Building | 2017-12-09 20:15 | 51467.9145 | 79.992
Devonshire Building | 2017-12-09 20:30 | 51467.9345 | 79.992
Devonshire Building | 2017-12-09 20:45 | 51467.9495 | 60.012
Devonshire Building | 2017-12-09 21:00 | 51467.9695 | 79.992
Devonshire Building | 2017-12-09 21:15 | 51467.9895 | 79.992
Devonshire Building | 2017-12-09 21:30 | 51468.0095 | 79.992
Devonshire Building | 2017-12-09 21:45 | 51468.0295 | 79.992
Devonshire Building | 2017-12-09 22:00 | 51468.0495 | 79.992
Devonshire Building | 2017-12-09 22:15 | 51468.0695 | 79.992
Devonshire Building | 2017-12-09 22:30 | 51468.0895 | 79.992
Devonshire Building | 2017-12-09 22:45 | 51468.1095 | 79.992
Devonshire Building | 2017-12-09 23:00 | 51468.1345 | 100.008
Devonshire Building | 2017-12-09 23:15 | 51468.1545 | 79.992
Devonshire Building | 2017-12-09 23:30 | 51468.1745 | 79.992
Devonshire Building | 2017-12-09 23:45 | 51468.1995 | 100.008
Devonshire Building | 2017-12-10 | 51468.2188 | 79.992
Devonshire Building | 2017-12-10 00:15 | 51468.2438 | 100.008
Devonshire Building | 2017-12-10 00:30 | 51468.2637 | 79.992
Devonshire Building | 2017-12-10 00:45 | 51468.2937 | 119.988
Devonshire Building | 2017-12-10 01:00 | 51468.3287 | 140.004
Devonshire Building | 2017-12-10 01:15 | 51468.3637 | 140.004
Devonshire Building | 2017-12-10 01:30 | 51468.3888 | 100.008
Devonshire Building | 2017-12-10 01:45 | 51468.4087 | 79.992
Devonshire Building | 2017-12-10 02:00 | 51468.4338 | 100.008
Devonshire Building | 2017-12-10 02:15 | 51468.4588 | 100.008
Devonshire Building | 2017-12-10 02:30 | 51468.4788 | 79.992
Devonshire Building | 2017-12-10 02:45 | 51468.5038 | 100.008
Devonshire Building | 2017-12-10 03:00 | 51468.5288 | 100.008
Devonshire Building | 2017-12-10 03:15 | 51468.5538 | 100.008
Devonshire Building | 2017-12-10 03:30 | 51468.5788 | 100.008
Devonshire Building | 2017-12-10 03:45 | 51468.6038 | 100.008
Devonshire Building | 2017-12-10 04:00 | 51468.6288 | 100.008
Devonshire Building | 2017-12-10 04:15 | 51468.6538 | 100.008
Devonshire Building | 2017-12-10 04:30 | 51468.6788 | 100.008
Devonshire Building | 2017-12-10 04:45 | 51468.7088 | 119.988
Devonshire Building | 2017-12-10 05:00 | 51468.7488 | 159.984
Devonshire Building | 2017-12-10 05:15 | 51468.7788 | 119.988
Devonshire Building | 2017-12-10 05:30 | 51468.8088 | 119.988
Devonshire Building | 2017-12-10 05:45 | 51468.8338 | 100.008
Devonshire Building | 2017-12-10 06:00 | 51468.8588 | 100.008
Devonshire Building | 2017-12-10 06:15 | 51468.8788 | 79.992
Devonshire Building | 2017-12-10 06:30 | 51468.9038 | 100.008
Devonshire Building | 2017-12-10 06:45 | 51468.9288 | 100.008
Devonshire Building | 2017-12-10 07:00 | 51468.9538 | 100.008
Devonshire Building | 2017-12-10 07:15 | 51468.9788 | 100.008
Devonshire Building | 2017-12-10 07:30 | 51469.0038 | 100.008
Devonshire Building | 2017-12-10 07:45 | 51469.0388 | 140.004
Devonshire Building | 2017-12-10 08:00 | 51469.0788 | 159.984
Devonshire Building | 2017-12-10 08:15 | 51469.1138 | 140.004
Devonshire Building | 2017-12-10 08:30 | 51469.1538 | 159.984
Devonshire Building | 2017-12-10 08:45 | 51469.1938 | 159.984
Devonshire Building | 2017-12-10 09:00 | 51469.2338 | 159.984
Devonshire Building | 2017-12-10 09:15 | 51469.2737 | 159.984
Devonshire Building | 2017-12-10 09:30 | 51469.3087 | 140.004
Devonshire Building | 2017-12-10 09:45 | 51469.3487 | 159.984
Devonshire Building | 2017-12-10 10:00 | 51469.3887 | 159.984
Devonshire Building | 2017-12-10 10:15 | 51469.4237 | 140.004
Devonshire Building | 2017-12-10 10:30 | 51469.4637 | 159.984
Devonshire Building | 2017-12-10 10:45 | 51469.5037 | 159.984
Devonshire Building | 2017-12-10 11:00 | 51469.5437 | 159.984
Devonshire Building | 2017-12-10 11:15 | 51469.5837 | 159.984
Devonshire Building | 2017-12-10 11:30 | 51469.6137 | 119.988
Devonshire Building | 2017-12-10 11:45 | 51469.6337 | 79.992
Devonshire Building | 2017-12-10 12:00 | 51469.6487 | 60.012
Devonshire Building | 2017-12-10 12:15 | 51469.6637 | 60.012
Devonshire Building | 2017-12-10 12:30 | 51469.6787 | 60.012
Devonshire Building | 2017-12-10 12:45 | 51469.6937 | 60.012
Devonshire Building | 2017-12-10 13:00 | 51469.7037 | 39.996
Devonshire Building | 2017-12-10 13:15 | 51469.7187 | 60.012
Devonshire Building | 2017-12-10 13:30 | 51469.7337 | 60.012
Devonshire Building | 2017-12-10 13:45 | 51469.7487 | 60.012
Devonshire Building | 2017-12-10 14:00 | 51469.7637 | 60.012
Devonshire Building | 2017-12-10 14:15 | 51469.7787 | 60.012
Devonshire Building | 2017-12-10 14:30 | 51469.7937 | 60.012
Devonshire Building | 2017-12-10 14:45 | 51469.8088 | 60.012
Devonshire Building | 2017-12-10 15:00 | 51469.8188 | 39.996
Devonshire Building | 2017-12-10 15:15 | 51469.8338 | 60.012
Devonshire Building | 2017-12-10 15:30 | 51469.8488 | 60.012
Devonshire Building | 2017-12-10 15:45 | 51469.8588 | 39.996
Devonshire Building | 2017-12-10 16:00 | 51469.8738 | 60.012
Devonshire Building | 2017-12-10 16:15 | 51469.8888 | 60.012
Devonshire Building | 2017-12-10 16:30 | 51469.8988 | 39.996
Devonshire Building | 2017-12-10 16:45 | 51469.9138 | 60.012
Devonshire Building | 2017-12-10 17:00 | 51469.9238 | 39.996
Devonshire Building | 2017-12-10 17:15 | 51469.9388 | 60.012
Devonshire Building | 2017-12-10 17:30 | 51470.2288 | 1159.992
Devonshire Building | 2017-12-10 17:45 | 51470.2438 | 60.012
Devonshire Building | 2017-12-10 18:00 | 51470.2538 | 39.996
Devonshire Building | 2017-12-10 18:15 | 51470.2638 | 39.996
Devonshire Building | 2017-12-10 18:30 | 51470.2788 | 60.012
Devonshire Building | 2017-12-10 18:45 | 51470.2888 | 39.996
Devonshire Building | 2017-12-10 19:00 | 51470.2988 | 39.996
Devonshire Building | 2017-12-10 19:15 | 51470.3088 | 39.996
Devonshire Building | 2017-12-10 19:30 | 51470.3238 | 60.012
Devonshire Building | 2017-12-10 19:45 | 51470.3338 | 39.996
Devonshire Building | 2017-12-10 20:00 | 51470.3488 | 60.012
Devonshire Building | 2017-12-10 20:15 | 51470.3638 | 60.012
Devonshire Building | 2017-12-10 20:30 | 51470.3788 | 60.012
Devonshire Building | 2017-12-10 20:45 | 51470.3938 | 60.012
Devonshire Building | 2017-12-10 21:00 | 51470.4088 | 60.012
Devonshire Building | 2017-12-10 21:15 | 51470.4188 | 39.996
Devonshire Building | 2017-12-10 21:30 | 51470.4338 | 60.012
Devonshire Building | 2017-12-10 21:45 | 51470.4688 | 140.004
Devonshire Building | 2017-12-10 22:00 | 51470.4838 | 60.012
Devonshire Building | 2017-12-10 22:15 | 51470.4988 | 60.012
Devonshire Building | 2017-12-10 22:30 | 51470.5088 | 39.996
Devonshire Building | 2017-12-10 22:45 | 51470.5238 | 60.012
Devonshire Building | 2017-12-10 23:00 | 51470.5338 | 39.996
Devonshire Building | 2017-12-10 23:15 | 51470.5488 | 60.012
Devonshire Building | 2017-12-10 23:30 | 51470.5588 | 39.996
Devonshire Building | 2017-12-10 23:45 | 51470.8438 | 1140.012
Devonshire Building | 2017-12-11 | 51470.8594 | 60.012
Devonshire Building | 2017-12-11 00:15 | 51470.8694 | 39.996
Devonshire Building | 2017-12-11 00:30 | 51470.8794 | 39.996
Devonshire Building | 2017-12-11 00:45 | 51470.8944 | 60.012
Devonshire Building | 2017-12-11 01:00 | 51470.9044 | 39.996
Devonshire Building | 2017-12-11 01:15 | 51470.9144 | 39.996
Devonshire Building | 2017-12-11 01:30 | 51470.9294 | 60.012
Devonshire Building | 2017-12-11 01:45 | 51470.9394 | 39.996
Devonshire Building | 2017-12-11 02:00 | 51470.9494 | 39.996
Devonshire Building | 2017-12-11 02:15 | 51470.9644 | 60.012
Devonshire Building | 2017-12-11 02:30 | 51470.9794 | 60.012
Devonshire Building | 2017-12-11 02:45 | 51470.9944 | 60.012
Devonshire Building | 2017-12-11 03:00 | 51471.0044 | 39.996
Devonshire Building | 2017-12-11 03:15 | 51471.0194 | 60.012
Devonshire Building | 2017-12-11 03:30 | 51471.0344 | 60.012
Devonshire Building | 2017-12-11 03:45 | 51471.0494 | 60.012
Devonshire Building | 2017-12-11 04:00 | 51471.0594 | 39.996
Devonshire Building | 2017-12-11 04:15 | 51471.0744 | 60.012
Devonshire Building | 2017-12-11 04:30 | 51471.0844 | 39.996
Devonshire Building | 2017-12-11 04:45 | 51471.0994 | 60.012
Devonshire Building | 2017-12-11 05:00 | 51471.1094 | 39.996
Devonshire Building | 2017-12-11 05:15 | 51471.1244 | 60.012
Devonshire Building | 2017-12-11 05:30 | 51471.1344 | 39.996
Devonshire Building | 2017-12-11 05:45 | 51471.1494 | 60.012
Devonshire Building | 2017-12-11 06:00 | 51471.4394 | 1159.992
Devonshire Building | 2017-12-11 06:15 | 51471.4494 | 39.996
Devonshire Building | 2017-12-11 06:30 | 51471.4594 | 39.996
Devonshire Building | 2017-12-11 06:45 | 51471.4744 | 60.012
Devonshire Building | 2017-12-11 07:00 | 51471.4844 | 39.996
Devonshire Building | 2017-12-11 07:15 | 51471.4944 | 39.996
Devonshire Building | 2017-12-11 07:30 | 51471.5094 | 60.012
Devonshire Building | 2017-12-11 07:45 | 51471.5294 | 79.992
Devonshire Building | 2017-12-11 08:00 | 51471.5544 | 100.008
Devonshire Building | 2017-12-11 08:15 | 51471.5894 | 140.004
Devonshire Building | 2017-12-11 08:30 | 51471.6144 | 100.008
Devonshire Building | 2017-12-11 08:45 | 51471.9544 | 1360.008
Devonshire Building | 2017-12-11 09:00 | 51471.9894 | 140.004
Devonshire Building | 2017-12-11 09:15 | 51472.0194 | 119.988
Devonshire Building | 2017-12-11 09:30 | 51472.0544 | 140.004
Devonshire Building | 2017-12-11 09:45 | 51472.0894 | 140.004
Devonshire Building | 2017-12-11 10:00 | 51472.4294 | 1360.008
Devonshire Building | 2017-12-11 10:15 | 51472.4644 | 140.004
Devonshire Building | 2017-12-11 10:30 | 51472.5044 | 159.984
Devonshire Building | 2017-12-11 10:45 | 51472.8444 | 1360.008
Devonshire Building | 2017-12-11 11:00 | 51472.8994 | 219.996
Devonshire Building | 2017-12-11 11:15 | 51472.9844 | 339.984
Devonshire Building | 2017-12-11 11:30 | 51473.4244 | 1760.004
Devonshire Building | 2017-12-11 11:45 | 51473.5494 | 500.004
Devonshire Building | 2017-12-11 12:00 | 51473.6744 | 500.004
Devonshire Building | 2017-12-11 12:15 | 51473.8344 | 640.008
Devonshire Building | 2017-12-11 12:30 | 51474.1594 | 1299.996
Devonshire Building | 2017-12-11 12:45 | 51474.2394 | 320.004
Devonshire Building | 2017-12-11 13:00 | 51474.6494 | 1640.016
Devonshire Building | 2017-12-11 13:15 | 51474.7444 | 380.016
Devonshire Building | 2017-12-11 13:30 | 51474.8444 | 399.996
Devonshire Building | 2017-12-11 13:45 | 51474.9344 | 360
Devonshire Building | 2017-12-11 14:00 | 51475.1544 | 879.984
Devonshire Building | 2017-12-11 14:15 | 51475.4144 | 1040.004
Devonshire Building | 2017-12-11 14:30 | 51475.4894 | 299.988
Devonshire Building | 2017-12-11 14:45 | 51475.5644 | 299.988
Devonshire Building | 2017-12-11 15:00 | 51475.6894 | 500.004
Devonshire Building | 2017-12-11 15:15 | 51475.9894 | 1199.988
Devonshire Building | 2017-12-11 15:30 | 51476.0494 | 240.012
Devonshire Building | 2017-12-11 15:45 | 51476.1044 | 219.996
Devonshire Building | 2017-12-11 16:00 | 51476.1594 | 219.996
Devonshire Building | 2017-12-11 16:15 | 51476.3294 | 680.004
Devonshire Building | 2017-12-11 16:30 | 51476.6694 | 1360.008
Devonshire Building | 2017-12-11 16:45 | 51476.7894 | 479.988
Devonshire Building | 2017-12-11 17:00 | 51476.8994 | 439.992
Devonshire Building | 2017-12-11 17:15 | 51476.9644 | 259.992
Devonshire Building | 2017-12-11 17:30 | 51476.9894 | 100.008
Devonshire Building | 2017-12-11 17:45 | 51477.0144 | 100.008
Devonshire Building | 2017-12-11 18:00 | 51477.0394 | 100.008
Devonshire Building | 2017-12-11 18:15 | 51477.0644 | 100.008
Devonshire Building | 2017-12-11 18:30 | 51477.0844 | 79.992
Devonshire Building | 2017-12-11 18:45 | 51477.1094 | 100.008
Devonshire Building | 2017-12-11 19:00 | 51477.4094 | 1199.988
Devonshire Building | 2017-12-11 19:15 | 51477.4344 | 100.008
Devonshire Building | 2017-12-11 19:30 | 51477.4544 | 79.992
Devonshire Building | 2017-12-11 19:45 | 51477.4694 | 60.012
Devonshire Building | 2017-12-11 20:00 | 51477.4894 | 79.992
Devonshire Building | 2017-12-11 20:15 | 51477.5044 | 60.012
Devonshire Building | 2017-12-11 20:30 | 51477.5244 | 79.992
Devonshire Building | 2017-12-11 20:45 | 51477.5394 | 60.012
Devonshire Building | 2017-12-11 21:00 | 51477.5594 | 79.992
Devonshire Building | 2017-12-11 21:15 | 51477.5794 | 79.992
Devonshire Building | 2017-12-11 21:30 | 51477.5994 | 79.992
Devonshire Building | 2017-12-11 21:45 | 51477.6344 | 140.004
Devonshire Building | 2017-12-11 22:00 | 51477.6544 | 79.992
Devonshire Building | 2017-12-11 22:15 | 51477.6694 | 60.012
Devonshire Building | 2017-12-11 22:30 | 51477.6844 | 60.012
Devonshire Building | 2017-12-11 22:45 | 51477.6994 | 60.012
Devonshire Building | 2017-12-11 23:00 | 51477.7144 | 60.012
Devonshire Building | 2017-12-11 23:15 | 51477.7294 | 60.012
Devonshire Building | 2017-12-11 23:30 | 51477.7444 | 60.012
Devonshire Building | 2017-12-11 23:45 | 51477.7594 | 60.012
Devonshire Building | 2017-12-12 | 51477.7734 | 60.012
Devonshire Building | 2017-12-12 00:15 | 51478.0634 | 1159.992
Devonshire Building | 2017-12-12 00:30 | 51478.0784 | 60.012
Devonshire Building | 2017-12-12 00:45 | 51478.0884 | 39.996
Devonshire Building | 2017-12-12 01:00 | 51478.1034 | 60.012
Devonshire Building | 2017-12-12 01:15 | 51478.1134 | 39.996
Devonshire Building | 2017-12-12 01:30 | 51478.1284 | 60.012
Devonshire Building | 2017-12-12 01:45 | 51478.1384 | 39.996
Devonshire Building | 2017-12-12 02:00 | 51478.1484 | 39.996
Devonshire Building | 2017-12-12 02:15 | 51478.1634 | 60.012
Devonshire Building | 2017-12-12 02:30 | 51478.1734 | 39.996
Devonshire Building | 2017-12-12 02:45 | 51478.1884 | 60.012
Devonshire Building | 2017-12-12 03:00 | 51478.2035 | 60.012
Devonshire Building | 2017-12-12 03:15 | 51478.2185 | 60.012
Devonshire Building | 2017-12-12 03:30 | 51478.2335 | 60.012
Devonshire Building | 2017-12-12 03:45 | 51478.2485 | 60.012
Devonshire Building | 2017-12-12 04:00 | 51478.2585 | 39.996
Devonshire Building | 2017-12-12 04:15 | 51478.2735 | 60.012
Devonshire Building | 2017-12-12 04:30 | 51478.2885 | 60.012
Devonshire Building | 2017-12-12 04:45 | 51478.2985 | 39.996
Devonshire Building | 2017-12-12 05:00 | 51478.3135 | 60.012
Devonshire Building | 2017-12-12 05:15 | 51478.3235 | 39.996
Devonshire Building | 2017-12-12 05:30 | 51478.3335 | 39.996
Devonshire Building | 2017-12-12 05:45 | 51478.3485 | 60.012
Devonshire Building | 2017-12-12 06:00 | 51478.3635 | 60.012
Devonshire Building | 2017-12-12 06:15 | 51478.6735 | 1239.984
Devonshire Building | 2017-12-12 06:30 | 51478.6835 | 39.996
Devonshire Building | 2017-12-12 06:45 | 51478.6985 | 60.012
Devonshire Building | 2017-12-12 07:00 | 51478.7085 | 39.996
Devonshire Building | 2017-12-12 07:15 | 51478.7185 | 39.996
Devonshire Building | 2017-12-12 07:30 | 51478.7285 | 39.996
Devonshire Building | 2017-12-12 07:45 | 51478.7485 | 79.992
Devonshire Building | 2017-12-12 08:00 | 51478.7785 | 119.988
Devonshire Building | 2017-12-12 08:15 | 51478.8035 | 100.008
Devonshire Building | 2017-12-12 08:30 | 51478.8335 | 119.988
Devonshire Building | 2017-12-12 08:45 | 51479.1835 | 1400.004
Devonshire Building | 2017-12-12 09:00 | 51479.2185 | 140.004
Devonshire Building | 2017-12-12 09:15 | 51479.2485 | 119.988
Devonshire Building | 2017-12-12 09:30 | 51479.2885 | 159.984
Devonshire Building | 2017-12-12 09:45 | 51479.3235 | 140.004
Devonshire Building | 2017-12-12 10:00 | 51479.5085 | 740.016
Devonshire Building | 2017-12-12 10:15 | 51480.0785 | 2279.988
Devonshire Building | 2017-12-12 10:30 | 51480.2385 | 640.008
Devonshire Building | 2017-12-12 10:45 | 51480.3335 | 380.016
Devonshire Building | 2017-12-12 11:00 | 51480.7885 | 1820.016
Devonshire Building | 2017-12-12 11:15 | 51480.8335 | 180
Devonshire Building | 2017-12-12 11:30 | 51480.8835 | 200.016
Devonshire Building | 2017-12-12 11:45 | 51481.2185 | 1339.992
Devonshire Building | 2017-12-12 12:00 | 51481.2485 | 119.988
Devonshire Building | 2017-12-12 12:15 | 51481.6085 | 1440
Devonshire Building | 2017-12-12 12:30 | 51481.6385 | 119.988
Devonshire Building | 2017-12-12 12:45 | 51481.6685 | 119.988
Devonshire Building | 2017-12-12 13:00 | 51482.0235 | 1419.984
Devonshire Building | 2017-12-12 13:15 | 51482.0785 | 219.996
Devonshire Building | 2017-12-12 13:30 | 51482.1585 | 320.004
Devonshire Building | 2017-12-12 13:45 | 51482.6485 | 1959.984
Devonshire Building | 2017-12-12 14:00 | 51482.8385 | 759.996
Devonshire Building | 2017-12-12 14:15 | 51482.9834 | 579.996
Devonshire Building | 2017-12-12 14:30 | 51483.0885 | 420.012
Devonshire Building | 2017-12-12 14:45 | 51483.4835 | 1580.004
Devonshire Building | 2017-12-12 15:00 | 51483.5335 | 200.016
Devonshire Building | 2017-12-12 15:15 | 51483.5885 | 219.996
Devonshire Building | 2017-12-12 15:30 | 51483.9885 | 1599.984
Devonshire Building | 2017-12-12 15:45 | 51484.0235 | 140.004
Devonshire Building | 2017-12-12 16:00 | 51484.0635 | 159.984
Devonshire Building | 2017-12-12 16:15 | 51484.1184 | 219.996
Devonshire Building | 2017-12-12 16:30 | 51484.5184 | 1599.984
Devonshire Building | 2017-12-12 16:45 | 51484.6684 | 600.012
Devonshire Building | 2017-12-12 17:00 | 51484.8384 | 680.004
Devonshire Building | 2017-12-12 17:15 | 51485.2685 | 1720.008
Devonshire Building | 2017-12-12 17:30 | 51485.3585 | 360
Devonshire Building | 2017-12-12 17:45 | 51485.4234 | 259.992
Devonshire Building | 2017-12-12 18:00 | 51485.4835 | 240.012
Devonshire Building | 2017-12-12 18:15 | 51485.5335 | 200.016
Devonshire Building | 2017-12-12 18:30 | 51485.5785 | 180
Devonshire Building | 2017-12-12 18:45 | 51485.6135 | 140.004
Devonshire Building | 2017-12-12 19:00 | 51485.6485 | 140.004
Devonshire Building | 2017-12-12 19:15 | 51485.6785 | 119.988
Devonshire Building | 2017-12-12 19:30 | 51485.7085 | 119.988
Devonshire Building | 2017-12-12 19:45 | 51485.7335 | 100.008
Devonshire Building | 2017-12-12 20:00 | 51485.7585 | 100.008
Devonshire Building | 2017-12-12 20:15 | 51485.7785 | 79.992
Devonshire Building | 2017-12-12 20:30 | 51486.0735 | 1180.008
Devonshire Building | 2017-12-12 20:45 | 51486.0835 | 39.996
Devonshire Building | 2017-12-12 21:00 | 51486.0935 | 39.996
Devonshire Building | 2017-12-12 21:15 | 51486.0985 | 20.016
Devonshire Building | 2017-12-12 21:30 | 51486.1085 | 39.996
Devonshire Building | 2017-12-12 21:45 | 51486.1285 | 79.992
Devonshire Building | 2017-12-12 22:00 | 51486.1385 | 39.996
Devonshire Building | 2017-12-12 22:15 | 51486.1435 | 20.016
Devonshire Building | 2017-12-12 22:30 | 51486.1535 | 39.996
Devonshire Building | 2017-12-12 22:45 | 51486.1635 | 39.996
Devonshire Building | 2017-12-12 23:00 | 51486.1685 | 20.016
Devonshire Building | 2017-12-12 23:15 | 51486.1785 | 39.996
Devonshire Building | 2017-12-12 23:30 | 51486.1885 | 39.996
Devonshire Building | 2017-12-12 23:45 | 51486.1985 | 39.996
Devonshire Building | 2017-12-13 | 51486.2031 | 20.016
Devonshire Building | 2017-12-13 00:15 | 51486.2131 | 39.996
Devonshire Building | 2017-12-13 00:30 | 51486.2231 | 39.996
Devonshire Building | 2017-12-13 00:45 | 51486.2281 | 20.016
Devonshire Building | 2017-12-13 01:00 | 51486.2381 | 39.996
Devonshire Building | 2017-12-13 01:15 | 51486.2481 | 39.996
Devonshire Building | 2017-12-13 01:30 | 51486.2581 | 39.996
Devonshire Building | 2017-12-13 01:45 | 51486.5631 | 1220.004
Devonshire Building | 2017-12-13 02:00 | 51486.5731 | 39.996
Devonshire Building | 2017-12-13 02:15 | 51486.5831 | 39.996
Devonshire Building | 2017-12-13 02:30 | 51486.5931 | 39.996
Devonshire Building | 2017-12-13 02:45 | 51486.5981 | 20.016
Devonshire Building | 2017-12-13 03:00 | 51486.6081 | 39.996
Devonshire Building | 2017-12-13 03:15 | 51486.6181 | 39.996
Devonshire Building | 2017-12-13 03:30 | 51486.6231 | 20.016
Devonshire Building | 2017-12-13 03:45 | 51486.6331 | 39.996
Devonshire Building | 2017-12-13 04:00 | 51486.6381 | 20.016
Devonshire Building | 2017-12-13 04:15 | 51486.6481 | 39.996
Devonshire Building | 2017-12-13 04:30 | 51486.6581 | 39.996
Devonshire Building | 2017-12-13 04:45 | 51486.6631 | 20.016
Devonshire Building | 2017-12-13 05:00 | 51486.6731 | 39.996
Devonshire Building | 2017-12-13 05:15 | 51486.6781 | 20.016
Devonshire Building | 2017-12-13 05:30 | 51486.6881 | 39.996
Devonshire Building | 2017-12-13 05:45 | 51486.6981 | 39.996
Devonshire Building | 2017-12-13 06:00 | 51486.7031 | 20.016
Devonshire Building | 2017-12-13 06:15 | 51486.7131 | 39.996
Devonshire Building | 2017-12-13 06:30 | 51486.7181 | 20.016
Devonshire Building | 2017-12-13 06:45 | 51486.7281 | 39.996
Devonshire Building | 2017-12-13 07:00 | 51486.7381 | 39.996
Devonshire Building | 2017-12-13 07:15 | 51486.7481 | 39.996
Devonshire Building | 2017-12-13 07:30 | 51486.7531 | 20.016
Devonshire Building | 2017-12-13 07:45 | 51487.0631 | 1239.984
Devonshire Building | 2017-12-13 08:00 | 51487.0881 | 100.008
Devonshire Building | 2017-12-13 08:15 | 51487.1131 | 100.008
Devonshire Building | 2017-12-13 08:30 | 51487.1381 | 100.008
Devonshire Building | 2017-12-13 08:45 | 51487.1781 | 159.984
Devonshire Building | 2017-12-13 09:00 | 51487.4081 | 920.016
Devonshire Building | 2017-12-13 09:15 | 51487.6482 | 960.012
Devonshire Building | 2017-12-13 09:30 | 51487.7382 | 360
Devonshire Building | 2017-12-13 09:45 | 51487.8882 | 600.012
Devonshire Building | 2017-12-13 10:00 | 51488.0332 | 579.996
Devonshire Building | 2017-12-13 10:15 | 51488.2332 | 799.992
Devonshire Building | 2017-12-13 10:30 | 51488.3682 | 540
Devonshire Building | 2017-12-13 10:45 | 51488.5232 | 619.992
Devonshire Building | 2017-12-13 11:00 | 51488.7231 | 799.992
Devonshire Building | 2017-12-13 11:15 | 51488.8981 | 699.984
Devonshire Building | 2017-12-13 11:30 | 51489.0831 | 740.016
Devonshire Building | 2017-12-13 11:45 | 51489.2281 | 579.996
Devonshire Building | 2017-12-13 12:00 | 51489.4081 | 720
Devonshire Building | 2017-12-13 12:15 | 51489.5531 | 579.996
Devonshire Building | 2017-12-13 12:30 | 51489.7031 | 600.012
Devonshire Building | 2017-12-13 12:45 | 51489.8231 | 479.988
Devonshire Building | 2017-12-13 13:00 | 51489.9681 | 579.996
Devonshire Building | 2017-12-13 13:15 | 51490.1081 | 560.016
Devonshire Building | 2017-12-13 13:30 | 51490.2431 | 540
Devonshire Building | 2017-12-13 13:45 | 51490.3832 | 560.016
Devonshire Building | 2017-12-13 14:00 | 51490.5131 | 519.984
Devonshire Building | 2017-12-13 14:15 | 51490.6082 | 380.016
Devonshire Building | 2017-12-13 14:30 | 51490.7381 | 519.984
Devonshire Building | 2017-12-13 14:45 | 51490.8581 | 479.988
Devonshire Building | 2017-12-13 15:00 | 51490.9631 | 420.012
Devonshire Building | 2017-12-13 15:15 | 51491.0831 | 479.988
Devonshire Building | 2017-12-13 15:30 | 51491.1781 | 380.016
Devonshire Building | 2017-12-13 15:45 | 51491.2981 | 479.988
Devonshire Building | 2017-12-13 16:00 | 51491.4031 | 420.012
Devonshire Building | 2017-12-13 16:15 | 51491.5532 | 600.012
Devonshire Building | 2017-12-13 16:30 | 51491.6882 | 540
Devonshire Building | 2017-12-13 16:45 | 51491.7582 | 280.008
Devonshire Building | 2017-12-13 17:00 | 51491.7982 | 159.984
Devonshire Building | 2017-12-13 17:15 | 51491.8332 | 140.004
Devonshire Building | 2017-12-13 17:30 | 51491.8731 | 159.984
Devonshire Building | 2017-12-13 17:45 | 51491.9081 | 140.004
Devonshire Building | 2017-12-13 18:00 | 51491.9381 | 119.988
Devonshire Building | 2017-12-13 18:15 | 51492.2731 | 1339.992
Devonshire Building | 2017-12-13 18:30 | 51492.2981 | 100.008
Devonshire Building | 2017-12-13 18:45 | 51492.3231 | 100.008
Devonshire Building | 2017-12-13 19:00 | 51492.3481 | 100.008
Devonshire Building | 2017-12-13 19:15 | 51492.3732 | 100.008
Devonshire Building | 2017-12-13 19:30 | 51492.3982 | 100.008
Devonshire Building | 2017-12-13 19:45 | 51492.4282 | 119.988
Devonshire Building | 2017-12-13 20:00 | 51492.4532 | 100.008
Devonshire Building | 2017-12-13 20:15 | 51492.4732 | 79.992
Devonshire Building | 2017-12-13 20:30 | 51492.4982 | 100.008
Devonshire Building | 2017-12-13 20:45 | 51492.5232 | 100.008
Devonshire Building | 2017-12-13 21:00 | 51492.5432 | 79.992
Devonshire Building | 2017-12-13 21:15 | 51492.5682 | 100.008
Devonshire Building | 2017-12-13 21:30 | 51492.5882 | 79.992
Devonshire Building | 2017-12-13 21:45 | 51492.6232 | 140.004
Devonshire Building | 2017-12-13 22:00 | 51492.6332 | 39.996
Devonshire Building | 2017-12-13 22:15 | 51492.6482 | 60.012
Devonshire Building | 2017-12-13 22:30 | 51492.6582 | 39.996
Devonshire Building | 2017-12-13 22:45 | 51492.6682 | 39.996
Devonshire Building | 2017-12-13 23:00 | 51492.6782 | 39.996
Devonshire Building | 2017-12-13 23:15 | 51492.6932 | 60.012
Devonshire Building | 2017-12-13 23:30 | 51492.7032 | 39.996
Devonshire Building | 2017-12-13 23:45 | 51493.0032 | 1199.988
Devonshire Building | 2017-12-14 | 51493.0156 | 39.996
Devonshire Building | 2017-12-14 00:15 | 51493.0256 | 39.996
Devonshire Building | 2017-12-14 00:30 | 51493.0356 | 39.996
Devonshire Building | 2017-12-14 00:45 | 51493.0456 | 39.996
Devonshire Building | 2017-12-14 01:00 | 51493.0556 | 39.996
Devonshire Building | 2017-12-14 01:15 | 51493.0606 | 20.016
Devonshire Building | 2017-12-14 01:30 | 51493.0706 | 39.996
Devonshire Building | 2017-12-14 01:45 | 51493.0806 | 39.996
Devonshire Building | 2017-12-14 02:00 | 51493.0906 | 39.996
Devonshire Building | 2017-12-14 02:15 | 51493.1006 | 39.996
Devonshire Building | 2017-12-14 02:30 | 51493.1106 | 39.996
Devonshire Building | 2017-12-14 02:45 | 51493.1156 | 20.016
Devonshire Building | 2017-12-14 03:00 | 51493.1256 | 39.996
Devonshire Building | 2017-12-14 03:15 | 51493.1356 | 39.996
Devonshire Building | 2017-12-14 03:30 | 51493.1456 | 39.996
Devonshire Building | 2017-12-14 03:45 | 51493.1556 | 39.996
Devonshire Building | 2017-12-14 04:00 | 51493.1656 | 39.996
Devonshire Building | 2017-12-14 04:15 | 51493.1756 | 39.996
Devonshire Building | 2017-12-14 04:30 | 51493.1856 | 39.996
Devonshire Building | 2017-12-14 04:45 | 51493.1956 | 39.996
Devonshire Building | 2017-12-14 05:00 | 51493.2056 | 39.996
Devonshire Building | 2017-12-14 05:15 | 51493.2156 | 39.996
Devonshire Building | 2017-12-14 05:30 | 51493.2956 | 320.004
Devonshire Building | 2017-12-14 05:45 | 51493.5256 | 920.016
Devonshire Building | 2017-12-14 06:00 | 51493.5356 | 39.996
Devonshire Building | 2017-12-14 06:15 | 51493.5456 | 39.996
Devonshire Building | 2017-12-14 06:30 | 51493.5556 | 39.996
Devonshire Building | 2017-12-14 06:45 | 51493.5656 | 39.996
Devonshire Building | 2017-12-14 07:00 | 51493.5706 | 20.016
Devonshire Building | 2017-12-14 07:15 | 51493.5806 | 39.996
Devonshire Building | 2017-12-14 07:30 | 51493.5906 | 39.996
Devonshire Building | 2017-12-14 07:45 | 51493.6156 | 100.008
Devonshire Building | 2017-12-14 08:00 | 51493.6406 | 100.008
Devonshire Building | 2017-12-14 08:15 | 51493.6706 | 119.988
Devonshire Building | 2017-12-14 08:30 | 51493.9906 | 1280.016
Devonshire Building | 2017-12-14 08:45 | 51494.0206 | 119.988
Devonshire Building | 2017-12-14 09:00 | 51494.0506 | 119.988
Devonshire Building | 2017-12-14 09:15 | 51494.0806 | 119.988
Devonshire Building | 2017-12-14 09:30 | 51494.1156 | 140.004
Devonshire Building | 2017-12-14 09:45 | 51494.3956 | 1119.996
Devonshire Building | 2017-12-14 10:00 | 51494.5356 | 560.016
Devonshire Building | 2017-12-14 10:15 | 51494.5756 | 159.984
Devonshire Building | 2017-12-14 10:30 | 51494.6156 | 159.984
Devonshire Building | 2017-12-14 10:45 | 51494.9756 | 1440
Devonshire Building | 2017-12-14 11:00 | 51495.0256 | 200.016
Devonshire Building | 2017-12-14 11:15 | 51495.0956 | 280.008
Devonshire Building | 2017-12-14 11:30 | 51495.4906 | 1580.004
Devonshire Building | 2017-12-14 11:45 | 51495.5856 | 380.016
Devonshire Building | 2017-12-14 12:00 | 51495.7156 | 519.984
Devonshire Building | 2017-12-14 12:15 | 51496.1306 | 1659.996
Devonshire Building | 2017-12-14 12:30 | 51496.2156 | 339.984
Devonshire Building | 2017-12-14 12:45 | 51496.3056 | 360
Devonshire Building | 2017-12-14 13:00 | 51496.6256 | 1280.016
Devonshire Building | 2017-12-14 13:15 | 51496.7456 | 479.988
Devonshire Building | 2017-12-14 13:30 | 51496.8006 | 219.996
Devonshire Building | 2017-12-14 13:45 | 51496.8606 | 240.012
Devonshire Building | 2017-12-14 14:00 | 51497.1106 | 1000.008
Devonshire Building | 2017-12-14 14:15 | 51497.2606 | 600.012
Devonshire Building | 2017-12-14 14:30 | 51497.2956 | 140.004
Devonshire Building | 2017-12-14 14:45 | 51497.3356 | 159.984
Devonshire Building | 2017-12-14 15:00 | 51497.7006 | 1460.016
Devonshire Building | 2017-12-14 15:15 | 51497.7406 | 159.984
Devonshire Building | 2017-12-14 15:30 | 51497.7856 | 180
Devonshire Building | 2017-12-14 15:45 | 51497.8256 | 159.984
Devonshire Building | 2017-12-14 16:00 | 51498.1656 | 1360.008
Devonshire Building | 2017-12-14 16:15 | 51498.2156 | 200.016
Devonshire Building | 2017-12-14 16:30 | 51498.2656 | 200.016
Devonshire Building | 2017-12-14 16:45 | 51498.6306 | 1460.016
Devonshire Building | 2017-12-14 17:00 | 51498.7756 | 579.996
Devonshire Building | 2017-12-14 17:15 | 51498.8756 | 399.996
Devonshire Building | 2017-12-14 17:30 | 51499.0056 | 519.984
Devonshire Building | 2017-12-14 17:45 | 51499.0706 | 259.992
Devonshire Building | 2017-12-14 18:00 | 51499.1356 | 259.992
Devonshire Building | 2017-12-14 18:15 | 51499.2006 | 259.992
Devonshire Building | 2017-12-14 18:30 | 51499.2556 | 219.996
Devonshire Building | 2017-12-14 18:45 | 51499.3056 | 200.016
Devonshire Building | 2017-12-14 19:00 | 51499.3506 | 180
Devonshire Building | 2017-12-14 19:15 | 51499.3956 | 180
Devonshire Building | 2017-12-14 19:30 | 51499.4356 | 159.984
Devonshire Building | 2017-12-14 19:45 | 51499.4906 | 219.996
Devonshire Building | 2017-12-14 20:00 | 51499.5356 | 180
Devonshire Building | 2017-12-14 20:15 | 51499.5756 | 159.984
Devonshire Building | 2017-12-14 20:30 | 51499.6056 | 119.988
Devonshire Building | 2017-12-14 20:45 | 51499.6406 | 140.004
Devonshire Building | 2017-12-14 21:00 | 51499.6706 | 119.988
Devonshire Building | 2017-12-14 21:15 | 51499.7006 | 119.988
Devonshire Building | 2017-12-14 21:30 | 51499.7306 | 119.988
Devonshire Building | 2017-12-14 21:45 | 51499.7606 | 119.988
Devonshire Building | 2017-12-14 22:00 | 51499.7956 | 140.004
Devonshire Building | 2017-12-14 22:15 | 51499.8306 | 140.004
Devonshire Building | 2017-12-14 22:30 | 51499.8606 | 119.988
Devonshire Building | 2017-12-14 22:45 | 51499.8956 | 140.004
Devonshire Building | 2017-12-14 23:00 | 51499.9206 | 100.008
Devonshire Building | 2017-12-14 23:15 | 51499.9506 | 119.988
Devonshire Building | 2017-12-14 23:30 | 51499.9806 | 119.988
Devonshire Building | 2017-12-14 23:45 | 51500.0106 | 119.988
Devonshire Building | 2017-12-15 | 51500.0391 | 119.988
Devonshire Building | 2017-12-15 00:15 | 51500.0641 | 100.008
Devonshire Building | 2017-12-15 00:30 | 51500.0941 | 119.988
Devonshire Building | 2017-12-15 00:45 | 51500.1191 | 100.008
Devonshire Building | 2017-12-15 01:00 | 51500.1441 | 100.008
Devonshire Building | 2017-12-15 01:15 | 51500.1741 | 119.988
Devonshire Building | 2017-12-15 01:30 | 51500.1991 | 100.008
Devonshire Building | 2017-12-15 01:45 | 51500.2191 | 79.992
Devonshire Building | 2017-12-15 02:00 | 51500.2441 | 100.008
Devonshire Building | 2017-12-15 02:15 | 51500.2691 | 100.008
Devonshire Building | 2017-12-15 02:30 | 51500.2941 | 100.008
Devonshire Building | 2017-12-15 02:45 | 51500.3191 | 100.008
Devonshire Building | 2017-12-15 03:00 | 51500.3441 | 100.008
Devonshire Building | 2017-12-15 03:15 | 51500.3691 | 100.008
Devonshire Building | 2017-12-15 03:30 | 51500.3941 | 100.008
Devonshire Building | 2017-12-15 03:45 | 51500.4141 | 79.992
Devonshire Building | 2017-12-15 04:00 | 51500.4391 | 100.008
Devonshire Building | 2017-12-15 04:15 | 51500.4641 | 100.008
Devonshire Building | 2017-12-15 04:30 | 51500.4891 | 100.008
Devonshire Building | 2017-12-15 04:45 | 51500.5141 | 100.008
Devonshire Building | 2017-12-15 05:00 | 51500.5391 | 100.008
Devonshire Building | 2017-12-15 05:15 | 51500.5641 | 100.008
Devonshire Building | 2017-12-15 05:30 | 51500.5891 | 100.008
Devonshire Building | 2017-12-15 05:45 | 51500.6241 | 140.004
Devonshire Building | 2017-12-15 06:00 | 51500.6641 | 159.984
Devonshire Building | 2017-12-15 06:15 | 51500.6941 | 119.988
Devonshire Building | 2017-12-15 06:30 | 51500.7091 | 60.012
Devonshire Building | 2017-12-15 06:45 | 51500.7191 | 39.996
Devonshire Building | 2017-12-15 07:00 | 51500.7341 | 60.012
Devonshire Building | 2017-12-15 07:15 | 51500.7441 | 39.996
Devonshire Building | 2017-12-15 07:30 | 51500.7541 | 39.996
Devonshire Building | 2017-12-15 07:45 | 51500.7741 | 79.992
Devonshire Building | 2017-12-15 08:00 | 51500.7991 | 100.008
Devonshire Building | 2017-12-15 08:15 | 51500.8291 | 119.988
Devonshire Building | 2017-12-15 08:30 | 51500.8591 | 119.988
Devonshire Building | 2017-12-15 08:45 | 51501.0391 | 720
Devonshire Building | 2017-12-15 09:00 | 51501.2341 | 780.012
Devonshire Building | 2017-12-15 09:15 | 51501.2691 | 140.004
Devonshire Building | 2017-12-15 09:30 | 51501.3041 | 140.004
Devonshire Building | 2017-12-15 09:45 | 51501.3391 | 140.004
Devonshire Building | 2017-12-15 10:00 | 51501.6591 | 1280.016
Devonshire Building | 2017-12-15 10:15 | 51501.7041 | 180
Devonshire Building | 2017-12-15 10:30 | 51501.7641 | 240.012
Devonshire Building | 2017-12-15 10:45 | 51502.1241 | 1440
Devonshire Building | 2017-12-15 11:00 | 51502.1941 | 280.008
Devonshire Building | 2017-12-15 11:15 | 51502.2741 | 320.004
Devonshire Building | 2017-12-15 11:30 | 51502.3391 | 259.992
Devonshire Building | 2017-12-15 11:45 | 51502.7141 | 1500.012
Devonshire Building | 2017-12-15 12:00 | 51502.7741 | 240.012
Devonshire Building | 2017-12-15 12:15 | 51502.8391 | 259.992
Devonshire Building | 2017-12-15 12:30 | 51503.2091 | 1479.996
Devonshire Building | 2017-12-15 12:45 | 51503.2791 | 280.008
Devonshire Building | 2017-12-15 13:00 | 51503.3441 | 259.992
Devonshire Building | 2017-12-15 13:15 | 51503.4141 | 280.008
Devonshire Building | 2017-12-15 13:30 | 51503.4791 | 259.992
Devonshire Building | 2017-12-15 13:45 | 51503.8241 | 1379.988
Devonshire Building | 2017-12-15 14:00 | 51503.8841 | 240.012
Devonshire Building | 2017-12-15 14:15 | 51503.9441 | 240.012
Devonshire Building | 2017-12-15 14:30 | 51504.2891 | 1379.988
Devonshire Building | 2017-12-15 14:45 | 51504.3391 | 200.016
Devonshire Building | 2017-12-15 15:00 | 51504.3891 | 200.016
Devonshire Building | 2017-12-15 15:15 | 51504.4391 | 200.016
Devonshire Building | 2017-12-15 15:30 | 51504.7841 | 1379.988
Devonshire Building | 2017-12-15 15:45 | 51504.8141 | 119.988
Devonshire Building | 2017-12-15 16:00 | 51504.8541 | 159.984
Devonshire Building | 2017-12-15 16:15 | 51504.8841 | 119.988
Devonshire Building | 2017-12-15 16:30 | 51505.1441 | 1040.004
Devonshire Building | 2017-12-15 16:45 | 51505.2541 | 439.992
Devonshire Building | 2017-12-15 17:00 | 51505.2841 | 119.988
Devonshire Building | 2017-12-15 17:15 | 51505.3141 | 119.988
Devonshire Building | 2017-12-15 17:30 | 51505.3441 | 119.988
Devonshire Building | 2017-12-15 17:45 | 51505.3791 | 140.004
Devonshire Building | 2017-12-15 18:00 | 51505.4241 | 180
Devonshire Building | 2017-12-15 18:15 | 51505.7891 | 1460.016
Devonshire Building | 2017-12-15 18:30 | 51505.8391 | 200.016
Devonshire Building | 2017-12-15 18:45 | 51505.8941 | 219.996
Devonshire Building | 2017-12-15 19:00 | 51505.9491 | 219.996
Devonshire Building | 2017-12-15 19:15 | 51506.0041 | 219.996
Devonshire Building | 2017-12-15 19:30 | 51506.0541 | 200.016
Devonshire Building | 2017-12-15 19:45 | 51506.0991 | 180
Devonshire Building | 2017-12-15 20:00 | 51506.1391 | 159.984
Devonshire Building | 2017-12-15 20:15 | 51506.1741 | 140.004
Devonshire Building | 2017-12-15 20:30 | 51506.2141 | 159.984
Devonshire Building | 2017-12-15 20:45 | 51506.2441 | 119.988
Devonshire Building | 2017-12-15 21:00 | 51506.2741 | 119.988
Devonshire Building | 2017-12-15 21:15 | 51506.2991 | 100.008
Devonshire Building | 2017-12-15 21:30 | 51506.3241 | 100.008
Devonshire Building | 2017-12-15 21:45 | 51506.3641 | 159.984
Devonshire Building | 2017-12-15 22:00 | 51506.3791 | 60.012
Devonshire Building | 2017-12-15 22:15 | 51506.3891 | 39.996
Devonshire Building | 2017-12-15 22:30 | 51506.4041 | 60.012
Devonshire Building | 2017-12-15 22:45 | 51506.4191 | 60.012
Devonshire Building | 2017-12-15 23:00 | 51506.7091 | 1159.992
Devonshire Building | 2017-12-15 23:15 | 51506.7191 | 39.996
Devonshire Building | 2017-12-15 23:30 | 51506.7291 | 39.996
Devonshire Building | 2017-12-15 23:45 | 51506.7391 | 39.996
Devonshire Building | 2017-12-16 | 51506.75 | 39.996
Devonshire Building | 2017-12-16 00:15 | 51506.76 | 39.996
Devonshire Building | 2017-12-16 00:30 | 51506.775 | 60.012
Devonshire Building | 2017-12-16 00:45 | 51506.785 | 39.996
Devonshire Building | 2017-12-16 01:00 | 51506.795 | 39.996
Devonshire Building | 2017-12-16 01:15 | 51506.805 | 39.996
Devonshire Building | 2017-12-16 01:30 | 51506.815 | 39.996
Devonshire Building | 2017-12-16 01:45 | 51506.825 | 39.996
Devonshire Building | 2017-12-16 02:00 | 51506.835 | 39.996
Devonshire Building | 2017-12-16 02:15 | 51506.845 | 39.996
Devonshire Building | 2017-12-16 02:30 | 51506.86 | 60.012
Devonshire Building | 2017-12-16 02:45 | 51506.87 | 39.996
Devonshire Building | 2017-12-16 03:00 | 51506.88 | 39.996
Devonshire Building | 2017-12-16 03:15 | 51506.89 | 39.996
Devonshire Building | 2017-12-16 03:30 | 51506.905 | 60.012
Devonshire Building | 2017-12-16 03:45 | 51506.915 | 39.996
Devonshire Building | 2017-12-16 04:00 | 51506.925 | 39.996
Devonshire Building | 2017-12-16 04:15 | 51506.935 | 39.996
Devonshire Building | 2017-12-16 04:30 | 51506.945 | 39.996
Devonshire Building | 2017-12-16 04:45 | 51507.235 | 1159.992
Devonshire Building | 2017-12-16 05:00 | 51507.245 | 39.996
Devonshire Building | 2017-12-16 05:15 | 51507.255 | 39.996
Devonshire Building | 2017-12-16 05:30 | 51507.265 | 39.996
Devonshire Building | 2017-12-16 05:45 | 51507.275 | 39.996
Devonshire Building | 2017-12-16 06:00 | 51507.285 | 39.996
Devonshire Building | 2017-12-16 06:15 | 51507.295 | 39.996
Devonshire Building | 2017-12-16 06:30 | 51507.305 | 39.996
Devonshire Building | 2017-12-16 06:45 | 51507.31 | 20.016
Devonshire Building | 2017-12-16 07:00 | 51507.32 | 39.996
Devonshire Building | 2017-12-16 07:15 | 51507.33 | 39.996
Devonshire Building | 2017-12-16 07:30 | 51507.34 | 39.996
Devonshire Building | 2017-12-16 07:45 | 51507.355 | 60.012
Devonshire Building | 2017-12-16 08:00 | 51507.38 | 100.008
Devonshire Building | 2017-12-16 08:15 | 51507.405 | 100.008
Devonshire Building | 2017-12-16 08:30 | 51507.43 | 100.008
Devonshire Building | 2017-12-16 08:45 | 51507.455 | 100.008
Devonshire Building | 2017-12-16 09:00 | 51507.48 | 100.008
Devonshire Building | 2017-12-16 09:15 | 51507.51 | 119.988
Devonshire Building | 2017-12-16 09:30 | 51507.535 | 100.008
Devonshire Building | 2017-12-16 09:45 | 51507.84 | 1220.004
Devonshire Building | 2017-12-16 10:00 | 51507.865 | 100.008
Devonshire Building | 2017-12-16 10:15 | 51507.89 | 100.008
Devonshire Building | 2017-12-16 10:30 | 51507.915 | 100.008
Devonshire Building | 2017-12-16 10:45 | 51507.94 | 100.008
Devonshire Building | 2017-12-16 11:00 | 51507.965 | 100.008
Devonshire Building | 2017-12-16 11:15 | 51507.985 | 79.992
Devonshire Building | 2017-12-16 11:30 | 51507.995 | 39.996
Devonshire Building | 2017-12-16 11:45 | 51508.005 | 39.996
Devonshire Building | 2017-12-16 12:00 | 51508.015 | 39.996
Devonshire Building | 2017-12-16 12:15 | 51508.025 | 39.996
Devonshire Building | 2017-12-16 12:30 | 51508.04 | 60.012
Devonshire Building | 2017-12-16 12:45 | 51508.05 | 39.996
Devonshire Building | 2017-12-16 13:00 | 51508.065 | 60.012
Devonshire Building | 2017-12-16 13:15 | 51508.08 | 60.012
Devonshire Building | 2017-12-16 13:30 | 51508.095 | 60.012
Devonshire Building | 2017-12-16 13:45 | 51508.11 | 60.012
Devonshire Building | 2017-12-16 14:00 | 51508.125 | 60.012
Devonshire Building | 2017-12-16 14:15 | 51508.14 | 60.012
Devonshire Building | 2017-12-16 14:30 | 51508.15 | 39.996
Devonshire Building | 2017-12-16 14:45 | 51508.445 | 1180.008
Devonshire Building | 2017-12-16 15:00 | 51508.46 | 60.012
Devonshire Building | 2017-12-16 15:15 | 51508.475 | 60.012
Devonshire Building | 2017-12-16 15:30 | 51508.485 | 39.996
Devonshire Building | 2017-12-16 15:45 | 51508.5 | 60.012
Devonshire Building | 2017-12-16 16:00 | 51508.515 | 60.012
Devonshire Building | 2017-12-16 16:15 | 51508.525 | 39.996
Devonshire Building | 2017-12-16 16:30 | 51508.54 | 60.012
Devonshire Building | 2017-12-16 16:45 | 51508.555 | 60.012
Devonshire Building | 2017-12-16 17:00 | 51508.57 | 60.012
Devonshire Building | 2017-12-16 17:15 | 51508.585 | 60.012
Devonshire Building | 2017-12-16 17:30 | 51508.6 | 60.012
Devonshire Building | 2017-12-16 17:45 | 51508.62 | 79.992
Devonshire Building | 2017-12-16 18:00 | 51508.635 | 60.012
Devonshire Building | 2017-12-16 18:15 | 51508.6501 | 60.012
Devonshire Building | 2017-12-16 18:30 | 51508.6651 | 60.012
Devonshire Building | 2017-12-16 18:45 | 51508.6801 | 60.012
Devonshire Building | 2017-12-16 19:00 | 51508.6951 | 60.012
Devonshire Building | 2017-12-16 19:15 | 51508.7101 | 60.012
Devonshire Building | 2017-12-16 19:30 | 51508.7251 | 60.012
Devonshire Building | 2017-12-16 19:45 | 51508.7801 | 219.996
Devonshire Building | 2017-12-16 20:00 | 51509.0301 | 1000.008
Devonshire Building | 2017-12-16 20:15 | 51509.0451 | 60.012
Devonshire Building | 2017-12-16 20:30 | 51509.0601 | 60.012
Devonshire Building | 2017-12-16 20:45 | 51509.0751 | 60.012
Devonshire Building | 2017-12-16 21:00 | 51509.0851 | 39.996
Devonshire Building | 2017-12-16 21:15 | 51509.1001 | 60.012
Devonshire Building | 2017-12-16 21:30 | 51509.1101 | 39.996
Devonshire Building | 2017-12-16 21:45 | 51509.1451 | 140.004
Devonshire Building | 2017-12-16 22:00 | 51509.1651 | 79.992
Devonshire Building | 2017-12-16 22:15 | 51509.1801 | 60.012
Devonshire Building | 2017-12-16 22:30 | 51509.2001 | 79.992
Devonshire Building | 2017-12-16 22:45 | 51509.2151 | 60.012
Devonshire Building | 2017-12-16 23:00 | 51509.2301 | 60.012
Devonshire Building | 2017-12-16 23:15 | 51509.2501 | 79.992
Devonshire Building | 2017-12-16 23:30 | 51509.2651 | 60.012
Devonshire Building | 2017-12-16 23:45 | 51509.2801 | 60.012
Devonshire Building | 2017-12-17 | 51509.293 | 60.012
Devonshire Building | 2017-12-17 00:15 | 51509.313 | 79.992
Devonshire Building | 2017-12-17 00:30 | 51509.328 | 60.012
Devonshire Building | 2017-12-17 00:45 | 51509.343 | 60.012
Devonshire Building | 2017-12-17 01:00 | 51509.358 | 60.012
Devonshire Building | 2017-12-17 01:15 | 51509.448 | 360
Devonshire Building | 2017-12-17 01:30 | 51509.663 | 860.004
Devonshire Building | 2017-12-17 01:45 | 51509.673 | 39.996
Devonshire Building | 2017-12-17 02:00 | 51509.688 | 60.012
Devonshire Building | 2017-12-17 02:15 | 51509.698 | 39.996
Devonshire Building | 2017-12-17 02:30 | 51509.708 | 39.996
Devonshire Building | 2017-12-17 02:45 | 51509.723 | 60.012
Devonshire Building | 2017-12-17 03:00 | 51509.733 | 39.996
Devonshire Building | 2017-12-17 03:15 | 51509.743 | 39.996
Devonshire Building | 2017-12-17 03:30 | 51509.758 | 60.012
Devonshire Building | 2017-12-17 03:45 | 51509.768 | 39.996
Devonshire Building | 2017-12-17 04:00 | 51509.783 | 60.012
Devonshire Building | 2017-12-17 04:15 | 51509.798 | 60.012
Devonshire Building | 2017-12-17 04:30 | 51509.813 | 60.012
Devonshire Building | 2017-12-17 04:45 | 51509.828 | 60.012
Devonshire Building | 2017-12-17 05:00 | 51509.838 | 39.996
Devonshire Building | 2017-12-17 05:15 | 51509.853 | 60.012
Devonshire Building | 2017-12-17 05:30 | 51509.868 | 60.012
Devonshire Building | 2017-12-17 05:45 | 51509.883 | 60.012
Devonshire Building | 2017-12-17 06:00 | 51509.893 | 39.996
Devonshire Building | 2017-12-17 06:15 | 51509.908 | 60.012
Devonshire Building | 2017-12-17 06:30 | 51509.918 | 39.996
Devonshire Building | 2017-12-17 06:45 | 51509.933 | 60.012
Devonshire Building | 2017-12-17 07:00 | 51510.218 | 1140.012
Devonshire Building | 2017-12-17 07:15 | 51510.233 | 60.012
Devonshire Building | 2017-12-17 07:30 | 51510.243 | 39.996
Devonshire Building | 2017-12-17 07:45 | 51510.263 | 79.992
Devonshire Building | 2017-12-17 08:00 | 51510.288 | 100.008
Devonshire Building | 2017-12-17 08:15 | 51510.313 | 100.008
Devonshire Building | 2017-12-17 08:30 | 51510.338 | 100.008
Devonshire Building | 2017-12-17 08:45 | 51510.363 | 100.008
Devonshire Building | 2017-12-17 09:00 | 51510.393 | 119.988
Devonshire Building | 2017-12-17 09:15 | 51510.418 | 100.008
Devonshire Building | 2017-12-17 09:30 | 51510.443 | 100.008
Devonshire Building | 2017-12-17 09:45 | 51510.473 | 119.988
Devonshire Building | 2017-12-17 10:00 | 51510.503 | 119.988
Devonshire Building | 2017-12-17 10:15 | 51510.528 | 100.008
Devonshire Building | 2017-12-17 10:30 | 51510.558 | 119.988
Devonshire Building | 2017-12-17 10:45 | 51510.588 | 119.988
Devonshire Building | 2017-12-17 11:00 | 51510.613 | 100.008
Devonshire Building | 2017-12-17 11:15 | 51510.638 | 100.008
Devonshire Building | 2017-12-17 11:30 | 51510.653 | 60.012
Devonshire Building | 2017-12-17 11:45 | 51510.663 | 39.996
Devonshire Building | 2017-12-17 12:00 | 51510.958 | 1180.008
Devonshire Building | 2017-12-17 12:15 | 51510.973 | 60.012
Devonshire Building | 2017-12-17 12:30 | 51510.983 | 39.996
Devonshire Building | 2017-12-17 12:45 | 51510.993 | 39.996
Devonshire Building | 2017-12-17 13:00 | 51511.008 | 60.012
Devonshire Building | 2017-12-17 13:15 | 51511.018 | 39.996
Devonshire Building | 2017-12-17 13:30 | 51511.028 | 39.996
Devonshire Building | 2017-12-17 13:45 | 51511.038 | 39.996
Devonshire Building | 2017-12-17 14:00 | 51511.053 | 60.012
Devonshire Building | 2017-12-17 14:15 | 51511.063 | 39.996
Devonshire Building | 2017-12-17 14:30 | 51511.073 | 39.996
Devonshire Building | 2017-12-17 14:45 | 51511.088 | 60.012
Devonshire Building | 2017-12-17 15:00 | 51511.103 | 60.012
Devonshire Building | 2017-12-17 15:15 | 51511.118 | 60.012
Devonshire Building | 2017-12-17 15:30 | 51511.128 | 39.996
Devonshire Building | 2017-12-17 15:45 | 51511.143 | 60.012
Devonshire Building | 2017-12-17 16:00 | 51511.158 | 60.012
Devonshire Building | 2017-12-17 16:15 | 51511.168 | 39.996
Devonshire Building | 2017-12-17 16:30 | 51511.408 | 960.012
Devonshire Building | 2017-12-17 16:45 | 51511.473 | 259.992
Devonshire Building | 2017-12-17 17:00 | 51511.488 | 60.012
Devonshire Building | 2017-12-17 17:15 | 51511.498 | 39.996
Devonshire Building | 2017-12-17 17:30 | 51511.508 | 39.996
Devonshire Building | 2017-12-17 17:45 | 51511.523 | 60.012
Devonshire Building | 2017-12-17 18:00 | 51511.533 | 39.996
Devonshire Building | 2017-12-17 18:15 | 51511.543 | 39.996
Devonshire Building | 2017-12-17 18:30 | 51511.558 | 60.012
Devonshire Building | 2017-12-17 18:45 | 51511.568 | 39.996
Devonshire Building | 2017-12-17 19:00 | 51511.578 | 39.996
Devonshire Building | 2017-12-17 19:15 | 51511.593 | 60.012
Devonshire Building | 2017-12-17 19:30 | 51511.608 | 60.012
Devonshire Building | 2017-12-17 19:45 | 51511.623 | 60.012
Devonshire Building | 2017-12-17 20:00 | 51511.633 | 39.996
Devonshire Building | 2017-12-17 20:15 | 51511.648 | 60.012
Devonshire Building | 2017-12-17 20:30 | 51511.663 | 60.012
Devonshire Building | 2017-12-17 20:45 | 51511.673 | 39.996
Devonshire Building | 2017-12-17 21:00 | 51511.688 | 60.012
Devonshire Building | 2017-12-17 21:15 | 51511.7031 | 60.012
Devonshire Building | 2017-12-17 21:30 | 51511.7131 | 39.996
Devonshire Building | 2017-12-17 21:45 | 51511.7481 | 140.004
Devonshire Building | 2017-12-17 22:00 | 51511.7631 | 60.012
Devonshire Building | 2017-12-17 22:15 | 51511.7781 | 60.012
Devonshire Building | 2017-12-17 22:30 | 51511.7881 | 39.996
Devonshire Building | 2017-12-17 22:45 | 51512.0881 | 1199.988
Devonshire Building | 2017-12-17 23:00 | 51512.0981 | 39.996
Devonshire Building | 2017-12-17 23:15 | 51512.1131 | 60.012
Devonshire Building | 2017-12-17 23:30 | 51512.1231 | 39.996
Devonshire Building | 2017-12-17 23:45 | 51512.1331 | 39.996
Devonshire Building | 2017-12-18 | 51512.1445 | 39.996
Devonshire Building | 2017-12-18 00:15 | 51512.1595 | 60.012
Devonshire Building | 2017-12-18 00:30 | 51512.1695 | 39.996
Devonshire Building | 2017-12-18 00:45 | 51512.1795 | 39.996
Devonshire Building | 2017-12-18 01:00 | 51512.1945 | 60.012
Devonshire Building | 2017-12-18 01:15 | 51512.2045 | 39.996
Devonshire Building | 2017-12-18 01:30 | 51512.2195 | 60.012
Devonshire Building | 2017-12-18 01:45 | 51512.2345 | 60.012
Devonshire Building | 2017-12-18 02:00 | 51512.2445 | 39.996
Devonshire Building | 2017-12-18 02:15 | 51512.2595 | 60.012
Devonshire Building | 2017-12-18 02:30 | 51512.2745 | 60.012
Devonshire Building | 2017-12-18 02:45 | 51512.2895 | 60.012
Devonshire Building | 2017-12-18 03:00 | 51512.2995 | 39.996
Devonshire Building | 2017-12-18 03:15 | 51512.3145 | 60.012
Devonshire Building | 2017-12-18 03:30 | 51512.3296 | 60.012
Devonshire Building | 2017-12-18 03:45 | 51512.3896 | 240.012
Devonshire Building | 2017-12-18 04:00 | 51512.6296 | 960.012
Devonshire Building | 2017-12-18 04:15 | 51512.6396 | 39.996
Devonshire Building | 2017-12-18 04:30 | 51512.6496 | 39.996
Devonshire Building | 2017-12-18 04:45 | 51512.6646 | 60.012
Devonshire Building | 2017-12-18 05:00 | 51512.6746 | 39.996
Devonshire Building | 2017-12-18 05:15 | 51512.6846 | 39.996
Devonshire Building | 2017-12-18 05:30 | 51512.6946 | 39.996
Devonshire Building | 2017-12-18 05:45 | 51512.7096 | 60.012
Devonshire Building | 2017-12-18 06:00 | 51512.7196 | 39.996
Devonshire Building | 2017-12-18 06:15 | 51512.7296 | 39.996
Devonshire Building | 2017-12-18 06:30 | 51512.7446 | 60.012
Devonshire Building | 2017-12-18 06:45 | 51512.7596 | 60.012
Devonshire Building | 2017-12-18 07:00 | 51512.7796 | 79.992
Devonshire Building | 2017-12-18 07:15 | 51512.7946 | 60.012
Devonshire Building | 2017-12-18 07:30 | 51512.8096 | 60.012
Devonshire Building | 2017-12-18 07:45 | 51512.8346 | 100.008
Devonshire Building | 2017-12-18 08:00 | 51513.1946 | 1440
Devonshire Building | 2017-12-18 08:15 | 51513.2196 | 100.008
Devonshire Building | 2017-12-18 08:30 | 51513.2496 | 119.988
Devonshire Building | 2017-12-18 08:45 | 51513.3046 | 219.996
Devonshire Building | 2017-12-18 09:00 | 51513.6296 | 1299.996
Devonshire Building | 2017-12-18 09:15 | 51513.6596 | 119.988
Devonshire Building | 2017-12-18 09:30 | 51513.6946 | 140.004
Devonshire Building | 2017-12-18 09:45 | 51513.7246 | 119.988
Devonshire Building | 2017-12-18 10:00 | 51513.8196 | 380.016
Devonshire Building | 2017-12-18 10:15 | 51514.1546 | 1339.992
Devonshire Building | 2017-12-18 10:30 | 51514.1946 | 159.984
Devonshire Building | 2017-12-18 10:45 | 51514.3796 | 740.016
Devonshire Building | 2017-12-18 11:00 | 51514.6896 | 1239.984
Devonshire Building | 2017-12-18 11:15 | 51514.7446 | 219.996
Devonshire Building | 2017-12-18 11:30 | 51515.0896 | 1379.988
Devonshire Building | 2017-12-18 11:45 | 51515.1846 | 380.016
Devonshire Building | 2017-12-18 12:00 | 51515.2546 | 280.008
Devonshire Building | 2017-12-18 12:15 | 51515.3196 | 259.992
Devonshire Building | 2017-12-18 12:30 | 51515.7096 | 1559.988
Devonshire Building | 2017-12-18 12:45 | 51515.7746 | 259.992
Devonshire Building | 2017-12-18 13:00 | 51515.8846 | 439.992
Devonshire Building | 2017-12-18 13:15 | 51516.3195 | 1739.988
Devonshire Building | 2017-12-18 13:30 | 51516.4596 | 560.016
Devonshire Building | 2017-12-18 13:45 | 51516.6446 | 740.016
Devonshire Building | 2017-12-18 14:00 | 51516.8396 | 780.012
Devonshire Building | 2017-12-18 14:15 | 51517.1446 | 1220.004
Devonshire Building | 2017-12-18 14:30 | 51517.2196 | 299.988
Devonshire Building | 2017-12-18 14:45 | 51517.2846 | 259.992
Devonshire Building | 2017-12-18 15:00 | 51517.6696 | 1540.008
Devonshire Building | 2017-12-18 15:15 | 51517.7346 | 259.992
Devonshire Building | 2017-12-18 15:30 | 51517.7996 | 259.992
Devonshire Building | 2017-12-18 15:45 | 51517.8596 | 240.012
Devonshire Building | 2017-12-18 16:00 | 51517.9796 | 479.988
Devonshire Building | 2017-12-18 16:15 | 51518.2696 | 1159.992
Devonshire Building | 2017-12-18 16:30 | 51518.3046 | 140.004
Devonshire Building | 2017-12-18 16:45 | 51518.3396 | 140.004
Devonshire Building | 2017-12-18 17:00 | 51518.3996 | 240.012
Devonshire Building | 2017-12-18 17:15 | 51518.7846 | 1540.008
Devonshire Building | 2017-12-18 17:30 | 51518.8546 | 280.008
Devonshire Building | 2017-12-18 17:45 | 51518.9196 | 259.992
Devonshire Building | 2017-12-18 18:00 | 51518.9796 | 240.012
Devonshire Building | 2017-12-18 18:15 | 51519.0296 | 200.016
Devonshire Building | 2017-12-18 18:30 | 51519.3546 | 1299.996
Devonshire Building | 2017-12-18 18:45 | 51519.3846 | 119.988
Devonshire Building | 2017-12-18 19:00 | 51519.4146 | 119.988
Devonshire Building | 2017-12-18 19:15 | 51519.4446 | 119.988
Devonshire Building | 2017-12-18 19:30 | 51519.4746 | 119.988
Devonshire Building | 2017-12-18 19:45 | 51519.4996 | 100.008
Devonshire Building | 2017-12-18 20:00 | 51519.5296 | 119.988
Devonshire Building | 2017-12-18 20:15 | 51519.5546 | 100.008
Devonshire Building | 2017-12-18 20:30 | 51519.5796 | 100.008
Devonshire Building | 2017-12-18 20:45 | 51519.5996 | 79.992
Devonshire Building | 2017-12-18 21:00 | 51519.6246 | 100.008
Devonshire Building | 2017-12-18 21:15 | 51519.6446 | 79.992
Devonshire Building | 2017-12-18 21:30 | 51519.6646 | 79.992
Devonshire Building | 2017-12-18 21:45 | 51519.6945 | 119.988
Devonshire Building | 2017-12-18 22:00 | 51519.7045 | 39.996
Devonshire Building | 2017-12-18 22:15 | 51519.7145 | 39.996
Devonshire Building | 2017-12-18 22:30 | 51519.7245 | 39.996
Devonshire Building | 2017-12-18 22:45 | 51519.7345 | 39.996
Devonshire Building | 2017-12-18 23:00 | 51519.7395 | 20.016
Devonshire Building | 2017-12-18 23:15 | 51519.7495 | 39.996
Devonshire Building | 2017-12-18 23:30 | 51519.7595 | 39.996
Devonshire Building | 2017-12-18 23:45 | 51519.8245 | 259.992
Devonshire Building | 2017-12-19 | 51520.0742 | 1000.008
Devonshire Building | 2017-12-19 00:15 | 51520.0792 | 20.016
Devonshire Building | 2017-12-19 00:30 | 51520.0892 | 39.996
Devonshire Building | 2017-12-19 00:45 | 51520.0992 | 39.996
Devonshire Building | 2017-12-19 01:00 | 51520.1042 | 20.016
Devonshire Building | 2017-12-19 01:15 | 51520.1142 | 39.996
Devonshire Building | 2017-12-19 01:30 | 51520.1242 | 39.996
Devonshire Building | 2017-12-19 01:45 | 51520.1292 | 20.016
Devonshire Building | 2017-12-19 02:00 | 51520.1392 | 39.996
Devonshire Building | 2017-12-19 02:15 | 51520.1492 | 39.996
Devonshire Building | 2017-12-19 02:30 | 51520.1542 | 20.016
Devonshire Building | 2017-12-19 02:45 | 51520.1642 | 39.996
Devonshire Building | 2017-12-19 03:00 | 51520.1742 | 39.996
Devonshire Building | 2017-12-19 03:15 | 51520.1792 | 20.016
Devonshire Building | 2017-12-19 03:30 | 51520.1892 | 39.996
Devonshire Building | 2017-12-19 03:45 | 51520.1942 | 20.016
Devonshire Building | 2017-12-19 04:00 | 51520.2042 | 39.996
Devonshire Building | 2017-12-19 04:15 | 51520.2092 | 20.016
Devonshire Building | 2017-12-19 04:30 | 51520.2192 | 39.996
Devonshire Building | 2017-12-19 04:45 | 51520.2292 | 39.996
Devonshire Building | 2017-12-19 05:00 | 51520.2342 | 20.016
Devonshire Building | 2017-12-19 05:15 | 51520.2442 | 39.996
Devonshire Building | 2017-12-19 05:30 | 51520.2542 | 39.996
Devonshire Building | 2017-12-19 05:45 | 51520.4992 | 979.992
Devonshire Building | 2017-12-19 06:00 | 51520.5642 | 259.992
Devonshire Building | 2017-12-19 06:15 | 51520.5742 | 39.996
Devonshire Building | 2017-12-19 06:30 | 51520.5842 | 39.996
Devonshire Building | 2017-12-19 06:45 | 51520.5942 | 39.996
Devonshire Building | 2017-12-19 07:00 | 51520.6042 | 39.996
Devonshire Building | 2017-12-19 07:15 | 51520.6092 | 20.016
Devonshire Building | 2017-12-19 07:30 | 51520.6292 | 79.992
Devonshire Building | 2017-12-19 07:45 | 51520.6542 | 100.008
Devonshire Building | 2017-12-19 08:00 | 51520.6792 | 100.008
Devonshire Building | 2017-12-19 08:15 | 51520.7092 | 119.988
Devonshire Building | 2017-12-19 08:30 | 51520.7392 | 119.988
Devonshire Building | 2017-12-19 08:45 | 51521.1092 | 1479.996
Devonshire Building | 2017-12-19 09:00 | 51521.1492 | 159.984
Devonshire Building | 2017-12-19 09:15 | 51521.2042 | 219.996
Devonshire Building | 2017-12-19 09:30 | 51521.3092 | 420.012
Devonshire Building | 2017-12-19 09:45 | 51521.4092 | 399.996
Devonshire Building | 2017-12-19 10:00 | 51521.7742 | 1460.016
Devonshire Building | 2017-12-19 10:15 | 51521.9242 | 600.012
Devonshire Building | 2017-12-19 10:30 | 51522.0092 | 339.984
Devonshire Building | 2017-12-19 10:45 | 51522.0792 | 280.008
Devonshire Building | 2017-12-19 11:00 | 51522.1542 | 299.988
Devonshire Building | 2017-12-19 11:15 | 51522.2442 | 360
Devonshire Building | 2017-12-19 11:30 | 51522.3242 | 320.004
Devonshire Building | 2017-12-19 11:45 | 51522.5742 | 1000.008
Devonshire Building | 2017-12-19 12:00 | 51522.6242 | 200.016
Devonshire Building | 2017-12-19 12:15 | 51522.6692 | 180
Devonshire Building | 2017-12-19 12:30 | 51522.7142 | 180
Devonshire Building | 2017-12-19 12:45 | 51522.7642 | 200.016
Devonshire Building | 2017-12-19 13:00 | 51523.0592 | 1180.008
Devonshire Building | 2017-12-19 13:15 | 51523.1192 | 240.012
Devonshire Building | 2017-12-19 13:30 | 51523.2042 | 339.984
Devonshire Building | 2017-12-19 13:45 | 51523.3392 | 540
Devonshire Building | 2017-12-19 14:00 | 51523.4592 | 479.988
Devonshire Building | 2017-12-19 14:15 | 51523.9292 | 1879.992
Devonshire Building | 2017-12-19 14:30 | 51524.0092 | 320.004
Devonshire Building | 2017-12-19 14:45 | 51524.0742 | 259.992
Devonshire Building | 2017-12-19 15:00 | 51524.1292 | 219.996
Devonshire Building | 2017-12-19 15:15 | 51524.1792 | 200.016
Devonshire Building | 2017-12-19 15:30 | 51524.6092 | 1720.008
Devonshire Building | 2017-12-19 15:45 | 51524.6392 | 119.988
Devonshire Building | 2017-12-19 16:00 | 51524.6642 | 100.008
Devonshire Building | 2017-12-19 16:15 | 51524.6792 | 60.012
Devonshire Building | 2017-12-19 16:30 | 51524.8542 | 699.984
Devonshire Building | 2017-12-19 16:45 | 51525.1492 | 1180.008
Devonshire Building | 2017-12-19 17:00 | 51525.1742 | 100.008
Devonshire Building | 2017-12-19 17:15 | 51525.1992 | 100.008
Devonshire Building | 2017-12-19 17:30 | 51525.2292 | 119.988
Devonshire Building | 2017-12-19 17:45 | 51525.2592 | 119.988
Devonshire Building | 2017-12-19 18:00 | 51525.2892 | 119.988
Devonshire Building | 2017-12-19 18:15 | 51525.3192 | 119.988
Devonshire Building | 2017-12-19 18:30 | 51525.3492 | 119.988
Devonshire Building | 2017-12-19 18:45 | 51525.3742 | 100.008
Devonshire Building | 2017-12-19 19:00 | 51525.3992 | 100.008
Devonshire Building | 2017-12-19 19:15 | 51525.4242 | 100.008
Devonshire Building | 2017-12-19 19:30 | 51525.8492 | 1699.992
Devonshire Building | 2017-12-19 19:45 | 51525.8792 | 119.988
Devonshire Building | 2017-12-19 20:00 | 51525.9092 | 119.988
Devonshire Building | 2017-12-19 20:15 | 51525.9442 | 140.004
Devonshire Building | 2017-12-19 20:30 | 51525.9792 | 140.004
Devonshire Building | 2017-12-19 20:45 | 51526.0142 | 140.004
Devonshire Building | 2017-12-19 21:00 | 51526.0492 | 140.004
Devonshire Building | 2017-12-19 21:15 | 51526.0792 | 119.988
Devonshire Building | 2017-12-19 21:30 | 51526.1092 | 119.988
Devonshire Building | 2017-12-19 21:45 | 51526.1542 | 180
Devonshire Building | 2017-12-19 22:00 | 51526.1742 | 79.992
Devonshire Building | 2017-12-19 22:15 | 51526.1992 | 100.008
Devonshire Building | 2017-12-19 22:30 | 51526.2192 | 79.992
Devonshire Building | 2017-12-19 22:45 | 51526.2392 | 79.992
Devonshire Building | 2017-12-19 23:00 | 51526.2592 | 79.992
Devonshire Building | 2017-12-19 23:15 | 51526.2842 | 100.008
Devonshire Building | 2017-12-19 23:30 | 51526.3042 | 79.992
Devonshire Building | 2017-12-19 23:45 | 51526.3242 | 79.992
Devonshire Building | 2017-12-20 | 51526.3398 | 60.012
Devonshire Building | 2017-12-20 00:15 | 51526.3598 | 79.992
Devonshire Building | 2017-12-20 00:30 | 51526.3798 | 79.992
Devonshire Building | 2017-12-20 00:45 | 51526.3998 | 79.992
Devonshire Building | 2017-12-20 01:00 | 51526.4148 | 60.012
Devonshire Building | 2017-12-20 01:15 | 51526.4348 | 79.992
Devonshire Building | 2017-12-20 01:30 | 51526.4548 | 79.992
Devonshire Building | 2017-12-20 01:45 | 51526.4698 | 60.012
Devonshire Building | 2017-12-20 02:00 | 51526.4898 | 79.992
Devonshire Building | 2017-12-20 02:15 | 51526.5048 | 60.012
Devonshire Building | 2017-12-20 02:30 | 51526.5198 | 60.012
Devonshire Building | 2017-12-20 02:45 | 51526.5398 | 79.992
Devonshire Building | 2017-12-20 03:00 | 51526.5548 | 60.012
Devonshire Building | 2017-12-20 03:15 | 51526.5698 | 60.012
Devonshire Building | 2017-12-20 03:30 | 51526.5848 | 60.012
Devonshire Building | 2017-12-20 03:45 | 51526.6048 | 79.992
Devonshire Building | 2017-12-20 04:00 | 51526.6198 | 60.012
Devonshire Building | 2017-12-20 04:15 | 51526.6349 | 60.012
Devonshire Building | 2017-12-20 04:30 | 51527.0248 | 1559.988
Devonshire Building | 2017-12-20 04:45 | 51527.0399 | 60.012
Devonshire Building | 2017-12-20 05:00 | 51527.0549 | 60.012
Devonshire Building | 2017-12-20 05:15 | 51527.0649 | 39.996
Devonshire Building | 2017-12-20 05:30 | 51527.0799 | 60.012
Devonshire Building | 2017-12-20 05:45 | 51527.0899 | 39.996
Devonshire Building | 2017-12-20 06:00 | 51527.1049 | 60.012
Devonshire Building | 2017-12-20 06:15 | 51527.1199 | 60.012
Devonshire Building | 2017-12-20 06:30 | 51527.1349 | 60.012
Devonshire Building | 2017-12-20 06:45 | 51527.1499 | 60.012
Devonshire Building | 2017-12-20 07:00 | 51527.1649 | 60.012
Devonshire Building | 2017-12-20 07:15 | 51527.1799 | 60.012
Devonshire Building | 2017-12-20 07:30 | 51527.1999 | 79.992
Devonshire Building | 2017-12-20 07:45 | 51527.2249 | 100.008
Devonshire Building | 2017-12-20 08:00 | 51527.2649 | 159.984
Devonshire Building | 2017-12-20 08:15 | 51527.3149 | 200.016
Devonshire Building | 2017-12-20 08:30 | 51527.7649 | 1800
Devonshire Building | 2017-12-20 08:45 | 51527.8249 | 240.012
Devonshire Building | 2017-12-20 09:00 | 51527.9049 | 320.004
Devonshire Building | 2017-12-20 09:15 | 51527.9749 | 280.008
Devonshire Building | 2017-12-20 09:30 | 51528.0449 | 280.008
Devonshire Building | 2017-12-20 09:45 | 51528.1199 | 299.988
Devonshire Building | 2017-12-20 10:00 | 51528.4649 | 1379.988
Devonshire Building | 2017-12-20 10:15 | 51528.6549 | 759.996
Devonshire Building | 2017-12-20 10:30 | 51528.7199 | 259.992
Devonshire Building | 2017-12-20 10:45 | 51528.7899 | 280.008
Devonshire Building | 2017-12-20 11:00 | 51528.8699 | 320.004
Devonshire Building | 2017-12-20 11:15 | 51529.3899 | 2080.008
Devonshire Building | 2017-12-20 11:30 | 51529.4649 | 299.988
Devonshire Building | 2017-12-20 11:45 | 51529.5449 | 320.004
Devonshire Building | 2017-12-20 12:00 | 51529.6149 | 280.008
Devonshire Building | 2017-12-20 12:15 | 51530.1149 | 2000.016
Devonshire Building | 2017-12-20 12:30 | 51530.1749 | 240.012
Devonshire Building | 2017-12-20 12:45 | 51530.2449 | 280.008
Devonshire Building | 2017-12-20 13:00 | 51530.3149 | 280.008
Devonshire Building | 2017-12-20 13:15 | 51530.3749 | 240.012
Devonshire Building | 2017-12-20 13:30 | 51530.4399 | 259.992
Devonshire Building | 2017-12-20 13:45 | 51530.8299 | 1559.988
Devonshire Building | 2017-12-20 14:00 | 51530.9799 | 600.012
Devonshire Building | 2017-12-20 14:15 | 51531.0349 | 219.996
Devonshire Building | 2017-12-20 14:30 | 51531.0949 | 240.012
Devonshire Building | 2017-12-20 14:45 | 51531.1499 | 219.996
Devonshire Building | 2017-12-20 15:00 | 51531.3449 | 780.012
Devonshire Building | 2017-12-20 15:15 | 51531.6549 | 1239.984
Devonshire Building | 2017-12-20 15:30 | 51531.6949 | 159.984
Devonshire Building | 2017-12-20 15:45 | 51531.7399 | 180
Devonshire Building | 2017-12-20 16:00 | 51531.7799 | 159.984
Devonshire Building | 2017-12-20 16:15 | 51531.8199 | 159.984
Devonshire Building | 2017-12-20 16:30 | 51531.8949 | 299.988
Devonshire Building | 2017-12-20 16:45 | 51532.2999 | 1620
Devonshire Building | 2017-12-20 17:00 | 51532.3449 | 180
Devonshire Building | 2017-12-20 17:15 | 51532.3899 | 180
Devonshire Building | 2017-12-20 17:30 | 51532.4349 | 180
Devonshire Building | 2017-12-20 17:45 | 51532.4749 | 159.984
Devonshire Building | 2017-12-20 18:00 | 51532.5199 | 180
Devonshire Building | 2017-12-20 18:15 | 51532.5549 | 140.004
Devonshire Building | 2017-12-20 18:30 | 51532.5949 | 159.984
Devonshire Building | 2017-12-20 18:45 | 51532.6249 | 119.988
Devonshire Building | 2017-12-20 19:00 | 51532.6599 | 140.004
Devonshire Building | 2017-12-20 19:15 | 51532.6899 | 119.988
Devonshire Building | 2017-12-20 19:30 | 51532.7149 | 100.008
Devonshire Building | 2017-12-20 19:45 | 51532.7399 | 100.008
Devonshire Building | 2017-12-20 20:00 | 51532.7649 | 100.008
Devonshire Building | 2017-12-20 20:15 | 51533.1649 | 1599.984
Devonshire Building | 2017-12-20 20:30 | 51533.1799 | 60.012
Devonshire Building | 2017-12-20 20:45 | 51533.1949 | 60.012
Devonshire Building | 2017-12-20 21:00 | 51533.2099 | 60.012
Devonshire Building | 2017-12-20 21:15 | 51533.2249 | 60.012
Devonshire Building | 2017-12-20 21:30 | 51533.2399 | 60.012
Devonshire Building | 2017-12-20 21:45 | 51533.2699 | 119.988
Devonshire Building | 2017-12-20 22:00 | 51533.2799 | 39.996
Devonshire Building | 2017-12-20 22:15 | 51533.2949 | 60.012
Devonshire Building | 2017-12-20 22:30 | 51533.3049 | 39.996
Devonshire Building | 2017-12-20 22:45 | 51533.3199 | 60.012
Devonshire Building | 2017-12-20 23:00 | 51533.3349 | 60.012
Devonshire Building | 2017-12-20 23:15 | 51533.3449 | 39.996
Devonshire Building | 2017-12-20 23:30 | 51533.3599 | 60.012
Devonshire Building | 2017-12-20 23:45 | 51533.3699 | 39.996
Devonshire Building | 2017-12-21 | 51533.3828 | 60.012
Devonshire Building | 2017-12-21 00:15 | 51533.3928 | 39.996
Devonshire Building | 2017-12-21 00:30 | 51533.4078 | 60.012
Devonshire Building | 2017-12-21 00:45 | 51533.4178 | 39.996
Devonshire Building | 2017-12-21 01:00 | 51533.4278 | 39.996
Devonshire Building | 2017-12-21 01:15 | 51533.4428 | 60.012
Devonshire Building | 2017-12-21 01:30 | 51533.4528 | 39.996
Devonshire Building | 2017-12-21 01:45 | 51533.4628 | 39.996
Devonshire Building | 2017-12-21 02:00 | 51533.4728 | 39.996
Devonshire Building | 2017-12-21 02:15 | 51533.4828 | 39.996
Devonshire Building | 2017-12-21 02:30 | 51533.4978 | 60.012
Devonshire Building | 2017-12-21 02:45 | 51533.5078 | 39.996
Devonshire Building | 2017-12-21 03:00 | 51533.5178 | 39.996
Devonshire Building | 2017-12-21 03:15 | 51533.5278 | 39.996
Devonshire Building | 2017-12-21 03:30 | 51533.5378 | 39.996
Devonshire Building | 2017-12-21 03:45 | 51533.5478 | 39.996
Devonshire Building | 2017-12-21 04:00 | 51533.5578 | 39.996
Devonshire Building | 2017-12-21 04:15 | 51533.9528 | 1580.004
Devonshire Building | 2017-12-21 04:30 | 51533.9628 | 39.996
Devonshire Building | 2017-12-21 04:45 | 51533.9728 | 39.996
Devonshire Building | 2017-12-21 05:00 | 51533.9828 | 39.996
Devonshire Building | 2017-12-21 05:15 | 51533.9928 | 39.996
Devonshire Building | 2017-12-21 05:30 | 51534.0028 | 39.996
Devonshire Building | 2017-12-21 05:45 | 51534.0128 | 39.996
Devonshire Building | 2017-12-21 06:00 | 51534.0228 | 39.996
Devonshire Building | 2017-12-21 06:15 | 51534.0328 | 39.996
Devonshire Building | 2017-12-21 06:30 | 51534.0428 | 39.996
Devonshire Building | 2017-12-21 06:45 | 51534.0528 | 39.996
Devonshire Building | 2017-12-21 07:00 | 51534.0678 | 60.012
Devonshire Building | 2017-12-21 07:15 | 51534.0778 | 39.996
Devonshire Building | 2017-12-21 07:30 | 51534.0878 | 39.996
Devonshire Building | 2017-12-21 07:45 | 51534.1078 | 79.992
Devonshire Building | 2017-12-21 08:00 | 51534.1378 | 119.988
Devonshire Building | 2017-12-21 08:15 | 51534.1628 | 100.008
Devonshire Building | 2017-12-21 08:30 | 51534.1928 | 119.988
Devonshire Building | 2017-12-21 08:45 | 51534.2228 | 119.988
Devonshire Building | 2017-12-21 09:00 | 51534.2528 | 119.988
Devonshire Building | 2017-12-21 09:15 | 51534.6978 | 1779.984
Devonshire Building | 2017-12-21 09:30 | 51534.7278 | 119.988
Devonshire Building | 2017-12-21 09:45 | 51534.7628 | 140.004
Devonshire Building | 2017-12-21 10:00 | 51534.7928 | 119.988
Devonshire Building | 2017-12-21 10:15 | 51534.8228 | 119.988
Devonshire Building | 2017-12-21 10:30 | 51534.8528 | 119.988
Devonshire Building | 2017-12-21 10:45 | 51535.2978 | 1779.984
Devonshire Building | 2017-12-21 11:00 | 51535.3378 | 159.984
Devonshire Building | 2017-12-21 11:15 | 51535.3878 | 200.016
Devonshire Building | 2017-12-21 11:30 | 51535.4228 | 140.004
Devonshire Building | 2017-12-21 11:45 | 51535.4678 | 180
Devonshire Building | 2017-12-21 12:00 | 51535.5078 | 159.984
Devonshire Building | 2017-12-21 12:15 | 51536.0228 | 2059.992
Devonshire Building | 2017-12-21 12:30 | 51536.0678 | 180
Devonshire Building | 2017-12-21 12:45 | 51536.1178 | 200.016
Devonshire Building | 2017-12-21 13:00 | 51536.1678 | 200.016
Devonshire Building | 2017-12-21 13:15 | 51536.2178 | 200.016
Devonshire Building | 2017-12-21 13:30 | 51536.3328 | 460.008
Devonshire Building | 2017-12-21 13:45 | 51536.7378 | 1620
Devonshire Building | 2017-12-21 14:00 | 51536.7778 | 159.984
Devonshire Building | 2017-12-21 14:15 | 51536.8228 | 180
Devonshire Building | 2017-12-21 14:30 | 51536.8678 | 180
Devonshire Building | 2017-12-21 14:45 | 51536.9128 | 180
Devonshire Building | 2017-12-21 15:00 | 51536.9578 | 180
Devonshire Building | 2017-12-21 15:15 | 51537.1678 | 839.988
Devonshire Building | 2017-12-21 15:30 | 51537.2028 | 140.004
Devonshire Building | 2017-12-21 15:45 | 51537.2428 | 159.984
Devonshire Building | 2017-12-21 16:00 | 51537.2778 | 140.004
Devonshire Building | 2017-12-21 16:15 | 51537.3078 | 119.988
Devonshire Building | 2017-12-21 16:30 | 51537.3528 | 180
Devonshire Building | 2017-12-21 16:45 | 51537.4378 | 339.984
Devonshire Building | 2017-12-21 17:00 | 51537.6528 | 860.004
Devonshire Building | 2017-12-21 17:15 | 51537.6778 | 100.008
Devonshire Building | 2017-12-21 17:30 | 51537.7078 | 119.988
Devonshire Building | 2017-12-21 17:45 | 51537.7328 | 100.008
Devonshire Building | 2017-12-21 18:00 | 51537.7628 | 119.988
Devonshire Building | 2017-12-21 18:15 | 51537.7878 | 100.008
Devonshire Building | 2017-12-21 18:30 | 51537.8178 | 119.988
Devonshire Building | 2017-12-21 18:45 | 51537.8428 | 100.008
Devonshire Building | 2017-12-21 19:00 | 51537.8678 | 100.008
Devonshire Building | 2017-12-21 19:15 | 51537.8928 | 100.008
Devonshire Building | 2017-12-21 19:30 | 51537.9178 | 100.008
Devonshire Building | 2017-12-21 19:45 | 51537.9378 | 79.992
Devonshire Building | 2017-12-21 20:00 | 51537.9628 | 100.008
Devonshire Building | 2017-12-21 20:15 | 51537.9828 | 79.992
Devonshire Building | 2017-12-21 20:30 | 51538.0028 | 79.992
Devonshire Building | 2017-12-21 20:45 | 51538.0278 | 100.008
Devonshire Building | 2017-12-21 21:00 | 51538.0478 | 79.992
Devonshire Building | 2017-12-21 21:15 | 51538.4528 | 1620
Devonshire Building | 2017-12-21 21:30 | 51538.4678 | 60.012
Devonshire Building | 2017-12-21 21:45 | 51538.5028 | 140.004
Devonshire Building | 2017-12-21 22:00 | 51538.5128 | 39.996
Devonshire Building | 2017-12-21 22:15 | 51538.5278 | 60.012
Devonshire Building | 2017-12-21 22:30 | 51538.5428 | 60.012
Devonshire Building | 2017-12-21 22:45 | 51538.5528 | 39.996
Devonshire Building | 2017-12-21 23:00 | 51538.5678 | 60.012
Devonshire Building | 2017-12-21 23:15 | 51538.5828 | 60.012
Devonshire Building | 2017-12-21 23:30 | 51538.5978 | 60.012
Devonshire Building | 2017-12-21 23:45 | 51538.6178 | 79.992
Devonshire Building | 2017-12-22 | 51538.6328 | 60.012
Devonshire Building | 2017-12-22 00:15 | 51538.6478 | 60.012
Devonshire Building | 2017-12-22 00:30 | 51538.6628 | 60.012
Devonshire Building | 2017-12-22 00:45 | 51538.6778 | 60.012
Devonshire Building | 2017-12-22 01:00 | 51538.6928 | 60.012
Devonshire Building | 2017-12-22 01:15 | 51538.7078 | 60.012
Devonshire Building | 2017-12-22 01:30 | 51538.7228 | 60.012
Devonshire Building | 2017-12-22 01:45 | 51538.7378 | 60.012
Devonshire Building | 2017-12-22 02:00 | 51538.7478 | 39.996
Devonshire Building | 2017-12-22 02:15 | 51538.7628 | 60.012
Devonshire Building | 2017-12-22 02:30 | 51538.7778 | 60.012
Devonshire Building | 2017-12-22 02:45 | 51538.7878 | 39.996
Devonshire Building | 2017-12-22 03:00 | 51538.8028 | 60.012
Devonshire Building | 2017-12-22 03:15 | 51538.8128 | 39.996
Devonshire Building | 2017-12-22 03:30 | 51538.8228 | 39.996
Devonshire Building | 2017-12-22 03:45 | 51538.8378 | 60.012
Devonshire Building | 2017-12-22 04:00 | 51538.8478 | 39.996
Devonshire Building | 2017-12-22 04:15 | 51538.8578 | 39.996
Devonshire Building | 2017-12-22 04:30 | 51538.8728 | 60.012
Devonshire Building | 2017-12-22 04:45 | 51538.8828 | 39.996
Devonshire Building | 2017-12-22 05:00 | 51538.8928 | 39.996
Devonshire Building | 2017-12-22 05:15 | 51538.9028 | 39.996
Devonshire Building | 2017-12-22 05:30 | 51538.9128 | 39.996
Devonshire Building | 2017-12-22 05:45 | 51538.9228 | 39.996
Devonshire Building | 2017-12-22 06:00 | 51538.9378 | 60.012
Devonshire Building | 2017-12-22 06:15 | 51539.3278 | 1559.988
Devonshire Building | 2017-12-22 06:30 | 51539.3378 | 39.996
Devonshire Building | 2017-12-22 06:45 | 51539.3528 | 60.012
Devonshire Building | 2017-12-22 07:00 | 51539.3628 | 39.996
Devonshire Building | 2017-12-22 07:15 | 51539.3728 | 39.996
Devonshire Building | 2017-12-22 07:30 | 51539.3828 | 39.996
Devonshire Building | 2017-12-22 07:45 | 51539.4028 | 79.992
Devonshire Building | 2017-12-22 08:00 | 51539.4328 | 119.988
Devonshire Building | 2017-12-22 08:15 | 51539.4628 | 119.988
Devonshire Building | 2017-12-22 08:30 | 51539.4878 | 100.008
Devonshire Building | 2017-12-22 08:45 | 51539.5128 | 100.008
Devonshire Building | 2017-12-22 09:00 | 51539.5428 | 119.988
Devonshire Building | 2017-12-22 09:15 | 51539.9778 | 1739.988
Devonshire Building | 2017-12-22 09:30 | 51540.0078 | 119.988
Devonshire Building | 2017-12-22 09:45 | 51540.0378 | 119.988
Devonshire Building | 2017-12-22 10:00 | 51540.0728 | 140.004
Devonshire Building | 2017-12-22 10:15 | 51540.1078 | 140.004
Devonshire Building | 2017-12-22 10:30 | 51540.1428 | 140.004
Devonshire Building | 2017-12-22 10:45 | 51540.1878 | 180
Devonshire Building | 2017-12-22 11:00 | 51540.2328 | 180
Devonshire Building | 2017-12-22 11:15 | 51540.2778 | 180
Devonshire Building | 2017-12-22 11:30 | 51540.7078 | 1720.008
Devonshire Building | 2017-12-22 11:45 | 51540.7428 | 140.004
Devonshire Building | 2017-12-22 12:00 | 51540.7778 | 140.004
Devonshire Building | 2017-12-22 12:15 | 51540.8178 | 159.984
Devonshire Building | 2017-12-22 12:30 | 51540.8578 | 159.984
Devonshire Building | 2017-12-22 12:45 | 51540.8928 | 140.004
Devonshire Building | 2017-12-22 13:00 | 51540.9278 | 140.004
Devonshire Building | 2017-12-22 13:15 | 51541.1578 | 920.016
Devonshire Building | 2017-12-22 13:30 | 51541.4028 | 979.992
Devonshire Building | 2017-12-22 13:45 | 51541.4378 | 140.004
Devonshire Building | 2017-12-22 14:00 | 51541.4678 | 119.988
Devonshire Building | 2017-12-22 14:15 | 51541.4978 | 119.988
Devonshire Building | 2017-12-22 14:30 | 51541.5328 | 140.004
Devonshire Building | 2017-12-22 14:45 | 51541.5678 | 140.004
Devonshire Building | 2017-12-22 15:00 | 51541.5978 | 119.988
Devonshire Building | 2017-12-22 15:15 | 51541.6278 | 119.988
Devonshire Building | 2017-12-22 15:30 | 51542.0578 | 1720.008
Devonshire Building | 2017-12-22 15:45 | 51542.1078 | 200.016
Devonshire Building | 2017-12-22 16:00 | 51542.1578 | 200.016
Devonshire Building | 2017-12-22 16:15 | 51542.2078 | 200.016
Devonshire Building | 2017-12-22 16:30 | 51542.2528 | 180
Devonshire Building | 2017-12-22 16:45 | 51542.2928 | 159.984
Devonshire Building | 2017-12-22 17:00 | 51542.3378 | 180
Devonshire Building | 2017-12-22 17:15 | 51542.3728 | 140.004
Devonshire Building | 2017-12-22 17:30 | 51542.4078 | 140.004
Devonshire Building | 2017-12-22 17:45 | 51542.4378 | 119.988
Devonshire Building | 2017-12-22 18:00 | 51542.4678 | 119.988
Devonshire Building | 2017-12-22 18:15 | 51542.4978 | 119.988
Devonshire Building | 2017-12-22 18:30 | 51542.5228 | 100.008
Devonshire Building | 2017-12-22 18:45 | 51542.5478 | 100.008
Devonshire Building | 2017-12-22 19:00 | 51542.6278 | 320.004
Devonshire Building | 2017-12-22 19:15 | 51542.9678 | 1360.008
Devonshire Building | 2017-12-22 19:30 | 51542.9828 | 60.012
Devonshire Building | 2017-12-22 19:45 | 51542.9978 | 60.012
Devonshire Building | 2017-12-22 20:00 | 51543.0078 | 39.996
Devonshire Building | 2017-12-22 20:15 | 51543.0228 | 60.012
Devonshire Building | 2017-12-22 20:30 | 51543.0378 | 60.012
Devonshire Building | 2017-12-22 20:45 | 51543.0528 | 60.012
Devonshire Building | 2017-12-22 21:00 | 51543.0628 | 39.996
Devonshire Building | 2017-12-22 21:15 | 51543.0828 | 79.992
Devonshire Building | 2017-12-22 21:30 | 51543.0978 | 60.012
Devonshire Building | 2017-12-22 21:45 | 51543.1328 | 140.004
Devonshire Building | 2017-12-22 22:00 | 51543.1428 | 39.996
Devonshire Building | 2017-12-22 22:15 | 51543.1578 | 60.012
Devonshire Building | 2017-12-22 22:30 | 51543.1678 | 39.996
Devonshire Building | 2017-12-22 22:45 | 51543.1828 | 60.012
Devonshire Building | 2017-12-22 23:00 | 51543.1928 | 39.996
Devonshire Building | 2017-12-22 23:15 | 51543.2078 | 60.012
Devonshire Building | 2017-12-22 23:30 | 51543.2178 | 39.996
Devonshire Building | 2017-12-22 23:45 | 51543.2278 | 39.996
Devonshire Building | 2017-12-23 | 51543.2383 | 39.996
Devonshire Building | 2017-12-23 00:15 | 51543.2483 | 39.996
Devonshire Building | 2017-12-23 00:30 | 51543.2633 | 60.012
Devonshire Building | 2017-12-23 00:45 | 51543.2733 | 39.996
Devonshire Building | 2017-12-23 01:00 | 51543.2833 | 39.996
Devonshire Building | 2017-12-23 01:15 | 51543.2933 | 39.996
Devonshire Building | 2017-12-23 01:30 | 51543.3033 | 39.996
Devonshire Building | 2017-12-23 01:45 | 51543.3133 | 39.996
Devonshire Building | 2017-12-23 02:00 | 51543.3233 | 39.996
Devonshire Building | 2017-12-23 02:15 | 51543.3333 | 39.996
Devonshire Building | 2017-12-23 02:30 | 51543.3433 | 39.996
Devonshire Building | 2017-12-23 02:45 | 51543.3533 | 39.996
Devonshire Building | 2017-12-23 03:00 | 51543.3633 | 39.996
Devonshire Building | 2017-12-23 03:15 | 51543.3733 | 39.996
Devonshire Building | 2017-12-23 03:30 | 51543.3833 | 39.996
Devonshire Building | 2017-12-23 03:45 | 51543.7733 | 1559.988
Devonshire Building | 2017-12-23 04:00 | 51543.7833 | 39.996
Devonshire Building | 2017-12-23 04:15 | 51543.7933 | 39.996
Devonshire Building | 2017-12-23 04:30 | 51543.8033 | 39.996
Devonshire Building | 2017-12-23 04:45 | 51543.8133 | 39.996
Devonshire Building | 2017-12-23 05:00 | 51543.8233 | 39.996
Devonshire Building | 2017-12-23 05:15 | 51543.8333 | 39.996
Devonshire Building | 2017-12-23 05:30 | 51543.8433 | 39.996
Devonshire Building | 2017-12-23 05:45 | 51543.8533 | 39.996
Devonshire Building | 2017-12-23 06:00 | 51543.8583 | 20.016
Devonshire Building | 2017-12-23 06:15 | 51543.8683 | 39.996
Devonshire Building | 2017-12-23 06:30 | 51543.8783 | 39.996
Devonshire Building | 2017-12-23 06:45 | 51543.8883 | 39.996
Devonshire Building | 2017-12-23 07:00 | 51543.8983 | 39.996
Devonshire Building | 2017-12-23 07:15 | 51543.9083 | 39.996
Devonshire Building | 2017-12-23 07:30 | 51543.9183 | 39.996
Devonshire Building | 2017-12-23 07:45 | 51543.9383 | 79.992
Devonshire Building | 2017-12-23 08:00 | 51543.9633 | 100.008
Devonshire Building | 2017-12-23 08:15 | 51543.9883 | 100.008
Devonshire Building | 2017-12-23 08:30 | 51544.0133 | 100.008
Devonshire Building | 2017-12-23 08:45 | 51544.0433 | 119.988
Devonshire Building | 2017-12-23 09:00 | 51544.0683 | 100.008
Devonshire Building | 2017-12-23 09:15 | 51544.0933 | 100.008
Devonshire Building | 2017-12-23 09:30 | 51544.1183 | 100.008
Devonshire Building | 2017-12-23 09:45 | 51544.1433 | 100.008
Devonshire Building | 2017-12-23 10:00 | 51544.1683 | 100.008
Devonshire Building | 2017-12-23 10:15 | 51544.1933 | 100.008
Devonshire Building | 2017-12-23 10:30 | 51544.2183 | 100.008
Devonshire Building | 2017-12-23 10:45 | 51544.2433 | 100.008
Devonshire Building | 2017-12-23 11:00 | 51544.2683 | 100.008
Devonshire Building | 2017-12-23 11:15 | 51544.2783 | 39.996
Devonshire Building | 2017-12-23 11:30 | 51544.2883 | 39.996
Devonshire Building | 2017-12-23 11:45 | 51544.3083 | 79.992
Devonshire Building | 2017-12-23 12:00 | 51544.7033 | 1580.004
Devonshire Building | 2017-12-23 12:15 | 51544.7183 | 60.012
Devonshire Building | 2017-12-23 12:30 | 51544.7283 | 39.996
Devonshire Building | 2017-12-23 12:45 | 51544.7383 | 39.996
Devonshire Building | 2017-12-23 13:00 | 51544.7483 | 39.996
Devonshire Building | 2017-12-23 13:15 | 51544.7583 | 39.996
Devonshire Building | 2017-12-23 13:30 | 51544.7733 | 60.012
Devonshire Building | 2017-12-23 13:45 | 51544.7833 | 39.996
Devonshire Building | 2017-12-23 14:00 | 51544.7933 | 39.996
Devonshire Building | 2017-12-23 14:15 | 51544.8033 | 39.996
Devonshire Building | 2017-12-23 14:30 | 51544.8183 | 60.012
Devonshire Building | 2017-12-23 14:45 | 51544.8283 | 39.996
Devonshire Building | 2017-12-23 15:00 | 51544.8433 | 60.012
Devonshire Building | 2017-12-23 15:15 | 51544.8583 | 60.012
Devonshire Building | 2017-12-23 15:30 | 51544.8733 | 60.012
Devonshire Building | 2017-12-23 15:45 | 51544.8883 | 60.012
Devonshire Building | 2017-12-23 16:00 | 51544.8983 | 39.996
Devonshire Building | 2017-12-23 16:15 | 51544.9133 | 60.012
Devonshire Building | 2017-12-23 16:30 | 51544.9283 | 60.012
Devonshire Building | 2017-12-23 16:45 | 51544.9433 | 60.012
Devonshire Building | 2017-12-23 17:00 | 51544.9533 | 39.996
Devonshire Building | 2017-12-23 17:15 | 51544.9683 | 60.012
Devonshire Building | 2017-12-23 17:30 | 51544.9833 | 60.012
Devonshire Building | 2017-12-23 17:45 | 51544.9933 | 39.996
Devonshire Building | 2017-12-23 18:00 | 51545.0083 | 60.012
Devonshire Building | 2017-12-23 18:15 | 51545.0183 | 39.996
Devonshire Building | 2017-12-23 18:30 | 51545.0333 | 60.012
Devonshire Building | 2017-12-23 18:45 | 51545.0433 | 39.996
Devonshire Building | 2017-12-23 19:00 | 51545.0533 | 39.996
Devonshire Building | 2017-12-23 19:15 | 51545.0683 | 60.012
Devonshire Building | 2017-12-23 19:30 | 51545.0783 | 39.996
Devonshire Building | 2017-12-23 19:45 | 51545.0933 | 60.012
Devonshire Building | 2017-12-23 20:00 | 51545.1033 | 39.996
Devonshire Building | 2017-12-23 20:15 | 51545.2383 | 540
Devonshire Building | 2017-12-23 20:30 | 51545.5133 | 1100.016
Devonshire Building | 2017-12-23 20:45 | 51545.5233 | 39.996
Devonshire Building | 2017-12-23 21:00 | 51545.5333 | 39.996
Devonshire Building | 2017-12-23 21:15 | 51545.5433 | 39.996
Devonshire Building | 2017-12-23 21:30 | 51545.5583 | 60.012
Devonshire Building | 2017-12-23 21:45 | 51545.5883 | 119.988
Devonshire Building | 2017-12-23 22:00 | 51545.5983 | 39.996
Devonshire Building | 2017-12-23 22:15 | 51545.6133 | 60.012
Devonshire Building | 2017-12-23 22:30 | 51545.6233 | 39.996
Devonshire Building | 2017-12-23 22:45 | 51545.6333 | 39.996
Devonshire Building | 2017-12-23 23:00 | 51545.6483 | 60.012
Devonshire Building | 2017-12-23 23:15 | 51545.6633 | 60.012
Devonshire Building | 2017-12-23 23:30 | 51545.6783 | 60.012
Devonshire Building | 2017-12-23 23:45 | 51545.6933 | 60.012
Devonshire Building | 2017-12-24 | 51545.7109 | 60.012
Devonshire Building | 2017-12-24 00:15 | 51545.7259 | 60.012
Devonshire Building | 2017-12-24 00:30 | 51545.7409 | 60.012
Devonshire Building | 2017-12-24 00:45 | 51545.7559 | 60.012
Devonshire Building | 2017-12-24 01:00 | 51545.7659 | 39.996
Devonshire Building | 2017-12-24 01:15 | 51545.781 | 60.012
Devonshire Building | 2017-12-24 01:30 | 51545.796 | 60.012
Devonshire Building | 2017-12-24 01:45 | 51545.811 | 60.012
Devonshire Building | 2017-12-24 02:00 | 51545.821 | 39.996
Devonshire Building | 2017-12-24 02:15 | 51545.836 | 60.012
Devonshire Building | 2017-12-24 02:30 | 51545.851 | 60.012
Devonshire Building | 2017-12-24 02:45 | 51545.861 | 39.996
Devonshire Building | 2017-12-24 03:00 | 51545.876 | 60.012
Devonshire Building | 2017-12-24 03:15 | 51545.886 | 39.996
Devonshire Building | 2017-12-24 03:30 | 51545.901 | 60.012
Devonshire Building | 2017-12-24 03:45 | 51545.911 | 39.996
Devonshire Building | 2017-12-24 04:00 | 51545.921 | 39.996
Devonshire Building | 2017-12-24 04:15 | 51545.936 | 60.012
Devonshire Building | 2017-12-24 04:30 | 51545.946 | 39.996
Devonshire Building | 2017-12-24 04:45 | 51545.956 | 39.996
Devonshire Building | 2017-12-24 05:00 | 51545.971 | 60.012
Devonshire Building | 2017-12-24 05:15 | 51546.361 | 1559.988
Devonshire Building | 2017-12-24 05:30 | 51546.371 | 39.996
Devonshire Building | 2017-12-24 05:45 | 51546.381 | 39.996
Devonshire Building | 2017-12-24 06:00 | 51546.391 | 39.996
Devonshire Building | 2017-12-24 06:15 | 51546.401 | 39.996
Devonshire Building | 2017-12-24 06:30 | 51546.411 | 39.996
Devonshire Building | 2017-12-24 06:45 | 51546.421 | 39.996
Devonshire Building | 2017-12-24 07:00 | 51546.431 | 39.996
Devonshire Building | 2017-12-24 07:15 | 51546.441 | 39.996
Devonshire Building | 2017-12-24 07:30 | 51546.456 | 60.012
Devonshire Building | 2017-12-24 07:45 | 51546.481 | 100.008
Devonshire Building | 2017-12-24 08:00 | 51546.506 | 100.008
Devonshire Building | 2017-12-24 08:15 | 51546.531 | 100.008
Devonshire Building | 2017-12-24 08:30 | 51546.556 | 100.008
Devonshire Building | 2017-12-24 08:45 | 51546.586 | 119.988
Devonshire Building | 2017-12-24 09:00 | 51546.611 | 100.008
Devonshire Building | 2017-12-24 09:15 | 51546.636 | 100.008
Devonshire Building | 2017-12-24 09:30 | 51546.666 | 119.988
Devonshire Building | 2017-12-24 09:45 | 51546.691 | 100.008
Devonshire Building | 2017-12-24 10:00 | 51546.721 | 119.988
Devonshire Building | 2017-12-24 10:15 | 51546.746 | 100.008
Devonshire Building | 2017-12-24 10:30 | 51546.771 | 100.008
Devonshire Building | 2017-12-24 10:45 | 51546.801 | 119.988
Devonshire Building | 2017-12-24 11:00 | 51546.826 | 100.008
Devonshire Building | 2017-12-24 11:15 | 51546.851 | 100.008
Devonshire Building | 2017-12-24 11:30 | 51546.871 | 79.992
Devonshire Building | 2017-12-24 11:45 | 51546.881 | 39.996
Devonshire Building | 2017-12-24 12:00 | 51546.891 | 39.996
Devonshire Building | 2017-12-24 12:15 | 51546.906 | 60.012
Devonshire Building | 2017-12-24 12:30 | 51546.916 | 39.996
Devonshire Building | 2017-12-24 12:45 | 51546.926 | 39.996
Devonshire Building | 2017-12-24 13:00 | 51546.936 | 39.996
Devonshire Building | 2017-12-24 13:15 | 51546.951 | 60.012
Devonshire Building | 2017-12-24 13:30 | 51547.351 | 1599.984
Devonshire Building | 2017-12-24 13:45 | 51547.361 | 39.996
Devonshire Building | 2017-12-24 14:00 | 51547.371 | 39.996
Devonshire Building | 2017-12-24 14:15 | 51547.381 | 39.996
Devonshire Building | 2017-12-24 14:30 | 51547.391 | 39.996
Devonshire Building | 2017-12-24 14:45 | 51547.401 | 39.996
Devonshire Building | 2017-12-24 15:00 | 51547.411 | 39.996
Devonshire Building | 2017-12-24 15:15 | 51547.421 | 39.996
Devonshire Building | 2017-12-24 15:30 | 51547.431 | 39.996
Devonshire Building | 2017-12-24 15:45 | 51547.441 | 39.996
Devonshire Building | 2017-12-24 16:00 | 51547.451 | 39.996
Devonshire Building | 2017-12-24 16:15 | 51547.461 | 39.996
Devonshire Building | 2017-12-24 16:30 | 51547.471 | 39.996
Devonshire Building | 2017-12-24 16:45 | 51547.481 | 39.996
Devonshire Building | 2017-12-24 17:00 | 51547.491 | 39.996
Devonshire Building | 2017-12-24 17:15 | 51547.506 | 60.012
Devonshire Building | 2017-12-24 17:30 | 51547.516 | 39.996
Devonshire Building | 2017-12-24 17:45 | 51547.526 | 39.996
Devonshire Building | 2017-12-24 18:00 | 51547.541 | 60.012
Devonshire Building | 2017-12-24 18:15 | 51547.551 | 39.996
Devonshire Building | 2017-12-24 18:30 | 51547.566 | 60.012
Devonshire Building | 2017-12-24 18:45 | 51547.576 | 39.996
Devonshire Building | 2017-12-24 19:00 | 51547.586 | 39.996
Devonshire Building | 2017-12-24 19:15 | 51547.596 | 39.996
Devonshire Building | 2017-12-24 19:30 | 51547.611 | 60.012
Devonshire Building | 2017-12-24 19:45 | 51547.621 | 39.996
Devonshire Building | 2017-12-24 20:00 | 51547.631 | 39.996
Devonshire Building | 2017-12-24 20:15 | 51547.641 | 39.996
Devonshire Building | 2017-12-24 20:30 | 51547.651 | 39.996
Devonshire Building | 2017-12-24 20:45 | 51547.661 | 39.996
Devonshire Building | 2017-12-24 21:00 | 51547.671 | 39.996
Devonshire Building | 2017-12-24 21:15 | 51547.686 | 60.012
Devonshire Building | 2017-12-24 21:30 | 51547.696 | 39.996
Devonshire Building | 2017-12-24 21:45 | 51548.086 | 1559.988
Devonshire Building | 2017-12-24 22:00 | 51548.0959 | 39.996
Devonshire Building | 2017-12-24 22:15 | 51548.1059 | 39.996
Devonshire Building | 2017-12-24 22:30 | 51548.1159 | 39.996
Devonshire Building | 2017-12-24 22:45 | 51548.1259 | 39.996
Devonshire Building | 2017-12-24 23:00 | 51548.1359 | 39.996
Devonshire Building | 2017-12-24 23:15 | 51548.1459 | 39.996
Devonshire Building | 2017-12-24 23:30 | 51548.1559 | 39.996
Devonshire Building | 2017-12-24 23:45 | 51548.1659 | 39.996
Devonshire Building | 2017-12-25 | 51548.1758 | 39.996
Devonshire Building | 2017-12-25 00:15 | 51548.1908 | 60.012
Devonshire Building | 2017-12-25 00:30 | 51548.2008 | 39.996
Devonshire Building | 2017-12-25 00:45 | 51548.2108 | 39.996
Devonshire Building | 2017-12-25 01:00 | 51548.2208 | 39.996
Devonshire Building | 2017-12-25 01:15 | 51548.2358 | 60.012
Devonshire Building | 2017-12-25 01:30 | 51548.2458 | 39.996
Devonshire Building | 2017-12-25 01:45 | 51548.2608 | 60.012
Devonshire Building | 2017-12-25 02:00 | 51548.2708 | 39.996
Devonshire Building | 2017-12-25 02:15 | 51548.2808 | 39.996
Devonshire Building | 2017-12-25 02:30 | 51548.2958 | 60.012
Devonshire Building | 2017-12-25 02:45 | 51548.3058 | 39.996
Devonshire Building | 2017-12-25 03:00 | 51548.3158 | 39.996
Devonshire Building | 2017-12-25 03:15 | 51548.3308 | 60.012
Devonshire Building | 2017-12-25 03:30 | 51548.3408 | 39.996
Devonshire Building | 2017-12-25 03:45 | 51548.3508 | 39.996
Devonshire Building | 2017-12-25 04:00 | 51548.3608 | 39.996
Devonshire Building | 2017-12-25 04:15 | 51548.3758 | 60.012
Devonshire Building | 2017-12-25 04:30 | 51548.3858 | 39.996
Devonshire Building | 2017-12-25 04:45 | 51548.3958 | 39.996
Devonshire Building | 2017-12-25 05:00 | 51548.4058 | 39.996
Devonshire Building | 2017-12-25 05:15 | 51548.4158 | 39.996
Devonshire Building | 2017-12-25 05:30 | 51548.4258 | 39.996
Devonshire Building | 2017-12-25 05:45 | 51548.4358 | 39.996
Devonshire Building | 2017-12-25 06:00 | 51548.7808 | 1379.988
Devonshire Building | 2017-12-25 06:15 | 51548.8458 | 259.992
Devonshire Building | 2017-12-25 06:30 | 51548.8558 | 39.996
Devonshire Building | 2017-12-25 06:45 | 51548.8658 | 39.996
Devonshire Building | 2017-12-25 07:00 | 51548.8758 | 39.996
Devonshire Building | 2017-12-25 07:15 | 51548.8858 | 39.996
Devonshire Building | 2017-12-25 07:30 | 51548.8958 | 39.996
Devonshire Building | 2017-12-25 07:45 | 51548.9158 | 79.992
Devonshire Building | 2017-12-25 08:00 | 51548.9408 | 100.008
Devonshire Building | 2017-12-25 08:15 | 51548.9658 | 100.008
Devonshire Building | 2017-12-25 08:30 | 51548.9908 | 100.008
Devonshire Building | 2017-12-25 08:45 | 51549.0108 | 79.992
Devonshire Building | 2017-12-25 09:00 | 51549.0358 | 100.008
Devonshire Building | 2017-12-25 09:15 | 51549.0608 | 100.008
Devonshire Building | 2017-12-25 09:30 | 51549.0858 | 100.008
Devonshire Building | 2017-12-25 09:45 | 51549.1158 | 119.988
Devonshire Building | 2017-12-25 10:00 | 51549.1408 | 100.008
Devonshire Building | 2017-12-25 10:15 | 51549.1658 | 100.008
Devonshire Building | 2017-12-25 10:30 | 51549.1908 | 100.008
Devonshire Building | 2017-12-25 10:45 | 51549.2158 | 100.008
Devonshire Building | 2017-12-25 11:00 | 51549.2458 | 119.988
Devonshire Building | 2017-12-25 11:15 | 51549.2658 | 79.992
Devonshire Building | 2017-12-25 11:30 | 51549.2758 | 39.996
Devonshire Building | 2017-12-25 11:45 | 51549.2858 | 39.996
Devonshire Building | 2017-12-25 12:00 | 51549.3008 | 60.012
Devonshire Building | 2017-12-25 12:15 | 51549.3108 | 39.996
Devonshire Building | 2017-12-25 12:30 | 51549.3208 | 39.996
Devonshire Building | 2017-12-25 12:45 | 51549.3308 | 39.996
Devonshire Building | 2017-12-25 13:00 | 51549.3408 | 39.996
Devonshire Building | 2017-12-25 13:15 | 51549.3508 | 39.996
Devonshire Building | 2017-12-25 13:30 | 51549.3608 | 39.996
Devonshire Building | 2017-12-25 13:45 | 51549.3708 | 39.996
Devonshire Building | 2017-12-25 14:00 | 51549.3858 | 60.012
Devonshire Building | 2017-12-25 14:15 | 51549.3958 | 39.996
Devonshire Building | 2017-12-25 14:30 | 51549.4058 | 39.996
Devonshire Building | 2017-12-25 14:45 | 51549.7908 | 1540.008
Devonshire Building | 2017-12-25 15:00 | 51549.8008 | 39.996
Devonshire Building | 2017-12-25 15:15 | 51549.8108 | 39.996
Devonshire Building | 2017-12-25 15:30 | 51549.8208 | 39.996
Devonshire Building | 2017-12-25 15:45 | 51549.8308 | 39.996
Devonshire Building | 2017-12-25 16:00 | 51549.8408 | 39.996
Devonshire Building | 2017-12-25 16:15 | 51549.8508 | 39.996
Devonshire Building | 2017-12-25 16:30 | 51549.8558 | 20.016
Devonshire Building | 2017-12-25 16:45 | 51549.8708 | 60.012
Devonshire Building | 2017-12-25 17:00 | 51549.8808 | 39.996
Devonshire Building | 2017-12-25 17:15 | 51549.8858 | 20.016
Devonshire Building | 2017-12-25 17:30 | 51549.8958 | 39.996
Devonshire Building | 2017-12-25 17:45 | 51549.9058 | 39.996
Devonshire Building | 2017-12-25 18:00 | 51549.9158 | 39.996
Devonshire Building | 2017-12-25 18:15 | 51549.9258 | 39.996
Devonshire Building | 2017-12-25 18:30 | 51549.9358 | 39.996
Devonshire Building | 2017-12-25 18:45 | 51549.9458 | 39.996
Devonshire Building | 2017-12-25 19:00 | 51549.9608 | 60.012
Devonshire Building | 2017-12-25 19:15 | 51549.9708 | 39.996
Devonshire Building | 2017-12-25 19:30 | 51549.9808 | 39.996
Devonshire Building | 2017-12-25 19:45 | 51549.9908 | 39.996
Devonshire Building | 2017-12-25 20:00 | 51550.0008 | 39.996
Devonshire Building | 2017-12-25 20:15 | 51550.0108 | 39.996
Devonshire Building | 2017-12-25 20:30 | 51550.0258 | 60.012
Devonshire Building | 2017-12-25 20:45 | 51550.0358 | 39.996
Devonshire Building | 2017-12-25 21:00 | 51550.0458 | 39.996
Devonshire Building | 2017-12-25 21:15 | 51550.0558 | 39.996
Devonshire Building | 2017-12-25 21:30 | 51550.0658 | 39.996
Devonshire Building | 2017-12-25 21:45 | 51550.0958 | 119.988
Devonshire Building | 2017-12-25 22:00 | 51550.1058 | 39.996
Devonshire Building | 2017-12-25 22:15 | 51550.1158 | 39.996
Devonshire Building | 2017-12-25 22:30 | 51550.1258 | 39.996
Devonshire Building | 2017-12-25 22:45 | 51550.1358 | 39.996
Devonshire Building | 2017-12-25 23:00 | 51550.1458 | 39.996
Devonshire Building | 2017-12-25 23:15 | 51550.5458 | 1599.984
Devonshire Building | 2017-12-25 23:30 | 51550.5558 | 39.996
Devonshire Building | 2017-12-25 23:45 | 51550.5658 | 39.996
Devonshire Building | 2017-12-26 | 51550.5742 | 39.996
Devonshire Building | 2017-12-26 00:15 | 51550.5842 | 39.996
Devonshire Building | 2017-12-26 00:30 | 51550.5942 | 39.996
Devonshire Building | 2017-12-26 00:45 | 51550.5992 | 20.016
Devonshire Building | 2017-12-26 01:00 | 51550.6092 | 39.996
Devonshire Building | 2017-12-26 01:15 | 51550.6192 | 39.996
Devonshire Building | 2017-12-26 01:30 | 51550.6292 | 39.996
Devonshire Building | 2017-12-26 01:45 | 51550.6392 | 39.996
Devonshire Building | 2017-12-26 02:00 | 51550.6442 | 20.016
Devonshire Building | 2017-12-26 02:15 | 51550.6542 | 39.996
Devonshire Building | 2017-12-26 02:30 | 51550.6642 | 39.996
Devonshire Building | 2017-12-26 02:45 | 51550.6742 | 39.996
Devonshire Building | 2017-12-26 03:00 | 51550.6842 | 39.996
Devonshire Building | 2017-12-26 03:15 | 51550.6942 | 39.996
Devonshire Building | 2017-12-26 03:30 | 51550.7042 | 39.996
Devonshire Building | 2017-12-26 03:45 | 51550.7142 | 39.996
Devonshire Building | 2017-12-26 04:00 | 51550.7242 | 39.996
Devonshire Building | 2017-12-26 04:15 | 51550.7342 | 39.996
Devonshire Building | 2017-12-26 04:30 | 51550.7442 | 39.996
Devonshire Building | 2017-12-26 04:45 | 51550.7542 | 39.996
Devonshire Building | 2017-12-26 05:00 | 51550.7642 | 39.996
Devonshire Building | 2017-12-26 05:15 | 51550.7792 | 60.012
Devonshire Building | 2017-12-26 05:30 | 51550.7892 | 39.996
Devonshire Building | 2017-12-26 05:45 | 51550.7992 | 39.996
Devonshire Building | 2017-12-26 06:00 | 51550.8092 | 39.996
Devonshire Building | 2017-12-26 06:15 | 51550.8142 | 20.016
Devonshire Building | 2017-12-26 06:30 | 51550.8242 | 39.996
Devonshire Building | 2017-12-26 06:45 | 51550.8342 | 39.996
Devonshire Building | 2017-12-26 07:00 | 51550.8442 | 39.996
Devonshire Building | 2017-12-26 07:15 | 51550.8542 | 39.996
Devonshire Building | 2017-12-26 07:30 | 51550.8642 | 39.996
Devonshire Building | 2017-12-26 07:45 | 51551.2642 | 1599.984
Devonshire Building | 2017-12-26 08:00 | 51551.2892 | 100.008
Devonshire Building | 2017-12-26 08:15 | 51551.3142 | 100.008
Devonshire Building | 2017-12-26 08:30 | 51551.3342 | 79.992
Devonshire Building | 2017-12-26 08:45 | 51551.3592 | 100.008
Devonshire Building | 2017-12-26 09:00 | 51551.3792 | 79.992
Devonshire Building | 2017-12-26 09:15 | 51551.4042 | 100.008
Devonshire Building | 2017-12-26 09:30 | 51551.4292 | 100.008
Devonshire Building | 2017-12-26 09:45 | 51551.4492 | 79.992
Devonshire Building | 2017-12-26 10:00 | 51551.4742 | 100.008
Devonshire Building | 2017-12-26 10:15 | 51551.4942 | 79.992
Devonshire Building | 2017-12-26 10:30 | 51551.5192 | 100.008
Devonshire Building | 2017-12-26 10:45 | 51551.5392 | 79.992
Devonshire Building | 2017-12-26 11:00 | 51551.5642 | 100.008
Devonshire Building | 2017-12-26 11:15 | 51551.5792 | 60.012
Devonshire Building | 2017-12-26 11:30 | 51551.5892 | 39.996
Devonshire Building | 2017-12-26 11:45 | 51551.5992 | 39.996
Devonshire Building | 2017-12-26 12:00 | 51551.6042 | 20.016
Devonshire Building | 2017-12-26 12:15 | 51551.6142 | 39.996
Devonshire Building | 2017-12-26 12:30 | 51551.6242 | 39.996
Devonshire Building | 2017-12-26 12:45 | 51551.6292 | 20.016
Devonshire Building | 2017-12-26 13:00 | 51551.6392 | 39.996
Devonshire Building | 2017-12-26 13:15 | 51551.6492 | 39.996
Devonshire Building | 2017-12-26 13:30 | 51551.6592 | 39.996
Devonshire Building | 2017-12-26 13:45 | 51551.6692 | 39.996
Devonshire Building | 2017-12-26 14:00 | 51551.6792 | 39.996
Devonshire Building | 2017-12-26 14:15 | 51551.6842 | 20.016
Devonshire Building | 2017-12-26 14:30 | 51551.6942 | 39.996
Devonshire Building | 2017-12-26 14:45 | 51551.7042 | 39.996
Devonshire Building | 2017-12-26 15:00 | 51551.7142 | 39.996
Devonshire Building | 2017-12-26 15:15 | 51551.7242 | 39.996
Devonshire Building | 2017-12-26 15:30 | 51551.7342 | 39.996
Devonshire Building | 2017-12-26 15:45 | 51551.7392 | 20.016
Devonshire Building | 2017-12-26 16:00 | 51552.1392 | 1599.984
Devonshire Building | 2017-12-26 16:15 | 51552.1492 | 39.996
Devonshire Building | 2017-12-26 16:30 | 51552.1592 | 39.996
Devonshire Building | 2017-12-26 16:45 | 51552.1642 | 20.016
Devonshire Building | 2017-12-26 17:00 | 51552.1742 | 39.996
Devonshire Building | 2017-12-26 17:15 | 51552.1842 | 39.996
Devonshire Building | 2017-12-26 17:30 | 51552.1892 | 20.016
Devonshire Building | 2017-12-26 17:45 | 51552.1992 | 39.996
Devonshire Building | 2017-12-26 18:00 | 51552.2092 | 39.996
Devonshire Building | 2017-12-26 18:15 | 51552.2142 | 20.016
Devonshire Building | 2017-12-26 18:30 | 51552.2242 | 39.996
Devonshire Building | 2017-12-26 18:45 | 51552.2292 | 20.016
Devonshire Building | 2017-12-26 19:00 | 51552.2392 | 39.996
Devonshire Building | 2017-12-26 19:15 | 51552.2442 | 20.016
Devonshire Building | 2017-12-26 19:30 | 51552.2542 | 39.996
Devonshire Building | 2017-12-26 19:45 | 51552.2642 | 39.996
Devonshire Building | 2017-12-26 20:00 | 51552.2692 | 20.016
Devonshire Building | 2017-12-26 20:15 | 51552.2792 | 39.996
Devonshire Building | 2017-12-26 20:30 | 51552.2892 | 39.996
Devonshire Building | 2017-12-26 20:45 | 51552.2942 | 20.016
Devonshire Building | 2017-12-26 21:00 | 51552.3042 | 39.996
Devonshire Building | 2017-12-26 21:15 | 51552.3142 | 39.996
Devonshire Building | 2017-12-26 21:30 | 51552.3192 | 20.016
Devonshire Building | 2017-12-26 21:45 | 51552.3542 | 140.004
Devonshire Building | 2017-12-26 22:00 | 51552.3592 | 20.016
Devonshire Building | 2017-12-26 22:15 | 51552.3692 | 39.996
Devonshire Building | 2017-12-26 22:30 | 51552.3792 | 39.996
Devonshire Building | 2017-12-26 22:45 | 51552.3892 | 39.996
Devonshire Building | 2017-12-26 23:00 | 51552.3942 | 20.016
Devonshire Building | 2017-12-26 23:15 | 51552.4042 | 39.996
Devonshire Building | 2017-12-26 23:30 | 51552.4142 | 39.996
Devonshire Building | 2017-12-26 23:45 | 51552.4242 | 39.996
Devonshire Building | 2017-12-27 | 51552.4297 | 20.016
Devonshire Building | 2017-12-27 00:15 | 51552.4397 | 39.996
Devonshire Building | 2017-12-27 00:30 | 51552.8347 | 1580.004
Devonshire Building | 2017-12-27 00:45 | 51552.8397 | 20.016
Devonshire Building | 2017-12-27 01:00 | 51552.8497 | 39.996
Devonshire Building | 2017-12-27 01:15 | 51552.8597 | 39.996
Devonshire Building | 2017-12-27 01:30 | 51552.8647 | 20.016
Devonshire Building | 2017-12-27 01:45 | 51552.8747 | 39.996
Devonshire Building | 2017-12-27 02:00 | 51552.8797 | 20.016
Devonshire Building | 2017-12-27 02:15 | 51552.8897 | 39.996
Devonshire Building | 2017-12-27 02:30 | 51552.8997 | 39.996
Devonshire Building | 2017-12-27 02:45 | 51552.9047 | 20.016
Devonshire Building | 2017-12-27 03:00 | 51552.9147 | 39.996
Devonshire Building | 2017-12-27 03:15 | 51552.9197 | 20.016
Devonshire Building | 2017-12-27 03:30 | 51552.9297 | 39.996
Devonshire Building | 2017-12-27 03:45 | 51552.9397 | 39.996
Devonshire Building | 2017-12-27 04:00 | 51552.9447 | 20.016
Devonshire Building | 2017-12-27 04:15 | 51552.9547 | 39.996
Devonshire Building | 2017-12-27 04:30 | 51552.9597 | 20.016
Devonshire Building | 2017-12-27 04:45 | 51552.9697 | 39.996
Devonshire Building | 2017-12-27 05:00 | 51552.9797 | 39.996
Devonshire Building | 2017-12-27 05:15 | 51552.9847 | 20.016
Devonshire Building | 2017-12-27 05:30 | 51552.9947 | 39.996
Devonshire Building | 2017-12-27 05:45 | 51553.0047 | 39.996
Devonshire Building | 2017-12-27 06:00 | 51553.0097 | 20.016
Devonshire Building | 2017-12-27 06:15 | 51553.0197 | 39.996
Devonshire Building | 2017-12-27 06:30 | 51553.0297 | 39.996
Devonshire Building | 2017-12-27 06:45 | 51553.0397 | 39.996
Devonshire Building | 2017-12-27 07:00 | 51553.0447 | 20.016
Devonshire Building | 2017-12-27 07:15 | 51553.0547 | 39.996
Devonshire Building | 2017-12-27 07:30 | 51553.0647 | 39.996
Devonshire Building | 2017-12-27 07:45 | 51553.0797 | 60.012
Devonshire Building | 2017-12-27 08:00 | 51553.1047 | 100.008
Devonshire Building | 2017-12-27 08:15 | 51553.1297 | 100.008
Devonshire Building | 2017-12-27 08:30 | 51553.1497 | 79.992
Devonshire Building | 2017-12-27 08:45 | 51553.5597 | 1640.016
Devonshire Building | 2017-12-27 09:00 | 51553.5847 | 100.008
Devonshire Building | 2017-12-27 09:15 | 51553.6047 | 79.992
Devonshire Building | 2017-12-27 09:30 | 51553.6297 | 100.008
Devonshire Building | 2017-12-27 09:45 | 51553.6497 | 79.992
Devonshire Building | 2017-12-27 10:00 | 51553.6747 | 100.008
Devonshire Building | 2017-12-27 10:15 | 51553.6947 | 79.992
Devonshire Building | 2017-12-27 10:30 | 51553.7197 | 100.008
Devonshire Building | 2017-12-27 10:45 | 51553.7397 | 79.992
Devonshire Building | 2017-12-27 11:00 | 51553.7647 | 100.008
Devonshire Building | 2017-12-27 11:15 | 51553.7847 | 79.992
Devonshire Building | 2017-12-27 11:30 | 51553.8047 | 79.992
Devonshire Building | 2017-12-27 11:45 | 51553.8297 | 100.008
Devonshire Building | 2017-12-27 12:00 | 51553.8547 | 100.008
Devonshire Building | 2017-12-27 12:15 | 51553.8797 | 100.008
Devonshire Building | 2017-12-27 12:30 | 51553.8997 | 79.992
Devonshire Building | 2017-12-27 12:45 | 51553.9247 | 100.008
Devonshire Building | 2017-12-27 13:00 | 51553.9497 | 100.008
Devonshire Building | 2017-12-27 13:15 | 51553.9697 | 79.992
Devonshire Building | 2017-12-27 13:30 | 51553.9947 | 100.008
Devonshire Building | 2017-12-27 13:45 | 51554.0147 | 79.992
Devonshire Building | 2017-12-27 14:00 | 51554.0397 | 100.008
Devonshire Building | 2017-12-27 14:15 | 51554.0597 | 79.992
Devonshire Building | 2017-12-27 14:30 | 51554.0847 | 100.008
Devonshire Building | 2017-12-27 14:45 | 51554.0997 | 60.012
Devonshire Building | 2017-12-27 15:00 | 51554.1097 | 39.996
Devonshire Building | 2017-12-27 15:15 | 51554.1197 | 39.996
Devonshire Building | 2017-12-27 15:30 | 51554.1247 | 20.016
Devonshire Building | 2017-12-27 15:45 | 51554.1347 | 39.996
Devonshire Building | 2017-12-27 16:00 | 51554.1447 | 39.996
Devonshire Building | 2017-12-27 16:15 | 51554.1547 | 39.996
Devonshire Building | 2017-12-27 16:30 | 51554.5547 | 1599.984
Devonshire Building | 2017-12-27 16:45 | 51554.5647 | 39.996
Devonshire Building | 2017-12-27 17:00 | 51554.5697 | 20.016
Devonshire Building | 2017-12-27 17:15 | 51554.5797 | 39.996
Devonshire Building | 2017-12-27 17:30 | 51554.5897 | 39.996
Devonshire Building | 2017-12-27 17:45 | 51554.5947 | 20.016
Devonshire Building | 2017-12-27 18:00 | 51554.6047 | 39.996
Devonshire Building | 2017-12-27 18:15 | 51554.6097 | 20.016
Devonshire Building | 2017-12-27 18:30 | 51554.6197 | 39.996
Devonshire Building | 2017-12-27 18:45 | 51554.6297 | 39.996
Devonshire Building | 2017-12-27 19:00 | 51554.6347 | 20.016
Devonshire Building | 2017-12-27 19:15 | 51554.6447 | 39.996
Devonshire Building | 2017-12-27 19:30 | 51554.6497 | 20.016
Devonshire Building | 2017-12-27 19:45 | 51554.6597 | 39.996
Devonshire Building | 2017-12-27 20:00 | 51554.6647 | 20.016
Devonshire Building | 2017-12-27 20:15 | 51554.6747 | 39.996
Devonshire Building | 2017-12-27 20:30 | 51554.6797 | 20.016
Devonshire Building | 2017-12-27 20:45 | 51554.6897 | 39.996
Devonshire Building | 2017-12-27 21:00 | 51554.6997 | 39.996
Devonshire Building | 2017-12-27 21:15 | 51554.7047 | 20.016
Devonshire Building | 2017-12-27 21:30 | 51554.7147 | 39.996
Devonshire Building | 2017-12-27 21:45 | 51554.7447 | 119.988
Devonshire Building | 2017-12-27 22:00 | 51554.7547 | 39.996
Devonshire Building | 2017-12-27 22:15 | 51554.7597 | 20.016
Devonshire Building | 2017-12-27 22:30 | 51554.7697 | 39.996
Devonshire Building | 2017-12-27 22:45 | 51554.7797 | 39.996
Devonshire Building | 2017-12-27 23:00 | 51554.7847 | 20.016
Devonshire Building | 2017-12-27 23:15 | 51554.7947 | 39.996
Devonshire Building | 2017-12-27 23:30 | 51554.8047 | 39.996
Devonshire Building | 2017-12-27 23:45 | 51554.8097 | 20.016
Devonshire Building | 2017-12-28 | 51554.8203 | 39.996
Devonshire Building | 2017-12-28 00:15 | 51554.8303 | 39.996
Devonshire Building | 2017-12-28 00:30 | 51554.8353 | 20.016
Devonshire Building | 2017-12-28 00:45 | 51554.8453 | 39.996
Devonshire Building | 2017-12-28 01:00 | 51554.8553 | 39.996
Devonshire Building | 2017-12-28 01:15 | 51555.2453 | 1559.988
Devonshire Building | 2017-12-28 01:30 | 51555.2553 | 39.996
Devonshire Building | 2017-12-28 01:45 | 51555.2603 | 20.016
Devonshire Building | 2017-12-28 02:00 | 51555.2703 | 39.996
Devonshire Building | 2017-12-28 02:15 | 51555.2753 | 20.016
Devonshire Building | 2017-12-28 02:30 | 51555.2853 | 39.996
Devonshire Building | 2017-12-28 02:45 | 51555.2903 | 20.016
Devonshire Building | 2017-12-28 03:00 | 51555.3003 | 39.996
Devonshire Building | 2017-12-28 03:15 | 51555.3103 | 39.996
Devonshire Building | 2017-12-28 03:30 | 51555.3153 | 20.016
Devonshire Building | 2017-12-28 03:45 | 51555.3253 | 39.996
Devonshire Building | 2017-12-28 04:00 | 51555.3303 | 20.016
Devonshire Building | 2017-12-28 04:15 | 51555.3403 | 39.996
Devonshire Building | 2017-12-28 04:30 | 51555.3453 | 20.016
Devonshire Building | 2017-12-28 04:45 | 51555.3553 | 39.996
Devonshire Building | 2017-12-28 05:00 | 51555.3653 | 39.996
Devonshire Building | 2017-12-28 05:15 | 51555.3703 | 20.016
Devonshire Building | 2017-12-28 05:30 | 51555.3803 | 39.996
Devonshire Building | 2017-12-28 05:45 | 51555.3853 | 20.016
Devonshire Building | 2017-12-28 06:00 | 51555.3953 | 39.996
Devonshire Building | 2017-12-28 06:15 | 51555.4003 | 20.016
Devonshire Building | 2017-12-28 06:30 | 51555.4103 | 39.996
Devonshire Building | 2017-12-28 06:45 | 51555.4203 | 39.996
Devonshire Building | 2017-12-28 07:00 | 51555.4253 | 20.016
Devonshire Building | 2017-12-28 07:15 | 51555.4353 | 39.996
Devonshire Building | 2017-12-28 07:30 | 51555.4403 | 20.016
Devonshire Building | 2017-12-28 07:45 | 51555.4503 | 39.996
Devonshire Building | 2017-12-28 08:00 | 51555.4653 | 60.012
Devonshire Building | 2017-12-28 08:15 | 51555.4903 | 100.008
Devonshire Building | 2017-12-28 08:30 | 51555.5103 | 79.992
Devonshire Building | 2017-12-28 08:45 | 51555.5353 | 100.008
Devonshire Building | 2017-12-28 09:00 | 51555.5553 | 79.992
Devonshire Building | 2017-12-28 09:15 | 51555.5803 | 100.008
Devonshire Building | 2017-12-28 09:30 | 51555.6053 | 100.008
Devonshire Building | 2017-12-28 09:45 | 51555.6253 | 79.992
Devonshire Building | 2017-12-28 10:00 | 51556.0403 | 1659.996
Devonshire Building | 2017-12-28 10:15 | 51556.0603 | 79.992
Devonshire Building | 2017-12-28 10:30 | 51556.0853 | 100.008
Devonshire Building | 2017-12-28 10:45 | 51556.1003 | 60.012
Devonshire Building | 2017-12-28 11:00 | 51556.1053 | 20.016
Devonshire Building | 2017-12-28 11:15 | 51556.1153 | 39.996
Devonshire Building | 2017-12-28 11:30 | 51556.1253 | 39.996
Devonshire Building | 2017-12-28 11:45 | 51556.1303 | 20.016
Devonshire Building | 2017-12-28 12:00 | 51556.1403 | 39.996
Devonshire Building | 2017-12-28 12:15 | 51556.1454 | 20.016
Devonshire Building | 2017-12-28 12:30 | 51556.1554 | 39.996
Devonshire Building | 2017-12-28 12:45 | 51556.1604 | 20.016
Devonshire Building | 2017-12-28 13:00 | 51556.1704 | 39.996
Devonshire Building | 2017-12-28 13:15 | 51556.1804 | 39.996
Devonshire Building | 2017-12-28 13:30 | 51556.1854 | 20.016
Devonshire Building | 2017-12-28 13:45 | 51556.1954 | 39.996
Devonshire Building | 2017-12-28 14:00 | 51556.2004 | 20.016
Devonshire Building | 2017-12-28 14:15 | 51556.2104 | 39.996
Devonshire Building | 2017-12-28 14:30 | 51556.2204 | 39.996
Devonshire Building | 2017-12-28 14:45 | 51556.2254 | 20.016
Devonshire Building | 2017-12-28 15:00 | 51556.2354 | 39.996
Devonshire Building | 2017-12-28 15:15 | 51556.2404 | 20.016
Devonshire Building | 2017-12-28 15:30 | 51556.2504 | 39.996
Devonshire Building | 2017-12-28 15:45 | 51556.2554 | 20.016
Devonshire Building | 2017-12-28 16:00 | 51556.2654 | 39.996
Devonshire Building | 2017-12-28 16:15 | 51556.2704 | 20.016
Devonshire Building | 2017-12-28 16:30 | 51556.2804 | 39.996
Devonshire Building | 2017-12-28 16:45 | 51556.2854 | 20.016
Devonshire Building | 2017-12-28 17:00 | 51556.6904 | 1620
Devonshire Building | 2017-12-28 17:15 | 51556.6954 | 20.016
Devonshire Building | 2017-12-28 17:30 | 51556.7054 | 39.996
Devonshire Building | 2017-12-28 17:45 | 51556.7104 | 20.016
Devonshire Building | 2017-12-28 18:00 | 51556.7204 | 39.996
Devonshire Building | 2017-12-28 18:15 | 51556.7254 | 20.016
Devonshire Building | 2017-12-28 18:30 | 51556.7354 | 39.996
Devonshire Building | 2017-12-28 18:45 | 51556.7404 | 20.016
Devonshire Building | 2017-12-28 19:00 | 51556.7504 | 39.996
Devonshire Building | 2017-12-28 19:15 | 51556.7604 | 39.996
Devonshire Building | 2017-12-28 19:30 | 51556.7654 | 20.016
Devonshire Building | 2017-12-28 19:45 | 51556.7754 | 39.996
Devonshire Building | 2017-12-28 20:00 | 51556.7804 | 20.016
Devonshire Building | 2017-12-28 20:15 | 51556.7904 | 39.996
Devonshire Building | 2017-12-28 20:30 | 51556.7954 | 20.016
Devonshire Building | 2017-12-28 20:45 | 51556.8054 | 39.996
Devonshire Building | 2017-12-28 21:00 | 51556.8104 | 20.016
Devonshire Building | 2017-12-28 21:15 | 51556.8204 | 39.996
Devonshire Building | 2017-12-28 21:30 | 51556.8254 | 20.016
Devonshire Building | 2017-12-28 21:45 | 51556.8554 | 119.988
Devonshire Building | 2017-12-28 22:00 | 51556.8654 | 39.996
Devonshire Building | 2017-12-28 22:15 | 51556.8704 | 20.016
Devonshire Building | 2017-12-28 22:30 | 51556.8804 | 39.996
Devonshire Building | 2017-12-28 22:45 | 51556.8904 | 39.996
Devonshire Building | 2017-12-28 23:00 | 51556.8954 | 20.016
Devonshire Building | 2017-12-28 23:15 | 51556.9054 | 39.996
Devonshire Building | 2017-12-28 23:30 | 51556.9104 | 20.016
Devonshire Building | 2017-12-28 23:45 | 51556.9204 | 39.996
Devonshire Building | 2017-12-29 | 51556.9258 | 20.016
Devonshire Building | 2017-12-29 00:15 | 51556.9358 | 39.996
Devonshire Building | 2017-12-29 00:30 | 51556.9408 | 20.016
Devonshire Building | 2017-12-29 00:45 | 51556.9508 | 39.996
Devonshire Building | 2017-12-29 01:00 | 51556.9608 | 39.996
Devonshire Building | 2017-12-29 01:15 | 51556.9658 | 20.016
Devonshire Building | 2017-12-29 01:30 | 51557.0558 | 360
Devonshire Building | 2017-12-29 01:45 | 51557.3708 | 1260
Devonshire Building | 2017-12-29 02:00 | 51557.3808 | 39.996
Devonshire Building | 2017-12-29 02:15 | 51557.3858 | 20.016
Devonshire Building | 2017-12-29 02:30 | 51557.3958 | 39.996
Devonshire Building | 2017-12-29 02:45 | 51557.4008 | 20.016
Devonshire Building | 2017-12-29 03:00 | 51557.4108 | 39.996
Devonshire Building | 2017-12-29 03:15 | 51557.4158 | 20.016
Devonshire Building | 2017-12-29 03:30 | 51557.4258 | 39.996
Devonshire Building | 2017-12-29 03:45 | 51557.4308 | 20.016
Devonshire Building | 2017-12-29 04:00 | 51557.4408 | 39.996
Devonshire Building | 2017-12-29 04:15 | 51557.4458 | 20.016
Devonshire Building | 2017-12-29 04:30 | 51557.4558 | 39.996
Devonshire Building | 2017-12-29 04:45 | 51557.4608 | 20.016
Devonshire Building | 2017-12-29 05:00 | 51557.4708 | 39.996
Devonshire Building | 2017-12-29 05:15 | 51557.4808 | 39.996
Devonshire Building | 2017-12-29 05:30 | 51557.4858 | 20.016
Devonshire Building | 2017-12-29 05:45 | 51557.4958 | 39.996
Devonshire Building | 2017-12-29 06:00 | 51557.5008 | 20.016
Devonshire Building | 2017-12-29 06:15 | 51557.5108 | 39.996
Devonshire Building | 2017-12-29 06:30 | 51557.5158 | 20.016
Devonshire Building | 2017-12-29 06:45 | 51557.5258 | 39.996
Devonshire Building | 2017-12-29 07:00 | 51557.5308 | 20.016
Devonshire Building | 2017-12-29 07:15 | 51557.5408 | 39.996
Devonshire Building | 2017-12-29 07:30 | 51557.5458 | 20.016
Devonshire Building | 2017-12-29 07:45 | 51557.5608 | 60.012
Devonshire Building | 2017-12-29 08:00 | 51557.5858 | 100.008
Devonshire Building | 2017-12-29 08:15 | 51557.6058 | 79.992
Devonshire Building | 2017-12-29 08:30 | 51557.6308 | 100.008
Devonshire Building | 2017-12-29 08:45 | 51557.6508 | 79.992
Devonshire Building | 2017-12-29 09:00 | 51557.6758 | 100.008
Devonshire Building | 2017-12-29 09:15 | 51557.6958 | 79.992
Devonshire Building | 2017-12-29 09:30 | 51557.7208 | 100.008
Devonshire Building | 2017-12-29 09:45 | 51557.7408 | 79.992
Devonshire Building | 2017-12-29 10:00 | 51557.7658 | 100.008
Devonshire Building | 2017-12-29 10:15 | 51557.7858 | 79.992
Devonshire Building | 2017-12-29 10:30 | 51558.2008 | 1659.996
Devonshire Building | 2017-12-29 10:45 | 51558.2208 | 79.992
Devonshire Building | 2017-12-29 11:00 | 51558.2458 | 100.008
Devonshire Building | 2017-12-29 11:15 | 51558.2558 | 39.996
Devonshire Building | 2017-12-29 11:30 | 51558.2658 | 39.996
Devonshire Building | 2017-12-29 11:45 | 51558.2708 | 20.016
Devonshire Building | 2017-12-29 12:00 | 51558.2808 | 39.996
Devonshire Building | 2017-12-29 12:15 | 51558.2858 | 20.016
Devonshire Building | 2017-12-29 12:30 | 51558.2958 | 39.996
Devonshire Building | 2017-12-29 12:45 | 51558.3008 | 20.016
Devonshire Building | 2017-12-29 13:00 | 51558.3108 | 39.996
Devonshire Building | 2017-12-29 13:15 | 51558.3158 | 20.016
Devonshire Building | 2017-12-29 13:30 | 51558.3308 | 60.012
Devonshire Building | 2017-12-29 13:45 | 51558.3408 | 39.996
Devonshire Building | 2017-12-29 14:00 | 51558.3458 | 20.016
Devonshire Building | 2017-12-29 14:15 | 51558.3508 | 20.016
Devonshire Building | 2017-12-29 14:30 | 51558.3608 | 39.996
Devonshire Building | 2017-12-29 14:45 | 51558.3708 | 39.996
Devonshire Building | 2017-12-29 15:00 | 51558.3758 | 20.016
Devonshire Building | 2017-12-29 15:15 | 51558.3858 | 39.996
Devonshire Building | 2017-12-29 15:30 | 51558.3908 | 20.016
Devonshire Building | 2017-12-29 15:45 | 51558.4008 | 39.996
Devonshire Building | 2017-12-29 16:00 | 51558.4058 | 20.016
Devonshire Building | 2017-12-29 16:15 | 51558.4158 | 39.996
Devonshire Building | 2017-12-29 16:30 | 51558.4209 | 20.016
Devonshire Building | 2017-12-29 16:45 | 51558.4308 | 39.996
Devonshire Building | 2017-12-29 17:00 | 51558.4359 | 20.016
Devonshire Building | 2017-12-29 17:15 | 51558.4459 | 39.996
Devonshire Building | 2017-12-29 17:30 | 51558.4509 | 20.016
Devonshire Building | 2017-12-29 17:45 | 51558.4609 | 39.996
Devonshire Building | 2017-12-29 18:00 | 51558.8559 | 1580.004
Devonshire Building | 2017-12-29 18:15 | 51558.8609 | 20.016
Devonshire Building | 2017-12-29 18:30 | 51558.8709 | 39.996
Devonshire Building | 2017-12-29 18:45 | 51558.8759 | 20.016
Devonshire Building | 2017-12-29 19:00 | 51558.8859 | 39.996
Devonshire Building | 2017-12-29 19:15 | 51558.8909 | 20.016
Devonshire Building | 2017-12-29 19:30 | 51558.9009 | 39.996
Devonshire Building | 2017-12-29 19:45 | 51558.9059 | 20.016
Devonshire Building | 2017-12-29 20:00 | 51558.9159 | 39.996
Devonshire Building | 2017-12-29 20:15 | 51558.9209 | 20.016
Devonshire Building | 2017-12-29 20:30 | 51558.9309 | 39.996
Devonshire Building | 2017-12-29 20:45 | 51558.9359 | 20.016
Devonshire Building | 2017-12-29 21:00 | 51558.9459 | 39.996
Devonshire Building | 2017-12-29 21:15 | 51558.9509 | 20.016
Devonshire Building | 2017-12-29 21:30 | 51558.9609 | 39.996
Devonshire Building | 2017-12-29 21:45 | 51558.9859 | 100.008
Devonshire Building | 2017-12-29 22:00 | 51558.9959 | 39.996
Devonshire Building | 2017-12-29 22:15 | 51559.0009 | 20.016
Devonshire Building | 2017-12-29 22:30 | 51559.0109 | 39.996
Devonshire Building | 2017-12-29 22:45 | 51559.0159 | 20.016
Devonshire Building | 2017-12-29 23:00 | 51559.0259 | 39.996
Devonshire Building | 2017-12-29 23:15 | 51559.0309 | 20.016
Devonshire Building | 2017-12-29 23:30 | 51559.0409 | 39.996
Devonshire Building | 2017-12-29 23:45 | 51559.0459 | 20.016
Devonshire Building | 2017-12-30 | 51559.0547 | 39.996
Devonshire Building | 2017-12-30 00:15 | 51559.0647 | 39.996
Devonshire Building | 2017-12-30 00:30 | 51559.0697 | 20.016
Devonshire Building | 2017-12-30 00:45 | 51559.0797 | 39.996
Devonshire Building | 2017-12-30 01:00 | 51559.0847 | 20.016
Devonshire Building | 2017-12-30 01:15 | 51559.0947 | 39.996
Devonshire Building | 2017-12-30 01:30 | 51559.0997 | 20.016
Devonshire Building | 2017-12-30 01:45 | 51559.1097 | 39.996
Devonshire Building | 2017-12-30 02:00 | 51559.1147 | 20.016
Devonshire Building | 2017-12-30 02:15 | 51559.1247 | 39.996
Devonshire Building | 2017-12-30 02:30 | 51559.1997 | 299.988
Devonshire Building | 2017-12-30 02:45 | 51559.5347 | 1339.992
Devonshire Building | 2017-12-30 03:00 | 51559.5447 | 39.996
Devonshire Building | 2017-12-30 03:15 | 51559.5497 | 20.016
Devonshire Building | 2017-12-30 03:30 | 51559.5597 | 39.996
Devonshire Building | 2017-12-30 03:45 | 51559.5647 | 20.016
Devonshire Building | 2017-12-30 04:00 | 51559.5747 | 39.996
Devonshire Building | 2017-12-30 04:15 | 51559.5797 | 20.016
Devonshire Building | 2017-12-30 04:30 | 51559.5897 | 39.996
Devonshire Building | 2017-12-30 04:45 | 51559.5947 | 20.016
Devonshire Building | 2017-12-30 05:00 | 51559.6047 | 39.996
Devonshire Building | 2017-12-30 05:15 | 51559.6097 | 20.016
Devonshire Building | 2017-12-30 05:30 | 51559.6197 | 39.996
Devonshire Building | 2017-12-30 05:45 | 51559.6247 | 20.016
Devonshire Building | 2017-12-30 06:00 | 51559.6347 | 39.996
Devonshire Building | 2017-12-30 06:15 | 51559.6397 | 20.016
Devonshire Building | 2017-12-30 06:30 | 51559.6497 | 39.996
Devonshire Building | 2017-12-30 06:45 | 51559.6547 | 20.016
Devonshire Building | 2017-12-30 07:00 | 51559.6647 | 39.996
Devonshire Building | 2017-12-30 07:15 | 51559.6697 | 20.016
Devonshire Building | 2017-12-30 07:30 | 51559.6797 | 39.996
Devonshire Building | 2017-12-30 07:45 | 51559.6947 | 60.012
Devonshire Building | 2017-12-30 08:00 | 51559.7197 | 100.008
Devonshire Building | 2017-12-30 08:15 | 51559.7397 | 79.992
Devonshire Building | 2017-12-30 08:30 | 51559.7597 | 79.992
Devonshire Building | 2017-12-30 08:45 | 51559.7847 | 100.008
Devonshire Building | 2017-12-30 09:00 | 51559.8047 | 79.992
Devonshire Building | 2017-12-30 09:15 | 51559.8297 | 100.008
Devonshire Building | 2017-12-30 09:30 | 51559.8497 | 79.992
Devonshire Building | 2017-12-30 09:45 | 51559.8747 | 100.008
Devonshire Building | 2017-12-30 10:00 | 51559.8947 | 79.992
Devonshire Building | 2017-12-30 10:15 | 51559.9197 | 100.008
Devonshire Building | 2017-12-30 10:30 | 51559.9397 | 79.992
Devonshire Building | 2017-12-30 10:45 | 51559.9647 | 100.008
Devonshire Building | 2017-12-30 11:00 | 51559.9847 | 79.992
Devonshire Building | 2017-12-30 11:15 | 51559.9947 | 39.996
Devonshire Building | 2017-12-30 11:30 | 51560.0047 | 39.996
Devonshire Building | 2017-12-30 11:45 | 51560.3997 | 1580.004
Devonshire Building | 2017-12-30 12:00 | 51560.4097 | 39.996
Devonshire Building | 2017-12-30 12:15 | 51560.4147 | 20.016
Devonshire Building | 2017-12-30 12:30 | 51560.4247 | 39.996
Devonshire Building | 2017-12-30 12:45 | 51560.4297 | 20.016
Devonshire Building | 2017-12-30 13:00 | 51560.4397 | 39.996
Devonshire Building | 2017-12-30 13:15 | 51560.4447 | 20.016
Devonshire Building | 2017-12-30 13:30 | 51560.4547 | 39.996
Devonshire Building | 2017-12-30 13:45 | 51560.4597 | 20.016
Devonshire Building | 2017-12-30 14:00 | 51560.4697 | 39.996
Devonshire Building | 2017-12-30 14:15 | 51560.4747 | 20.016
Devonshire Building | 2017-12-30 14:30 | 51560.4847 | 39.996
Devonshire Building | 2017-12-30 14:45 | 51560.4947 | 39.996
Devonshire Building | 2017-12-30 15:00 | 51560.5047 | 39.996
Devonshire Building | 2017-12-30 15:15 | 51560.5097 | 20.016
Devonshire Building | 2017-12-30 15:30 | 51560.5197 | 39.996
Devonshire Building | 2017-12-30 15:45 | 51560.5297 | 39.996
Devonshire Building | 2017-12-30 16:00 | 51560.5397 | 39.996
Devonshire Building | 2017-12-30 16:15 | 51560.5497 | 39.996
Devonshire Building | 2017-12-30 16:30 | 51560.5547 | 20.016
Devonshire Building | 2017-12-30 16:45 | 51560.5647 | 39.996
Devonshire Building | 2017-12-30 17:00 | 51560.5747 | 39.996
Devonshire Building | 2017-12-30 17:15 | 51560.5797 | 20.016
Devonshire Building | 2017-12-30 17:30 | 51560.5897 | 39.996
Devonshire Building | 2017-12-30 17:45 | 51560.5997 | 39.996
Devonshire Building | 2017-12-30 18:00 | 51560.6047 | 20.016
Devonshire Building | 2017-12-30 18:15 | 51560.6147 | 39.996
Devonshire Building | 2017-12-30 18:30 | 51560.6197 | 20.016
Devonshire Building | 2017-12-30 18:45 | 51560.6297 | 39.996
Devonshire Building | 2017-12-30 19:00 | 51560.6347 | 20.016
Devonshire Building | 2017-12-30 19:15 | 51560.7797 | 579.996
Devonshire Building | 2017-12-30 19:30 | 51561.0497 | 1080
Devonshire Building | 2017-12-30 19:45 | 51561.0597 | 39.996
Devonshire Building | 2017-12-30 20:00 | 51561.0647 | 20.016
Devonshire Building | 2017-12-30 20:15 | 51561.0747 | 39.996
Devonshire Building | 2017-12-30 20:30 | 51561.0798 | 20.016
Devonshire Building | 2017-12-30 20:45 | 51561.0898 | 39.996
Devonshire Building | 2017-12-30 21:00 | 51561.0948 | 20.016
Devonshire Building | 2017-12-30 21:15 | 51561.1048 | 39.996
Devonshire Building | 2017-12-30 21:30 | 51561.1148 | 39.996
Devonshire Building | 2017-12-30 21:45 | 51561.1398 | 100.008
Devonshire Building | 2017-12-30 22:00 | 51561.1498 | 39.996
Devonshire Building | 2017-12-30 22:15 | 51561.1548 | 20.016
Devonshire Building | 2017-12-30 22:30 | 51561.1648 | 39.996
Devonshire Building | 2017-12-30 22:45 | 51561.1748 | 39.996
Devonshire Building | 2017-12-30 23:00 | 51561.1798 | 20.016
Devonshire Building | 2017-12-30 23:15 | 51561.1898 | 39.996
Devonshire Building | 2017-12-30 23:30 | 51561.1948 | 20.016
Devonshire Building | 2017-12-30 23:45 | 51561.2048 | 39.996
Devonshire Building | 2017-12-31 | 51561.2109 | 20.016
Devonshire Building | 2017-12-31 00:15 | 51561.2209 | 39.996
Devonshire Building | 2017-12-31 00:30 | 51561.2259 | 20.016
Devonshire Building | 2017-12-31 00:45 | 51561.2359 | 39.996
Devonshire Building | 2017-12-31 01:00 | 51561.2409 | 20.016
Devonshire Building | 2017-12-31 01:15 | 51561.2509 | 39.996
Devonshire Building | 2017-12-31 01:30 | 51561.2559 | 20.016
Devonshire Building | 2017-12-31 01:45 | 51561.2659 | 39.996
Devonshire Building | 2017-12-31 02:00 | 51561.271 | 20.016
Devonshire Building | 2017-12-31 02:15 | 51561.281 | 39.996
Devonshire Building | 2017-12-31 02:30 | 51561.286 | 20.016
Devonshire Building | 2017-12-31 02:45 | 51561.296 | 39.996
Devonshire Building | 2017-12-31 03:00 | 51561.306 | 39.996
Devonshire Building | 2017-12-31 03:15 | 51561.311 | 20.016
Devonshire Building | 2017-12-31 03:30 | 51561.321 | 39.996
Devonshire Building | 2017-12-31 03:45 | 51561.326 | 20.016
Devonshire Building | 2017-12-31 04:00 | 51561.336 | 39.996
Devonshire Building | 2017-12-31 04:15 | 51561.341 | 20.016
Devonshire Building | 2017-12-31 04:30 | 51561.746 | 1620
Devonshire Building | 2017-12-31 04:45 | 51561.756 | 39.996
Devonshire Building | 2017-12-31 05:00 | 51561.761 | 20.016
Devonshire Building | 2017-12-31 05:15 | 51561.771 | 39.996
Devonshire Building | 2017-12-31 05:30 | 51561.776 | 20.016
Devonshire Building | 2017-12-31 05:45 | 51561.786 | 39.996
Devonshire Building | 2017-12-31 06:00 | 51561.791 | 20.016
Devonshire Building | 2017-12-31 06:15 | 51561.801 | 39.996
Devonshire Building | 2017-12-31 06:30 | 51561.806 | 20.016
Devonshire Building | 2017-12-31 06:45 | 51561.816 | 39.996
Devonshire Building | 2017-12-31 07:00 | 51561.821 | 20.016
Devonshire Building | 2017-12-31 07:15 | 51561.831 | 39.996
Devonshire Building | 2017-12-31 07:30 | 51561.836 | 20.016
Devonshire Building | 2017-12-31 07:45 | 51561.856 | 79.992
Devonshire Building | 2017-12-31 08:00 | 51561.876 | 79.992
Devonshire Building | 2017-12-31 08:15 | 51561.901 | 100.008
Devonshire Building | 2017-12-31 08:30 | 51561.921 | 79.992
Devonshire Building | 2017-12-31 08:45 | 51561.946 | 100.008
Devonshire Building | 2017-12-31 09:00 | 51561.966 | 79.992
Devonshire Building | 2017-12-31 09:15 | 51561.991 | 100.008
Devonshire Building | 2017-12-31 09:30 | 51562.011 | 79.992
Devonshire Building | 2017-12-31 09:45 | 51562.031 | 79.992
Devonshire Building | 2017-12-31 10:00 | 51562.056 | 100.008
Devonshire Building | 2017-12-31 10:15 | 51562.076 | 79.992
Devonshire Building | 2017-12-31 10:30 | 51562.101 | 100.008
Devonshire Building | 2017-12-31 10:45 | 51562.121 | 79.992
Devonshire Building | 2017-12-31 11:00 | 51562.141 | 79.992
Devonshire Building | 2017-12-31 11:15 | 51562.156 | 60.012
Devonshire Building | 2017-12-31 11:30 | 51562.161 | 20.016
Devonshire Building | 2017-12-31 11:45 | 51562.171 | 39.996
Devonshire Building | 2017-12-31 12:00 | 51562.176 | 20.016
Devonshire Building | 2017-12-31 12:15 | 51562.186 | 39.996
Devonshire Building | 2017-12-31 12:30 | 51562.191 | 20.016
Devonshire Building | 2017-12-31 12:45 | 51562.256 | 259.992
Devonshire Building | 2017-12-31 13:00 | 51562.596 | 1360.008
Devonshire Building | 2017-12-31 13:15 | 51562.601 | 20.016
Devonshire Building | 2017-12-31 13:30 | 51562.611 | 39.996
Devonshire Building | 2017-12-31 13:45 | 51562.616 | 20.016
Devonshire Building | 2017-12-31 14:00 | 51562.626 | 39.996
Devonshire Building | 2017-12-31 14:15 | 51562.631 | 20.016
Devonshire Building | 2017-12-31 14:30 | 51562.641 | 39.996
Devonshire Building | 2017-12-31 14:45 | 51562.651 | 39.996
Devonshire Building | 2017-12-31 15:00 | 51562.656 | 20.016
Devonshire Building | 2017-12-31 15:15 | 51562.666 | 39.996
Devonshire Building | 2017-12-31 15:30 | 51562.676 | 39.996
Devonshire Building | 2017-12-31 15:45 | 51562.681 | 20.016
Devonshire Building | 2017-12-31 16:00 | 51562.691 | 39.996
Devonshire Building | 2017-12-31 16:15 | 51562.696 | 20.016
Devonshire Building | 2017-12-31 16:30 | 51562.706 | 39.996
Devonshire Building | 2017-12-31 16:45 | 51562.716 | 39.996
Devonshire Building | 2017-12-31 17:00 | 51562.721 | 20.016
Devonshire Building | 2017-12-31 17:15 | 51562.731 | 39.996
Devonshire Building | 2017-12-31 17:30 | 51562.736 | 20.016
Devonshire Building | 2017-12-31 17:45 | 51562.746 | 39.996
Devonshire Building | 2017-12-31 18:00 | 51562.751 | 20.016
Devonshire Building | 2017-12-31 18:15 | 51562.761 | 39.996
Devonshire Building | 2017-12-31 18:30 | 51562.766 | 20.016
Devonshire Building | 2017-12-31 18:45 | 51562.776 | 39.996
Devonshire Building | 2017-12-31 19:00 | 51562.781 | 20.016
Devonshire Building | 2017-12-31 19:15 | 51562.791 | 39.996
Devonshire Building | 2017-12-31 19:30 | 51562.796 | 20.016
Devonshire Building | 2017-12-31 19:45 | 51563.196 | 1599.984
Devonshire Building | 2017-12-31 20:00 | 51563.206 | 39.996
Devonshire Building | 2017-12-31 20:15 | 51563.211 | 20.016
Devonshire Building | 2017-12-31 20:30 | 51563.221 | 39.996
Devonshire Building | 2017-12-31 20:45 | 51563.226 | 20.016
Devonshire Building | 2017-12-31 21:00 | 51563.236 | 39.996
Devonshire Building | 2017-12-31 21:15 | 51563.241 | 20.016
Devonshire Building | 2017-12-31 21:30 | 51563.251 | 39.996
Devonshire Building | 2017-12-31 21:45 | 51563.281 | 119.988
Devonshire Building | 2017-12-31 22:00 | 51563.286 | 20.016
Devonshire Building | 2017-12-31 22:15 | 51563.296 | 39.996
Devonshire Building | 2017-12-31 22:30 | 51563.301 | 20.016
Devonshire Building | 2017-12-31 22:45 | 51563.311 | 39.996
Devonshire Building | 2017-12-31 23:00 | 51563.316 | 20.016
Devonshire Building | 2017-12-31 23:15 | 51563.326 | 39.996
Devonshire Building | 2017-12-31 23:30 | 51563.331 | 20.016
Devonshire Building | 2017-12-31 23:45 | 51563.341 | 39.996

## EconomicsMetering
Metering costs | Meters (2021) |  | Annual metering costs |  | Costs to date
£ per meter and year | # |  | £ |  | £
278 | 47 |  | 13066 |  | 65330
Savings in 2016
Baseflow at the end |  | Annual water bill for final leak |  |  | Reclaim DB | Annual bill merz court | Boathouse reclaim |  | Savings in 2016
l/h |  | £ |  |  | £ | £ | £ |  | £
1640.016 |  | 25833.425 |  |  | 80000 | 15751.9347 | 10000 |  | 131585.3598
Years worth of monitoring
10.0708
Water wastage
Water use 2016 per staff and student (Sustainability team) |  |  |  | # staff students | Water use 2016 uni | Water losses/wastage in 2016 |  | Water losses/wastage in 2016
m3 per year |  |  |  |  | m3 per year | m3 per year |  | %
15 |  |  |  | 25000 | 375000 | 23126.5402 |  | 6.1671

## USB MainsWaterMonitoringUSB
| Date time | Meter reading (m3) | Manual reading inlet (m3) | Daily consumption (l/h) | Daytime (l/h) | Nighttime (l/h) | Flooding event (m3) |  | Bill (£)
USB ¦ Main | 2019-08-22 18:30 | 5427.5283 |  |  |  |  | 298.5569 |  | 573.6212
USB ¦ Main | 2019-08-23 06:30 | 5427.6183 |  |  |  | 7.5007
USB ¦ Main | 2019-08-23 18:30 | 5432.3773 |  | 202.0426 | 396.5846 |  | Difference street versus inlet
USB ¦ Main | 2019-08-24 06:30 | 5432.3774 |  |  |  | 0.0018333
USB ¦ Main | 2019-08-24 18:30 | 5432.3774 |  | 0.00091667 | 0 |  | 2020-01-24 18:30 | 1394.8861
USB ¦ Main | 2019-08-25 06:30 | 5432.3774 |  |  |  | 0 | 2020-01-27 18:30 | 1388.5543
USB ¦ Main | 2019-08-25 18:30 | 5432.3774 |  | 0 | 0 |  | 2020-01-28 18:30 | 1390.753
USB ¦ Main | 2019-08-26 06:30 | 5432.3774 |  |  |  | 0 | 2020-01-29 18:30 | 1529.6315
USB ¦ Main | 2019-08-26 18:30 | 5433.067 |  | 28.7353 | 57.4707 |  | 2020-02-19 18:30 | 2114.6196 |  | 8760000
USB ¦ Main | 2019-08-27 06:30 | 5433.067 |  |  |  | 0.0018333 | 2020-02-20 18:30 | 2054.568
USB ¦ Main | 2019-08-27 18:30 | 5439.7458 |  | 278.2809 | 556.56 |  | 2020-02-21 18:30 | 2055.4665
USB ¦ Main | 2019-08-28 06:30 | 5439.7458 |  |  |  | 0 | 2020-02-21 18:30 | 2055.4665
USB ¦ Main | 2019-08-28 18:30 | 5445.804 |  | 252.4275 | 504.855 |  | 2020-02-24 18:30 | 2057.3942
USB ¦ Main | 2019-08-29 06:30 | 5445.804 |  |  |  | 0 | 2020-02-25 18:30 | 2273.2229
USB ¦ Main | 2019-08-29 18:30 | 5452.7628 |  | 289.9491 | 579.8982 |  | 2020-02-26 18:30 | 2358.3716
USB ¦ Main | 2019-08-30 06:30 | 5452.7628 |  |  |  | 0.0018333 | 2020-10-13 18:30 | 2550.9512
USB ¦ Main | 2019-08-30 18:30 | 5458.2116 |  | 227.0315 | 454.0612 |  | 2021-04-18 18:30 | 2656.4712
USB ¦ Main | 2019-08-31 06:30 | 5458.2116 |  |  |  | 0.0029167
USB ¦ Main | 2019-08-31 18:30 | 5458.2116 |  | 0.0014583 | 0 |  | Value gap | 5313.9405
USB ¦ Main | 2019-09-01 06:30 | 5458.2116 |  |  |  | 0
USB ¦ Main | 2019-09-01 18:30 | 5458.7914 |  | 24.1594 | 48.3187 |  | Average ordinare weekday water use
USB ¦ Main | 2019-09-02 06:30 | 5458.7914 |  |  |  | 0.0029167 | l/h | 991.9997
USB ¦ Main | 2019-09-02 18:30 | 5466.1996 |  | 308.6733 | 617.3437
USB ¦ Main | 2019-09-03 06:30 | 5466.1996 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-03 18:30 | 5473.8877 |  | 320.3396 | 640.6762
USB ¦ Main | 2019-09-04 06:30 | 5473.8878 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-04 18:30 | 5481.2658 |  | 307.4218 | 614.8407
USB ¦ Main | 2019-09-05 06:30 | 5481.2659 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-05 18:30 | 5488.8947 |  | 317.8697 | 635.7375
USB ¦ Main | 2019-09-06 06:30 | 5488.8947 |  |  |  | 0
USB ¦ Main | 2019-09-06 18:30 | 5496.7934 |  | 329.1103 | 658.2207
USB ¦ Main | 2019-09-07 06:30 | 5496.7934 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-07 18:30 | 5497.1533 |  | 14.9972 | 29.9925
USB ¦ Main | 2019-09-08 06:30 | 5497.1533 |  |  |  | 0
USB ¦ Main | 2019-09-08 18:30 | 5497.1533 |  | 0 | 0
USB ¦ Main | 2019-09-09 06:30 | 5497.1533 |  |  |  | 0
USB ¦ Main | 2019-09-09 18:30 | 5504.1015 |  | 289.5103 | 579.0207
USB ¦ Main | 2019-09-10 06:30 | 5504.1016 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-10 18:30 | 5517.2102 |  | 546.194 | 1092.3863
USB ¦ Main | 2019-09-11 06:30 | 5517.2102 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-11 18:30 | 5523.8389 |  | 276.1946 | 552.3863
USB ¦ Main | 2019-09-12 06:30 | 5523.8389 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-12 18:30 | 5532.0572 |  | 342.4318 | 684.8607
USB ¦ Main | 2019-09-13 06:30 | 5532.0573 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-13 18:30 | 5537.3262 |  | 219.539 | 439.0763
USB ¦ Main | 2019-09-14 06:30 | 5537.3262 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-14 18:30 | 5538.296 |  | 40.4115 | 80.82
USB ¦ Main | 2019-09-15 06:30 | 5538.476 |  |  |  | 14.9992
USB ¦ Main | 2019-09-15 18:30 | 5538.496 |  | 8.3321 | 1.665
USB ¦ Main | 2019-09-16 06:30 | 5538.496 |  |  |  | 0
USB ¦ Main | 2019-09-16 18:30 | 5544.1552 |  | 235.8 | 471.6
USB ¦ Main | 2019-09-17 06:30 | 5544.1552 |  |  |  | 0
USB ¦ Main | 2019-09-17 18:30 | 5549.7939 |  | 234.945 | 469.89
USB ¦ Main | 2019-09-18 06:30 | 5549.7939 |  |  |  | 0
USB ¦ Main | 2019-09-18 18:30 | 5557.3623 |  | 315.3487 | 630.6975
USB ¦ Main | 2019-09-19 06:30 | 5557.3623 |  |  |  | 0
USB ¦ Main | 2019-09-19 18:30 | 5607.8707 |  | 2104.5178 | 4209.0357
USB ¦ Main | 2019-09-20 06:30 | 5607.8707 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-20 18:30 | 5628.2402 |  | 848.729 | 1697.4563
USB ¦ Main | 2019-09-21 06:30 | 5628.4302 |  |  |  | 15.8362
USB ¦ Main | 2019-09-21 18:30 | 5628.6302 |  | 16.2487 | 16.6612
USB ¦ Main | 2019-09-22 06:30 | 5628.8202 |  |  |  | 15.8363
USB ¦ Main | 2019-09-22 18:30 | 5629.0101 |  | 15.8325 | 15.8288
USB ¦ Main | 2019-09-23 06:30 | 5629.0102 |  |  |  | 0.0029167
USB ¦ Main | 2019-09-23 18:30 | 5636.8988 |  | 328.6927 | 657.3825
USB ¦ Main | 2019-09-24 06:30 | 5636.8988 |  |  |  | 0
USB ¦ Main | 2019-09-24 18:30 | 5643.1677 |  | 261.2053 | 522.4107
USB ¦ Main | 2019-09-25 06:30 | 5643.1677 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-25 18:30 | 5647.987 |  | 200.805 | 401.6082
USB ¦ Main | 2019-09-26 06:30 | 5647.987 |  |  |  | 0.0018333
USB ¦ Main | 2019-09-26 18:30 | 5655.5761 |  | 316.2103 | 632.4188
USB ¦ Main | 2019-09-27 06:30 | 5655.5861 |  |  |  | 0.83517
USB ¦ Main | 2019-09-27 18:30 | 5662.3353 |  | 281.634 | 562.4328
USB ¦ Main | 2019-09-28 06:30 | 5662.3353 |  |  |  | 0
USB ¦ Main | 2019-09-28 18:30 | 5662.5552 |  | 9.1631 | 18.3262
USB ¦ Main | 2019-09-29 06:30 | 5662.7452 |  |  |  | 15.8363
USB ¦ Main | 2019-09-29 18:30 | 5662.7452 |  | 7.9181 | 0
USB ¦ Main | 2019-09-30 06:30 | 5662.7452 |  |  |  | 0
USB ¦ Main | 2019-09-30 18:30 | 5674.7041 |  | 498.285 | 996.57
USB ¦ Main | 2019-10-01 06:30 | 5674.7041 |  |  |  | 0
USB ¦ Main | 2019-10-01 18:30 | 5685.5731 |  | 452.8744 | 905.7488
USB ¦ Main | 2019-10-02 06:30 | 5685.783 |  |  |  | 17.4989
USB ¦ Main | 2019-10-02 18:30 | 5817.8014 |  | 5509.5146 | 11001.5303
USB ¦ Main | 2019-10-03 06:30 | 5817.8214 |  |  |  | 1.6683
USB ¦ Main | 2019-10-03 18:30 | 5828.54 |  | 447.4425 | 893.2167
USB ¦ Main | 2019-10-04 06:30 | 5828.5401 |  |  |  | 0.0029167
USB ¦ Main | 2019-10-04 18:30 | 5839.0288 |  | 437.0302 | 874.0575
USB ¦ Main | 2019-10-05 06:30 | 5839.0288 |  |  |  | 0
USB ¦ Main | 2019-10-05 18:30 | 5839.3987 |  | 15.4153 | 30.8307
USB ¦ Main | 2019-10-06 06:30 | 5839.3987 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-06 18:30 | 5839.9887 |  | 24.5822 | 49.1625
USB ¦ Main | 2019-10-07 06:30 | 5840.1787 |  |  |  | 15.8317
USB ¦ Main | 2019-10-07 18:30 | 5852.5969 |  | 525.3427 | 1034.8537
USB ¦ Main | 2019-10-08 06:30 | 5852.597 |  |  |  | 0.0029167
USB ¦ Main | 2019-10-08 18:30 | 5864.9949 |  | 516.5846 | 1033.1663
USB ¦ Main | 2019-10-09 06:30 | 5865.205 |  |  |  | 17.501
USB ¦ Main | 2019-10-09 18:30 | 5876.1838 |  | 466.201 | 914.9009
USB ¦ Main | 2019-10-10 06:30 | 5876.1838 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-10 18:30 | 5887.3924 |  | 467.025 | 934.0482
USB ¦ Main | 2019-10-11 06:30 | 5887.7322 |  |  |  | 28.3218
USB ¦ Main | 2019-10-11 18:30 | 5898.3404 |  | 456.1678 | 884.0138
USB ¦ Main | 2019-10-12 06:30 | 5898.5304 |  |  |  | 15.8362
USB ¦ Main | 2019-10-12 18:30 | 5899.0702 |  | 30.4097 | 44.9832
USB ¦ Main | 2019-10-13 06:30 | 5899.0702 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-13 18:30 | 5899.6301 |  | 23.3278 | 46.6538
USB ¦ Main | 2019-10-14 06:30 | 5899.8101 |  |  |  | 15.0037
USB ¦ Main | 2019-10-14 18:30 | 5911.6885 |  | 502.4344 | 989.865
USB ¦ Main | 2019-10-15 06:30 | 5912.0584 |  |  |  | 30.8238
USB ¦ Main | 2019-10-15 18:30 | 5923.3571 |  | 486.1894 | 941.555
USB ¦ Main | 2019-10-16 06:30 | 5923.527 |  |  |  | 14.1638
USB ¦ Main | 2019-10-16 18:30 | 5934.4356 |  | 461.6044 | 909.045
USB ¦ Main | 2019-10-17 06:30 | 5934.6055 |  |  |  | 14.16
USB ¦ Main | 2019-10-17 18:30 | 5945.9039 |  | 477.8475 | 941.535
USB ¦ Main | 2019-10-18 06:30 | 5945.9039 |  |  |  | 0
USB ¦ Main | 2019-10-18 18:30 | 5956.1926 |  | 428.6953 | 857.3907
USB ¦ Main | 2019-10-19 06:30 | 5956.1926 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-19 18:30 | 5956.9425 |  | 31.245 | 62.4882
USB ¦ Main | 2019-10-20 06:30 | 5956.9425 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-20 18:30 | 5957.4925 |  | 22.9172 | 45.8325
USB ¦ Main | 2019-10-21 06:30 | 5957.5025 |  |  |  | 0.8325
USB ¦ Main | 2019-10-21 18:30 | 5969.6511 |  | 506.61 | 1012.3875
USB ¦ Main | 2019-10-22 06:30 | 5969.9411 |  |  |  | 24.165
USB ¦ Main | 2019-10-22 18:30 | 6104.5095 |  | 5619.0994 | 11214.0337
USB ¦ Main | 2019-10-23 06:30 | 6104.5096 |  |  |  | 0.00375
USB ¦ Main | 2019-10-23 18:30 | 6117.008 |  | 520.77 | 1041.5362
USB ¦ Main | 2019-10-24 06:30 | 6117.1879 |  |  |  | 14.9879
USB ¦ Main | 2019-10-24 18:30 | 6128.7563 |  | 489.5115 | 964.035
USB ¦ Main | 2019-10-25 06:30 | 6128.7563 |  |  |  | 0
USB ¦ Main | 2019-10-25 18:30 | 6138.205 |  | 393.6966 | 787.3932
USB ¦ Main | 2019-10-26 06:30 | 6138.205 |  |  |  | 0.0018333
USB ¦ Main | 2019-10-26 18:30 | 6139.0648 |  | 35.8265 | 71.6513
USB ¦ Main | 2019-10-27 06:30 | 6139.4148 |  |  |  | 29.1629
USB ¦ Main | 2019-10-27 18:30 | 6139.7547 |  | 28.7452 | 28.3275
USB ¦ Main | 2019-10-28 06:30 | 6139.7547 |  |  |  | 0
USB ¦ Main | 2019-10-28 18:30 | 6152.693 |  | 539.0944 | 1078.1887
USB ¦ Main | 2019-10-29 06:30 | 6152.8029 |  |  |  | 9.1604
USB ¦ Main | 2019-10-29 18:30 | 6164.9213 |  | 509.514 | 1009.8675
USB ¦ Main | 2019-10-30 06:30 | 6165.0112 |  |  |  | 7.4925
USB ¦ Main | 2019-10-30 18:30 | 6175.1098 |  | 424.5216 | 841.5507
USB ¦ Main | 2019-10-31 06:30 | 6175.1798 |  |  |  | 5.8293
USB ¦ Main | 2019-10-31 18:30 | 6187.0383 |  | 497.0203 | 988.2112
USB ¦ Main | 2019-11-01 06:30 | 6187.4583 |  |  |  | 34.9988
USB ¦ Main | 2019-11-01 18:30 | 6197.1271 |  | 420.3647 | 805.7307
USB ¦ Main | 2019-11-02 06:30 | 6197.507 |  |  |  | 31.6593
USB ¦ Main | 2019-11-02 18:30 | 6197.8869 |  | 31.6612 | 31.6632
USB ¦ Main | 2019-11-03 06:30 | 6197.887 |  |  |  | 0.0018333
USB ¦ Main | 2019-11-03 18:30 | 6198.0768 |  | 7.9097 | 15.8175
USB ¦ Main | 2019-11-04 06:30 | 6198.0768 |  |  |  | 0
USB ¦ Main | 2019-11-04 18:30 | 6208.1154 |  | 418.275 | 836.55
USB ¦ Main | 2019-11-05 06:30 | 6208.2452 |  |  |  | 10.8225
USB ¦ Main | 2019-11-05 18:30 | 6218.7135 |  | 441.5878 | 872.3532
USB ¦ Main | 2019-11-06 06:30 | 6219.1534 |  |  |  | 36.661
USB ¦ Main | 2019-11-06 18:30 | 6239.9521 |  | 884.9433 | 1733.2257
USB ¦ Main | 2019-11-07 06:30 | 6240.3121 |  |  |  | 29.9943
USB ¦ Main | 2019-11-07 18:30 | 6249.8304 |  | 411.5963 | 793.1982
USB ¦ Main | 2019-11-08 06:30 | 6249.9603 |  |  |  | 10.8243
USB ¦ Main | 2019-11-08 18:30 | 6258.7981 |  | 373.6528 | 736.4812
USB ¦ Main | 2019-11-09 06:30 | 6258.8281 |  |  |  | 2.5004
USB ¦ Main | 2019-11-09 18:30 | 6259.048 |  | 10.4133 | 18.3263
USB ¦ Main | 2019-11-10 06:30 | 6259.0481 |  |  |  | 0.0029167
USB ¦ Main | 2019-11-10 18:30 | 6259.2778 |  | 9.5752 | 19.1475
USB ¦ Main | 2019-11-11 06:30 | 6259.2778 |  |  |  | 0
USB ¦ Main | 2019-11-11 18:30 | 6273.3265 |  | 585.36 | 1170.72
USB ¦ Main | 2019-11-12 06:30 | 6276.2758 |  |  |  | 245.7817
USB ¦ Main | 2019-11-12 18:30 | 6289.3941 |  | 669.4833 | 1093.185
USB ¦ Main | 2019-11-13 06:30 | 6290.024 |  |  |  | 52.4925
USB ¦ Main | 2019-11-13 18:30 | 6327.0826 |  | 1570.3538 | 3088.215
USB ¦ Main | 2019-11-14 06:30 | 6327.0826 |  |  |  | 0
USB ¦ Main | 2019-11-14 18:30 | 6345.0016 |  | 746.6288 | 1493.2575
USB ¦ Main | 2019-11-15 06:30 | 6346.3014 |  |  |  | 108.315
USB ¦ Main | 2019-11-15 18:30 | 6357.1701 |  | 507.0206 | 905.7263
USB ¦ Main | 2019-11-16 06:30 | 6357.9901 |  |  |  | 68.3287
USB ¦ Main | 2019-11-16 18:30 | 6359.06 |  | 78.7425 | 89.1563
USB ¦ Main | 2019-11-17 06:30 | 6359.5899 |  |  |  | 44.1638
USB ¦ Main | 2019-11-17 18:30 | 6361.2997 |  | 93.3225 | 142.4812
USB ¦ Main | 2019-11-18 06:30 | 6361.9296 |  |  |  | 52.4954
USB ¦ Main | 2019-11-18 18:30 | 6401.8981 |  | 1691.5993 | 3330.7032
USB ¦ Main | 2019-11-19 06:30 | 6402.338 |  |  |  | 36.661
USB ¦ Main | 2019-11-19 18:30 | 6415.1463 |  | 552.008 | 1067.355
USB ¦ Main | 2019-11-20 06:30 | 6415.7662 |  |  |  | 51.66
USB ¦ Main | 2019-11-20 18:30 | 6433.1449 |  | 749.9419 | 1448.2237
USB ¦ Main | 2019-11-21 06:30 | 6434.1749 |  |  |  | 85.8337
USB ¦ Main | 2019-11-21 18:30 | 6445.4034 |  | 510.7706 | 935.7075
USB ¦ Main | 2019-11-22 06:30 | 6445.4034 |  |  |  | 0
USB ¦ Main | 2019-11-22 18:30 | 6455.5617 |  | 423.2644 | 846.5287
USB ¦ Main | 2019-11-23 06:30 | 6455.5617 |  |  |  | 0.0029167
USB ¦ Main | 2019-11-23 18:30 | 6456.5116 |  | 39.579 | 79.155
USB ¦ Main | 2019-11-24 06:30 | 6456.5116 |  |  |  | 0
USB ¦ Main | 2019-11-24 18:30 | 6456.7315 |  | 9.1631 | 18.3263
USB ¦ Main | 2019-11-25 06:30 | 6456.9515 |  |  |  | 18.3338
USB ¦ Main | 2019-11-25 18:30 | 6490.8996 |  | 1423.6688 | 2829.0038
USB ¦ Main | 2019-11-26 06:30 | 6491.4595 |  |  |  | 46.6612
USB ¦ Main | 2019-11-26 18:30 | 6632.7282 |  | 5909.5247 | 11772.3882
USB ¦ Main | 2019-11-27 06:30 | 6633.0881 |  |  |  | 29.9943
USB ¦ Main | 2019-11-27 18:30 | 6643.3164 |  | 441.1753 | 852.3563
USB ¦ Main | 2019-11-28 06:30 | 6643.7063 |  |  |  | 32.4929
USB ¦ Main | 2019-11-28 18:30 | 6663.1953 |  | 828.2883 | 1624.0838
USB ¦ Main | 2019-11-29 06:30 | 6693.7838 |  |  |  | 2549.0432
USB ¦ Main | 2019-11-29 18:30 | 6703.0928 |  | 1662.3956 | 775.748
USB ¦ Main | 2019-11-30 06:30 | 6703.4628 |  |  |  | 30.8325
USB ¦ Main | 2019-11-30 18:30 | 6704.1827 |  | 45.4116 | 59.9907
USB ¦ Main | 2019-12-01 06:30 | 6704.5326 |  |  |  | 29.1618
USB ¦ Main | 2019-12-01 18:30 | 6705.5724 |  | 57.9047 | 86.6475
USB ¦ Main | 2019-12-02 06:30 | 6705.5724 |  |  |  | 0
USB ¦ Main | 2019-12-02 18:30 | 6716.111 |  | 439.11 | 878.22
USB ¦ Main | 2019-12-03 06:30 | 6716.7709 |  |  |  | 54.99
USB ¦ Main | 2019-12-03 18:30 | 6795.2494 |  | 3297.4313 | 6539.8725
USB ¦ Main | 2019-12-04 06:30 | 6796.1492 |  |  |  | 74.985
USB ¦ Main | 2019-12-04 18:30 | 6807.9877 |  | 530.7656 | 986.5463
USB ¦ Main | 2019-12-05 06:30 | 6808.5478 |  |  |  | 46.6679
USB ¦ Main | 2019-12-05 18:30 | 6820.8261 |  | 534.9305 | 1023.1932
USB ¦ Main | 2019-12-06 06:30 | 6821.276 |  |  |  | 37.4935
USB ¦ Main | 2019-12-06 18:30 | 6831.9749 |  | 464.5336 | 891.5737
USB ¦ Main | 2019-12-07 06:30 | 6832.8148 |  |  |  | 69.9938
USB ¦ Main | 2019-12-07 18:30 | 6834.1446 |  | 90.4031 | 110.8125
USB ¦ Main | 2019-12-08 06:30 | 6834.5645 |  |  |  | 34.995
USB ¦ Main | 2019-12-08 18:30 | 6835.6344 |  | 62.0756 | 89.1562
USB ¦ Main | 2019-12-09 06:30 | 6835.6344 |  |  |  | 0.0029167
USB ¦ Main | 2019-12-09 18:30 | 6848.4828 |  | 535.3496 | 1070.6963
USB ¦ Main | 2019-12-10 06:30 | 6849.2127 |  |  |  | 60.8288
USB ¦ Main | 2019-12-10 18:30 | 6861.1113 |  | 526.1906 | 991.5525
USB ¦ Main | 2019-12-11 06:30 | 6862.1512 |  |  |  | 86.655
USB ¦ Main | 2019-12-11 18:30 | 6874.4795 |  | 557.0053 | 1027.3557
USB ¦ Main | 2019-12-12 06:30 | 6875.3693 |  |  |  | 74.1543
USB ¦ Main | 2019-12-12 18:30 | 6887.8078 |  | 555.3478 | 1036.5413
USB ¦ Main | 2019-12-13 06:30 | 6888.3377 |  |  |  | 44.1563
USB ¦ Main | 2019-12-13 18:30 | 7084.4462 |  | 8193.2681 | 16342.38
USB ¦ Main | 2019-12-14 06:30 | 7084.6862 |  |  |  | 19.995
USB ¦ Main | 2019-12-14 18:30 | 7085.2362 |  | 32.9137 | 45.8325
USB ¦ Main | 2019-12-15 06:30 | 7085.2362 |  |  |  | 0
USB ¦ Main | 2019-12-15 18:30 | 7085.816 |  | 24.1594 | 48.3187
USB ¦ Main | 2019-12-16 06:30 | 7085.816 |  |  |  | 0.0029167
USB ¦ Main | 2019-12-16 18:30 | 7093.5549 |  | 322.4546 | 644.9063
USB ¦ Main | 2019-12-17 06:30 | 7093.5549 |  |  |  | 0.0029167
USB ¦ Main | 2019-12-17 18:30 | 7100.6942 |  | 297.4683 | 594.9338
USB ¦ Main | 2019-12-18 06:30 | 7100.6942 |  |  |  | 0.0029167
USB ¦ Main | 2019-12-18 18:30 | 7105.7633 |  | 211.2146 | 422.4263
USB ¦ Main | 2019-12-19 06:30 | 7105.7633 |  |  |  | 0.0029167
USB ¦ Main | 2019-12-19 18:30 | 7110.7427 |  | 207.474 | 414.945
USB ¦ Main | 2019-12-20 06:30 | 7110.7427 |  |  |  | 0
USB ¦ Main | 2019-12-20 18:30 | 7114.7822 |  | 168.3141 | 336.6282
USB ¦ Main | 2019-12-21 06:30 | 7114.7822 |  |  |  | 0.0018333
USB ¦ Main | 2019-12-21 18:30 | 7114.7822 |  | 0.00091667 | 0
USB ¦ Main | 2019-12-22 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-22 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-23 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-23 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-24 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-24 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-25 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-25 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-26 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-26 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-27 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-27 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-28 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-28 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-29 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-29 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-30 06:30 | 7114.7822 |  |  |  | 0
USB ¦ Main | 2019-12-30 18:30 | 7114.7822 |  | 0 | 0
USB ¦ Main | 2019-12-31 06:30 | 7115.1822 |  |  |  | 33.3298
USB ¦ Main | 2019-12-31 18:30 | 7115.1822 |  | 16.665 | 0.00025
USB ¦ Main | 2020-01-01 06:30 | 7115.1822 |  |  |  | 0
USB ¦ Main | 2020-01-01 18:30 | 7115.1822 |  | 0 | 0
USB ¦ Main | 2020-01-02 06:30 | 7115.1822 |  |  |  | 0
USB ¦ Main | 2020-01-02 18:30 | 7119.1815 |  | 166.6378 | 333.2757
USB ¦ Main | 2020-01-03 06:30 | 7119.1815 |  |  |  | 0.0018333
USB ¦ Main | 2020-01-03 18:30 | 7119.9611 |  | 32.4825 | 64.9632
USB ¦ Main | 2020-01-04 06:30 | 7120.031 |  |  |  | 5.8293
USB ¦ Main | 2020-01-04 18:30 | 7120.1709 |  | 8.7422 | 11.655
USB ¦ Main | 2020-01-05 06:30 | 7120.1709 |  |  |  | 0
USB ¦ Main | 2020-01-05 18:30 | 7120.2708 |  | 4.1625 | 8.325
USB ¦ Main | 2020-01-06 06:30 | 7120.2808 |  |  |  | 0.83225
USB ¦ Main | 2020-01-06 18:30 | 7129.7392 |  | 394.5178 | 788.2034
USB ¦ Main | 2020-01-07 06:30 | 7129.959 |  |  |  | 18.3168
USB ¦ Main | 2020-01-07 18:30 | 7138.3572 |  | 359.0812 | 699.8457
USB ¦ Main | 2020-01-08 06:30 | 7138.7572 |  |  |  | 33.331
USB ¦ Main | 2020-01-08 18:30 | 7147.5255 |  | 382.0149 | 730.6987
USB ¦ Main | 2020-01-09 06:30 | 7147.6754 |  |  |  | 12.4904
USB ¦ Main | 2020-01-09 18:30 | 7156.6539 |  | 380.3471 | 748.2038
USB ¦ Main | 2020-01-10 06:30 | 7156.6539 |  |  |  | 0.0029167
USB ¦ Main | 2020-01-10 18:30 | 7165.9925 |  | 389.1108 | 778.2187
USB ¦ Main | 2020-01-11 06:30 | 7166.4125 |  |  |  | 34.9988
USB ¦ Main | 2020-01-11 18:30 | 7167.0924 |  | 45.8269 | 56.655
USB ¦ Main | 2020-01-12 06:30 | 7167.1223 |  |  |  | 2.4972
USB ¦ Main | 2020-01-12 18:30 | 7168.402 |  | 54.5681 | 106.639
USB ¦ Main | 2020-01-13 06:30 | 7168.792 |  |  |  | 32.5012
USB ¦ Main | 2020-01-13 18:30 | 7180.1504 |  | 489.5185 | 946.5357
USB ¦ Main | 2020-01-14 06:30 | 7180.3404 |  |  |  | 15.826
USB ¦ Main | 2020-01-14 18:30 | 7191.3088 |  | 464.933 | 914.04
USB ¦ Main | 2020-01-15 06:30 | 7191.9087 |  |  |  | 49.9867
USB ¦ Main | 2020-01-15 18:30 | 7201.8771 |  | 440.3462 | 830.7057
USB ¦ Main | 2020-01-16 06:30 | 7201.9871 |  |  |  | 9.1593
USB ¦ Main | 2020-01-16 18:30 | 7212.4656 |  | 441.1865 | 873.2137
USB ¦ Main | 2020-01-17 06:30 | 7212.7256 |  |  |  | 21.6638
USB ¦ Main | 2020-01-17 18:30 | 7222.6544 |  | 424.531 | 827.3982
USB ¦ Main | 2020-01-18 06:30 | 7222.6644 |  |  |  | 0.83433
USB ¦ Main | 2020-01-18 18:30 | 7223.964 |  | 54.569 | 108.3038
USB ¦ Main | 2020-01-19 06:30 | 7224.174 |  |  |  | 17.5012
USB ¦ Main | 2020-01-19 18:30 | 7224.4838 |  | 21.6572 | 25.8132
USB ¦ Main | 2020-01-20 06:30 | 7224.5038 |  |  |  | 1.6668
USB ¦ Main | 2020-01-20 18:30 | 7236.7422 |  | 510.7678 | 1019.8687
USB ¦ Main | 2020-01-21 06:30 | 7237.2321 |  |  |  | 40.8263
USB ¦ Main | 2020-01-21 18:30 | 7248.401 |  | 485.7806 | 930.735
USB ¦ Main | 2020-01-22 06:30 | 7248.411 |  |  |  | 0.8325
USB ¦ Main | 2020-01-22 18:30 | 7260.6295 |  | 509.5238 | 1018.215
USB ¦ Main | 2020-01-23 06:30 | 7261.1193 |  |  |  | 40.815
USB ¦ Main | 2020-01-23 18:30 | 7273.7675 |  | 547.4166 | 1054.0182
USB ¦ Main | 2020-01-24 06:30 | 7274.2175 |  |  |  | 37.4935
USB ¦ Main | 2020-01-24 18:30 | 7414.8861 | 6020 | 5879.9405 | 11722.3875
USB ¦ Main | 2020-01-25 06:30 | 7414.8861 |  |  |  | 0
USB ¦ Main | 2020-01-25 18:30 | 7416.6657 |  | 74.1516 | 148.3032
USB ¦ Main | 2020-01-26 06:30 | 7416.8857 |  |  |  | 18.3301
USB ¦ Main | 2020-01-26 18:30 | 7417.1057 |  | 18.33 | 18.3299
USB ¦ Main | 2020-01-27 06:30 | 7417.3156 |  |  |  | 17.4978
USB ¦ Main | 2020-01-27 18:30 | 7428.5543 | 6040 | 477.0262 | 936.5547
USB ¦ Main | 2020-01-28 06:30 | 7428.9742 |  |  |  | 34.9951
USB ¦ Main | 2020-01-28 18:30 | 7441.753 | 6051 | 549.945 | 1064.8949
USB ¦ Main | 2020-01-29 06:30 | 7442.7629 |  |  |  | 84.1588
USB ¦ Main | 2020-01-29 18:30 | 7660.6315 | 6131 | 9119.9372 | 18155.7155
USB ¦ Main | 2020-01-30 06:30 | 7661.0614 |  |  |  | 35.8275
USB ¦ Main | 2020-01-30 18:30 | 7673.0201 |  | 516.1931 | 996.5588
USB ¦ Main | 2020-01-31 06:30 | 7673.57 |  |  |  | 45.8287
USB ¦ Main | 2020-01-31 18:30 | 7682.5687 |  | 397.8572 | 749.8857
USB ¦ Main | 2020-02-01 06:30 | 7682.7687 |  |  |  | 16.6668
USB ¦ Main | 2020-02-01 18:30 | 7682.9886 |  | 17.4965 | 18.3262
USB ¦ Main | 2020-02-02 06:30 | 7682.9886 |  |  |  | 0.0029167
USB ¦ Main | 2020-02-02 18:30 | 7682.9886 |  | 0.0014583 | 0
USB ¦ Main | 2020-02-03 06:30 | 7682.9886 |  |  |  | 0
USB ¦ Main | 2020-02-03 18:30 | 7695.6973 |  | 529.5291 | 1059.0582
USB ¦ Main | 2020-02-04 06:30 | 7695.6973 |  |  |  | 0.0018333
USB ¦ Main | 2020-02-04 18:30 | 7707.8261 |  | 505.365 | 1010.7282
USB ¦ Main | 2020-02-05 06:30 | 7708.2758 |  |  |  | 37.4793
USB ¦ Main | 2020-02-05 18:30 | 7720.1146 |  | 512.0213 | 986.5632
USB ¦ Main | 2020-02-06 06:30 | 7720.1146 |  |  |  | 0.0018333
USB ¦ Main | 2020-02-06 18:30 | 7952.3031 |  | 9674.5228 | 19349.0438
USB ¦ Main | 2020-02-07 06:30 | 7952.5032 |  |  |  | 16.6688
USB ¦ Main | 2020-02-07 18:30 | 7964.6418 |  | 514.1119 | 1011.555
USB ¦ Main | 2020-02-08 06:30 | 7964.8418 |  |  |  | 16.6642
USB ¦ Main | 2020-02-08 18:30 | 7965.2617 |  | 25.8287 | 34.9932
USB ¦ Main | 2020-02-09 06:30 | 7965.4617 |  |  |  | 16.6668
USB ¦ Main | 2020-02-09 18:30 | 7965.6816 |  | 17.4965 | 18.3263
USB ¦ Main | 2020-02-10 06:30 | 7965.8816 |  |  |  | 16.6612
USB ¦ Main | 2020-02-10 18:30 | 7977.74 |  | 502.4306 | 988.2
USB ¦ Main | 2020-02-11 06:30 | 7977.74 |  |  |  | 0
USB ¦ Main | 2020-02-11 18:30 | 7990.1685 |  | 517.8544 | 1035.7087
USB ¦ Main | 2020-02-12 06:30 | 7990.3785 |  |  |  | 17.5013
USB ¦ Main | 2020-02-12 18:30 | 8201.8369 |  | 8819.52 | 17621.5387
USB ¦ Main | 2020-02-13 06:30 | 8201.837 |  |  |  | 0.00375
USB ¦ Main | 2020-02-13 18:30 | 8213.3756 |  | 480.7763 | 961.5488
USB ¦ Main | 2020-02-14 06:30 | 8213.5756 |  |  |  | 16.6688
USB ¦ Main | 2020-02-14 18:30 | 8239.3244 |  | 1081.2019 | 2145.735
USB ¦ Main | 2020-02-15 06:30 | 8239.3244 |  |  |  | 0
USB ¦ Main | 2020-02-15 18:30 | 8240.2443 |  | 38.3287 | 76.6575
USB ¦ Main | 2020-02-16 06:30 | 8240.2443 |  |  |  | 0
USB ¦ Main | 2020-02-16 18:30 | 8240.4742 |  | 9.5794 | 19.1588
USB ¦ Main | 2020-02-17 06:30 | 8240.4742 |  |  |  | 0.0029167
USB ¦ Main | 2020-02-17 18:30 | 8251.953 |  | 478.284 | 956.565
USB ¦ Main | 2020-02-18 06:30 | 8252.4029 |  |  |  | 37.4925
USB ¦ Main | 2020-02-18 18:30 | 8458.0714 |  | 8588.265 | 17139.0375
USB ¦ Main | 2020-02-19 06:30 | 8458.4213 |  |  |  | 29.16
USB ¦ Main | 2020-02-19 18:30 | 8470.6196 | 6356 | 522.8438 | 1016.5275
USB ¦ Main | 2020-02-20 06:30 | 8470.8196 |  |  |  | 16.6642
USB ¦ Main | 2020-02-20 18:30 | 8484.568 | 6430 | 581.1821 | 1145.7
USB ¦ Main | 2020-02-21 06:30 | 8484.7878 |  |  |  | 18.315
USB ¦ Main | 2020-02-21 18:30 | 8494.4665 | 6439 | 412.4391 | 806.5632
USB ¦ Main | 2020-02-22 06:30 | 8495.6964 |  |  |  | 102.4889
USB ¦ Main | 2020-02-22 18:30 | 8498.026 |  | 148.3125 | 194.1361
USB ¦ Main | 2020-02-23 06:30 | 8498.0261 |  |  |  | 0.0018333
USB ¦ Main | 2020-02-23 18:30 | 8498.916 |  | 37.0809 | 74.16
USB ¦ Main | 2020-02-24 06:30 | 8499.2559 |  |  |  | 28.3275
USB ¦ Main | 2020-02-24 18:30 | 8508.3942 | 6451 | 394.9256 | 761.5238
USB ¦ Main | 2020-02-25 06:30 | 8508.3942 |  |  |  | 0.0029167
USB ¦ Main | 2020-02-25 18:30 | 8735.2229 | 6462 | 9451.1968 | 18902.3907
USB ¦ Main | 2020-02-26 06:30 | 8735.9528 |  |  |  | 60.8268
USB ¦ Main | 2020-02-26 18:30 | 8830.3716 | 6472 | 3964.5272 | 7868.2275
USB ¦ Main | 2020-02-27 06:30 | 9052.6396 |  |  |  | 18522.3362
USB ¦ Main | 2020-02-27 18:30 | 9128.9285 |  | 12439.8703 | 6357.4045
USB ¦ Main | 2020-02-28 06:30 | 9129.0284 |  |  |  | 8.3264
USB ¦ Main | 2020-02-28 18:30 | 9139.1268 |  | 424.9303 | 841.5342
USB ¦ Main | 2020-02-29 06:30 | 9139.4665 |  |  |  | 28.3079
USB ¦ Main | 2020-02-29 18:30 | 9139.8961 |  | 32.0527 | 35.7975
USB ¦ Main | 2020-03-01 06:30 | 9139.966 |  |  |  | 5.8275
USB ¦ Main | 2020-03-01 18:30 | 9140.7552 |  | 35.7975 | 65.7675
USB ¦ Main | 2020-03-02 06:30 | 9140.8551 |  |  |  | 8.325
USB ¦ Main | 2020-03-02 18:30 | 9151.6033 |  | 452.0053 | 895.6857
USB ¦ Main | 2020-03-03 06:30 | 9151.933 |  |  |  | 27.4741
USB ¦ Main | 2020-03-03 18:30 | 9162.9915 |  | 474.5063 | 921.5384
USB ¦ Main | 2020-03-04 06:30 | 9163.3811 |  |  |  | 32.4689
USB ¦ Main | 2020-03-04 18:30 | 9174.7792 |  | 491.1562 | 949.8436
USB ¦ Main | 2020-03-05 06:30 | 9174.989 |  |  |  | 17.4841
USB ¦ Main | 2020-03-05 18:30 | 9187.5171 |  | 530.745 | 1044.0059
USB ¦ Main | 2020-03-06 06:30 | 9188.0066 |  |  |  | 40.7939
USB ¦ Main | 2020-03-06 18:30 | 9197.975 |  | 435.7472 | 830.7004
USB ¦ Main | 2020-03-07 06:30 | 9198.2248 |  |  |  | 20.8125
USB ¦ Main | 2020-03-07 18:30 | 9200.2934 |  | 96.5981 | 172.3838
USB ¦ Main | 2020-03-08 06:30 | 9200.4033 |  |  |  | 9.1604
USB ¦ Main | 2020-03-08 18:30 | 9200.8029 |  | 21.2302 | 33.3
USB ¦ Main | 2020-03-09 06:30 | 9200.8928 |  |  |  | 7.4925
USB ¦ Main | 2020-03-09 18:30 | 9212.3811 |  | 482.4253 | 957.3582
USB ¦ Main | 2020-03-10 06:30 | 9212.6709 |  |  |  | 24.1443
USB ¦ Main | 2020-03-10 18:30 | 9224.499 |  | 504.9122 | 985.68
USB ¦ Main | 2020-03-11 06:30 | 9224.8288 |  |  |  | 27.48
USB ¦ Main | 2020-03-11 18:30 | 9234.977 |  | 436.5825 | 845.685
USB ¦ Main | 2020-03-12 06:30 | 9235.2267 |  |  |  | 20.8118
USB ¦ Main | 2020-03-12 18:30 | 9245.775 |  | 449.9156 | 879.0194
USB ¦ Main | 2020-03-13 06:30 | 9246.0447 |  |  |  | 22.4804
USB ¦ Main | 2020-03-13 18:30 | 9253.463 |  | 320.334 | 618.1875
USB ¦ Main | 2020-03-14 06:30 | 9253.5229 |  |  |  | 4.995
USB ¦ Main | 2020-03-14 18:30 | 9253.9525 |  | 20.3962 | 35.7975
USB ¦ Main | 2020-03-15 06:30 | 9254.2322 |  |  |  | 23.31
USB ¦ Main | 2020-03-15 18:30 | 9254.5019 |  | 22.8938 | 22.4775
USB ¦ Main | 2020-03-16 06:30 | 9254.5519 |  |  |  | 4.1625
USB ¦ Main | 2020-03-16 18:30 | 9261.2202 |  | 279.9253 | 555.6882
USB ¦ Main | 2020-03-17 06:30 | 9261.3101 |  |  |  | 7.4941
USB ¦ Main | 2020-03-17 18:30 | 9264.2187 |  | 124.9378 | 242.3815
USB ¦ Main | 2020-03-18 06:30 | 9265.3183 |  |  |  | 91.6368
USB ¦ Main | 2020-03-18 18:30 | 9267.7468 |  | 147.0052 | 202.3736
USB ¦ Main | 2020-03-19 06:30 | 9267.7768 |  |  |  | 2.4973
USB ¦ Main | 2020-03-19 18:30 | 9269.3355 |  | 66.195 | 129.8928
USB ¦ Main | 2020-03-20 06:30 | 9269.3554 |  |  |  | 1.665
USB ¦ Main | 2020-03-20 18:30 | 9270.2447 |  | 37.8844 | 74.1038
USB ¦ Main | 2020-03-21 06:30 | 9270.2447 |  |  |  | 0.0029167
USB ¦ Main | 2020-03-21 18:30 | 9270.2547 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-03-22 06:30 | 9270.2547 |  |  |  | 0
USB ¦ Main | 2020-03-22 18:30 | 9270.2547 |  | 0 | 0
USB ¦ Main | 2020-03-23 06:30 | 9270.2647 |  |  |  | 0.83225
USB ¦ Main | 2020-03-23 18:30 | 9270.7743 |  | 21.6478 | 42.4634
USB ¦ Main | 2020-03-24 06:30 | 9270.7743 |  |  |  | 0.0018333
USB ¦ Main | 2020-03-24 18:30 | 9271.394 |  | 25.8225 | 51.6432
USB ¦ Main | 2020-03-25 06:30 | 9271.394 |  |  |  | 0.0018333
USB ¦ Main | 2020-03-25 18:30 | 9271.414 |  | 0.83342 | 1.665
USB ¦ Main | 2020-03-26 06:30 | 9271.414 |  |  |  | 0
USB ¦ Main | 2020-03-26 18:30 | 9271.444 |  | 1.2487 | 2.4975
USB ¦ Main | 2020-03-27 06:30 | 9271.454 |  |  |  | 0.83225
USB ¦ Main | 2020-03-27 18:30 | 9271.454 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-03-28 06:30 | 9271.454 |  |  |  | 0
USB ¦ Main | 2020-03-28 18:30 | 9271.454 |  | 0 | 0
USB ¦ Main | 2020-03-29 06:30 | 9271.464 |  |  |  | 0.83225
USB ¦ Main | 2020-03-29 18:30 | 9271.464 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-03-30 06:30 | 9271.464 |  |  |  | 0
USB ¦ Main | 2020-03-30 18:30 | 9271.4739 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-03-31 06:30 | 9271.4739 |  |  |  | 0
USB ¦ Main | 2020-03-31 18:30 | 9271.4839 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-04-01 06:30 | 9271.4839 |  |  |  | 0
USB ¦ Main | 2020-04-01 18:30 | 9271.5439 |  | 2.4975 | 4.995
USB ¦ Main | 2020-04-02 06:30 | 9271.5439 |  |  |  | 0
USB ¦ Main | 2020-04-02 18:30 | 9271.5439 |  | 0 | 0
USB ¦ Main | 2020-04-03 06:30 | 9271.5439 |  |  |  | 0
USB ¦ Main | 2020-04-03 18:30 | 9271.7337 |  | 7.9087 | 15.8175
USB ¦ Main | 2020-04-04 06:30 | 9271.7437 |  |  |  | 0.83225
USB ¦ Main | 2020-04-04 18:30 | 9271.7437 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-04-05 06:30 | 9271.7437 |  |  |  | 0
USB ¦ Main | 2020-04-05 18:30 | 9271.7437 |  | 0 | 0
USB ¦ Main | 2020-04-06 06:30 | 9271.7437 |  |  |  | 0
USB ¦ Main | 2020-04-06 18:30 | 9271.7936 |  | 2.0813 | 4.1625
USB ¦ Main | 2020-04-07 06:30 | 9271.8036 |  |  |  | 0.83225
USB ¦ Main | 2020-04-07 18:30 | 9271.8236 |  | 1.2487 | 1.6653
USB ¦ Main | 2020-04-08 06:30 | 9271.8336 |  |  |  | 0.83225
USB ¦ Main | 2020-04-08 18:30 | 9279.3519 |  | 313.6781 | 626.524
USB ¦ Main | 2020-04-09 06:30 | 9285.9796 |  |  |  | 552.3095
USB ¦ Main | 2020-04-09 18:30 | 9292.1775 |  | 534.4018 | 516.4941
USB ¦ Main | 2020-04-10 06:30 | 9298.8052 |  |  |  | 552.308
USB ¦ Main | 2020-04-10 18:30 | 9305.2431 |  | 544.3997 | 536.4913
USB ¦ Main | 2020-04-11 06:30 | 9311.8109 |  |  |  | 547.3118
USB ¦ Main | 2020-04-11 18:30 | 9318.2188 |  | 540.6525 | 533.9932
USB ¦ Main | 2020-04-12 06:30 | 9324.7965 |  |  |  | 548.1441
USB ¦ Main | 2020-04-12 18:30 | 9331.2244 |  | 541.9012 | 535.6584
USB ¦ Main | 2020-04-13 06:30 | 9337.8121 |  |  |  | 548.9764
USB ¦ Main | 2020-04-13 18:30 | 9344.27 |  | 543.5663 | 538.1561
USB ¦ Main | 2020-04-14 06:30 | 9350.5777 |  |  |  | 525.6441
USB ¦ Main | 2020-04-14 18:30 | 9351.2674 |  | 291.5606 | 57.4772
USB ¦ Main | 2020-04-15 06:30 | 9351.2675 |  |  |  | 0.0029167
USB ¦ Main | 2020-04-15 18:30 | 9354.6074 |  | 139.164 | 278.325
USB ¦ Main | 2020-04-16 06:30 | 9354.6274 |  |  |  | 1.665
USB ¦ Main | 2020-04-16 18:30 | 9354.7473 |  | 5.8303 | 9.9957
USB ¦ Main | 2020-04-17 06:30 | 9354.7473 |  |  |  | 0.0018333
USB ¦ Main | 2020-04-17 18:30 | 9354.7473 |  | 0.00091667 | 0
USB ¦ Main | 2020-04-18 06:30 | 9354.7573 |  |  |  | 0.83225
USB ¦ Main | 2020-04-18 18:30 | 9354.7573 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-04-19 06:30 | 9354.7573 |  |  |  | 0
USB ¦ Main | 2020-04-19 18:30 | 9354.7573 |  | 0 | 0
USB ¦ Main | 2020-04-20 06:30 | 9354.7573 |  |  |  | 0
USB ¦ Main | 2020-04-20 18:30 | 9354.8572 |  | 4.1625 | 8.325
USB ¦ Main | 2020-04-21 06:30 | 9354.8572 |  |  |  | 0
USB ¦ Main | 2020-04-21 18:30 | 9355.117 |  | 10.8253 | 21.6507
USB ¦ Main | 2020-04-22 06:30 | 9355.127 |  |  |  | 0.83433
USB ¦ Main | 2020-04-22 18:30 | 9358.5066 |  | 141.2334 | 281.6325
USB ¦ Main | 2020-04-23 06:30 | 9358.5166 |  |  |  | 0.83225
USB ¦ Main | 2020-04-23 18:30 | 9358.6165 |  | 4.5787 | 8.3253
USB ¦ Main | 2020-04-24 06:30 | 9358.6265 |  |  |  | 0.83225
USB ¦ Main | 2020-04-24 18:30 | 9358.6365 |  | 0.8325 | 0.83275
USB ¦ Main | 2020-04-25 06:30 | 9358.6365 |  |  |  | 0
USB ¦ Main | 2020-04-25 18:30 | 9358.6365 |  | 0 | 0
USB ¦ Main | 2020-04-26 06:30 | 9358.6365 |  |  |  | 0
USB ¦ Main | 2020-04-26 18:30 | 9358.6465 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-04-27 06:30 | 9358.6465 |  |  |  | 0
USB ¦ Main | 2020-04-27 18:30 | 9358.6864 |  | 1.665 | 3.33
USB ¦ Main | 2020-04-28 06:30 | 9358.6964 |  |  |  | 0.83225
USB ¦ Main | 2020-04-28 18:30 | 9358.8563 |  | 7.0791 | 13.3259
USB ¦ Main | 2020-04-29 06:30 | 9358.8664 |  |  |  | 0.83433
USB ¦ Main | 2020-04-29 18:30 | 9361.6162 |  | 114.9928 | 229.1512
USB ¦ Main | 2020-04-30 06:30 | 9361.8062 |  |  |  | 15.8343
USB ¦ Main | 2020-04-30 18:30 | 9362.126 |  | 21.2415 | 26.6486
USB ¦ Main | 2020-05-01 06:30 | 9362.146 |  |  |  | 1.665
USB ¦ Main | 2020-05-01 18:30 | 9362.2858 |  | 6.66 | 11.655
USB ¦ Main | 2020-05-02 06:30 | 9362.2958 |  |  |  | 0.8325
USB ¦ Main | 2020-05-02 18:30 | 9362.3058 |  | 0.8325 | 0.8325
USB ¦ Main | 2020-05-03 06:30 | 9362.3158 |  |  |  | 0.8325
USB ¦ Main | 2020-05-03 18:30 | 9362.3358 |  | 1.2487 | 1.665
USB ¦ Main | 2020-05-04 06:30 | 9362.3358 |  |  |  | 0
USB ¦ Main | 2020-05-04 18:30 | 9362.4556 |  | 4.995 | 9.99
USB ¦ Main | 2020-05-05 06:30 | 9362.4656 |  |  |  | 0.8325
USB ¦ Main | 2020-05-05 18:30 | 9362.6056 |  | 6.2466 | 11.6607
USB ¦ Main | 2020-05-06 06:30 | 9362.6156 |  |  |  | 0.83433
USB ¦ Main | 2020-05-06 18:30 | 9365.8253 |  | 134.1572 | 267.48
USB ¦ Main | 2020-05-07 06:30 | 9365.8253 |  |  |  | 0
USB ¦ Main | 2020-05-07 18:30 | 9366.0152 |  | 7.9116 | 15.8232
USB ¦ Main | 2020-05-08 06:30 | 9366.0252 |  |  |  | 0.83408
USB ¦ Main | 2020-05-08 18:30 | 9366.0252 |  | 0.41717 | 0.00025
USB ¦ Main | 2020-05-09 06:30 | 9366.0252 |  |  |  | 0
USB ¦ Main | 2020-05-09 18:30 | 9366.0252 |  | 0 | 0
USB ¦ Main | 2020-05-10 06:30 | 9366.0252 |  |  |  | 0
USB ¦ Main | 2020-05-10 18:30 | 9366.0452 |  | 0.8325 | 1.665
USB ¦ Main | 2020-05-11 06:30 | 9366.0452 |  |  |  | 0
USB ¦ Main | 2020-05-11 18:30 | 9366.225 |  | 7.4925 | 14.985
USB ¦ Main | 2020-05-12 06:30 | 9366.225 |  |  |  | 0
USB ¦ Main | 2020-05-12 18:30 | 9366.225 |  | 0 | 0
USB ¦ Main | 2020-05-13 06:30 | 9366.235 |  |  |  | 0.83225
USB ¦ Main | 2020-05-13 18:30 | 9374.3235 |  | 337.4353 | 674.0384
USB ¦ Main | 2020-05-14 06:30 | 9380.4916 |  |  |  | 514.013
USB ¦ Main | 2020-05-14 18:30 | 9386.6399 |  | 513.1837 | 512.3545
USB ¦ Main | 2020-05-15 06:30 | 9392.7881 |  |  |  | 512.348
USB ¦ Main | 2020-05-15 18:30 | 9398.6762 |  | 501.5147 | 490.6813
USB ¦ Main | 2020-05-16 06:30 | 9405.0841 |  |  |  | 533.9921
USB ¦ Main | 2020-05-16 18:30 | 9411.4021 |  | 530.2463 | 526.5004
USB ¦ Main | 2020-05-17 06:30 | 9417.7901 |  |  |  | 532.3272
USB ¦ Main | 2020-05-17 18:30 | 9424.0781 |  | 528.165 | 524.0028
USB ¦ Main | 2020-05-18 06:30 | 9430.466 |  |  |  | 532.3271
USB ¦ Main | 2020-05-18 18:30 | 9431.8355 |  | 323.2266 | 114.1261
USB ¦ Main | 2020-05-19 06:30 | 9431.8555 |  |  |  | 1.6668
USB ¦ Main | 2020-05-19 18:30 | 9431.9855 |  | 6.2475 | 10.8282
USB ¦ Main | 2020-05-20 06:30 | 9431.9855 |  |  |  | 0.0018333
USB ¦ Main | 2020-05-20 18:30 | 9434.7653 |  | 115.8253 | 231.6487
USB ¦ Main | 2020-05-21 06:30 | 9434.7653 |  |  |  | 0.0029167
USB ¦ Main | 2020-05-21 18:30 | 9434.9652 |  | 8.3293 | 16.6557
USB ¦ Main | 2020-05-22 06:30 | 9434.9752 |  |  |  | 0.83433
USB ¦ Main | 2020-05-22 18:30 | 9434.9852 |  | 0.83342 | 0.8325
USB ¦ Main | 2020-05-23 06:30 | 9434.9852 |  |  |  | 0
USB ¦ Main | 2020-05-23 18:30 | 9434.9852 |  | 0 | 0
USB ¦ Main | 2020-05-24 06:30 | 9434.9852 |  |  |  | 0
USB ¦ Main | 2020-05-24 18:30 | 9434.9852 |  | 0 | 0
USB ¦ Main | 2020-05-25 06:30 | 9435.0052 |  |  |  | 1.665
USB ¦ Main | 2020-05-25 18:30 | 9435.0052 |  | 0.8325 | 0
USB ¦ Main | 2020-05-26 06:30 | 9435.0052 |  |  |  | 0
USB ¦ Main | 2020-05-26 18:30 | 9435.3949 |  | 16.2394 | 32.4788
USB ¦ Main | 2020-05-27 06:30 | 9435.3949 |  |  |  | 0.0029167
USB ¦ Main | 2020-05-27 18:30 | 9438.0447 |  | 110.409 | 220.815
USB ¦ Main | 2020-05-28 06:30 | 9438.0447 |  |  |  | 0
USB ¦ Main | 2020-05-28 18:30 | 9438.1047 |  | 2.4975 | 4.995
USB ¦ Main | 2020-05-29 06:30 | 9438.1147 |  |  |  | 0.8325
USB ¦ Main | 2020-05-29 18:30 | 9438.1147 |  | 0.41625 | 0
USB ¦ Main | 2020-05-30 06:30 | 9438.1846 |  |  |  | 5.8262
USB ¦ Main | 2020-05-30 18:30 | 9438.2046 |  | 3.7463 | 1.6663
USB ¦ Main | 2020-05-31 06:30 | 9438.2146 |  |  |  | 0.83225
USB ¦ Main | 2020-05-31 18:30 | 9438.2945 |  | 3.7463 | 6.6603
USB ¦ Main | 2020-06-01 06:30 | 9438.3644 |  |  |  | 5.8262
USB ¦ Main | 2020-06-01 18:30 | 9438.4643 |  | 7.0762 | 8.3263
USB ¦ Main | 2020-06-02 06:30 | 9438.4643 |  |  |  | 0
USB ¦ Main | 2020-06-02 18:30 | 9438.7141 |  | 10.4091 | 20.8182
USB ¦ Main | 2020-06-03 06:30 | 9438.7841 |  |  |  | 5.8293
USB ¦ Main | 2020-06-03 18:30 | 9442.1133 |  | 141.6328 | 277.4363
USB ¦ Main | 2020-06-04 06:30 | 9442.1133 |  |  |  | 0.0029167
USB ¦ Main | 2020-06-04 18:30 | 9442.1633 |  | 2.0827 | 4.1625
USB ¦ Main | 2020-06-05 06:30 | 9442.1633 |  |  |  | 0
USB ¦ Main | 2020-06-05 18:30 | 9442.1933 |  | 1.2487 | 2.4975
USB ¦ Main | 2020-06-06 06:30 | 9442.2033 |  |  |  | 0.8325
USB ¦ Main | 2020-06-06 18:30 | 9442.2033 |  | 0.41625 | 0
USB ¦ Main | 2020-06-07 06:30 | 9442.2033 |  |  |  | 0
USB ¦ Main | 2020-06-07 18:30 | 9442.2033 |  | 0 | 0
USB ¦ Main | 2020-06-08 06:30 | 9442.2033 |  |  |  | 0
USB ¦ Main | 2020-06-08 18:30 | 9442.3931 |  | 7.9116 | 15.8232
USB ¦ Main | 2020-06-09 06:30 | 9442.3932 |  |  |  | 0.0018333
USB ¦ Main | 2020-06-09 18:30 | 9442.4331 |  | 1.6659 | 3.33
USB ¦ Main | 2020-06-10 06:30 | 9442.4431 |  |  |  | 0.8325
USB ¦ Main | 2020-06-10 18:30 | 9445.2326 |  | 116.6456 | 232.4588
USB ¦ Main | 2020-06-11 06:30 | 9445.2326 |  |  |  | 0.0029167
USB ¦ Main | 2020-06-11 18:30 | 9445.4626 |  | 9.5808 | 19.1588
USB ¦ Main | 2020-06-12 06:30 | 9445.4626 |  |  |  | 0.0029167
USB ¦ Main | 2020-06-12 18:30 | 9445.4726 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-06-13 06:30 | 9445.4726 |  |  |  | 0
USB ¦ Main | 2020-06-13 18:30 | 9445.4926 |  | 0.8325 | 1.665
USB ¦ Main | 2020-06-14 06:30 | 9445.4926 |  |  |  | 0
USB ¦ Main | 2020-06-14 18:30 | 9445.4926 |  | 0 | 0
USB ¦ Main | 2020-06-15 06:30 | 9445.4926 |  |  |  | 0
USB ¦ Main | 2020-06-15 18:30 | 9445.4926 |  | 0 | 0
USB ¦ Main | 2020-06-16 06:30 | 9445.4926 |  |  |  | 0
USB ¦ Main | 2020-06-16 18:30 | 9445.6125 |  | 4.9978 | 9.9957
USB ¦ Main | 2020-06-17 06:30 | 9445.6125 |  |  |  | 0.0018333
USB ¦ Main | 2020-06-17 18:30 | 9448.2124 |  | 108.3272 | 216.6525
USB ¦ Main | 2020-06-18 06:30 | 9448.2124 |  |  |  | 0
USB ¦ Main | 2020-06-18 18:30 | 9448.4722 |  | 10.8281 | 21.6562
USB ¦ Main | 2020-06-19 06:30 | 9448.4723 |  |  |  | 0.0029167
USB ¦ Main | 2020-06-19 18:30 | 9448.4823 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-06-20 06:30 | 9448.4823 |  |  |  | 0
USB ¦ Main | 2020-06-20 18:30 | 9448.4823 |  | 0 | 0
USB ¦ Main | 2020-06-21 06:30 | 9448.4823 |  |  |  | 0
USB ¦ Main | 2020-06-21 18:30 | 9448.4823 |  | 0 | 0
USB ¦ Main | 2020-06-22 06:30 | 9448.4823 |  |  |  | 0
USB ¦ Main | 2020-06-22 18:30 | 9448.6122 |  | 5.4141 | 10.8282
USB ¦ Main | 2020-06-23 06:30 | 9448.6122 |  |  |  | 0.0018333
USB ¦ Main | 2020-06-23 18:30 | 9448.6422 |  | 1.2497 | 2.4975
USB ¦ Main | 2020-06-24 06:30 | 9448.6422 |  |  |  | 0
USB ¦ Main | 2020-06-24 18:30 | 9452.2704 |  | 151.1775 | 302.355
USB ¦ Main | 2020-06-25 06:30 | 9456.0268 |  |  |  | 313.0274
USB ¦ Main | 2020-06-25 18:30 | 9458.585 |  | 263.1066 | 213.1858
USB ¦ Main | 2020-06-26 06:30 | 9458.585 |  |  |  | 0.0018333
USB ¦ Main | 2020-06-26 18:30 | 9458.605 |  | 0.83342 | 1.665
USB ¦ Main | 2020-06-27 06:30 | 9458.605 |  |  |  | 0
USB ¦ Main | 2020-06-27 18:30 | 9458.615 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-06-28 06:30 | 9458.615 |  |  |  | 0
USB ¦ Main | 2020-06-28 18:30 | 9458.635 |  | 0.8325 | 1.665
USB ¦ Main | 2020-06-29 06:30 | 9458.645 |  |  |  | 0.83225
USB ¦ Main | 2020-06-29 18:30 | 9458.655 |  | 0.8325 | 0.83275
USB ¦ Main | 2020-06-30 06:30 | 9458.665 |  |  |  | 0.8325
USB ¦ Main | 2020-06-30 18:30 | 9458.7049 |  | 2.0813 | 3.33
USB ¦ Main | 2020-07-01 06:30 | 9458.7049 |  |  |  | 0
USB ¦ Main | 2020-07-01 18:30 | 9459.1946 |  | 20.4019 | 40.8037
USB ¦ Main | 2020-07-02 06:30 | 9459.1946 |  |  |  | 0.0029167
USB ¦ Main | 2020-07-02 18:30 | 9459.8443 |  | 27.0746 | 54.1463
USB ¦ Main | 2020-07-03 06:30 | 9459.8444 |  |  |  | 0.0029167
USB ¦ Main | 2020-07-03 18:30 | 9459.8444 |  | 0.0014583 | 0
USB ¦ Main | 2020-07-04 06:30 | 9459.8444 |  |  |  | 0
USB ¦ Main | 2020-07-04 18:30 | 9459.8444 |  | 0 | 0
USB ¦ Main | 2020-07-05 06:30 | 9459.8444 |  |  |  | 0
USB ¦ Main | 2020-07-05 18:30 | 9459.8444 |  | 0 | 0
USB ¦ Main | 2020-07-06 06:30 | 9459.8444 |  |  |  | 0
USB ¦ Main | 2020-07-06 18:30 | 9460.0243 |  | 7.4953 | 14.9907
USB ¦ Main | 2020-07-07 06:30 | 9460.0243 |  |  |  | 0.0018333
USB ¦ Main | 2020-07-07 18:30 | 9460.0543 |  | 1.2497 | 2.4975
USB ¦ Main | 2020-07-08 06:30 | 9460.0642 |  |  |  | 0.83225
USB ¦ Main | 2020-07-08 18:30 | 9465.1738 |  | 213.3141 | 425.7959
USB ¦ Main | 2020-07-09 06:30 | 9465.1738 |  |  |  | 0.0018333
USB ¦ Main | 2020-07-09 18:30 | 9465.2338 |  | 2.4984 | 4.995
USB ¦ Main | 2020-07-10 06:30 | 9465.2338 |  |  |  | 0
USB ¦ Main | 2020-07-10 18:30 | 9467.3735 |  | 89.1563 | 178.3125
USB ¦ Main | 2020-07-11 06:30 | 9467.3735 |  |  |  | 0
USB ¦ Main | 2020-07-11 18:30 | 9467.4135 |  | 1.665 | 3.33
USB ¦ Main | 2020-07-12 06:30 | 9467.4135 |  |  |  | 0
USB ¦ Main | 2020-07-12 18:30 | 9467.4634 |  | 2.0813 | 4.1625
USB ¦ Main | 2020-07-13 06:30 | 9467.4734 |  |  |  | 0.8325
USB ¦ Main | 2020-07-13 18:30 | 9467.7931 |  | 13.7362 | 26.64
USB ¦ Main | 2020-07-14 06:30 | 9467.893 |  |  |  | 8.3241
USB ¦ Main | 2020-07-14 18:30 | 9468.8521 |  | 44.1253 | 79.9266
USB ¦ Main | 2020-07-15 06:30 | 9469.5514 |  |  |  | 58.275
USB ¦ Main | 2020-07-15 18:30 | 9472.2602 |  | 142.004 | 225.7331
USB ¦ Main | 2020-07-16 06:30 | 9472.4001 |  |  |  | 11.6575
USB ¦ Main | 2020-07-16 18:30 | 9472.7298 |  | 19.5652 | 27.4729
USB ¦ Main | 2020-07-17 06:30 | 9472.8297 |  |  |  | 8.3248
USB ¦ Main | 2020-07-17 18:30 | 9473.0195 |  | 12.0712 | 15.8177
USB ¦ Main | 2020-07-18 06:30 | 9473.0694 |  |  |  | 4.1625
USB ¦ Main | 2020-07-18 18:30 | 9473.1893 |  | 7.0763 | 9.99
USB ¦ Main | 2020-07-19 06:30 | 9473.2193 |  |  |  | 2.4975
USB ¦ Main | 2020-07-19 18:30 | 9473.2892 |  | 4.1625 | 5.8275
USB ¦ Main | 2020-07-20 06:30 | 9473.3192 |  |  |  | 2.4975
USB ¦ Main | 2020-07-20 18:30 | 9473.4091 |  | 4.995 | 7.4925
USB ¦ Main | 2020-07-21 06:30 | 9473.4191 |  |  |  | 0.8325
USB ¦ Main | 2020-07-21 18:30 | 9473.5689 |  | 6.66 | 12.4875
USB ¦ Main | 2020-07-22 06:30 | 9473.5789 |  |  |  | 0.8325
USB ¦ Main | 2020-07-22 18:30 | 9491.2578 |  | 737.0353 | 1473.2382
USB ¦ Main | 2020-07-23 06:30 | 9510.0962 |  |  |  | 1569.8705
USB ¦ Main | 2020-07-23 18:30 | 9527.5837 |  | 1513.5788 | 1457.287
USB ¦ Main | 2020-07-24 06:30 | 9545.0924 |  |  |  | 1459.0582
USB ¦ Main | 2020-07-24 18:30 | 9550.4919 |  | 954.51 | 449.9618
USB ¦ Main | 2020-07-25 06:30 | 9550.4919 |  |  |  | 0.0018333
USB ¦ Main | 2020-07-25 18:30 | 9550.4919 |  | 0.00091667 | 0
USB ¦ Main | 2020-07-26 06:30 | 9550.5019 |  |  |  | 0.8325
USB ¦ Main | 2020-07-26 18:30 | 9550.5019 |  | 0.41625 | 0
USB ¦ Main | 2020-07-27 06:30 | 9550.5019 |  |  |  | 0
USB ¦ Main | 2020-07-27 18:30 | 9553.0117 |  | 104.5744 | 209.1487
USB ¦ Main | 2020-07-28 06:30 | 9553.0117 |  |  |  | 0.0029167
USB ¦ Main | 2020-07-28 18:30 | 9553.0517 |  | 1.6665 | 3.33
USB ¦ Main | 2020-07-29 06:30 | 9553.0517 |  |  |  | 0
USB ¦ Main | 2020-07-29 18:30 | 9554.9715 |  | 79.9931 | 159.9863
USB ¦ Main | 2020-07-30 06:30 | 9554.9815 |  |  |  | 0.83517
USB ¦ Main | 2020-07-30 18:30 | 9555.0115 |  | 1.6665 | 2.4978
USB ¦ Main | 2020-07-31 06:30 | 9555.0115 |  |  |  | 0
USB ¦ Main | 2020-07-31 18:30 | 9558.6002 |  | 149.5266 | 299.0532
USB ¦ Main | 2020-08-01 06:30 | 9559.1696 |  |  |  | 47.4541
USB ¦ Main | 2020-08-01 18:30 | 9560.4383 |  | 76.5909 | 105.7278
USB ¦ Main | 2020-08-02 06:30 | 9560.9378 |  |  |  | 41.6234
USB ¦ Main | 2020-08-02 18:30 | 9562.1366 |  | 70.7625 | 99.9016
USB ¦ Main | 2020-08-03 06:30 | 9562.6361 |  |  |  | 41.6239
USB ¦ Main | 2020-08-03 18:30 | 9564.9352 |  | 116.6062 | 191.5886
USB ¦ Main | 2020-08-04 06:30 | 9564.9552 |  |  |  | 1.6647
USB ¦ Main | 2020-08-04 18:30 | 9565.2249 |  | 12.0712 | 22.4777
USB ¦ Main | 2020-08-05 06:30 | 9565.2549 |  |  |  | 2.4968
USB ¦ Main | 2020-08-05 18:30 | 9567.194 |  | 82.0463 | 161.5957
USB ¦ Main | 2020-08-06 06:30 | 9567.3039 |  |  |  | 9.1571
USB ¦ Main | 2020-08-06 18:30 | 9568.1031 |  | 37.8788 | 66.6004
USB ¦ Main | 2020-08-07 06:30 | 9568.2629 |  |  |  | 13.3184
USB ¦ Main | 2020-08-07 18:30 | 9571.3925 |  | 137.0587 | 260.7991
USB ¦ Main | 2020-08-08 06:30 | 9571.3925 |  |  |  | 0
USB ¦ Main | 2020-08-08 18:30 | 9571.3925 |  | 0 | 0
USB ¦ Main | 2020-08-09 06:30 | 9571.3925 |  |  |  | 0
USB ¦ Main | 2020-08-09 18:30 | 9571.3925 |  | 0 | 0
USB ¦ Main | 2020-08-10 06:30 | 9571.4524 |  |  |  | 4.9937
USB ¦ Main | 2020-08-10 18:30 | 9573.6817 |  | 95.3831 | 185.7726
USB ¦ Main | 2020-08-11 06:30 | 9573.7017 |  |  |  | 1.6675
USB ¦ Main | 2020-08-11 18:30 | 9574.0813 |  | 16.6515 | 31.6354
USB ¦ Main | 2020-08-12 06:30 | 9574.0913 |  |  |  | 0.83225
USB ¦ Main | 2020-08-12 18:30 | 9575.2305 |  | 47.8828 | 94.9334
USB ¦ Main | 2020-08-13 06:30 | 9575.3204 |  |  |  | 7.4927
USB ¦ Main | 2020-08-13 18:30 | 9575.7101 |  | 19.9809 | 32.4691
USB ¦ Main | 2020-08-14 06:30 | 9575.74 |  |  |  | 2.4968
USB ¦ Main | 2020-08-14 18:30 | 9576.1297 |  | 17.4825 | 32.4682
USB ¦ Main | 2020-08-15 06:30 | 9576.1297 |  |  |  | 0
USB ¦ Main | 2020-08-15 18:30 | 9576.1297 |  | 0 | 0
USB ¦ Main | 2020-08-16 06:30 | 9576.1297 |  |  |  | 0
USB ¦ Main | 2020-08-16 18:30 | 9576.1297 |  | 0 | 0
USB ¦ Main | 2020-08-17 06:30 | 9576.1496 |  |  |  | 1.6646
USB ¦ Main | 2020-08-17 18:30 | 9576.5792 |  | 18.7312 | 35.7979
USB ¦ Main | 2020-08-18 06:30 | 9576.6491 |  |  |  | 5.8262
USB ¦ Main | 2020-08-18 18:30 | 9577.2186 |  | 26.64 | 47.4538
USB ¦ Main | 2020-08-19 06:30 | 9577.2485 |  |  |  | 2.4973
USB ¦ Main | 2020-08-19 18:30 | 9578.6676 |  | 60.3788 | 118.2602
USB ¦ Main | 2020-08-20 06:30 | 9578.7176 |  |  |  | 4.1614
USB ¦ Main | 2020-08-20 18:30 | 9579.1272 |  | 19.1475 | 34.1336
USB ¦ Main | 2020-08-21 06:30 | 9579.1671 |  |  |  | 3.3291
USB ¦ Main | 2020-08-21 18:30 | 9579.6067 |  | 19.98 | 36.6309
USB ¦ Main | 2020-08-22 06:30 | 9579.6067 |  |  |  | 0
USB ¦ Main | 2020-08-22 18:30 | 9579.6067 |  | 0 | 0
USB ¦ Main | 2020-08-23 06:30 | 9579.6067 |  |  |  | 0
USB ¦ Main | 2020-08-23 18:30 | 9579.6167 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-08-24 06:30 | 9579.6566 |  |  |  | 3.3291
USB ¦ Main | 2020-08-24 18:30 | 9581.5558 |  | 80.7975 | 158.2659
USB ¦ Main | 2020-08-25 06:30 | 9581.6058 |  |  |  | 4.1616
USB ¦ Main | 2020-08-25 18:30 | 9582.1153 |  | 23.31 | 42.4584
USB ¦ Main | 2020-08-26 06:30 | 9582.1952 |  |  |  | 6.6582
USB ¦ Main | 2020-08-26 18:30 | 9583.9241 |  | 75.3694 | 144.0806
USB ¦ Main | 2020-08-27 06:30 | 9583.9541 |  |  |  | 2.4997
USB ¦ Main | 2020-08-27 18:30 | 9584.9334 |  | 42.054 | 81.6082
USB ¦ Main | 2020-08-28 06:30 | 9584.9534 |  |  |  | 1.6646
USB ¦ Main | 2020-08-28 18:30 | 9586.743 |  | 75.3975 | 149.1304
USB ¦ Main | 2020-08-29 06:30 | 9586.743 |  |  |  | 0
USB ¦ Main | 2020-08-29 18:30 | 9586.743 |  | 0 | 0
USB ¦ Main | 2020-08-30 06:30 | 9586.743 |  |  |  | 0
USB ¦ Main | 2020-08-30 18:30 | 9586.753 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-08-31 06:30 | 9586.753 |  |  |  | 0
USB ¦ Main | 2020-08-31 18:30 | 9586.763 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-09-01 06:30 | 9586.8829 |  |  |  | 9.9974
USB ¦ Main | 2020-09-01 18:30 | 9587.5023 |  | 30.8053 | 51.6133
USB ¦ Main | 2020-09-02 06:30 | 9587.5622 |  |  |  | 4.9955
USB ¦ Main | 2020-09-02 18:30 | 9589.0116 |  | 62.8884 | 120.7813
USB ¦ Main | 2020-09-03 06:30 | 9589.0915 |  |  |  | 6.6582
USB ¦ Main | 2020-09-03 18:30 | 9589.611 |  | 24.975 | 43.2918
USB ¦ Main | 2020-09-04 06:30 | 9589.7009 |  |  |  | 7.4925
USB ¦ Main | 2020-09-04 18:30 | 9590.1005 |  | 20.3962 | 33.3
USB ¦ Main | 2020-09-05 06:30 | 9590.1005 |  |  |  | 0
USB ¦ Main | 2020-09-05 18:30 | 9590.1105 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-09-06 06:30 | 9590.1105 |  |  |  | 0
USB ¦ Main | 2020-09-06 18:30 | 9590.1205 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-09-07 06:30 | 9590.1205 |  |  |  | 0
USB ¦ Main | 2020-09-07 18:30 | 9591.2195 |  | 45.7931 | 91.5862
USB ¦ Main | 2020-09-08 06:30 | 9591.2995 |  |  |  | 6.6611
USB ¦ Main | 2020-09-08 18:30 | 9592.2686 |  | 43.7105 | 80.76
USB ¦ Main | 2020-09-09 06:30 | 9592.3185 |  |  |  | 4.1632
USB ¦ Main | 2020-09-09 18:30 | 9593.5474 |  | 53.2837 | 102.4042
USB ¦ Main | 2020-09-10 06:30 | 9593.5874 |  |  |  | 3.3309
USB ¦ Main | 2020-09-10 18:30 | 9594.7165 |  | 48.7134 | 94.0959
USB ¦ Main | 2020-09-11 06:30 | 9594.7864 |  |  |  | 5.8259
USB ¦ Main | 2020-09-11 18:30 | 9595.7556 |  | 43.2956 | 80.7653
USB ¦ Main | 2020-09-12 06:30 | 9595.7556 |  |  |  | 0.0029167
USB ¦ Main | 2020-09-12 18:30 | 9595.7556 |  | 0.0014583 | 0
USB ¦ Main | 2020-09-13 06:30 | 9595.7556 |  |  |  | 0
USB ¦ Main | 2020-09-13 18:30 | 9595.7556 |  | 0 | 0
USB ¦ Main | 2020-09-14 06:30 | 9595.7956 |  |  |  | 3.3291
USB ¦ Main | 2020-09-14 18:30 | 9596.8246 |  | 44.5388 | 85.7484
USB ¦ Main | 2020-09-15 06:30 | 9596.9445 |  |  |  | 9.9974
USB ¦ Main | 2020-09-15 18:30 | 9597.8637 |  | 43.2956 | 76.5938
USB ¦ Main | 2020-09-16 06:30 | 9597.9536 |  |  |  | 7.4954
USB ¦ Main | 2020-09-16 18:30 | 9599.9427 |  | 86.6265 | 165.7575
USB ¦ Main | 2020-09-17 06:30 | 9600.0426 |  |  |  | 8.3248
USB ¦ Main | 2020-09-17 18:30 | 9600.9817 |  | 43.29 | 78.2552
USB ¦ Main | 2020-09-18 06:30 | 9601.0916 |  |  |  | 9.1633
USB ¦ Main | 2020-09-18 18:30 | 9601.8708 |  | 37.0491 | 64.9348
USB ¦ Main | 2020-09-19 06:30 | 9601.8809 |  |  |  | 0.83433
USB ¦ Main | 2020-09-19 18:30 | 9601.8809 |  | 0.41717 | 0
USB ¦ Main | 2020-09-20 06:30 | 9601.8809 |  |  |  | 0
USB ¦ Main | 2020-09-20 18:30 | 9601.8809 |  | 0 | 0
USB ¦ Main | 2020-09-21 06:30 | 9602.0208 |  |  |  | 11.662
USB ¦ Main | 2020-09-21 18:30 | 9602.9399 |  | 44.1253 | 76.5887
USB ¦ Main | 2020-09-22 06:30 | 9603.0198 |  |  |  | 6.66
USB ¦ Main | 2020-09-22 18:30 | 9604.1487 |  | 50.3672 | 94.0743
USB ¦ Main | 2020-09-23 06:30 | 9604.2186 |  |  |  | 5.8264
USB ¦ Main | 2020-09-23 18:30 | 9605.6076 |  | 60.7894 | 115.7523
USB ¦ Main | 2020-09-24 06:30 | 9605.6776 |  |  |  | 5.8288
USB ¦ Main | 2020-09-24 18:30 | 9606.8066 |  | 49.9571 | 94.0853
USB ¦ Main | 2020-09-25 06:30 | 9606.8965 |  |  |  | 7.4954
USB ¦ Main | 2020-09-25 18:30 | 9818.6652 |  | 8827.4405 | 17647.3857
USB ¦ Main | 2020-09-26 06:30 | 9818.6652 |  |  |  | 0.0018333
USB ¦ Main | 2020-09-26 18:30 | 9818.6752 |  | 0.41717 | 0.8325
USB ¦ Main | 2020-09-27 06:30 | 9818.6752 |  |  |  | 0
USB ¦ Main | 2020-09-27 18:30 | 9818.6752 |  | 0 | 0
USB ¦ Main | 2020-09-28 06:30 | 9818.7251 |  |  |  | 4.1614
USB ¦ Main | 2020-09-28 18:30 | 9820.0938 |  | 59.1075 | 114.0536
USB ¦ Main | 2020-09-29 06:30 | 9820.3035 |  |  |  | 17.4818
USB ¦ Main | 2020-09-29 18:30 | 9821.7723 |  | 69.9412 | 122.4007
USB ¦ Main | 2020-09-30 06:30 | 9821.8023 |  |  |  | 2.4973
USB ¦ Main | 2020-09-30 18:30 | 9826.0008 |  | 176.1863 | 349.8752
USB ¦ Main | 2020-10-01 06:30 | 9826.1207 |  |  |  | 9.9898
USB ¦ Main | 2020-10-01 18:30 | 9827.4395 |  | 59.9456 | 109.9015
USB ¦ Main | 2020-10-02 06:30 | 9827.4795 |  |  |  | 3.332
USB ¦ Main | 2020-10-02 18:30 | 9828.2687 |  | 34.5502 | 65.7684
USB ¦ Main | 2020-10-03 06:30 | 9828.2687 |  |  |  | 0
USB ¦ Main | 2020-10-03 18:30 | 9828.2687 |  | 0 | 0
USB ¦ Main | 2020-10-04 06:30 | 9828.2687 |  |  |  | 0
USB ¦ Main | 2020-10-04 18:30 | 9828.2687 |  | 0 | 0
USB ¦ Main | 2020-10-05 06:30 | 9828.3486 |  |  |  | 6.6582
USB ¦ Main | 2020-10-05 18:30 | 9829.9873 |  | 71.6091 | 136.56
USB ¦ Main | 2020-10-06 06:30 | 9830.1073 |  |  |  | 9.9992
USB ¦ Main | 2020-10-06 18:30 | 9831.1963 |  | 50.3728 | 90.7463
USB ¦ Main | 2020-10-07 06:30 | 9831.2562 |  |  |  | 4.9966
USB ¦ Main | 2020-10-07 18:30 | 9834.8551 |  | 152.4502 | 299.9038
USB ¦ Main | 2020-10-08 06:30 | 9834.955 |  |  |  | 8.3248
USB ¦ Main | 2020-10-08 18:30 | 9836.1939 |  | 55.7831 | 103.2415
USB ¦ Main | 2020-10-09 06:30 | 9836.2538 |  |  |  | 4.9966
USB ¦ Main | 2020-10-09 18:30 | 9838.5628 |  | 98.7033 | 192.4101
USB ¦ Main | 2020-10-10 06:30 | 9838.5628 |  |  |  | 0.0029167
USB ¦ Main | 2020-10-10 18:30 | 9838.5728 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-10-11 06:30 | 9838.5928 |  |  |  | 1.6646
USB ¦ Main | 2020-10-11 18:30 | 9838.5928 |  | 0.8325 | 0.00041667
USB ¦ Main | 2020-10-12 06:30 | 9838.7326 |  |  |  | 11.6539
USB ¦ Main | 2020-10-12 18:30 | 9839.5519 |  | 39.9628 | 68.2718
USB ¦ Main | 2020-10-13 06:30 | 9839.5619 |  |  |  | 0.83408
USB ¦ Main | 2020-10-13 18:30 | 9840.9512 | 7290 | 58.304 | 115.774
USB ¦ Main | 2020-10-14 06:30 | 9841.0011 |  |  |  | 4.1643
USB ¦ Main | 2020-10-14 18:30 | 9844.8603 |  | 162.8818 | 321.5992
USB ¦ Main | 2020-10-15 06:30 | 9844.9103 |  |  |  | 4.1632
USB ¦ Main | 2020-10-15 18:30 | 9846.0093 |  | 47.8753 | 91.5873
USB ¦ Main | 2020-10-16 06:30 | 9846.0393 |  |  |  | 2.5
USB ¦ Main | 2020-10-16 18:30 | 9846.9484 |  | 39.129 | 75.7579
USB ¦ Main | 2020-10-17 06:30 | 9846.9584 |  |  |  | 0.83225
USB ¦ Main | 2020-10-17 18:30 | 9846.9584 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-10-18 06:30 | 9846.9584 |  |  |  | 0
USB ¦ Main | 2020-10-18 18:30 | 9846.9584 |  | 0 | 0
USB ¦ Main | 2020-10-19 06:30 | 9847.0283 |  |  |  | 5.8259
USB ¦ Main | 2020-10-19 18:30 | 9848.2473 |  | 53.7019 | 101.5778
USB ¦ Main | 2020-10-20 06:30 | 9848.3472 |  |  |  | 8.3277
USB ¦ Main | 2020-10-20 18:30 | 9849.5561 |  | 54.5358 | 100.744
USB ¦ Main | 2020-10-21 06:30 | 9849.6361 |  |  |  | 6.6611
USB ¦ Main | 2020-10-21 18:30 | 9852.2149 |  | 110.7802 | 214.8993
USB ¦ Main | 2020-10-22 06:30 | 9852.3548 |  |  |  | 11.6622
USB ¦ Main | 2020-10-22 18:30 | 9853.5437 |  | 55.3669 | 99.0716
USB ¦ Main | 2020-10-23 06:30 | 9853.6636 |  |  |  | 9.9923
USB ¦ Main | 2020-10-23 18:30 | 9854.9324 |  | 57.8658 | 105.7394
USB ¦ Main | 2020-10-24 06:30 | 9854.9325 |  |  |  | 0.0029167
USB ¦ Main | 2020-10-24 18:30 | 9854.9325 |  | 0.0014583 | 0
USB ¦ Main | 2020-10-25 06:30 | 9854.9325 |  |  |  | 0
USB ¦ Main | 2020-10-25 18:30 | 9854.9325 |  | 0 | 0
USB ¦ Main | 2020-10-26 06:30 | 9854.9325 |  |  |  | 0
USB ¦ Main | 2020-10-26 18:30 | 9856.2612 |  | 55.3613 | 110.7225
USB ¦ Main | 2020-10-27 06:30 | 9856.2711 |  |  |  | 0.8325
USB ¦ Main | 2020-10-27 18:30 | 9857.7 |  | 59.9541 | 119.0757
USB ¦ Main | 2020-10-28 06:30 | 9857.7101 |  |  |  | 0.83408
USB ¦ Main | 2020-10-28 18:30 | 9862.0086 |  | 179.5228 | 358.2115
USB ¦ Main | 2020-10-29 06:30 | 9862.0186 |  |  |  | 0.83517
USB ¦ Main | 2020-10-29 18:30 | 9863.3276 |  | 54.9577 | 109.0802
USB ¦ Main | 2020-10-30 06:30 | 9863.3276 |  |  |  | 0
USB ¦ Main | 2020-10-30 18:30 | 9864.1568 |  | 34.5488 | 69.0975
USB ¦ Main | 2020-10-31 06:30 | 9864.1667 |  |  |  | 0.83225
USB ¦ Main | 2020-10-31 18:30 | 9864.1767 |  | 0.8325 | 0.83275
USB ¦ Main | 2020-11-01 06:30 | 9864.1767 |  |  |  | 0
USB ¦ Main | 2020-11-01 18:30 | 9864.1867 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-11-02 06:30 | 9864.1867 |  |  |  | 0
USB ¦ Main | 2020-11-02 18:30 | 9865.6254 |  | 59.9456 | 119.8913
USB ¦ Main | 2020-11-03 06:30 | 9865.6254 |  |  |  | 0.0029167
USB ¦ Main | 2020-11-03 18:30 | 9867.3241 |  | 70.778 | 141.5532
USB ¦ Main | 2020-11-04 06:30 | 9867.3441 |  |  |  | 1.6664
USB ¦ Main | 2020-11-04 18:30 | 9870.1727 |  | 118.6913 | 235.7161
USB ¦ Main | 2020-11-05 06:30 | 9870.1727 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-05 18:30 | 9871.9513 |  | 74.1103 | 148.2188
USB ¦ Main | 2020-11-06 06:30 | 9871.9613 |  |  |  | 0.83517
USB ¦ Main | 2020-11-06 18:30 | 9873.2204 |  | 52.8765 | 104.9177
USB ¦ Main | 2020-11-07 06:30 | 9873.2204 |  |  |  | 0
USB ¦ Main | 2020-11-07 18:30 | 9873.2204 |  | 0 | 0
USB ¦ Main | 2020-11-08 06:30 | 9873.2303 |  |  |  | 0.83225
USB ¦ Main | 2020-11-08 18:30 | 9873.2303 |  | 0.41625 | 0.00025
USB ¦ Main | 2020-11-09 06:30 | 9873.2303 |  |  |  | 0
USB ¦ Main | 2020-11-09 18:30 | 9876.0489 |  | 117.4416 | 234.8832
USB ¦ Main | 2020-11-10 06:30 | 9876.059 |  |  |  | 0.83433
USB ¦ Main | 2020-11-10 18:30 | 9877.9776 |  | 80.3625 | 159.8907
USB ¦ Main | 2020-11-11 06:30 | 9877.9777 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-11 18:30 | 9881.2663 |  | 137.0287 | 274.0557
USB ¦ Main | 2020-11-12 06:30 | 9881.2664 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-12 18:30 | 9883.035 |  | 73.694 | 147.3863
USB ¦ Main | 2020-11-13 06:30 | 9883.035 |  |  |  | 0.0029167
USB ¦ Main | 2020-11-13 18:30 | 9884.8139 |  | 74.1193 | 148.2357
USB ¦ Main | 2020-11-14 06:30 | 9884.8139 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-14 18:30 | 9884.8139 |  | 0.00091667 | 0
USB ¦ Main | 2020-11-15 06:30 | 9884.8139 |  |  |  | 0
USB ¦ Main | 2020-11-15 18:30 | 9884.8139 |  | 0 | 0
USB ¦ Main | 2020-11-16 06:30 | 9884.8239 |  |  |  | 0.8325
USB ¦ Main | 2020-11-16 18:30 | 9886.9623 |  | 89.5191 | 178.2057
USB ¦ Main | 2020-11-17 06:30 | 9886.9624 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-17 18:30 | 9888.7509 |  | 74.5238 | 149.0457
USB ¦ Main | 2020-11-18 06:30 | 9888.7509 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-18 18:30 | 9893.2794 |  | 188.6887 | 377.3757
USB ¦ Main | 2020-11-19 06:30 | 9893.2795 |  |  |  | 0.0018333
USB ¦ Main | 2020-11-19 18:30 | 9909.408 |  | 672.0225 | 1344.0431
USB ¦ Main | 2020-11-20 06:30 | 9909.408 |  |  |  | 0.0019167
USB ¦ Main | 2020-11-20 18:30 | 9911.9066 |  | 104.1085 | 208.215
USB ¦ Main | 2020-11-21 06:30 | 9911.9066 |  |  |  | 0
USB ¦ Main | 2020-11-21 18:30 | 9911.9066 |  | 0 | 0
USB ¦ Main | 2020-11-22 06:30 | 9911.9266 |  |  |  | 1.665
USB ¦ Main | 2020-11-22 18:30 | 9911.9366 |  | 1.2487 | 0.8325
USB ¦ Main | 2020-11-23 06:30 | 9911.9366 |  |  |  | 0
USB ¦ Main | 2020-11-23 18:30 | 9925.1649 |  | 551.1825 | 1102.365
USB ¦ Main | 2020-11-24 06:30 | 9925.1649 |  |  |  | 0
USB ¦ Main | 2020-11-24 18:30 | 9927.0235 |  | 77.4394 | 154.8787
USB ¦ Main | 2020-11-25 06:30 | 9927.0235 |  |  |  | 0.0029167
USB ¦ Main | 2020-11-25 18:30 | 9931.0017 |  | 165.759 | 331.515
USB ¦ Main | 2020-11-26 06:30 | 9931.0117 |  |  |  | 0.83225
USB ¦ Main | 2020-11-26 18:30 | 9936.9403 |  | 247.4438 | 494.0552
USB ¦ Main | 2020-11-27 06:30 | 9936.9403 |  |  |  | 0
USB ¦ Main | 2020-11-27 18:30 | 9938.3591 |  | 59.1131 | 118.2263
USB ¦ Main | 2020-11-28 06:30 | 9938.3591 |  |  |  | 0.0029167
USB ¦ Main | 2020-11-28 18:30 | 9938.3591 |  | 0.0014583 | 0
USB ¦ Main | 2020-11-29 06:30 | 9938.3591 |  |  |  | 0
USB ¦ Main | 2020-11-29 18:30 | 9938.3591 |  | 0 | 0
USB ¦ Main | 2020-11-30 06:30 | 9938.3591 |  |  |  | 0
USB ¦ Main | 2020-11-30 18:30 | 9945.7975 |  | 309.9319 | 619.8637
USB ¦ Main | 2020-12-01 06:30 | 9945.8075 |  |  |  | 0.83542
USB ¦ Main | 2020-12-01 18:30 | 9947.6859 |  | 78.6868 | 156.5382
USB ¦ Main | 2020-12-02 06:30 | 9947.6959 |  |  |  | 0.83408
USB ¦ Main | 2020-12-02 18:30 | 9951.6742 |  | 166.1775 | 331.5209
USB ¦ Main | 2020-12-03 06:30 | 9951.6742 |  |  |  | 0.0018333
USB ¦ Main | 2020-12-03 18:30 | 9953.5329 |  | 77.4459 | 154.89
USB ¦ Main | 2020-12-04 06:30 | 9953.5329 |  |  |  | 0
USB ¦ Main | 2020-12-04 18:30 | 9955.0516 |  | 63.2812 | 126.5625
USB ¦ Main | 2020-12-05 06:30 | 9955.0516 |  |  |  | 0
USB ¦ Main | 2020-12-05 18:30 | 9955.0516 |  | 0 | 0
USB ¦ Main | 2020-12-06 06:30 | 9955.0516 |  |  |  | 0
USB ¦ Main | 2020-12-06 18:30 | 9955.0616 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-12-07 06:30 | 9955.0616 |  |  |  | 0
USB ¦ Main | 2020-12-07 18:30 | 9957.2301 |  | 90.3544 | 180.7087
USB ¦ Main | 2020-12-08 06:30 | 9957.2302 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-08 18:30 | 9959.2185 |  | 82.8465 | 165.69
USB ¦ Main | 2020-12-09 06:30 | 9959.2285 |  |  |  | 0.8325
USB ¦ Main | 2020-12-09 18:30 | 9962.8471 |  | 151.1944 | 301.5562
USB ¦ Main | 2020-12-10 06:30 | 9962.8472 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-10 18:30 | 9966.1055 |  | 135.7665 | 271.53
USB ¦ Main | 2020-12-11 06:30 | 9966.1055 |  |  |  | 0
USB ¦ Main | 2020-12-11 18:30 | 9967.7143 |  | 67.0331 | 134.0663
USB ¦ Main | 2020-12-12 06:30 | 9967.7144 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-12 18:30 | 9967.7243 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-12-13 06:30 | 9967.7243 |  |  |  | 0
USB ¦ Main | 2020-12-13 18:30 | 9967.7243 |  | 0 | 0
USB ¦ Main | 2020-12-14 06:30 | 9967.7243 |  |  |  | 0
USB ¦ Main | 2020-12-14 18:30 | 9969.3231 |  | 66.6169 | 133.2337
USB ¦ Main | 2020-12-15 06:30 | 9969.3232 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-15 18:30 | 9971.062 |  | 72.4515 | 144.9
USB ¦ Main | 2020-12-16 06:30 | 9971.062 |  |  |  | 0
USB ¦ Main | 2020-12-16 18:30 | 9976.7408 |  | 236.6156 | 473.2313
USB ¦ Main | 2020-12-17 06:30 | 9976.7408 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-17 18:30 | 9978.5393 |  | 74.9405 | 149.8782
USB ¦ Main | 2020-12-18 06:30 | 9978.5393 |  |  |  | 0.0018333
USB ¦ Main | 2020-12-18 18:30 | 9979.7785 |  | 51.6328 | 103.2638
USB ¦ Main | 2020-12-19 06:30 | 9979.7786 |  |  |  | 0.0029167
USB ¦ Main | 2020-12-19 18:30 | 9979.7885 |  | 0.41771 | 0.8325
USB ¦ Main | 2020-12-20 06:30 | 9979.7885 |  |  |  | 0
USB ¦ Main | 2020-12-20 18:30 | 9979.8085 |  | 0.8325 | 1.665
USB ¦ Main | 2020-12-21 06:30 | 9979.8085 |  |  |  | 0
USB ¦ Main | 2020-12-21 18:30 | 9979.8185 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-12-22 06:30 | 9979.8185 |  |  |  | 0
USB ¦ Main | 2020-12-22 18:30 | 9982.1082 |  | 95.4028 | 190.8057
USB ¦ Main | 2020-12-23 06:30 | 9982.1082 |  |  |  | 0.0018333
USB ¦ Main | 2020-12-23 18:30 | 9982.1182 |  | 0.41717 | 0.8325
USB ¦ Main | 2020-12-24 06:30 | 9982.1182 |  |  |  | 0
USB ¦ Main | 2020-12-24 18:30 | 9982.1182 |  | 0 | 0
USB ¦ Main | 2020-12-25 06:30 | 9982.1282 |  |  |  | 0.8325
USB ¦ Main | 2020-12-25 18:30 | 9982.1282 |  | 0.41625 | 0
USB ¦ Main | 2020-12-26 06:30 | 9982.1282 |  |  |  | 0
USB ¦ Main | 2020-12-26 18:30 | 9982.1282 |  | 0 | 0
USB ¦ Main | 2020-12-27 06:30 | 9982.1282 |  |  |  | 0
USB ¦ Main | 2020-12-27 18:30 | 9982.1382 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-12-28 06:30 | 9982.1382 |  |  |  | 0
USB ¦ Main | 2020-12-28 18:30 | 9982.1482 |  | 0.41625 | 0.8325
USB ¦ Main | 2020-12-29 06:30 | 9982.1482 |  |  |  | 0
USB ¦ Main | 2020-12-29 18:30 | 9982.1681 |  | 0.8325 | 1.665
USB ¦ Main | 2020-12-30 06:30 | 9982.1681 |  |  |  | 0
USB ¦ Main | 2020-12-30 18:30 | 9982.1881 |  | 0.8325 | 1.665
USB ¦ Main | 2020-12-31 06:30 | 9982.1881 |  |  |  | 0
USB ¦ Main | 2020-12-31 18:30 | 9982.2081 |  | 0.8325 | 1.665
USB ¦ Main | 2021-01-01 06:30 | 9982.2081 |  |  |  | 0
USB ¦ Main | 2021-01-01 18:30 | 9982.2081 |  | 0 | 0
USB ¦ Main | 2021-01-02 06:30 | 9982.2081 |  |  |  | 0
USB ¦ Main | 2021-01-02 18:30 | 9982.2181 |  | 0.41625 | 0.8325
USB ¦ Main | 2021-01-03 06:30 | 9982.2181 |  |  |  | 0
USB ¦ Main | 2021-01-03 18:30 | 9982.2181 |  | 0 | 0
USB ¦ Main | 2021-01-04 06:30 | 9982.2181 |  |  |  | 0
USB ¦ Main | 2021-01-04 18:30 | 9983.4072 |  | 49.545 | 99.09
USB ¦ Main | 2021-01-05 06:30 | 9983.4172 |  |  |  | 0.83225
USB ¦ Main | 2021-01-05 18:30 | 9985.3362 |  | 80.3756 | 159.919
USB ¦ Main | 2021-01-06 06:30 | 9985.3362 |  |  |  | 0.0029167
USB ¦ Main | 2021-01-06 18:30 | 9988.1554 |  | 117.4683 | 234.9338
USB ¦ Main | 2021-01-07 06:30 | 9988.1555 |  |  |  | 0.0029167
USB ¦ Main | 2021-01-07 18:30 | 9988.9347 |  | 32.4718 | 64.9407
USB ¦ Main | 2021-01-08 06:30 | 9988.9448 |  |  |  | 0.83408
USB ¦ Main | 2021-01-08 18:30 | 9991.2139 |  | 94.965 | 189.0959
USB ¦ Main | 2021-01-09 06:30 | 9991.2139 |  |  |  | 0.0018333
USB ¦ Main | 2021-01-09 18:30 | 9991.3038 |  | 3.7472 | 7.4925
USB ¦ Main | 2021-01-10 06:30 | 9991.4137 |  |  |  | 9.1571
USB ¦ Main | 2021-01-10 18:30 | 9991.6635 |  | 14.985 | 20.8129
USB ¦ Main | 2021-01-11 06:30 | 9991.7734 |  |  |  | 9.1575
USB ¦ Main | 2021-01-11 18:30 | 9993.1524 |  | 62.0381 | 114.9187
USB ¦ Main | 2021-01-12 06:30 | 9993.1624 |  |  |  | 0.83542
USB ¦ Main | 2021-01-12 18:30 | 9994.3415 |  | 49.5465 | 98.2575
USB ¦ Main | 2021-01-13 06:30 | 9994.3515 |  |  |  | 0.8325
USB ¦ Main | 2021-01-13 18:30 | 9998.1702 |  | 159.5278 | 318.2232
USB ¦ Main | 2021-01-14 06:30 | 9998.1902 |  |  |  | 1.6666
USB ¦ Main | 2021-01-14 18:30 | 9999.3893 |  | 50.7947 | 99.9227
USB ¦ Main | 2021-01-15 06:30 | 9999.3992 |  |  |  | 0.8325
USB ¦ Main | 2021-01-15 18:30 | 10000.728 |  | 55.7833 | 110.7342
USB ¦ Main | 2021-01-16 06:30 | 10000.7281 |  |  |  | 0.0025
USB ¦ Main | 2021-01-16 18:30 | 10000.7481 |  | 0.83375 | 1.665
USB ¦ Main | 2021-01-17 06:30 | 10000.7481 |  |  |  | 0
USB ¦ Main | 2021-01-17 18:30 | 10000.7481 |  | 0 | 0
USB ¦ Main | 2021-01-18 06:30 | 10000.7481 |  |  |  | 0
USB ¦ Main | 2021-01-18 18:30 | 10002.187 |  | 59.9571 | 119.9142
USB ¦ Main | 2021-01-19 06:30 | 10002.1971 |  |  |  | 0.835
USB ¦ Main | 2021-01-19 18:30 | 10003.496 |  | 54.5413 | 108.2475
USB ¦ Main | 2021-01-20 06:30 | 10003.516 |  |  |  | 1.665
USB ¦ Main | 2021-01-20 18:30 | 10007.7947 |  | 179.1113 | 356.5575
USB ¦ Main | 2021-01-21 06:30 | 10007.8846 |  |  |  | 7.4925
USB ¦ Main | 2021-01-21 18:30 | 10009.1236 |  | 55.3725 | 103.2525
USB ¦ Main | 2021-01-22 06:30 | 10009.1336 |  |  |  | 0.8325
USB ¦ Main | 2021-01-22 18:30 | 10010.2826 |  | 48.2908 | 95.7492
USB ¦ Main | 2021-01-23 06:30 | 10010.2926 |  |  |  | 0.835
USB ¦ Main | 2021-01-23 18:30 | 10010.2926 |  | 0.4175 | 0
USB ¦ Main | 2021-01-24 06:30 | 10010.2926 |  |  |  | 0
USB ¦ Main | 2021-01-24 18:30 | 10010.2926 |  | 0 | 0
USB ¦ Main | 2021-01-25 06:30 | 10010.2926 |  |  |  | 0
USB ¦ Main | 2021-01-25 18:30 | 10011.5815 |  | 53.7021 | 107.4042
USB ¦ Main | 2021-01-26 06:30 | 10011.5915 |  |  |  | 0.835
USB ¦ Main | 2021-01-26 18:30 | 10012.9005 |  | 54.9575 | 109.08
USB ¦ Main | 2021-01-27 06:30 | 10012.9005 |  |  |  | 0
USB ¦ Main | 2021-01-27 18:30 | 10015.8194 |  | 121.6237 | 243.2475
USB ¦ Main | 2021-01-28 06:30 | 10015.8394 |  |  |  | 1.665
USB ¦ Main | 2021-01-28 18:30 | 10016.8384 |  | 42.4575 | 83.25
USB ¦ Main | 2021-01-29 06:30 | 10016.8384 |  |  |  | 0
USB ¦ Main | 2021-01-29 18:30 | 10018.0074 |  | 48.7071 | 97.4142
USB ¦ Main | 2021-01-30 06:30 | 10018.0174 |  |  |  | 0.835
USB ¦ Main | 2021-01-30 18:30 | 10018.0174 |  | 0.4175 | 0
USB ¦ Main | 2021-01-31 06:30 | 10018.0174 |  |  |  | 0
USB ¦ Main | 2021-01-31 18:30 | 10018.0174 |  | 0 | 0
USB ¦ Main | 2021-02-01 06:30 | 10018.0374 |  |  |  | 1.665
USB ¦ Main | 2021-02-01 18:30 | 10019.2165 |  | 49.9612 | 98.2575
USB ¦ Main | 2021-02-02 06:30 | 10019.2265 |  |  |  | 0.8325
USB ¦ Main | 2021-02-02 18:30 | 10020.2955 |  | 44.9608 | 89.0892
USB ¦ Main | 2021-02-03 06:30 | 10020.3055 |  |  |  | 0.835
USB ¦ Main | 2021-02-03 18:30 | 10023.0544 |  | 114.9538 | 229.0725
USB ¦ Main | 2021-02-04 06:30 | 10023.0744 |  |  |  | 1.665
USB ¦ Main | 2021-02-04 18:30 | 10024.3834 |  | 55.3725 | 109.08
USB ¦ Main | 2021-02-05 06:30 | 10024.3934 |  |  |  | 0.8325
USB ¦ Main | 2021-02-05 18:30 | 10025.3425 |  | 39.9629 | 79.0933
USB ¦ Main | 2021-02-06 06:30 | 10025.3425 |  |  |  | 0.0016667
USB ¦ Main | 2021-02-06 18:30 | 10025.3425 |  | 0.00083333 | 0
USB ¦ Main | 2021-02-07 06:30 | 10025.3625 |  |  |  | 1.665
USB ¦ Main | 2021-02-07 18:30 | 10025.3625 |  | 0.8325 | 0
USB ¦ Main | 2021-02-08 06:30 | 10025.3725 |  |  |  | 0.8325
USB ¦ Main | 2021-02-08 18:30 | 10026.6413 |  | 53.2858 | 105.7392
USB ¦ Main | 2021-02-09 06:30 | 10026.6414 |  |  |  | 0.0025
USB ¦ Main | 2021-02-09 18:30 | 10027.6904 |  | 43.7104 | 87.4183
USB ¦ Main | 2021-02-10 06:30 | 10027.7204 |  |  |  | 2.4992
USB ¦ Main | 2021-02-10 18:30 | 10031.3895 |  | 154.1288 | 305.7583
USB ¦ Main | 2021-02-11 06:30 | 10031.4195 |  |  |  | 2.4992
USB ¦ Main | 2021-02-11 18:30 | 10032.4487 |  | 44.1346 | 85.77
USB ¦ Main | 2021-02-12 06:30 | 10032.4687 |  |  |  | 1.665
USB ¦ Main | 2021-02-12 18:30 | 10033.5977 |  | 47.8746 | 94.0842
USB ¦ Main | 2021-02-13 06:30 | 10033.6177 |  |  |  | 1.6675
USB ¦ Main | 2021-02-13 18:30 | 10033.6277 |  | 1.25 | 0.8325
USB ¦ Main | 2021-02-14 06:30 | 10033.6377 |  |  |  | 0.8325
USB ¦ Main | 2021-02-14 18:30 | 10033.6377 |  | 0.41625 | 0
USB ¦ Main | 2021-02-15 06:30 | 10033.6477 |  |  |  | 0.8325
USB ¦ Main | 2021-02-15 18:30 | 10034.9666 |  | 55.3725 | 109.9125
USB ¦ Main | 2021-02-16 06:30 | 10034.9866 |  |  |  | 1.665
USB ¦ Main | 2021-02-16 18:30 | 10036.2355 |  | 52.8696 | 104.0742
USB ¦ Main | 2021-02-17 06:30 | 10036.2655 |  |  |  | 2.5
USB ¦ Main | 2021-02-17 18:30 | 10039.0943 |  | 119.1192 | 235.7383
USB ¦ Main | 2021-02-18 06:30 | 10039.1143 |  |  |  | 1.6667
USB ¦ Main | 2021-02-18 18:30 | 10040.2233 |  | 47.04 | 92.4133
USB ¦ Main | 2021-02-19 06:30 | 10040.2333 |  |  |  | 0.83417
USB ¦ Main | 2021-02-19 18:30 | 10041.2125 |  | 41.2154 | 81.5967
USB ¦ Main | 2021-02-20 06:30 | 10041.2325 |  |  |  | 1.6675
USB ¦ Main | 2021-02-20 18:30 | 10041.2425 |  | 1.25 | 0.8325
USB ¦ Main | 2021-02-21 06:30 | 10041.2625 |  |  |  | 1.665
USB ¦ Main | 2021-02-21 18:30 | 10041.3524 |  | 4.5787 | 7.4925
USB ¦ Main | 2021-02-22 06:30 | 10041.3624 |  |  |  | 0.8325
USB ¦ Main | 2021-02-22 18:30 | 10043.1312 |  | 74.1179 | 147.4033
USB ¦ Main | 2021-02-23 06:30 | 10043.1812 |  |  |  | 4.1642
USB ¦ Main | 2021-02-23 18:30 | 10044.5101 |  | 57.4546 | 110.745
USB ¦ Main | 2021-02-24 06:30 | 10044.5301 |  |  |  | 1.665
USB ¦ Main | 2021-02-24 18:30 | 10047.9986 |  | 145.3558 | 289.0467
USB ¦ Main | 2021-02-25 06:30 | 10048.0187 |  |  |  | 1.6675
USB ¦ Main | 2021-02-25 18:30 | 10049.3973 |  | 58.2792 | 114.8908
USB ¦ Main | 2021-02-26 06:30 | 10049.4074 |  |  |  | 0.83417
USB ¦ Main | 2021-02-26 18:30 | 10050.5064 |  | 46.2104 | 91.5867
USB ¦ Main | 2021-02-27 06:30 | 10050.5164 |  |  |  | 0.835
USB ¦ Main | 2021-02-27 18:30 | 10050.5364 |  | 1.25 | 1.665
USB ¦ Main | 2021-02-28 06:30 | 10050.5464 |  |  |  | 0.8325
USB ¦ Main | 2021-02-28 18:30 | 10050.5764 |  | 1.665 | 2.4975
USB ¦ Main | 2021-03-01 06:30 | 10050.6163 |  |  |  | 3.3292
USB ¦ Main | 2021-03-01 18:30 | 10052.0253 |  | 60.3704 | 117.4117
USB ¦ Main | 2021-03-02 06:30 | 10052.0353 |  |  |  | 0.83417
USB ¦ Main | 2021-03-02 18:30 | 10053.3642 |  | 55.7896 | 110.745
USB ¦ Main | 2021-03-03 06:30 | 10053.3742 |  |  |  | 0.8325
USB ¦ Main | 2021-03-03 18:30 | 10056.3731 |  | 125.37 | 249.9075
USB ¦ Main | 2021-03-04 06:30 | 10056.3931 |  |  |  | 1.665
USB ¦ Main | 2021-03-04 18:30 | 10057.8519 |  | 61.6192 | 121.5733
USB ¦ Main | 2021-03-05 06:30 | 10057.852 |  |  |  | 0.0016667
USB ¦ Main | 2021-03-05 18:30 | 10059.4208 |  | 65.3692 | 130.7367
USB ¦ Main | 2021-03-06 06:30 | 10059.4408 |  |  |  | 1.6675
USB ¦ Main | 2021-03-06 18:30 | 10059.4508 |  | 1.25 | 0.8325
USB ¦ Main | 2021-03-07 06:30 | 10059.4608 |  |  |  | 0.8325
USB ¦ Main | 2021-03-07 18:30 | 10059.4608 |  | 0.41625 | 0
USB ¦ Main | 2021-03-08 06:30 | 10059.4908 |  |  |  | 2.4967
USB ¦ Main | 2021-03-08 18:30 | 10060.7797 |  | 54.9563 | 107.4158
USB ¦ Main | 2021-03-09 06:30 | 10060.7897 |  |  |  | 0.8325
USB ¦ Main | 2021-03-09 18:30 | 10062.0887 |  | 54.54 | 108.2475
USB ¦ Main | 2021-03-10 06:30 | 10062.0887 |  |  |  | 0
USB ¦ Main | 2021-03-10 18:30 | 10064.4575 |  | 98.6992 | 197.3983
USB ¦ Main | 2021-03-11 06:30 | 10064.4675 |  |  |  | 0.83417
USB ¦ Main | 2021-03-11 18:30 | 10065.5567 |  | 45.7996 | 90.765
USB ¦ Main | 2021-03-12 06:30 | 10065.5767 |  |  |  | 1.665
USB ¦ Main | 2021-03-12 18:30 | 10066.6456 |  | 45.3713 | 89.0775
USB ¦ Main | 2021-03-13 06:30 | 10066.6556 |  |  |  | 0.8325
USB ¦ Main | 2021-03-13 18:30 | 10066.6855 |  | 1.665 | 2.4975
USB ¦ Main | 2021-03-14 06:30 | 10066.6955 |  |  |  | 0.8325
USB ¦ Main | 2021-03-14 18:30 | 10066.7155 |  | 1.2487 | 1.665
USB ¦ Main | 2021-03-15 06:30 | 10066.7255 |  |  |  | 0.8325
USB ¦ Main | 2021-03-15 18:30 | 10068.2243 |  | 62.8679 | 124.9033
USB ¦ Main | 2021-03-16 06:30 | 10068.2843 |  |  |  | 4.9958
USB ¦ Main | 2021-03-16 18:30 | 10070.1031 |  | 78.2812 | 151.5667
USB ¦ Main | 2021-03-17 06:30 | 10070.1431 |  |  |  | 3.3317
USB ¦ Main | 2021-03-17 18:30 | 10074.4219 |  | 179.9504 | 356.5692
USB ¦ Main | 2021-03-18 06:30 | 10074.5018 |  |  |  | 6.6617
USB ¦ Main | 2021-03-18 18:30 | 10075.691 |  | 52.8792 | 99.0967
USB ¦ Main | 2021-03-19 06:30 | 10075.741 |  |  |  | 4.1642
USB ¦ Main | 2021-03-19 18:30 | 10076.81 |  | 46.6267 | 89.0892
USB ¦ Main | 2021-03-20 06:30 | 10076.8201 |  |  |  | 0.835
USB ¦ Main | 2021-03-20 18:30 | 10076.84 |  | 1.25 | 1.665
USB ¦ Main | 2021-03-21 06:30 | 10076.86 |  |  |  | 1.665
USB ¦ Main | 2021-03-21 18:30 | 10076.86 |  | 0.8325 | 0
USB ¦ Main | 2021-03-22 06:30 | 10076.88 |  |  |  | 1.665
USB ¦ Main | 2021-03-22 18:30 | 10078.539 |  | 69.9554 | 138.2458
USB ¦ Main | 2021-03-23 06:30 | 10078.549 |  |  |  | 0.83417
USB ¦ Main | 2021-03-23 18:30 | 10079.7679 |  | 51.2054 | 101.5767
USB ¦ Main | 2021-03-24 06:30 | 10079.8278 |  |  |  | 4.9975
USB ¦ Main | 2021-03-24 18:30 | 10082.1868 |  | 100.79 | 196.5825
USB ¦ Main | 2021-03-25 06:30 | 10082.2068 |  |  |  | 1.665
USB ¦ Main | 2021-03-25 18:30 | 10083.336 |  | 47.88 | 94.095
USB ¦ Main | 2021-03-26 06:30 | 10083.3559 |  |  |  | 1.665
USB ¦ Main | 2021-03-26 18:30 | 10084.685 |  | 56.2079 | 110.7508
USB ¦ Main | 2021-03-27 06:30 | 10086.8544 |  |  |  | 180.7883
USB ¦ Main | 2021-03-27 18:30 | 10089.0039 |  | 179.9579 | 179.1275
USB ¦ Main | 2021-03-28 06:30 | 10091.1036 |  |  |  | 174.97
USB ¦ Main | 2021-03-28 18:30 | 10093.2831 |  | 178.2992 | 181.6283
USB ¦ Main | 2021-03-29 06:30 | 10095.4428 |  |  |  | 179.9692
USB ¦ Main | 2021-03-29 18:30 | 10098.7715 |  | 228.6817 | 277.3942
USB ¦ Main | 2021-03-30 06:30 | 10100.8911 |  |  |  | 176.6325
USB ¦ Main | 2021-03-30 18:30 | 10103.1298 |  | 181.5975 | 186.5625
USB ¦ Main | 2021-03-31 06:30 | 10103.3697 |  |  |  | 19.9892
USB ¦ Main | 2021-03-31 18:30 | 10107.4486 |  | 179.9475 | 339.9058
USB ¦ Main | 2021-04-01 06:30 | 10109.4981 |  |  |  | 170.7975
USB ¦ Main | 2021-04-01 18:30 | 10112.3869 |  | 205.7654 | 240.7333
USB ¦ Main | 2021-04-02 06:30 | 10114.5365 |  |  |  | 179.1317
USB ¦ Main | 2021-04-02 18:30 | 10116.7061 |  | 179.9642 | 180.7967
USB ¦ Main | 2021-04-03 06:30 | 10118.7656 |  |  |  | 171.6283
USB ¦ Main | 2021-04-03 18:30 | 10120.9451 |  | 176.6267 | 181.625
USB ¦ Main | 2021-04-04 06:30 | 10123.1147 |  |  |  | 180.7975
USB ¦ Main | 2021-04-04 18:30 | 10125.2742 |  | 180.3804 | 179.9633
USB ¦ Main | 2021-04-05 06:30 | 10127.3836 |  |  |  | 175.7842
USB ¦ Main | 2021-04-05 18:30 | 10129.6032 |  | 180.3713 | 184.9583
USB ¦ Main | 2021-04-06 06:30 | 10131.7027 |  |  |  | 174.9658
USB ¦ Main | 2021-04-06 18:30 | 10135.2016 |  | 233.2675 | 291.5692
USB ¦ Main | 2021-04-07 06:30 | 10137.4011 |  |  |  | 183.2933
USB ¦ Main | 2021-04-07 18:30 | 10141.1898 |  | 249.5108 | 315.7283
USB ¦ Main | 2021-04-08 06:30 | 10143.2794 |  |  |  | 174.1342
USB ¦ Main | 2021-04-08 18:30 | 10146.7582 |  | 232.0146 | 289.895
USB ¦ Main | 2021-04-09 06:30 | 10148.8078 |  |  |  | 170.7992
USB ¦ Main | 2021-04-09 18:30 | 10150.9669 |  | 175.3621 | 179.925
USB ¦ Main | 2021-04-10 06:30 | 10150.9669 |  |  |  | 0.0016667
USB ¦ Main | 2021-04-10 18:30 | 10150.9969 |  | 1.2496 | 2.4975
USB ¦ Main | 2021-04-11 06:30 | 10151.0268 |  |  |  | 2.4975
USB ¦ Main | 2021-04-11 18:30 | 10151.0768 |  | 3.33 | 4.1625
USB ¦ Main | 2021-04-12 06:30 | 10151.1167 |  |  |  | 3.3292
USB ¦ Main | 2021-04-12 18:30 | 10152.5557 |  | 61.6221 | 119.915
USB ¦ Main | 2021-04-13 06:30 | 10152.6857 |  |  |  | 10.8325
USB ¦ Main | 2021-04-13 18:30 | 10153.9646 |  | 58.7037 | 106.575
USB ¦ Main | 2021-04-14 06:30 | 10153.9746 |  |  |  | 0.8325
USB ¦ Main | 2021-04-14 18:30 | 10157.0535 |  | 128.7029 | 256.5733
USB ¦ Main | 2021-04-15 06:30 | 10157.1635 |  |  |  | 9.165
USB ¦ Main | 2021-04-15 18:30 | 10158.8625 |  | 75.3758 | 141.5867
USB ¦ Main | 2021-04-16 06:30 | 10159.0024 |  |  |  | 11.655
USB ¦ Main | 2021-04-16 18:30 | 10160.3613 |  | 62.4517 | 113.2483
USB ¦ Main | 2021-04-17 06:30 | 10160.3713 |  |  |  | 0.83417
USB ¦ Main | 2021-04-17 18:30 | 10160.3913 |  | 1.2496 | 1.665
USB ¦ Main | 2021-04-18 06:30 | 10160.4213 |  |  |  | 2.4975
USB ¦ Main | 2021-04-18 18:30 | 10160.4712 | 7504 | 3.33 | 4.1625

## SolarRadiation Newcastle
From Figure 1b in
https://doi.org/10.1016/j.solener.2018.01.013
| Monthly global horizontal solar irradiance. | Average daily global horizontal solar irradiance
| kWh/m2 | kWh/m2
January | 19 | 0.6129
February | 33 | 1.1786
March | 74 | 2.3871
April | 121 | 4.0333
May | 150 | 4.8387
June | 146 | 4.8667
July | 145 | 4.6774
August | 102 | 3.2903
September | 85 | 2.8333
October | 50 | 1.6129
November | 28 | 0.93333
December | 15 | 0.48387
Year | 968
Year 2013 Drummond Building weather station
Monthly global horizontal solar irradiance.
kWh/m2
January | 13.07
February | 36.46
March | 65.53
April | 88.03
May | 126.75
June | 129.39
July | 157.09
August | 125.76
September | 80.65
October | 84.04
November | 17.52
December | 9.03

## DB Solar Panel Efficiency
Specific annual photovoltaic power output | kWp rating |  | Panel area |  | Average of efficiency measures before cleaning |  |  | Estimated electricity generation 2009-2019 |  |  |  | Predicted electricity 2004-2019 |  | Actual versus anticipated
kWh/kWp | kWp rating |  | m2 |  | % |  |  | MWh |  |  |  | MWh
956 | 25 |  | 150 |  | 13.9061 |  |  | 222.1079 |  |  |  | 382.4 |  | 58.08%
https://globalsolaratlas.info/map?c=55.128649,-1.838837,9&s=55.001251,-1.601584&m=site
Brian Russell report | Joseph Dakkak Meng thesis 2015 | [7 empty] | Xiaoshan Liang MSc thesis 2015 | [8 empty] | Jian Zang
Table 2
Date | Date | Start time | Time period | Solar Energy produced | Solar Power produced | Solar Radiation | Efficiency |  | Date | Time |  | Time passed | Displayboard reading | Solar Energy produced | Average solar power produced over interval | Average solar radiation over interval | Average efficiency over interval | Date | Time |  | Time passed | Displayboard reading | Solar Energy produced | Average solar power produced over interval | Average solar radiation over interval | Average efficiency over interval | Avg daily electricity generation | Avg daily solar irradiation | Avg efficiency
10/07/12 to 02/07/13 |  |  | h | MWh | W/m2 | W/m2 |  |  |  | h | min | h | MWh | MWh | W/m2 | W/m2 | % |  | h | min | h | kWh | MWh | W/m2 | W/m2 | % | kWh/(m2d) | kWh/(m2d)
kWh | 2015-03-04 | 9:30 | 7 | 0.08 | 76.1905 | 377 | 20.2097 |  | 20150423 | 11 | 33 |  | 103.41 |  |  |  |  | 2019-06-10 | 15 | 22 |  | 116462
17911.5 | 2015-03-05 | 9:30 | 7 | 0.03 | 28.5714 | 160 | 17.8571 |  | 20150526 | 15 | 24 | 795.85 | 106.14 |  |  |  |  | 2019-06-17 | 15 | 45 | 168 | 117246 | 0.784 | 31.1111 | 202.7778 | 15.3425 | 0.74667 | 4.8667 | 15.3425
| 2015-03-06 | 9:30 | 7 | 0.04 | 38.0952 | 248 | 15.361 |  | 20150529 | 16 | 24 | 73 | 106.42 | 0.28 | 25.5708 | 195.6822 | 13.0675 | 2019-06-24 | 16 | 7 | 168.25 | 118658 | 1.412 | 55.9485 | 202.7778 | 27.591 | 1.3428 | 4.8667 | 27.591
Efficiency | 2015-04-09 | 9:30 | 6 | 0.08 | 88.8889 | 542 | 16.4002 |  | 20150601 | 16 | 54 | 72.5 | 106.72 | 0.3 | 27.5862 | 228.1445 | 12.0915 | 2019-07-03 | 16 | 9 | 216 | 119456 | 0.798 | 24.6296 | 202.3148 | 12.1739 | 0.59111 | 4.8556 | 12.1739
12.3357 | 2015-04-13 | 10:20 | 6.17 | 0.05 | 54.0249 | 291 | 18.5652 |  | 20150602 | 16 | 20 | 23.43 | 106.82 | 0.1 | 28.4535 | 206.736 | 13.7632 | 2019-08-05 | 16 | 30 | 792.5 | 122538 | 3.082 | 25.9264 | 192.3401 | 13.4795 | 0.62223 | 4.6162 | 13.4795
| 2015-04-14 | 9:30 | 7 | 0.03 | 28.5714 | 282 | 10.1317 |  | 20150603 | 16 | 10 | 23.83 | 106.96 | 0.14 | 39.1663 | 224.4905 | 17.4468 | 2019-09-13 | 17 | 9 | 936.5 | 124494 | 1.956 | 13.9242 | 133.7963 | 10.407 | 0.33418 | 3.2111 | 10.407
Actual to theoretical | 2015-04-15 | 9:30 | 5 | 0.05 | 66.6667 | 349 | 19.1022 |  | 20150604 | 17 | 0 | 24.83 | 107.1 | 0.14 | 37.5889 | 265.4136 | 14.1624 | 2019-11-14 | 15 | 0 | 1486 | 126827 | 2.333 | 10.4666 | 75.8737 | 13.7947 | 0.2512 | 1.821 | 13.7947
0.74944 | 2015-04-16 | 9:10 | 7.75 | 0.1 | 86.0215 | 572 | 15.0387 |  | 20150605 | 16 | 10 | 23.17 | 107.19 | 0.09 | 25.8956 | 197.4783 | 13.1131 | 2020-02-17 | 15 | 0 | 2280 | 128894 | 2.067 | 6.0439 | 30.1608 | 20.0388 | 0.14505 | 0.72386 | 20.0388
| 2015-04-20 | 9:55 | 7 | 0.08 | 76.1905 | 569 | 13.3902 |  | 20150609 | 14 | 4 | 93.9 | 107.58 | 0.39 | 27.689 | 238.5853 | 11.6055 | 2020-02-24 | 15 | 48 | 168.75 | 129278 | 0.384 | 15.1704 | 45.8333 | 33.099 | 0.36409 | 1.1 | 33.099
| 2015-04-21 | 10:55 | 6 | 0.08 | 88.8889 | 600 | 14.8148 |  | 20150610 | 16 | 4 | 26 | 107.74 | 0.16 | 41.0256 | 350.7514 | 11.6965
| 2015-04-22 | 10:30 | 6 | 0.08 | 88.8889 | 626 | 14.1995 |  | 20150611 | 12 | 55 | 20.85 | 107.84 | 0.1 | 31.9744 | 266.1311 | 12.0145 | [7 empty] | Average | 18.2408
| 2015-04-24 | 9:55 | 7 | 0.07 | 66.6667 | 387 | 17.2265 |  | 20150616 | 12 | 18 | 119.38 | 108.27 | 0.43 | 24.013 | 210.4983 | 11.4077 | [7 empty] | Stdev | 8.1103
| 2015-04-28 | 9:25 | 7.5 | 0.08 | 71.1111 | 410 | 17.3442 |  | 20150617 | 14 | 29 | 26.18 | 108.33 | 0.06 | 15.2788 | 123.3882 | 12.3827
| 2015-04-29 | 9:55 | 7 | 0.06 | 57.1429 | 375 | 15.2381 |  | 20150618 | 15 | 16 | 24.78 | 108.41 | 0.08 | 21.5227 | 172.4315 | 12.4819 | [6 empty] | Before cleaning | Average | 15.4648
| 2015-04-30 | 9:55 | 7 | 0.05 | 47.619 | 410 | 11.6144 |  | 20150619 | 16 | 54 | 25.63 | 108.48 | 0.07 | 18.2078 | 137.6154 | 13.2309 | [7 empty] | Stdev | 6.8348
| 2015-05-05 | 10:25 | 6.5 | 0.03 | 30.7692 | 266 | 11.5674 |  | 20150623 | 12 | 20 | 91.43 | 108.65 | 0.17 | 12.3956 | 106.1727 | 11.675
| 2015-05-06 | 10:10 | 6.75 | 0.04 | 39.5062 | 317 | 12.4625 |  | 20150624 | 15 | 12 | 26.86 | 108.73 | 0.08 | 19.856 | 189.143 | 10.4979 | [6 empty] | After cleaning | Average | 26.5689
| 2015-05-07 | 9:50 | 7.1 | 0.08 | 75.1174 | 563 | 13.3423 |  | 20150625 | 13 | 12 | 22 | 108.77 | 0.04 | 12.1212 | 84.5634 | 14.3339 | [7 empty] | Stdev | 9.235
[9 empty] | 20150626 | 16 | 48 | 27.6 | 108.83 | 0.06 | 14.4928 | 125.5108 | 11.547
[6 empty] | Average | 15.2148 |  | 20150630 | 15 | 59 | 95.18 | 109.17 | 0.34 | 23.8145 | 204.0617 | 11.6703
[6 empty] | Stdev | 2.8286 |  | 20150701 | 12 | 2 | 20.05 | 109.24 | 0.07 | 23.2751 | 219.2384 | 10.6164
[9 empty] | 20150702 | 14 | 19 | 26.28 | 109.37 | 0.13 | 32.9782 | 238.8043 | 13.8097
[9 empty] | 20150703 | 16 | 43 | 26.4 | 109.5 | 0.13 | 32.8283 | 249.7555 | 13.1442
[9 empty] | 20150706 | 14 | 58 | 70.25 | 109.75 | 0.25 | 23.7248 | 190.0497 | 12.4835
[9 empty] | 20150708 | 13 | 20 | 46.36 | 109.86 | 0.11 | 15.8182 | 119.9343 | 13.1891
[9 empty] | 20150709 | 15 | 29 | 26.15 | 109.97 | 0.11 | 28.0433 | 233.1091 | 12.0301
[9 empty] | 20150713 | 13 | 16 | 93.783 | 110.31 | 0.34 | 24.1693 | 183.1058 | 13.1996
[9 empty] | 20150714 | 15 | 27 | 26.18 | 110.36 | 0.05 | 12.7324 | 113.9498 | 11.1737
[16 empty] | Average | 12.609
[16 empty] | Stdev | 1.4294

## USB Solar Panel Efficiency
kWp rating | Specific annual photovoltaic power output | Panel area
kWp | kWh/kWp | m2
34.5 | 956 | 202.9
| Average electricity generation in 2019 | Average solar electricity generation | Average solar radiation | Efficiency
| kWh/d | kWh/(m2d) | kWh/(m2d) | %
Jan | 13.815 | 68.0878 | 612.9032 | 11.11%
Feb | 42.4102 | 209.02 | 1178.5714 | 17.74%
Mar | 58.9224 | 290.4013 | 2387.0968 | 12.17%
Apr | 95.4919 | 470.6355 | 4033.3333 | 11.67%
May | 113.0515 | 557.1783 | 4838.7097 | 11.52%
June | 104.6563 | 515.8024 | 4866.6667 | 10.6%
July | 96.772 | 476.9444 | 4677.4194 | 10.2%
Aug | 91.0119 | 448.5556 | 3290.3226 | 13.63%
Sept | 79.7936 | 393.2655 | 2833.3333 | 13.88%
Oct | 52.7209 | 259.8369 | 1612.9032 | 16.11%
Nov | 14.7574 | 72.7326 | 933.3333 | 7.793%
Dec | 4.5926 | 22.6346 | 483.871 | 4.678%
|  |  | Average | 11.76%
Predicted performance | Actual performance |  | Stdev | 3.477%
kWh per year | kWh in 2019
32982 | 23385.9387
Ratio actual to theoretical
0.70905
Efficiency
%
11.9069
Generation over 4 years theory | Generation over 4 years actual | Ratio actual to theory
131.928 | 93.5438 | 0.70905

## NPV SPS DB theory
Initial investment | £ |  | 101012
Discount rate |  |  | 0.045 | BoE 2004
Inflation rate |  |  | 0.013 | CPI 2004
Theoretical annual electricity generation | kWh per year |  | 23900
Electricity charges | £ per kWh |  | 0.04584 | Commercial price medium 2004
Year
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
Costs |  |  |  | -101012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings |  |  |  |  | 1095.576 | 1109.8185 | 1124.2461 | 1138.8613 | 1153.6665 | 1168.6642 | 1183.8568 | 1199.247 | 1214.8372 | 1230.6301 | 1246.6282 | 1262.8344 | 1279.2513 | 1295.8815 | 1312.728 | 1329.7935 | 1347.0808 | 1364.5928 | 1382.3325 | 1400.3028 | 1418.5068 | 1436.9474 | 1455.6277 | 1474.5508 | 1493.72 | 1513.1384 | 1532.8092 | 1552.7357 | 1572.9213 | 1593.3692 | 1614.083 | 1635.0661 | 1656.322 | 1677.8542 | 1699.6663 | 1721.7619 | 1744.1448 | 1766.8187 | 1789.7873 | 1813.0546 | 1836.6243 | 1860.5004 | 1884.6869 | 1909.1878 | 1934.0073 | 1959.1494 | 1984.6183 | 2010.4184 | 2036.5538 | 2063.029 | 2089.8484 | 2117.0164 | 2144.5376 | 2172.4166 | 2200.658 | 2229.2666 | 2258.247 | 2287.6043 | 2317.3431 | 2347.4686 | 2377.9857 | 2408.8995 | 2440.2152 | 2471.938 | 2504.0732 | 2536.6261 | 2569.6022 | 2603.0071 | 2636.8462 | 2671.1252 | 2705.8498 | 2741.0258 | 2776.6592 | 2812.7558 | 2849.3216 | 2886.3628 | 2923.8855 | 2961.896 | 3000.4006 | 3039.4058 | 3078.9181 | 3118.944 | 3159.4903 | 3200.5637 | 3242.171 | 3284.3192 | 3327.0154 | 3370.2666 | 3414.0801 | 3458.4631 | 3503.4231 | 3548.9676 | 3595.1042 | 3641.8406 | 3689.1845 | 3737.1439 | 3785.7268 | 3834.9412 | 3884.7954 | 3935.2978
Net savings (minus costs) | £ |  |  | -101012 | 1095.576 | 1109.8185 | 1124.2461 | 1138.8613 | 1153.6665 | 1168.6642 | 1183.8568 | 1199.247 | 1214.8372 | 1230.6301 | 1246.6282 | 1262.8344 | 1279.2513 | 1295.8815 | 1312.728 | 1329.7935 | 1347.0808 | 1364.5928 | 1382.3325 | 1400.3028 | 1418.5068 | 1436.9474 | 1455.6277 | 1474.5508 | 1493.72 | 1513.1384 | 1532.8092 | 1552.7357 | 1572.9213 | 1593.3692 | 1614.083 | 1635.0661 | 1656.322 | 1677.8542 | 1699.6663 | 1721.7619 | 1744.1448 | 1766.8187 | 1789.7873 | 1813.0546 | 1836.6243 | 1860.5004 | 1884.6869 | 1909.1878 | 1934.0073 | 1959.1494 | 1984.6183 | 2010.4184 | 2036.5538 | 2063.029 | 2089.8484 | 2117.0164 | 2144.5376 | 2172.4166 | 2200.658 | 2229.2666 | 2258.247 | 2287.6043 | 2317.3431 | 2347.4686 | 2377.9857 | 2408.8995 | 2440.2152 | 2471.938 | 2504.0732 | 2536.6261 | 2569.6022 | 2603.0071 | 2636.8462 | 2671.1252 | 2705.8498 | 2741.0258 | 2776.6592 | 2812.7558 | 2849.3216 | 2886.3628 | 2923.8855 | 2961.896 | 3000.4006 | 3039.4058 | 3078.9181 | 3118.944 | 3159.4903 | 3200.5637 | 3242.171 | 3284.3192 | 3327.0154 | 3370.2666 | 3414.0801 | 3458.4631 | 3503.4231 | 3548.9676 | 3595.1042 | 3641.8406 | 3689.1845 | 3737.1439 | 3785.7268 | 3834.9412 | 3884.7954 | 3935.2978
|  | Year | NPV
£
|  | 0 | -101012
|  | 1 | -99963.6019
|  | 2 | -98947.3079
|  | 3 | -97962.1348
|  | 4 | -97007.1297
|  | 5 | -96081.3688
|  | 6 | -95183.9566
|  | 7 | -94314.0249
|  | 8 | -93470.7323
|  | 9 | -92653.2629
|  | 10 | -91860.8262
|  | 11 | -91092.6554
|  | 12 | -90348.0076
|  | 13 | -89626.1624
|  | 14 | -88926.4215
|  | 15 | -88248.1082
|  | 16 | -87590.5661
|  | 17 | -86953.1593
|  | 18 | -86335.2711
|  | 19 | -85736.304
|  | 20 | -85155.6784
|  | 21 | -84592.8328
|  | 22 | -84047.2226
|  | 23 | -83518.3201
|  | 24 | -83005.6136
|  | 25 | -82508.6073
|  | 26 | -82026.8202
|  | 27 | -81559.7865
|  | 28 | -81107.0543
|  | 29 | -80668.1856
|  | 30 | -80242.756
|  | 31 | -79830.3539
|  | 32 | -79430.5804
|  | 33 | -79043.0488
|  | 34 | -78667.3841
|  | 35 | -78303.2231
|  | 36 | -77950.2134
|  | 37 | -77608.0135
|  | 38 | -77276.2926
|  | 39 | -76954.7295
|  | 40 | -76643.0134
|  | 41 | -76340.8427
|  | 42 | -76047.925
|  | 43 | -75763.977
|  | 44 | -75488.7242
|  | 45 | -75221.9001
|  | 46 | -74963.2467
|  | 47 | -74712.5138
|  | 48 | -74469.4588
|  | 49 | -74233.8467
|  | 50 | -74005.4494
|  | 51 | -73784.0462
|  | 52 | -73569.4228
|  | 53 | -73361.3716
|  | 54 | -73159.6913
|  | 55 | -72964.1869
|  | 56 | -72774.6692
|  | 57 | -72590.9549
|  | 58 | -72412.8663
|  | 59 | -72240.2312
|  | 60 | -72072.8825
|  | 61 | -71910.6583
|  | 62 | -71753.4018
|  | 63 | -71600.9608
|  | 64 | -71453.1878
|  | 65 | -71309.94
|  | 66 | -71171.0787
|  | 67 | -71036.4695
|  | 68 | -70905.9824
|  | 69 | -70779.4911
|  | 70 | -70656.8732
|  | 71 | -70538.0101
|  | 72 | -70422.7868
|  | 73 | -70311.0919
|  | 74 | -70202.8173
|  | 75 | -70097.8583
|  | 76 | -69996.1134
|  | 77 | -69897.4841
|  | 78 | -69801.875
|  | 79 | -99963.6019
|  | 80 | -69619.3504
|  | 81 | -69532.2583
|  | 82 | -69447.8332
|  | 83 | -69365.9933
|  | 84 | -69286.6596
|  | 85 | -69209.7552
|  | 86 | -69135.2057
|  | 87 | -69062.9391
|  | 88 | -68992.8855
|  | 89 | -68924.977
|  | 90 | -68859.1481
|  | 91 | -68795.3349
|  | 92 | -68733.4759
|  | 93 | -68673.5111
|  | 94 | -68615.3825
|  | 95 | -68559.0339
|  | 96 | -68504.4109
|  | 97 | -68451.4605
|  | 98 | -68400.1316
|  | 99 | -68350.3744
|  | 100 | -68302.141

## NPV SPS DB real
Initial investment | £ |  | 101012
Discount rate |  |  | 0.045 | BoE 2004
Inflation rate |  |  | 0.013 | CPI 2004
Annual global horizontal solar irradiance | kWh per m2 and year |  | 968
Panel area | m2 |  | 150
Electricity charges | £ per kWh |  | 0.04584 | Commercial price medium 2004
Inverter replacement 2012 | £ |  | 9828
G59 protection 2012 | £ |  | 2388
Cable upgrade 2014 | £ |  | 4243
Panel cleaning 2019 | £ |  | 3814
|  |  |  | Efficiency % | 0 | 0 | 0 | 0 | 0 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 13.9061 | 26.5689
|  |  |  | Electricity price £/kWh | 0.04584 | 0.05904 | 0.07788 | 0.08064 | 0.09168 | 0.10248 | 0.09012 | 0.09492 | 0.10308 | 0.11004 | 0.11544 | 0.12048 | 0.12012 | 0.12588 | 0.13836 | 0.15072 | 0.15864
|  |  |  | Year | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Cost of repairs |  |  |  | 0: -101012; 9: -12216; 11: -4243; 16: -3814
Savings |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 2069.2375 | 1819.669 | 1916.5888 | 2081.3525 | 2221.8862 | 2330.9209 | 2432.6867 | 2425.4177 | 2541.7215 | 2793.7129 | 3043.2814 | 6120.0171
Net savings (minus costs) | £ |  |  | -101012 | 0 | 0 | 0 | 0 | 0 | 2069.2375 | 1819.669 | 1916.5888 | -10134.6475 | 2221.8862 | -1912.0791 | 2432.6867 | 2425.4177 | 2541.7215 | 2793.7129 | -770.7186
|  | Year | NPV
£
|  | 0 | -101012
|  | 1 | -101012
|  | 2 | -101012
|  | 3 | -101012
|  | 4 | -101012
|  | 5 | -101012
|  | 6 | -99423.0413
|  | 7 | -98085.8967
|  | 8 | -96738.18
|  | 9 | -103557.8292
|  | 10 | -102127.0952
|  | 11 | -103305.3159
|  | 12 | -101870.8484
|  | 13 | -100502.254
|  | 14 | -99129.7934
|  | 15 | -97686.2248 | 0: Gap
|  | 16 | -98067.3215 | 0: -10476.7554
17
18
19
20
21

## NPV SPS USB theory
Small scale solar costs 2016/17 10-50 kWh | £/kWh installed |  | 1230 | BEIS | https://www.gov.uk/government/statistics/solar-pv-cost-data
Initial investment | £ |  | 42435
Discount rate |  |  | 0.0025 | BoE 2017
Inflation rate |  |  | 0.027 | CPI 2017
Theoretical annual electricity generation | kWh per year |  | 32982
Electricity charges | £ per kWh |  | 0.12588 | Commercial price medium 2017
Year
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Costs |  |  |  | -42435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings |  |  |  |  | 4151.7742 | 4263.8721 | 4378.9966 | 4497.2295 | 4618.6547 | 4743.3584 | 4871.4291 | 5002.9577 | 5138.0375 | 5276.7645 | 5419.2372 | 5565.5566 | 5715.8266 | 5870.1539 | 6028.6481 | 6191.4216 | 6358.5899 | 6530.2719 | 6706.5892 | 6887.6671 | 7073.6341 | 7264.6223 | 7460.7671 | 7662.2078 | 7869.0874 | 8081.5527 | 8299.7547 | 8523.848 | 8753.9919
Net savings (minus costs) | £ |  |  | -42435 | 4151.7742 | 4263.8721 | 4378.9966 | 4497.2295 | 4618.6547 | 4743.3584 | 4871.4291 | 5002.9577 | 5138.0375 | 5276.7645 | 5419.2372 | 5565.5566 | 5715.8266 | 5870.1539 | 6028.6481 | 6191.4216 | 6358.5899 | 6530.2719 | 6706.5892 | 6887.6671 | 7073.6341 | 7264.6223 | 7460.7671 | 7662.2078 | 7869.0874 | 8081.5527 | 8299.7547 | 8523.848 | 8753.9919
|  | Year | NPV
£
|  | 0 | -42435
|  | 1 | -38293.5794
|  | 2 | -34050.947
|  | 3 | -29704.6293
|  | 4 | -25252.0924
|  | 5 | -20690.7404
|  | 6 | -16017.914
|  | 7 | -11230.8888
|  | 8 | -6326.8739
|  | 9 | -1303.0103
|  | 10 | 3843.631
|  | 11 | 9116.0505
|  | 12 | 14517.3223
|  | 13 | 20050.5951
|  | 14 | 25719.0951
|  | 15 | 31526.127
|  | 16 | 37475.0764
|  | 17 | 43569.4116
|  | 18 | 49812.6857
|  | 19 | 56208.5385
|  | 20 | 62760.699
|  | 21 | 69472.987
|  | 22 | 76349.3161
|  | 23 | 83393.695
|  | 24 | 90610.2309
|  | 25 | 98003.1309
|  | 26 | 105576.7054
|  | 27 | 113335.3696
|  | 28 | 121283.6472
|  | 29 | 129426.1719

## NPV SPS USB real
Initial investment | £ |  | 42435
Discount rate |  |  | 0.0025 | BoE 2017
Inflation rate |  |  | 0.027 | CPI 2017
Annual global horizontal solar irradiance | kWh per m2 and year |  | 968
Panel area | m2 |  | 202.9
Electricity charges | £ per kWh |  | 0.12588 | Commercial price medium 2017
|  |  |  | Efficiency % | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568 | 11.7568
|  |  |  | Electricity price £/kWh | 0.12588 | 0.13836 | 0.15072 | 0.15864 | 0.16292 | 0.16732 | 0.17184 | 0.17648 | 0.18124 | 0.18614 | 0.19116 | 0.19633 | 0.20163 | 0.20707 | 0.21266 | 0.2184 | 0.2243
|  |  |  | Year | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2022 | 2023 | 2024
|  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Cost of repairs |  |  |  | 0: -42435
Savings |  |  |  |  | 2906.7217 | 3194.9 | 3480.3074 | 3663.1898 | 3762.0959 | 3863.6725 | 3967.9917 | 4075.1274 | 4185.1559 | 4298.1551 | 4414.2053 | 4533.3888 | 4655.7903 | 4781.4967 | 4910.5971 | 5043.1832 | 5179.3491
Net savings (minus costs) | £ |  |  | -42435 | 2906.7217 | 3194.9 | 3480.3074 | 3663.1898 | 3762.0959 | 3863.6725 | 3967.9917 | 4075.1274 | 4185.1559 | 4298.1551 | 4414.2053 | 4533.3888 | 4655.7903 | 4781.4967 | 4910.5971 | 5043.1832
|  | Year | NPV
£
|  | 0 | -42435
|  | 1 | -39535.527
|  | 2 | -36356.5417
|  | 3 | -32902.2067 | 0: Gap
|  | 4 | -29275.421 | 0: -4023.3285
|  | 5 | -25560.0006
|  | 6 | -21753.7794
|  | 7 | -17854.5384
|  | 8 | -13860.0042
|  | 9 | -9767.8479
|  | 10 | -5575.6839
|  | 11 | -1281.068
|  | 12 | 3118.5037
|  | 13 | 7625.596
|  | 14 | 12242.8368
|  | 15 | 16972.9178
|  | 16 | 21818.5968
|  | 17 | 21818.5968
|  | 18 | 21818.5968
|  | 19 | 21818.5968
|  | 20 | 21818.5968
|  | 21 | 21818.5968
|  | 22 | 21818.5968
|  | 23 | 21818.5968
|  | 24 | 21818.5968
|  | 25 | 21818.5968
|  | 26 | 21818.5968
|  | 27 | 21818.5968
|  | 28 | 21818.5968
|  | 29 | 21818.5968
|  | 30 | 21818.5968
|  | 31 | 21818.5968
|  | 32 | 21818.5968
|  | 33 | 21818.5968
|  | 34 | 21818.5968
|  | 35 | 21818.5968
|  | 36 | 21818.5968
|  | 37 | 21818.5968
|  | 38 | 21818.5968
|  | 39 | 21818.5968
|  | 40 | 21818.5968
|  | 41 | 21818.5968
|  | 42 | 21818.5968
|  | 43 | 21818.5968
|  | 44 | 21818.5968
|  | 45 | 21818.5968
|  | 46 | 21818.5968
|  | 47 | 21818.5968
|  | 48 | 21818.5968
|  | 49 | 21818.5968
|  | 50 | 21818.5968
|  | 51 | 21818.5968
|  | 52 | 21818.5968
|  | 53 | 21818.5968
|  | 54 | 21818.5968
|  | 55 | 21818.5968
|  | 56 | 21818.5968
|  | 57 | 21818.5968
|  | 58 | 21818.5968
|  | 59 | 21818.5968
|  | 60 | 21818.5968
|  | 61 | 21818.5968
|  | 62 | 21818.5968
|  | 63 | 21818.5968
|  | 64 | 21818.5968
|  | 65 | 21818.5968
|  | 66 | 21818.5968
|  | 67 | 21818.5968
|  | 68 | 21818.5968
|  | 69 | 21818.5968
|  | 70 | 21818.5968
|  | 71 | 21818.5968
|  | 72 | 21818.5968
|  | 73 | 21818.5968
|  | 74 | 21818.5968
|  | 75 | 21818.5968
|  | 76 | 21818.5968
|  | 77 | 21818.5968
|  | 78 | 21818.5968
|  | 79 | 21818.5968
|  | 80 | 21818.5968
|  | 81 | 21818.5968
|  | 82 | 21818.5968
|  | 83 | 21818.5968
|  | 84 | 21818.5968
|  | 85 | 21818.5968
|  | 86 | 21818.5968
|  | 87 | 21818.5968
|  | 88 | 21818.5968
|  | 89 | 21818.5968
|  | 90 | 21818.5968
|  | 91 | 21818.5968
|  | 92 | 21818.5968
|  | 93 | 21818.5968
|  | 94 | 21818.5968
|  | 95 | 21818.5968
|  | 96 | 21818.5968
|  | 97 | 21818.5968
|  | 98 | 21818.5968
|  | 99 | 21818.5968
|  | 100 | 21818.5968