## TPC DS Load Data
Bus | P (MW) | Q (MVAr)
A-K | 0 | 0
1 | 0 | 0
2 | 0.1 | 0.05
3 | 0.3 | 0.2
4 | 0.35 | 0.25
5 | 0.22 | 0.1
6 | 1.1 | 0.8
7 | 0.4 | 0.32
8 | 0.3 | 0.2
9 | 0.3 | 0.23
10 | 0.3 | 0.26
11 | 0 | 0
12 | 1.2 | 0.8
13 | 0.8 | 0.6
14 | 0.7 | 0.5
15 | 0 | 0
16 | 0.3 | 0.15
17 | 0.5 | 0.35
18 | 0.7 | 0.4
19 | 1.2 | 1
20 | 0.3 | 0.3
21 | 0.4 | 0.35
22 | 0.05 | 0.02
23 | 0.05 | 0.02
24 | 0.05 | 0.01
25 | 0.05 | 0.03
26 | 0.1 | 0.06
27 | 0.1 | 0.07
28 | 1.8 | 1.3
29 | 0.2 | 0.12
30 | 0 | 0
31 | 1.8 | 1.6
32 | 0.2 | 0.15
33 | 0.2 | 0.1
34 | 0.8 | 0.6
35 | 0.1 | 0.06
36 | 0.1 | 0.06
37 | 0.02 | 0.01
38 | 0.02 | 0.01
39 | 0.02 | 0.01
40 | 0.02 | 0.01
41 | 0.2 | 0.16
42 | 0.05 | 0.03
43 | 0 | 0
44 | 0.03 | 0.02
45 | 0.8 | 0.7
46 | 0.2 | 0.15
47 | 0 | 0
48 | 0 | 0
49 | 0 | 0
50 | 0.2 | 0.16
51 | 0.8 | 0.6
52 | 0.5 | 0.3
53 | 0.5 | 0.35
54 | 0.5 | 0.3
55 | 0.2 | 0.08
56 | 0 | 0
57 | 0.03 | 0.02
58 | 0.6 | 0.42
59 | 0 | 0
60 | 0.02 | 0.01
61 | 0.02 | 0.01
62 | 0.2 | 0.13
63 | 0.3 | 0.24
64 | 0.3 | 0.2
65 | 0 | 0
66 | 0.05 | 0.03
67 | 0 | 0
68 | 0.4 | 0.36
69 | 0 | 0
70 | 0 | 0
71 | 2 | 1.5
72 | 0.2 | 0.15
73 | 0 | 0
74 | 0 | 0
75 | 1.2 | 0.95
76 | 0.3 | 0.18
77 | 0 | 0
78 | 0.4 | 0.36
79 | 2 | 1.3
80 | 0.2 | 0.14
81 | 0.5 | 0.36
82 | 0.1 | 0.03
83 | 0.4 | 0.36
The data have been obtained from C.-T. Su, C.-F. Chang, and J.-P. Chiou, "Distribution network reconfiguration for loss reduction by ant colony search algorithm," Elect. Power Syst. Res., vol. 75, pp. 190-199, Aug. 2005.

## TPC DS Branch Data
Branch | From Bus | To Bus | R (Ω) | X (Ω) | R (pu) | X (pu)
1 | 84 | 1 | 0.1944 | 0.6624 | 0.14958 | 0.5097
2 | 1 | 2 | 0.2096 | 0.4304 | 0.16128 | 0.33118
3 | 2 | 3 | 0.2358 | 0.4842 | 0.18144 | 0.37258
4 | 3 | 4 | 0.0917 | 0.1883 | 0.07056 | 0.14489
5 | 4 | 5 | 0.2096 | 0.4304 | 0.16128 | 0.33118
6 | 5 | 6 | 0.0393 | 0.0807 | 0.03024 | 0.062096
7 | 6 | 7 | 0.0405 | 0.138 | 0.031163 | 0.10619
8 | 7 | 8 | 0.1048 | 0.2152 | 0.08064 | 0.16559
9 | 7 | 9 | 0.2358 | 0.4842 | 0.18144 | 0.37258
10 | 7 | 10 | 0.1048 | 0.2152 | 0.08064 | 0.16559
11 | 84 | 11 | 0.0786 | 0.1614 | 0.06048 | 0.12419
12 | 11 | 12 | 0.3406 | 0.6944 | 0.26208 | 0.53432
13 | 12 | 13 | 0.0262 | 0.0538 | 0.02016 | 0.041397
14 | 12 | 14 | 0.0786 | 0.1614 | 0.06048 | 0.12419
15 | 84 | 15 | 0.1134 | 0.3864 | 0.087258 | 0.29732
16 | 15 | 16 | 0.0524 | 0.1076 | 0.04032 | 0.082795
17 | 16 | 17 | 0.0524 | 0.1076 | 0.04032 | 0.082795
18 | 17 | 18 | 0.1572 | 0.3228 | 0.12096 | 0.24838
19 | 18 | 19 | 0.0393 | 0.0807 | 0.03024 | 0.062096
20 | 19 | 20 | 0.1703 | 0.3497 | 0.13104 | 0.26908
21 | 20 | 21 | 0.2358 | 0.4842 | 0.18144 | 0.37258
22 | 21 | 22 | 0.1572 | 0.3228 | 0.12096 | 0.24838
23 | 21 | 23 | 0.1965 | 0.4035 | 0.1512 | 0.31048
24 | 23 | 24 | 0.131 | 0.269 | 0.1008 | 0.20699
25 | 84 | 25 | 0.0567 | 0.1932 | 0.043629 | 0.14866
26 | 25 | 26 | 0.1048 | 0.2152 | 0.08064 | 0.16559
27 | 26 | 27 | 0.2489 | 0.5111 | 0.19152 | 0.39327
28 | 27 | 28 | 0.0486 | 0.1656 | 0.037396 | 0.12742
29 | 28 | 29 | 0.131 | 0.269 | 0.1008 | 0.20699
30 | 84 | 30 | 0.1965 | 0.396 | 0.1512 | 0.30471
31 | 30 | 31 | 0.131 | 0.269 | 0.1008 | 0.20699
32 | 31 | 32 | 0.131 | 0.269 | 0.1008 | 0.20699
33 | 32 | 33 | 0.0262 | 0.0538 | 0.02016 | 0.041397
34 | 33 | 34 | 0.1703 | 0.3497 | 0.13104 | 0.26908
35 | 34 | 35 | 0.0524 | 0.1076 | 0.04032 | 0.082795
36 | 35 | 36 | 0.4978 | 1.0222 | 0.38304 | 0.78655
37 | 36 | 37 | 0.0393 | 0.0807 | 0.03024 | 0.062096
38 | 37 | 38 | 0.0393 | 0.0807 | 0.03024 | 0.062096
39 | 38 | 39 | 0.0786 | 0.1614 | 0.06048 | 0.12419
40 | 39 | 40 | 0.2096 | 0.4304 | 0.16128 | 0.33118
41 | 38 | 41 | 0.1965 | 0.4035 | 0.1512 | 0.31048
42 | 41 | 42 | 0.2096 | 0.4304 | 0.16128 | 0.33118
43 | 84 | 43 | 0.0486 | 0.1656 | 0.037396 | 0.12742
44 | 43 | 44 | 0.0393 | 0.0807 | 0.03024 | 0.062096
45 | 44 | 45 | 0.131 | 0.269 | 0.1008 | 0.20699
46 | 45 | 46 | 0.2358 | 0.4842 | 0.18144 | 0.37258
47 | 85 | 47 | 0.243 | 0.828 | 0.18698 | 0.63712
48 | 47 | 48 | 0.0655 | 0.1345 | 0.0504 | 0.10349
49 | 48 | 49 | 0.0655 | 0.1345 | 0.0504 | 0.10349
50 | 49 | 50 | 0.0393 | 0.0807 | 0.03024 | 0.062096
51 | 50 | 51 | 0.0786 | 0.1614 | 0.06048 | 0.12419
52 | 51 | 52 | 0.0393 | 0.0807 | 0.03024 | 0.062096
53 | 52 | 53 | 0.0786 | 0.1614 | 0.06048 | 0.12419
54 | 53 | 54 | 0.0524 | 0.1076 | 0.04032 | 0.082795
55 | 54 | 55 | 0.131 | 0.269 | 0.1008 | 0.20699
56 | 85 | 56 | 0.2268 | 0.7728 | 0.17452 | 0.59464
57 | 56 | 57 | 0.5371 | 1.1029 | 0.41328 | 0.84865
58 | 57 | 58 | 0.0524 | 0.1076 | 0.04032 | 0.082795
59 | 58 | 59 | 0.0405 | 0.138 | 0.031163 | 0.10619
60 | 59 | 60 | 0.0393 | 0.0807 | 0.03024 | 0.062096
61 | 60 | 61 | 0.0262 | 0.0538 | 0.02016 | 0.041397
62 | 61 | 62 | 0.1048 | 0.2152 | 0.08064 | 0.16559
63 | 62 | 63 | 0.2358 | 0.4842 | 0.18144 | 0.37258
64 | 63 | 64 | 0.0243 | 0.0828 | 0.018698 | 0.063712
65 | 85 | 65 | 0.0486 | 0.1656 | 0.037396 | 0.12742
66 | 65 | 66 | 0.1703 | 0.3497 | 0.13104 | 0.26908
67 | 66 | 67 | 0.1215 | 0.414 | 0.09349 | 0.31856
68 | 67 | 68 | 0.2187 | 0.7452 | 0.16828 | 0.57341
69 | 68 | 69 | 0.0486 | 0.1656 | 0.037396 | 0.12742
70 | 69 | 70 | 0.0729 | 0.2484 | 0.056094 | 0.19114
71 | 70 | 71 | 0.0567 | 0.1932 | 0.043629 | 0.14866
72 | 71 | 72 | 0.0262 | 0.0528 | 0.02016 | 0.040628
73 | 85 | 73 | 0.324 | 1.104 | 0.24931 | 0.84949
74 | 73 | 74 | 0.0324 | 0.1104 | 0.024931 | 0.084949
75 | 74 | 75 | 0.0567 | 0.1932 | 0.043629 | 0.14866
76 | 75 | 76 | 0.0486 | 0.1656 | 0.037396 | 0.12742
77 | 85 | 77 | 0.2511 | 0.8556 | 0.19321 | 0.65836
78 | 77 | 78 | 0.1296 | 0.4416 | 0.099723 | 0.3398
79 | 78 | 79 | 0.0486 | 0.1656 | 0.037396 | 0.12742
80 | 79 | 80 | 0.131 | 0.264 | 0.1008 | 0.20314
81 | 80 | 81 | 0.131 | 0.264 | 0.1008 | 0.20314
82 | 81 | 82 | 0.0917 | 0.1883 | 0.07056 | 0.14489
83 | 82 | 83 | 0.3144 | 0.6456 | 0.24192 | 0.49677
Extra branches for tie-line switches
84 | 5 | 55 | 0.131 | 0.269 | 0.1008 | 0.20699
85 | 7 | 60 | 0.131 | 0.269 | 0.1008 | 0.20699
86 | 11 | 43 | 0.131 | 0.269 | 0.1008 | 0.20699
87 | 12 | 72 | 0.3406 | 0.6994 | 0.26208 | 0.53817
88 | 13 | 76 | 0.4585 | 0.9415 | 0.3528 | 0.72445
89 | 14 | 18 | 0.5371 | 1.0824 | 0.41328 | 0.83287
90 | 16 | 26 | 0.0917 | 0.1883 | 0.07056 | 0.14489
91 | 20 | 83 | 0.0786 | 0.1614 | 0.06048 | 0.12419
92 | 28 | 32 | 0.0524 | 0.1076 | 0.04032 | 0.082795
93 | 29 | 39 | 0.0786 | 0.1614 | 0.06048 | 0.12419
94 | 34 | 46 | 0.0262 | 0.0538 | 0.02016 | 0.041397
95 | 40 | 42 | 0.1965 | 0.4035 | 0.1512 | 0.31048
96 | 53 | 64 | 0.0393 | 0.0807 | 0.03024 | 0.062096
The data have been obtained from C.-T. Su, C.-F. Chang, and J.-P. Chiou, "Distribution network reconfiguration for loss reduction by ant colony search algorithm," Elect. Power Syst. Res., vol. 75, pp. 190-199, Aug. 2005.

## RBTS Bus 4 DS
Feeder types and lengths
Feeder Type | Length (km) | Feeder Section Numbers
1 | 0.6 | 2, 6, 10, 14, 17, 21, 25, 28, 30, 34, 38, 41, 43, 46, 49, 51, 55, 58, 61, 64, 67
2 | 0.75 | 1, 4, 7, 9, 12, 16, 19, 22, 24, 27, 29, 32, 35, 37, 40, 42, 45, 48, 50, 53, 56, 60, 63, 65
3 | 0.8 | 3, 5, 8, 11, 13, 15, 18, 20, 23, 26, 31, 33, 36, 39, 44, 47, 52, 54, 57, 59, 62, 66
Customer data
Load Level per Load Point (MW)
Number of Load Points | Load Points | Customer Type | Average | Peak
15 | 1-4, 11-13, 18-21, 32-35 | Residential | 0.545 | 0.8869
7 | 5, 14, 15, 22, 23, 36, 37 | Residential | 0.5 | 0.8137
7 | 8, 10, 26-30 | Industrial | 1 | 1.63
2 | 9, 31 | Industrial | 1.5 | 2.445
7 | 6, 7, 16, 17, 24, 25, 38 | Commercial | 0.415 | 0.6714
Total | – | – | 24.58 | 40
The data have been obtained from R. N. Allan, R. Billinton, I. Sjarief, L. Goel, and K. S. So, "A reliability test system for educational purposes – Basic distribution system data and results," IEEE Trans. Power Syst., vol. 6, pp. 813-820, May 1991.
Load Points 8-10 and 26-31 (shown in bold in the table above) have been considered to be industrial, since there was no available Customer Damage Function for their original type (small users in the reference above).

## Component Reliability Data
Component Reliability Data
Component | permanent (total) failure rate (λp) [f/yr] | active failure rate (λΑ) [f/yr] | maintenance outage rate (λ'') [out/yr] | repair time (r) [hr] | maintenance outage time (r'') [hr] | probability that a circuit breaker fails to open when required (Pc)
Transformers
33/11 kV | 0.015 | 0.015 | 1 | 15 | 120 | –
11/0.4 kV | 0.015 | 0.015 | – | 10* | – | –
CBs
33 kV | 0.002 | 0.0015 | 0.5 | 4 | 96 | 0.05
11 kV | 0.006 | 0.004 | 1 | 4 | 72 | 0.05
Busbars
33 kV | 0.001 | 0.001 | 0.5 | 2 | 8 | –
11 kV | 0.001 | 0.001 | 1 | 2 | 8 | –
Lines**
33 kV | 0.046 | 0.046 | 0.5 | 8 | 8 | –
11 kV | 0.065 | 0.065 | – | 5 | – | –
* Replacement time by a spare
** Failure rates for lines in f/yr∙km
The data have been obtained from R. N. Allan, R. Billinton, I. Sjarief, L. Goel, and K. S. So, "A reliability test system for educational purposes – Basic distribution system data and results," IEEE Trans. Power Syst., vol. 6, pp. 813-820, May 1991.

## Condition-based Failure Rates
Failure rate model parameters for selected asset types (failure rate for OHLs/UGCs in f/yr∙km)
Asset Type | λ(0) | λ(0.5) | λ(1) | A | B | C
Transformer | 0.0075 | 0.04 | 0.14 | 0.01565 | 2.2479 | -0.0081
CB | 0.0005 | 0.01 | 0.06 | 0.00223 | 3.3215 | -0.0017
UGC | 0.0009 | 0.043 | 0.73 | 0.00282 | 5.5597 | -0.0019
OHL | 0.0062 | 0.062 | 0.373 | 0.01228 | 3.4296 | -0.0061
Busbar | 0.0005 | 0.01 | 0.076 | 0.0016 | 3.8767 | -0.0011
The data have been obtained from R. E. Brown, G. Frimpong, and H. L. Willis, "Failure rate modeling using equipment inspection data," IEEE Trans. Power Syst., vol. 19, pp. 782-787, May 2004.

## Customer Interruption Costs
Cost of interruption by customer type and outage duration (2019 $/kW)
Interruption Duration
User Sector | 1 min | 20 min | 1 hr | 4 hr | 8 hr
Industrial | 2.853 | 6.791 | 15.95 | 44.176 | 97.976
Commercial | 0.668 | 5.213 | 15.014 | 54.98 | 145.728
Residential | 0.002 | 0.163 | 0.846 | 8.267 | 27.545
Office Buildings | 8.389 | 17.342 | 36.982 | 120.837 | 209.197
The data have been obtained from R. Billinton and R. N. Allan, Reliability Evaluation of Power Systems, 2nd ed. New York: Plenum, 1996 and have been expressed in today's (2019) U.S. dollars.