## Networks config
|  |  | Gas network-Branch Data | [19 empty] | System Data
Branch# | From | To | Length(m) | Dia(mm) | Roughness(mm) | pipe Eff. Factor | [15 empty] | Parameter | value | Unit
1 | 1 | 2 | 200 | 45 | 0.01 | 0.98 | [15 empty] | MATPOWER Case Format | 2 | --
2 | 2 | 3 | 12 | 45 | 0.01 | 0.98 |  | Gas mix. Desc. | inj. Code | CH4 | C2H6 | C3H8 | C4H10 | CO2 | N2 | H2 | [5 empty] | system MVA base | 100 | --
3 | 3 | 4 | 100 | 45 | 0.01 | 0.98 |  | Natural Gas | 1 | 0.9 | 0.06 | 0.01 | 0.005 | 0.005 | 0.02 | 0 | [5 empty] | maximum number of matpower-Newton iterations | 1000 | --
4 | 3 | 5 | 177 | 45 | 0.01 | 0.98 |  | 30% H2 | 2 | 0.617 | 0.05 | 0.005 | 0.005 | 0.005 | 0.018 | 0.3 | [5 empty] | opex-Gas-Dist. | 9.5 | £/MWh
5 | 5 | 6 | 100 | 45 | 0.01 | 0.98 |  | high CH4 | 3 | 0.94 | 0 | 0 | 0 | 0.025 | 0.025 | 0.01 | [5 empty] | opex-Elec-Dist. | 28.06 | £/MWh
6 | 6 | 7 | 41 | 45 | 0.01 | 0.98 |  | 100% H2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [5 empty] | Emission-Gas | 232 | kg.CO2.eq./MWh
[8 empty] | 2 component NG | 5 | 0.95 | 0.05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Emission-Elec | 173 | kg.CO2.eq./MWh
[22 empty] | timestep | 5 | min.
[22 empty] | winter (1) or summer (2) week? | 1 | --
| gas | electric & heat |  | numbers of … | [17 empty] | wind profile multiplier | 1 | --
| node# | bus# | houses | commercials | PV | [16 empty] | PV profile multiplier | 1 | --
Zone C | 5 | 2 | 48 | 1 | 5 |  |  |  | Molar mass(kg/kmol) | 16.043 | 30.07 | 44.097 | 58.123 | 44.01 | 28.0135 | 2.0159 | [5 empty] | heat load multiplier | 1 | --
Zone B | 6 | 3 | 19 | 11 | 0 |  |  |  | sqrt(b_i)@STP | 0.049 | 0.1 | 0.1453 | 0.2069 | 0.0819 | 0.0224 | -0.004 | [5 empty] | electric load multiplier | 1 | --
Zone A | 7 | 4 | 23 | 0 | 0 |  |  |  | Dynamic viscosity (Pa.s) | 1.03e-05 | 8.5e-06 | 7.95e-06 | 8.1e-06 | 1.37e-05 | 1.7e-05 | 8.42e-06 | [5 empty] | electric heater efficiency | 95 | %
Zone D | 4 | 5 | 23 | 2 | 25 |  |  |  | Gross Calorific value (MJ/m^3) | 39.84 | 69.79 | 99.22 | 128.66 | 0 | 0 | 12.788 | [5 empty] | R_air | 287.058 | J/(kg.K)
Zone F | 3 | 6 | 15 | 23 | 0 | [16 empty] | T_system | 288.15 | K
Zone E | 2 | 7 | 26 | 19 | 0 | [16 empty] | P_atm | 1 | bar-gauge
[22 empty] | Air molar mass | 28.962 | kg/kmol
[7 empty] | Electricity network - Bus Data | [14 empty] | Air density@STP | 1.2929 | kg/m^3
| bus# | type | Pd (MW) | Qd (MVAr) | Gs | Bs | area | Vm | Va | baseKV | zone | Vmax | Vmin | [8 empty] | Air Compressibility @STP | 0.99941 | --
| 1 | 3 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | g(earth gravity) | 9.8066 | N/kg
| 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | Acceptable error of gas flow analysis | 1e-08 | --
| 3 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | sample gas boiler efficiency | 95 | %
| 4 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | Gas mix. Code | 1 | --
| 5 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | Ref. Pressure | 1 | gauge-bar
| 6 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | Scenario 3a Low heat pump penetration level | 20 | %
| 7 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 11 | 1 | 1.1 | 0.9 | [8 empty] | Scenario 3b High heat pump penetration level | 80 | %
[22 empty] | Scenario 3 heat pump COP | 4 | --
[22 empty] | DHN Source Node# | 1 | --
[11 empty] | Electricity network - Generator data | [10 empty] | T_Source_start | 80 | `C
| bus # | Pg (MW) | Qg (MVAr) | Qmax | Qmin | Vg | mBase | status | Pmax | Pmin | Pc1 | Pc2 | Qc1min | Qc1max | Qc2min | Qc2max | ramp_agc | ramp_10 | ramp_30 | ramp_q | apf | T_return from loads | 60 | `C
| 1 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T_ambient | 10 | `C
| 2 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Acc. Error (DHN) | 0.001 | --
| 3 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | c_p | 4182 | J/kg.K
| 4 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | water density | 1000 | kg/m^3
| 5 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | water kinematic viscosity | 3.65e-07 | m^2/s
| 6 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | delta_T_s_guess | 5 | `C
| 7 | 0 | 0 | 100 | -100 | 1 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Loops (Nodes#) | 0 | --
[22 empty] | geothermal pump connected to electric bus # | 1 | --
[8 empty] | Electricity network - Branch data | [13 empty] | DHN circulation pump / source electric heater / CHP connected to electric bus # | 1 | --
| From | To | r (p.u.) | x (p.u.) | b (p.u.) | rateA | rateB | rateC | ratio | angle | status | angmin | angmax | [8 empty] | geothermal water supply temp | 80 | 'C
1 | 1 | 2 | 9.7793 | 1.6966 | 2.3622e-08 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | geothermal water return temp | 75 | 'C
2 | 2 | 3 | 7.7003 | 1.3359 | 1.86e-08 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | geothermal water flow rate | 0.186 | m^3/s
3 | 3 | 4 | 3.1571 | 0.54767 | 7.626e-09 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | geothermal pump demand | 13.6 | kW
4 | 1 | 5 | 8.8553 | 1.5363 | 2.139e-08 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | geothermal pump efficiency | 67 | %
5 | 1 | 6 | 3.8501 | 0.66767 | 9.3e-09 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | DHN circulation pump efficiency | 90 | %
6 | 6 | 7 | 0.924 | 0.16033 | 2.232e-09 | 250 | 250 | 250 | 0 | 0 | 1 | -360 | 360 | [8 empty] | DHN circulation pump pressure head multiplier | 1.5 | --
[22 empty] | Scenario 4a&4b electric boiler efficiency | 95 | %
[22 empty] | DHN flow analysis max iteration | 1000 | --
|  |  |  | Heat network - Branch Data | [17 empty] | DHN flow analysis - delta T guess | 5 | 'C
| Branch# | From | To | Length(m) | Dia(m) | Roughness(mm) | U (W/m.K) | [14 empty] | CHP electric efficiency | 35 | %
| 1 | 1 | 2 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | CHP thermal efficiency | 40 | %
| 2 | 2 | 3 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | Sc 4b: heat output of geothermal heat pump | 1.02 | MW
| 3 | 3 | 4 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | Sc 4b: CoP of geothermal heat pump | 4 | --
| 4 | 1 | 5 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | Sc4b: electric demand of geothermal water pump | 4.8 | kW
| 5 | 1 | 6 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | Sc 4b: geo water pump and HP connected to electric bus # | 1 | --
| 6 | 6 | 7 | 50 | 0.1 | 0.4 | 0.05 | [14 empty] | Sc4b:geothermal water pump efficiency | 67 | %